## Reporting
Network Company Loss Factor Reporting
Distributor: | ABC Network Company
Network Study Area: | NSA1
Study Period End: | 2011-03-31
GXP: | GXP name
Application Date: | 2013-04-01
[6 empty] | Loss information for loads | [5 empty] | Loss information for generation |  |  | Consumption |  | Generation |  | Difference
Distributor's participant identifier | Network segment | Explanation of network segment | Loss category code published on registry | Consumption reconciliation loss factor | Generation reconciliation loss factor | Technical losses (kWh) | Reconciliation losses (kWh) | Non-technical losses (kWh) | Technical loss ratio | Reconciliation loss ratio | Non-technical loss ratio | Technical/reconciliation losses (kWh) | Technical/reconciliation loss ratio | Cross Checks | Raw (kWh) | Reconciled (kWh) | Raw (kWh) | Reconciled (kWh) | Reconciled (kWh)
XPOW | A | Subtransmission | - | - | - | 0 | 0 | 0 | - | - | - | 0 | - | OK | 0 | 0 | 0 | 0 | 0
XPOW | B | Zone substation transformers | - | - | - | 0 | 0 | 0 | - | - | - | 0 | - |  | 0 | 0 | 0 | 0 | 0
XPOW | C | HV network | HVNONSS | 1.0736 | 1.0647 | 183043.6622 | 208170.7892 | 25127.127 | 6.077% | 6.854% | 0.777% | -129.3972 | 6.077% |  | 2829174 | 3037344.7892 | -2000 | -2129.3972 | 3035215.392
XPOW | D | Distribution transformers | - | - | - | 0 | 0 | 0 | - | - | - | 0 | - |  | 0 | 0 | 0 | 0 | 0
XPOW | E | LV network | - | - | - | 0 | 0 | 0 | - | - | - | 0 | - |  | 0 | 0 | 0 | 0 | 0
XPOW | F | Customer service lines | LVNONSS | 1.1082 | 1.0993 | 3130521.8142 | 3410523.9867 | 280002.1725 | 9.033% | 9.762% | 0.7291% | -992.9754 | 9.033% |  | 31526679 | 34937202.9867 | -10000 | -10992.9754 | 34926210.0113
XPOW | A | Fred's Place | HVSS1 | 1.0326 |  | 9000 | 12376.1248 | 3376.1248 | 2.314% | 3.154% | 0.8405% |  |  | OK | 380000 | 392376.1248 |  |  | 392376.1248
XPOW | A | Bill's Place | HVSS2 | 1.0352 |  | 6000 | 8025.6749 | 2025.6749 | 2.564% | 3.4% | 0.8362% |  |  |  | 228000 | 236025.6749 |  |  | 236025.6749
XPOW | C | Jane's Place | HVSS3 | 1.042 |  | 22000 | 27908.2184 | 5908.2184 | 3.202% | 4.028% | 0.8254% |  |  |  | 665000 | 692908.2184 |  |  | 692908.2184
XPOW | C | John's Place | HVSS4 | 1.0536 |  | 17000 | 20376.1248 | 3376.1248 | 4.282% | 5.089% | 0.8071% |  |  |  | 380000 | 400376.1248 |  |  | 400376.1248
XPOW | D | Bob's Place | HVSS5 | 1.0589 |  | 5000 | 5888.4539 | 888.4539 | 4.762% | 5.561% | 0.7991% |  |  |  | 100000 | 105888.4539 |  |  | 105888.4539
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
| - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
| - | - | - | - |  | 0 | 0 | 0 | - | - | - |  |  |  | 0 | 0 |  |  | 0
XPOW | A | Sunny | SUNY1 |  | 1.0415 | [6 empty] | -17000 | 3.981% | OK |  |  | -410000 | -427000 | -427000
XPOW | B | Windy | WIND1 |  | 0.95 | [6 empty] | 78000 | -5.263% |  |  |  | -1560000 | -1482000 | -1482000
XPOW | C | Watery | WATY1 |  | 1.065 | [6 empty] | -520000 | 6.103% |  |  |  | -8000000 | -8520000 | -8520000
XPOW | - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
XPOW | D | Gassy | GASY1 |  | 0.97143 | [6 empty] | 40000 | -2.941% |  |  |  | -1400000 | -1360000 | -1360000
XPOW | - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
XPOW | - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
XPOW | - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
| - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
| - | - | - |  | - | [6 empty] | 0 | - |  |  |  | 0 | 0 | 0
[16 empty] | 39802122.3727 |  | -11802122.3727 | 28000000
Notes: 1) Insert new rows above the orange lines
2) If site specific loss factors have been determined for both the load and generation for a loss category code, it will need to appear twice in this table, once in the site specific loads and once in the site specific generators | [17 empty] | GXP Net Input (kWh) | 28000000
[18 empty] | Overall sheet balance | OK

## Base Data
Loss Factor Calculation
Overall Data |  |  |  |  | Notes
Description
Distributor's Name: | ABC Network Company
Participant Identifier: | XPOW
Network Study Area: | NSA1
Study Period Start: | 2010-04-01
Study Period End: | 2011-03-31
Application Date: | 2013-04-01
GXP Total
| Name | Connected at Network Level | Total
GXP Input (kWh) | GXP name | A | 29000000
GXP Export (kWh) | GXP name | A | -1000000
GXP Net Input (kWh) |  |  | 28000000
Calculated overall Technical Loss at Level (kWh)
| Network Level | Technical Loss at Level (kWh)
| A | 1040000
| B | 200000
| C | 600000
| D | 750000
| E | 267893.0667 |  |  | refer to LV network losses sheet
| F | 94550.037 |  |  | refer to LV network losses sheet
| Total | 2952443.1037
General (ie: Non SS) Consumption and Generation at Level (kWh)
Network Level | General (Non SS) Load at Level (kWh) | General (Non SS) Generation at Level (kWh) | General Load - Generation at Level (kWh)
A | 0 | 0 | 0
B | 0 | 0 | 0
C | 2829174 | -2000 | 2827174
D | 0 | 0 | 0
E | 0 | 0 | 0
F | 31526679 | -10000 | 31516679
| 34355853 | -12000 | 34343853
Total loads less generation at each level
Network Level | General Load - Generation at Level (kWh) | SS Load at Level (kWh) | SS Generation at Level (kWh) | Total Loads Less Generation at Level (kWh)
A | 0 | 608000 | -410000 | 198000
B | 0 | 0 | -1560000 | -1560000
C | 2827174 | 1045000 | -8000000 | -4127826
D | 0 | 100000 | -1400000 | -1300000
E | 0 | 0 | 0 | 0
F | 31516679 | 0 | 0 | 31516679
| 34343853 | 1753000 | -11370000 | 24726853
Overall Reconciliation Loss
| GXP Net Input | 28000000
| Total loads less generation | 24726853
| Reconciliation Loss | 3273147
Non-technical Loss allocation to Loads
| Allocate Non-technical Loss in proportion to 'Technical Loss' or 'Consumption' | Consumption
| Non-Technical Loss (kWh) | 320703.8963
| % Split to Site Specific | 4.856%

## Site Specific Load
Site Specific Loads
Totals |  | Site Specific Consumption |  |  | Incremental technical losses | [8 empty] | Non technical loss allocation
[5 empty] | SS Loss (kWh) | SS Loss allocated to level A | SS Loss allocated to level B | SS Loss allocated to level C | SS Loss allocated to level D | SS Loss allocated to level E | SS Loss allocated to level F |  |  | Non-technical losses (no profiling) (kWh) | Non-technical allocation based on |  | Cross Check
|  | 1753000 |  |  | 59000 | 41000 | 11000 | 5000 | 2000 | 0 | 0 |  |  | 15574.5968 | Consumption |  | OK
Site | Network Connection Level | Consumption | Incremental or pro-rated | Loss category code published on registry | SS Loss (kWh) | SS Loss allocated to level A | SS Loss allocated to level B | SS Loss allocated to level C | SS Loss allocated to level D | SS Loss allocated to level E | SS Loss allocated to level F | SS Load, Technical Loss Ratio (%) | SS Load, Technical Loss Factor (pu) | Allocation of Non-technical losses by Consumption | Reconciliation Loss Ratio | Reconciliation Loss Factor | Cross Check
Fred's Place | A | 380000 | I | HVSS1 | 9000 | 9000 | [5 empty] | 2.314% | 1.0237 | 3376.1248 | 3.154% | 1.0326 | 392376.1248
Bill's Place | A | 228000 | I | HVSS2 | 6000 | 6000 | [5 empty] | 2.564% | 1.0263 | 2025.6749 | 3.4% | 1.0352 | 236025.6749
Jane's Place | C | 665000 | P | HVSS3 | 22000 | 15000 | 5000 | 2000 |  |  |  | 3.202% | 1.0331 | 5908.2184 | 4.028% | 1.042 | 692908.2184
John's Place | C | 380000 | I | HVSS4 | 17000 | 10000 | 5000 | 2000 |  |  |  | 4.282% | 1.0447 | 3376.1248 | 5.089% | 1.0536 | 400376.1248
Bob's Place | D | 100000 | P | HVSS5 | 5000 | 1000 | 1000 | 1000 | 2000 |  |  | 4.762% | 1.05 | 888.4539 | 5.561% | 1.0589 | 105888.4539
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
- | - | 0 |  |  | 0 | [6 empty] | - | - | 0 | - | - | 0
Notes: 1) Insert new rows above the orange line

## Site Specific Gen
Site Specific Generation
Totals |  |  | Injection | Incremental technical losses
|  |  |  | SS Loss (kWh) | Generation Loss allocated to level A | Generation Loss allocated to level B | Generation Loss allocated to level C | Generation Loss allocated to level D | Generation Loss allocated to level E | Generation Loss allocated to level F |  |  | Cross Check
|  |  | -11370000 | -419000 | -42000 | -87000 | -310000 | 20000 | 0 | 0 |  |  | OK
Generator | Connection level | Loss category code published on registry | Injection (kWh) | Network Loss Change (kWh) (+ = loss increase, - = loss reduction) | Generation Loss allocated to level A | Generation Loss allocated to level B | Generation Loss allocated to level C | Generation Loss allocated to level D | Generation Loss allocated to level E | Generation Loss allocated to level F | SS Generation, Technical Loss Ratio (%) | SS Generation, Technical Loss Factor | SS Generation, Energy Injected (cross check)
Sunny | A | SUNY1 | -410000 | -17000 | -17000 | [5 empty] | 3.981% | 1.0415 | -427000
Windy | B | WIND1 | -1560000 | 78000 | 70000 | 8000 |  |  |  |  | -5.263% | 0.95 | -1482000
Watery | C | WATY1 | -8000000 | -520000 | -100000 | -100000 | -320000 |  |  |  | 6.103% | 1.065 | -8520000
- | - |  | 0 | 0 | [6 empty] | - | - | 0
Gassy | D | GASY1 | -1400000 | 40000 | 5000 | 5000 | 10000 | 20000 |  |  | -2.941% | 0.97143 | -1360000
- | - |  | 0 | 0 | [6 empty] | - | - | 0
- | - |  | 0 | 0 | [6 empty] | - | - | 0
- | - |  | 0 | 0 | [6 empty] | - | - | 0
- | - |  | 0 | 0 | [6 empty] | - | - | 0
- | - |  | 0 | 0 | [6 empty] | - | - | 0
Notes: 1) Insert new rows above the orange line
2) No non-technical losses are allocated to generation. Therefore, technical losses = reconciliation losses.

## General Loads and Generation
General Loads and Generation
1. Determine Losses that need to be attributed to non-specific loads ie general loads
|  |  | Losses on A | Losses on B | Losses on C | Losses on D | Losses on E | Losses on F | Total
|  | Total technical losses | 1040000 | 200000 | 600000 | 750000 | 267893.0667 | 94550.037 | 2952443.1037
|  | Tech Loss allocated to site specific loads | 41000 | 11000 | 5000 | 2000 | 0 | 0 | 59000
|  | Tech loss allocated to site specific generation (negative = loss reduction) | -42000 | -87000 | -310000 | 20000 | 0 | 0 | -419000
|  | Technical losses to allocate to general loads and generation | 1041000 | 276000 | 905000 | 728000 | 267893.0667 | 94550.037 | 3312443.1037
Non technical loss allocation
[13 empty] | Non-technical loss (no profiling) (kWh) | Non-technical allocation based on |  | Cross Check
[13 empty] | 305129.2995 | Consumption |  | OK
2. Attribute technical loss and non-technical loss to general loads
Network level | General (Non SS) Load at Level (kWh) | Loss category code published on registry | Allocation of technical loss to loads | [5 empty] | Total kWh Losses | General Loads Technical Loss Ratio | General Loads Technical Loss Factor | Cross Check | Allocation of Non-technical losses by Consumption | Reconciliation Loss Ratio | Reconciliation Loss Factor | Cross Check
|  |  | kWh Losses on A | kWh Losses on B | kWh Losses on C | kWh Losses on D | kWh Losses on E | kWh Losses on F
A | 0 |  | 0 | [5 empty] | 0 | - | - | 0 | 0 | - | - | 0
B | 0 |  | 0 | 0 |  |  |  |  | 0 | - | - | 0 | 0 | - | - | 0
C | 2829174 | HVNONSS | 85755.3791 | 22736.2965 | 74551.9866 |  |  |  | 183043.6622 | 6.077% | 1.0647 | 3012217.6622 | 25127.127 | 6.854% | 1.0736 | 3037344.7892
D | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | - | - | 0 | 0 | - | - | 0
E | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | - | - | 0 | 0 | - | - | 0
F | 31526679 | LVNONSS | 955608.3541 | 253360.14 | 830764.2272 | 728230.9888 | 267978.0671 | 94580.037 | 3130521.8142 | 9.033% | 1.0993 | 34657200.8142 | 280002.1725 | 9.762% | 1.1082 | 34937202.9867
Totals | 34355853 |  | 1041363.7332 | 276096.4365 | 905316.2138 | 728230.9888 | 267978.0671 | 94580.037 | 3313565.4764 | 8.796% | 1.0964 | 37669418.4764 | 305129.2995 | 9.529% | 1.1053 | 37974547.7759
3. Attribute technical loss to general (non SS) generation
Network level | General (Non SS) Generation at Level (kWh) | Loss category code published on registry | Allocation of technical loss to generators | [5 empty] | Total kWh Losses | General Generation Technical Loss Ratio | General Generation Technical Loss Factor | Cross Check
|  |  | kWh Losses on A | kWh Losses on B | kWh Losses on C | kWh Losses on D | kWh Losses on E | kWh Losses on F
A | 0 |  | 0 | [5 empty] | 0 | - | - | 0
B | 0 |  | 0 | 0 |  |  |  |  | 0 | - | - | 0
C | -2000 | HVNONSS | -60.6222 | -16.0727 | -52.7023 |  |  |  | -129.3972 | 6.077% | 1.0647 | -2129.3972
D | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | - | - | 0
E | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | - | - | 0
F | -10000 | LVNONSS | -303.111 | -80.3637 | -263.5115 | -230.9888 | -85.0004 | -30 | -992.9754 | 9.033% | 1.0993 | -10992.9754
Totals | -12000 |  | -363.7332 | -96.4365 | -316.2138 | -230.9888 | -85.0004 | -30 | -1122.3727 | 8.553% | 1.0935 | -13122.3727
Network level | General Load - Generation at Level (kWh)
A | 0
B | 0
C | 2827174
D | 0
E | 0
F | 31516679
Notes: 1) Ensure that the loss category codes entered in cells C15:C20 match those in cells C26:C31.

## LV network losses
LV Technical Network Loss Calculations
LV Mains Loss | 0.3%
Consumption at F (kWh) | 31516679
Hours in study period | 8760
Multiplier to scale for actual LV loads | 0.9857
Calculated losses kWh at E: | 267893.0667
Calculated losses kWh at F: | 94550.037
Totals |  |  |  |  | 3650 | 3597.7944 | 30.5814
Refer to Appendix E Hyland McQueen
LV Network Subtype | LV Network Transformer kVA | Number of Transformers | Percentage kWh Loss Ratio | Mean Load on Transformer | Estimated Mean Load kW | Scaled Estimated Mean Load kW | Estimated Mean Loss kW
CBD | 1000 | 1 | 0.61% | 22% | 220 | 216.8534 | 1.3228
CBD | 750 | 1 | 0.61% | 22% | 165 | 162.64 | 0.9921
CBD | 500 | 1 | 0.61% | 22% | 110 | 108.4267 | 0.6614
High Density | 500 | 3 | 0.34% | 32% | 480 | 473.1346 | 1.6087
High Density | 300 | 3 | 0.34% | 32% | 288 | 283.8808 | 0.96519
High Density | 200 | 3 | 0.34% | 32% | 192 | 189.2538 | 0.64346
Medium Density | 500 | 2 | 1.22% | 44% | 440 | 433.7067 | 5.2912
Medium Density | 400 | 5 | 1.22% | 44% | 880 | 867.4134 | 10.5824
Medium Density | 300 | 2 | 1.22% | 44% | 264 | 260.224 | 3.1747
Medium Density | 200 | 4 | 1.22% | 44% | 352 | 346.9654 | 4.233
Low Density | 100 | 2 | 0.51% | 47% | 94 | 92.6555 | 0.47254
Low Density | 50 | 3 | 0.51% | 47% | 70.5 | 69.4916 | 0.35441
Rural | 30 | 10 | 0.3% | 9% | 27 | 26.6138 | 0.079841
Rural | 15 | 50 | 0.3% | 9% | 67.5 | 66.5346 | 0.1996

## Appendix E Standing Data
LV Lookup table - Refer to Appendix E of Guidelines (Hyland McQueen report)
Network | Percentage kWh loss of the LV mains distribution [conductor loss /(conductor loss + consumption)] | Mean load on transformer (percentage of Tx. rating) | Maximum load on transformer (percentage of Tx. rating) | Voltage quality (on last node) /b
CBD | 0.61% | 22% | 76% | 98%
High Density | 0.34% | 32% | 85% | 99%
Medium Density | 1.22% | 44% | 94% | 96%
Low Density | 0.51% | 47% | 105% | 98%
Rural | 0.3% | 9% | 63% | 100%