## Instructions
Instructions for Population of the Data Sheet
Step | Description
1 | Paste the MW load profile for each required GXP area by halfhour into column C and D determined from GXP input after adding embedded generation and deducting site specific load.
2 | The MW load profile is intended to represent the profile of the general HV and LV metered load
3 | Adjust data in column C and D for any daylight saving halfhours
4 | Check named Sort Area is correct - especially for leap years
5 | Obtain No Load Loss in MW from techical loss study for zone sub and distribution transformer data and insert in Cell G11
6 | Insert Target Technical Loss in Cell E11
7 | Insert an Estimated Load Loss (MW) in Cell E13 and adjust it so that the Check Technical Loss in Cell E12 matches E11
8 | Insert Target Reconciliation Loss in Cell E6
9 | Insert an Estimated Non Technical Loss (MW) in Cell H11 and adjust it so that the Check Reconciliation Loss in Cell E7 matches E6
10 | Insert Target Loss Ratio for LV and HV Metered connections in cells C6 and D6 respectively
11 | Adjust the scaler % in cells C8 and D8 so that the respective Reconciliation Loss ratios in row 7 match those in row 6
12 | Check overall results for logical results
13 | Check Worksheet for Loss information by calendar month
14 | Check Worksheet for Loss information by summer, winter, day, night periods for reasonableness
Notes
1 | From the Technical Loss calculation exercise there will be an uncertainty associated with this calculation - estimated to be up to 1%
2 | Therefore only if the Reconciliation Loss is greater than the Technical Loss plus estimated uncertainty, should a Non-technical component be added.
3 | No load loss may result in a high % loss factor (summer night) for say an embedded residential subdivision where there are few connections relative to design.

## Data
Companion Workbook for calculation of Reconciliation Loss and Loss Factors by time periods
Relevant Network Area |  | Insert Name of Network Area
|  | LV | HV | Overall
Target Reconciliation Loss Ratio |  | 9.81% | 6.62% | 9.55%
Check Reconcilaition Loss Ratio |  | 9.808% | 6.624% | 9.546%
Scaler for LV & HV Reconciliation Loss |  | 106.4% | 71.9%
|  |  |  | Overall |  | No Loss Loss MW | Estimated Non Technical Loss & Uncertainty MW - see note 2
Target Technical Loss Ratio |  |  |  | 8.8% |  | 0.76558 | 0.48
Check Technical Loss Ratio |  |  |  | 8.802%
MW Load Loss at Max Load for Target Techical Loss |  |  |  | 7.252
| Summary | GXP A Inputs MW | GXP B Inputs MW | Total Load MW | Load Loss MW | No Load Loss MW | Estimated Non-Technical Loss MW | Total Reconciliation Loss MW | Total Reconciliation Loss Ratio % | Total LV Reconciliation Loss Ratio % | Total HV Reconciliation Loss Ratio % | Total Over All Loss Factor | Total LV Loss Factor | Total HV Loss Factor
| Max MW | 48.8311 | 18.1559 | 64.5671 | 7.252 | 0.76558 | 0.48 | 8.4976 |  |  |  | 1.1516 | 1.1628 | 1.1045
| Min MW | 10.4959 | 2.8373 | 15.2328 | 0.40364 | 0.76558 | 0.11324 | 1.2825 |  |  |  | 1.0875 | 1.0936 | 1.0614
| Energy MWh | 218641.68 | 84993.0138 | 303634.6938 | 20020.8882 | 6706.4633 | 2257.2574 | 28984.6089 | 9.546% | 9.808% | 6.624% | 1.1015 | 1.1087 | 1.0709
| Load Factor | 0.51113 | 0.53439 | 0.53683
| Loss at Max Load |  |  |  | 11.23% | 1.186% | 0.7434%
| Loss at Min Load |  |  |  | 2.65% | 5.026% | 0.7434%
| Overall Loss |  |  |  | 6.594% | 2.209% | 0.7434% | 9.546%
| Technical Loss |  |  |  |  | 8.802%
Time | Half Hr | GXP A Inputs MW | GXP B Inputs MW | Total Load MW | Load Loss MW | No Load Loss MW | Estimated Non-Technical Loss MW | Total Reconciliation Loss MW | Total Reconciliation Loss Ratio % | Total LV Reconciliation Loss Ratio % | Total HV Reconciliation Loss Ratio % | Total Over All Loss Factor | Total LV Loss Factor | Total HV Loss Factor
2010-04-01 | 1 | 15.5565 | 7.0293 | 22.5857 | 0.88737 | 0.76558 | 0.16791 | 1.8209 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-04-01 | 2 | 14.7932 | 6.8286 | 21.6218 | 0.81324 | 0.76558 | 0.16074 | 1.7396 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-01 | 3 | 13.9316 | 6.5411 | 20.4727 | 0.7291 | 0.76558 | 0.1522 | 1.6469 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-01 | 4 | 13.5578 | 6.2399 | 19.7977 | 0.68181 | 0.76558 | 0.14718 | 1.5946 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-01 | 5 | 13.3282 | 6.2996 | 19.6278 | 0.67016 | 0.76558 | 0.14592 | 1.5817 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-01 | 6 | 12.9974 | 6.1163 | 19.1137 | 0.63551 | 0.76558 | 0.14209 | 1.5432 | 8.074% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-04-01 | 7 | 12.7825 | 6.1096 | 18.8921 | 0.62086 | 0.76558 | 0.14045 | 1.5269 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-01 | 8 | 12.6677 | 6.1072 | 18.7749 | 0.61319 | 0.76558 | 0.13958 | 1.5183 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2010-04-01 | 9 | 13.0833 | 6.0648 | 19.1481 | 0.6378 | 0.76558 | 0.14235 | 1.5457 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-04-01 | 10 | 13.4144 | 6.1973 | 19.6117 | 0.66906 | 0.76558 | 0.1458 | 1.5804 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-01 | 11 | 13.9611 | 6.3377 | 20.2988 | 0.71676 | 0.76558 | 0.1509 | 1.6332 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-01 | 12 | 14.3223 | 6.6917 | 21.0139 | 0.76816 | 0.76558 | 0.15622 | 1.69 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-01 | 13 | 15.7314 | 8.3831 | 24.1145 | 1.0116 | 0.76558 | 0.17927 | 1.9564 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-04-01 | 14 | 18.5903 | 10.2037 | 28.7941 | 1.4422 | 0.76558 | 0.21406 | 2.4219 | 8.411% | 8.949% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-04-01 | 15 | 23.0441 | 11.5594 | 34.6035 | 2.0829 | 0.76558 | 0.25725 | 3.1058 | 8.975% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-04-01 | 16 | 26.4901 | 12.4574 | 38.9475 | 2.6387 | 0.76558 | 0.28954 | 3.6938 | 9.484% | 10.09% | 6.819% | 1.1048 | 1.1122 | 1.0732
2010-04-01 | 17 | 28.1851 | 12.7613 | 40.9463 | 2.9165 | 0.76558 | 0.3044 | 3.9865 | 9.736% | 10.36% | 7% | 1.1079 | 1.1156 | 1.0753
2010-04-01 | 18 | 28.5578 | 12.7627 | 41.3205 | 2.9701 | 0.76558 | 0.30718 | 4.0428 | 9.784% | 10.41% | 7.035% | 1.1085 | 1.1162 | 1.0757
2010-04-01 | 19 | 28.458 | 12.6462 | 41.1042 | 2.9391 | 0.76558 | 0.30557 | 4.0102 | 9.756% | 10.38% | 7.015% | 1.1081 | 1.1158 | 1.0754
2010-04-01 | 20 | 27.435 | 12.2791 | 39.7142 | 2.7436 | 0.76558 | 0.29524 | 3.8044 | 9.58% | 10.19% | 6.888% | 1.1059 | 1.1135 | 1.074
2010-04-01 | 21 | 26.6633 | 11.8665 | 38.5298 | 2.5824 | 0.76558 | 0.28644 | 3.6344 | 9.433% | 10.04% | 6.782% | 1.1042 | 1.1116 | 1.0728
2010-04-01 | 22 | 25.6008 | 11.7331 | 37.3339 | 2.4246 | 0.76558 | 0.27754 | 3.4677 | 9.288% | 9.883% | 6.678% | 1.1024 | 1.1097 | 1.0716
2010-04-01 | 23 | 24.3512 | 11.172 | 35.5232 | 2.1951 | 0.76558 | 0.26408 | 3.2248 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-04-01 | 24 | 23.417 | 10.7438 | 34.1608 | 2.03 | 0.76558 | 0.25396 | 3.0495 | 8.927% | 9.498% | 6.418% | 1.098 | 1.105 | 1.0686
2010-04-01 | 25 | 22.9136 | 10.5456 | 33.4591 | 1.9474 | 0.76558 | 0.24874 | 2.9618 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2010-04-01 | 26 | 21.8941 | 10.1831 | 32.0772 | 1.7899 | 0.76558 | 0.23847 | 2.7939 | 8.71% | 9.267% | 6.263% | 1.0954 | 1.1021 | 1.0668
2010-04-01 | 27 | 21.5482 | 9.7086 | 31.2568 | 1.6995 | 0.76558 | 0.23237 | 2.6975 | 8.63% | 9.182% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-04-01 | 28 | 21.0163 | 9.2723 | 30.2886 | 1.5959 | 0.76558 | 0.22517 | 2.5866 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-04-01 | 29 | 20.5146 | 9.2057 | 29.7204 | 1.5365 | 0.76558 | 0.22094 | 2.5231 | 8.489% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-04-01 | 30 | 20.1988 | 9.1247 | 29.3235 | 1.4958 | 0.76558 | 0.21799 | 2.4794 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2010-04-01 | 31 | 20.2557 | 9.015 | 29.2707 | 1.4904 | 0.76558 | 0.2176 | 2.4736 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-04-01 | 32 | 20.1814 | 9.3045 | 29.4858 | 1.5124 | 0.76558 | 0.2192 | 2.4972 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-04-01 | 33 | 20.5124 | 9.5547 | 30.0671 | 1.5726 | 0.76558 | 0.22352 | 2.5617 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-04-01 | 34 | 20.8425 | 9.6632 | 30.5057 | 1.6188 | 0.76558 | 0.22678 | 2.6112 | 8.56% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-04-01 | 35 | 21.4454 | 9.7477 | 31.1931 | 1.6926 | 0.76558 | 0.23189 | 2.6901 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-04-01 | 36 | 22.2351 | 10.4724 | 32.7075 | 1.8609 | 0.76558 | 0.24315 | 2.8697 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-04-01 | 37 | 23.3949 | 10.6251 | 34.0199 | 2.0133 | 0.76558 | 0.25291 | 3.0318 | 8.912% | 9.482% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-04-01 | 38 | 24.3661 | 10.5379 | 34.904 | 2.1193 | 0.76558 | 0.25948 | 3.1443 | 9.008% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2010-04-01 | 39 | 24.8407 | 10.6761 | 35.5168 | 2.1943 | 0.76558 | 0.26404 | 3.2239 | 9.077% | 9.658% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-04-01 | 40 | 25.9758 | 11.2827 | 37.2585 | 2.4148 | 0.76558 | 0.27698 | 3.4574 | 9.279% | 9.873% | 6.672% | 1.1023 | 1.1095 | 1.0715
2010-04-01 | 41 | 27.2078 | 11.3009 | 38.5087 | 2.5796 | 0.76558 | 0.28628 | 3.6315 | 9.43% | 10.03% | 6.78% | 1.1041 | 1.1115 | 1.0727
2010-04-01 | 42 | 26.662 | 11.0372 | 37.6992 | 2.4723 | 0.76558 | 0.28026 | 3.5181 | 9.332% | 9.929% | 6.71% | 1.1029 | 1.1102 | 1.0719
2010-04-01 | 43 | 25.2239 | 10.3443 | 35.5682 | 2.2007 | 0.76558 | 0.26442 | 3.2307 | 9.083% | 9.664% | 6.531% | 1.0999 | 1.107 | 1.0699
2010-04-01 | 44 | 24.1349 | 9.7559 | 33.8908 | 1.998 | 0.76558 | 0.25195 | 3.0155 | 8.898% | 9.467% | 6.398% | 1.0977 | 1.1046 | 1.0683
2010-04-01 | 45 | 22.2083 | 8.8337 | 31.042 | 1.6762 | 0.76558 | 0.23077 | 2.6726 | 8.61% | 9.161% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-04-01 | 46 | 19.8372 | 7.9577 | 27.7949 | 1.3439 | 0.76558 | 0.20663 | 2.3161 | 8.333% | 8.866% | 5.991% | 1.0909 | 1.0973 | 1.0637
2010-04-01 | 47 | 18.3308 | 7.5423 | 25.8731 | 1.1645 | 0.76558 | 0.19234 | 2.1224 | 8.203% | 8.728% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-04-01 | 48 | 17.4843 | 7.7167 | 25.201 | 1.1048 | 0.76558 | 0.18735 | 2.0577 | 8.165% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-04-02 | 1 | 15.8202 | 7.0836 | 22.9039 | 0.91254 | 0.76558 | 0.17027 | 1.8484 | 8.07% | 8.587% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-02 | 2 | 15.4163 | 6.7986 | 22.2149 | 0.85847 | 0.76558 | 0.16515 | 1.7892 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-02 | 3 | 14.769 | 6.394 | 21.163 | 0.7791 | 0.76558 | 0.15733 | 1.702 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 4 | 14.4094 | 6.2484 | 20.6578 | 0.74234 | 0.76558 | 0.15357 | 1.6615 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 5 | 13.9061 | 6.2834 | 20.1895 | 0.70906 | 0.76558 | 0.15009 | 1.6247 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 6 | 13.3332 | 6.2832 | 19.6164 | 0.66938 | 0.76558 | 0.14583 | 1.5808 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-02 | 7 | 13.0858 | 6.2625 | 19.3483 | 0.65121 | 0.76558 | 0.14384 | 1.5606 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-02 | 8 | 13.189 | 6.3193 | 19.5083 | 0.66202 | 0.76558 | 0.14503 | 1.5726 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-04-02 | 9 | 13.8919 | 6.5108 | 20.4027 | 0.72412 | 0.76558 | 0.15168 | 1.6414 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 10 | 13.9652 | 6.6589 | 20.6242 | 0.73992 | 0.76558 | 0.15332 | 1.6588 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 11 | 14.0083 | 6.7813 | 20.7896 | 0.75184 | 0.76558 | 0.15455 | 1.672 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 12 | 14.6272 | 7.108 | 21.7352 | 0.8218 | 0.76558 | 0.16158 | 1.749 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-02 | 13 | 16.6324 | 7.9248 | 24.5572 | 1.049 | 0.76558 | 0.18256 | 1.9972 | 8.133% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-04-02 | 14 | 19.0296 | 9.5014 | 28.5311 | 1.416 | 0.76558 | 0.2121 | 2.3937 | 8.39% | 8.927% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-04-02 | 15 | 23.4531 | 11.7812 | 35.2343 | 2.1596 | 0.76558 | 0.26194 | 3.1871 | 9.045% | 9.624% | 6.504% | 1.0994 | 1.1065 | 1.0696
2010-04-02 | 16 | 27.0964 | 13.4916 | 40.588 | 2.8657 | 0.76558 | 0.30174 | 3.933 | 9.69% | 10.31% | 6.967% | 1.1073 | 1.115 | 1.0749
2010-04-02 | 17 | 28.9216 | 14.2877 | 43.2093 | 3.2478 | 0.76558 | 0.32122 | 4.3346 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-04-02 | 18 | 29.1521 | 13.9871 | 43.1391 | 3.2373 | 0.76558 | 0.3207 | 4.3235 | 10.02% | 10.66% | 7.206% | 1.1114 | 1.1194 | 1.0777
2010-04-02 | 19 | 27.1862 | 12.6416 | 39.8278 | 2.7594 | 0.76558 | 0.29608 | 3.821 | 9.594% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-04-02 | 20 | 26.18 | 11.5628 | 37.7427 | 2.478 | 0.76558 | 0.28058 | 3.5242 | 9.337% | 9.935% | 6.714% | 1.103 | 1.1103 | 1.072
2010-04-02 | 21 | 25.8903 | 10.6951 | 36.5854 | 2.3284 | 0.76558 | 0.27198 | 3.3659 | 9.2% | 9.789% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-04-02 | 22 | 24.5268 | 10.3115 | 34.8383 | 2.1113 | 0.76558 | 0.25899 | 3.1359 | 9.001% | 9.577% | 6.472% | 1.0989 | 1.1059 | 1.0692
2010-04-02 | 23 | 23.3634 | 9.7044 | 33.0679 | 1.9022 | 0.76558 | 0.24583 | 2.9136 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-04-02 | 24 | 22.6021 | 9.5043 | 32.1063 | 1.7931 | 0.76558 | 0.23868 | 2.7974 | 8.713% | 9.271% | 6.265% | 1.0954 | 1.1022 | 1.0668
2010-04-02 | 25 | 21.6293 | 9.2208 | 30.8501 | 1.6556 | 0.76558 | 0.22934 | 2.6505 | 8.592% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-04-02 | 26 | 20.9515 | 8.7786 | 29.73 | 1.5375 | 0.76558 | 0.22102 | 2.5241 | 8.49% | 9.034% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-04-02 | 27 | 20.7943 | 8.9562 | 29.7505 | 1.5397 | 0.76558 | 0.22117 | 2.5264 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-04-02 | 28 | 20.6819 | 8.8727 | 29.5546 | 1.5194 | 0.76558 | 0.21971 | 2.5047 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-04-02 | 29 | 21.6561 | 9.4995 | 31.1556 | 1.6885 | 0.76558 | 0.23161 | 2.6857 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-04-02 | 30 | 23.7093 | 10.5807 | 34.29 | 2.0454 | 0.76558 | 0.25492 | 3.0659 | 8.941% | 9.513% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-04-02 | 31 | 22.601 | 9.6215 | 32.2225 | 1.8062 | 0.76558 | 0.23955 | 2.8113 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-04-02 | 32 | 21.9239 | 9.1883 | 31.1122 | 1.6838 | 0.76558 | 0.23129 | 2.6807 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-04-02 | 33 | 21.5526 | 9.2748 | 30.8274 | 1.6531 | 0.76558 | 0.22917 | 2.6479 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-04-02 | 34 | 21.2336 | 9.3575 | 30.5911 | 1.6279 | 0.76558 | 0.22742 | 2.6209 | 8.567% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-04-02 | 35 | 21.3201 | 9.6192 | 30.9392 | 1.6652 | 0.76558 | 0.23001 | 2.6607 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-04-02 | 36 | 21.8643 | 10.2728 | 32.137 | 1.7966 | 0.76558 | 0.23891 | 2.8011 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-04-02 | 37 | 22.9393 | 10.5507 | 33.49 | 1.951 | 0.76558 | 0.24897 | 2.9656 | 8.855% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2010-04-02 | 38 | 23.6448 | 10.7168 | 34.3616 | 2.0539 | 0.76558 | 0.25545 | 3.0749 | 8.949% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-04-02 | 39 | 24.6915 | 10.787 | 35.4785 | 2.1896 | 0.76558 | 0.26375 | 3.2189 | 9.073% | 9.654% | 6.523% | 1.0998 | 1.1069 | 1.0698
2010-04-02 | 40 | 25.783 | 11.1603 | 36.9433 | 2.3741 | 0.76558 | 0.27464 | 3.4144 | 9.242% | 9.834% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-04-02 | 41 | 26.557 | 11.2145 | 37.7715 | 2.4818 | 0.76558 | 0.2808 | 3.5282 | 9.341% | 9.939% | 6.716% | 1.103 | 1.1104 | 1.072
2010-04-02 | 42 | 26.1687 | 11.1788 | 37.3475 | 2.4264 | 0.76558 | 0.27765 | 3.4696 | 9.29% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-04-02 | 43 | 25.0192 | 10.4309 | 35.4501 | 2.1861 | 0.76558 | 0.26354 | 3.2152 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-04-02 | 44 | 23.5388 | 9.7089 | 33.2477 | 1.9229 | 0.76558 | 0.24717 | 2.9356 | 8.83% | 9.395% | 6.349% | 1.0968 | 1.1037 | 1.0678
2010-04-02 | 45 | 21.7276 | 8.9439 | 30.6716 | 1.6365 | 0.76558 | 0.22802 | 2.6301 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-04-02 | 46 | 19.4752 | 8.0545 | 27.5297 | 1.3184 | 0.76558 | 0.20466 | 2.2886 | 8.313% | 8.845% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-04-02 | 47 | 18.3847 | 7.4305 | 25.8152 | 1.1593 | 0.76558 | 0.19191 | 2.1168 | 8.2% | 8.724% | 5.896% | 1.0893 | 1.0956 | 1.0626
2010-04-02 | 48 | 17.3529 | 7.4065 | 24.7594 | 1.0664 | 0.76558 | 0.18406 | 2.016 | 8.142% | 8.664% | 5.854% | 1.0886 | 1.0949 | 1.0622
2010-04-03 | 1 | 16.1914 | 6.7449 | 22.9363 | 0.91513 | 0.76558 | 0.17051 | 1.8512 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-04-03 | 2 | 15.9032 | 6.3102 | 22.2134 | 0.85835 | 0.76558 | 0.16514 | 1.7891 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-03 | 3 | 14.8545 | 6.0263 | 20.8808 | 0.75845 | 0.76558 | 0.15523 | 1.6793 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-03 | 4 | 14.3664 | 5.8126 | 20.179 | 0.70833 | 0.76558 | 0.15001 | 1.6239 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-03 | 5 | 13.8903 | 5.8056 | 19.6959 | 0.67482 | 0.76558 | 0.14642 | 1.5868 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-04-03 | 6 | 13.7631 | 5.8449 | 19.608 | 0.66881 | 0.76558 | 0.14577 | 1.5802 | 8.059% | 8.574% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-04-03 | 7 | 13.4618 | 5.9532 | 19.415 | 0.65571 | 0.76558 | 0.14433 | 1.5656 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2010-04-03 | 8 | 13.6038 | 5.9962 | 19.5999 | 0.66826 | 0.76558 | 0.14571 | 1.5795 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-04-03 | 9 | 13.8846 | 6.0071 | 19.8917 | 0.6883 | 0.76558 | 0.14788 | 1.6018 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-04-03 | 10 | 14.0006 | 6.0402 | 20.0408 | 0.69866 | 0.76558 | 0.14899 | 1.6132 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-03 | 11 | 14.6134 | 6.384 | 20.9974 | 0.76695 | 0.76558 | 0.1561 | 1.6886 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-03 | 12 | 15.1317 | 6.6506 | 21.7823 | 0.82535 | 0.76558 | 0.16193 | 1.7529 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-03 | 13 | 16.7394 | 7.4124 | 24.1518 | 1.0147 | 0.76558 | 0.17955 | 1.9598 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-04-03 | 14 | 19.1676 | 8.9904 | 28.158 | 1.3792 | 0.76558 | 0.20933 | 2.3541 | 8.36% | 8.896% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-04-03 | 15 | 23.5496 | 11.3735 | 34.9231 | 2.1216 | 0.76558 | 0.25962 | 3.1468 | 9.011% | 9.587% | 6.479% | 1.099 | 1.106 | 1.0693
2010-04-03 | 16 | 26.8659 | 13.3381 | 40.204 | 2.8117 | 0.76558 | 0.29888 | 3.8762 | 9.641% | 10.26% | 6.932% | 1.1067 | 1.1143 | 1.0745
2010-04-03 | 17 | 28.9875 | 14.1167 | 43.1042 | 3.232 | 0.76558 | 0.32044 | 4.318 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-04-03 | 18 | 29.2489 | 13.9491 | 43.198 | 3.2461 | 0.76558 | 0.32114 | 4.3328 | 10.03% | 10.67% | 7.212% | 1.1115 | 1.1195 | 1.0777
2010-04-03 | 19 | 28.5967 | 13.4287 | 42.0254 | 3.0723 | 0.76558 | 0.31242 | 4.1503 | 9.876% | 10.51% | 7.101% | 1.1096 | 1.1174 | 1.0764
2010-04-03 | 20 | 27.1907 | 12.5846 | 39.7753 | 2.7521 | 0.76558 | 0.29569 | 3.8134 | 9.587% | 10.2% | 6.893% | 1.106 | 1.1136 | 1.074
2010-04-03 | 21 | 26.5991 | 11.8016 | 38.4007 | 2.5652 | 0.76558 | 0.28548 | 3.6162 | 9.417% | 10.02% | 6.771% | 1.104 | 1.1114 | 1.0726
2010-04-03 | 22 | 25.3941 | 11.5516 | 36.9457 | 2.3744 | 0.76558 | 0.27466 | 3.4147 | 9.242% | 9.834% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-04-03 | 23 | 24.4081 | 10.9613 | 35.3694 | 2.1762 | 0.76558 | 0.26294 | 3.2047 | 9.061% | 9.64% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-04-03 | 24 | 23.5467 | 10.6308 | 34.1775 | 2.032 | 0.76558 | 0.25408 | 3.0516 | 8.929% | 9.5% | 6.42% | 1.098 | 1.105 | 1.0686
2010-04-03 | 25 | 22.1805 | 10.3582 | 32.5387 | 1.8418 | 0.76558 | 0.2419 | 2.8492 | 8.756% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-04-03 | 26 | 21.333 | 9.9313 | 31.2643 | 1.7003 | 0.76558 | 0.23242 | 2.6983 | 8.631% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-04-03 | 27 | 21.2189 | 10.0808 | 31.2997 | 1.7042 | 0.76558 | 0.23269 | 2.7024 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-04-03 | 28 | 20.931 | 9.9477 | 30.8786 | 1.6586 | 0.76558 | 0.22956 | 2.6538 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-04-03 | 29 | 20.7583 | 9.5125 | 30.2708 | 1.594 | 0.76558 | 0.22504 | 2.5846 | 8.538% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-04-03 | 30 | 20.4126 | 9.2313 | 29.6439 | 1.5286 | 0.76558 | 0.22038 | 2.5146 | 8.483% | 9.026% | 6.099% | 1.0927 | 1.0992 | 1.065
2010-04-03 | 31 | 20.628 | 9.258 | 29.886 | 1.5537 | 0.76558 | 0.22218 | 2.5415 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-04-03 | 32 | 20.5686 | 9.363 | 29.9316 | 1.5585 | 0.76558 | 0.22252 | 2.5465 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-04-03 | 33 | 20.7437 | 9.4862 | 30.2298 | 1.5897 | 0.76558 | 0.22473 | 2.58 | 8.535% | 9.081% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-04-03 | 34 | 21.1988 | 9.4051 | 30.6039 | 1.6293 | 0.76558 | 0.22751 | 2.6223 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-04-03 | 35 | 21.2041 | 9.5017 | 30.7059 | 1.6401 | 0.76558 | 0.22827 | 2.634 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-04-03 | 36 | 21.4939 | 9.721 | 31.2149 | 1.695 | 0.76558 | 0.23206 | 2.6926 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-04-03 | 37 | 22.1565 | 9.7634 | 31.9199 | 1.7724 | 0.76558 | 0.2373 | 2.7753 | 8.694% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-04-03 | 38 | 22.5012 | 9.8831 | 32.3843 | 1.8243 | 0.76558 | 0.24075 | 2.8307 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-04-03 | 39 | 22.9154 | 10.0015 | 32.9169 | 1.8848 | 0.76558 | 0.24471 | 2.8951 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2010-04-03 | 40 | 23.6633 | 10.2382 | 33.9015 | 1.9993 | 0.76558 | 0.25203 | 3.0169 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-04-03 | 41 | 23.9781 | 10.4932 | 34.4713 | 2.067 | 0.76558 | 0.25626 | 3.0889 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-04-03 | 42 | 24.0354 | 10.5243 | 34.5597 | 2.0777 | 0.76558 | 0.25692 | 3.1002 | 8.97% | 9.545% | 6.45% | 1.0985 | 1.1055 | 1.0689
2010-04-03 | 43 | 22.799 | 10.1889 | 32.9879 | 1.893 | 0.76558 | 0.24524 | 2.9038 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-04-03 | 44 | 21.954 | 9.7825 | 31.7365 | 1.7521 | 0.76558 | 0.23593 | 2.7536 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-04-03 | 45 | 20.4719 | 9.109 | 29.581 | 1.5222 | 0.76558 | 0.21991 | 2.5076 | 8.477% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-04-03 | 46 | 19.194 | 8.3711 | 27.5651 | 1.3218 | 0.76558 | 0.20492 | 2.2923 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-04-03 | 47 | 17.8741 | 8.1151 | 25.9892 | 1.175 | 0.76558 | 0.19321 | 2.1337 | 8.21% | 8.736% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-04-03 | 48 | 16.7141 | 8.1442 | 24.8584 | 1.0749 | 0.76558 | 0.1848 | 2.0253 | 8.147% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-04-04 | 1 | 15.0622 | 7.3556 | 22.4178 | 0.87422 | 0.76558 | 0.16666 | 1.8065 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-04 | 2 | 14.6719 | 6.8834 | 21.5553 | 0.80824 | 0.76558 | 0.16024 | 1.7341 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-04 | 3 | 13.7958 | 6.6681 | 20.4639 | 0.72847 | 0.76558 | 0.15213 | 1.6462 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-04 | 4 | 13.1071 | 6.4802 | 19.5873 | 0.6674 | 0.76558 | 0.14561 | 1.5786 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-04-04 | 5 | 12.4013 | 6.2689 | 18.6702 | 0.60636 | 0.76558 | 0.1388 | 1.5107 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-04-04 | 6 | 12.4731 | 6.2442 | 18.7173 | 0.60942 | 0.76558 | 0.13915 | 1.5141 | 8.09% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-04-04 | 7 | 12.3022 | 6.1038 | 18.406 | 0.58932 | 0.76558 | 0.13683 | 1.4917 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-04-04 | 8 | 12.0009 | 6.0027 | 18.0036 | 0.56384 | 0.76558 | 0.13384 | 1.4633 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-04 | 9 | 12.0009 | 5.9991 | 18 | 0.56361 | 0.76558 | 0.13381 | 1.463 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-04 | 10 | 12.2446 | 5.9514 | 18.196 | 0.57595 | 0.76558 | 0.13527 | 1.4768 | 8.116% | 8.636% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-04-04 | 11 | 12.6332 | 6.1012 | 18.7344 | 0.61054 | 0.76558 | 0.13927 | 1.5154 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-04-04 | 12 | 12.9505 | 6.3062 | 19.2567 | 0.64506 | 0.76558 | 0.14316 | 1.5538 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-04-04 | 13 | 13.3958 | 6.7429 | 20.1387 | 0.7055 | 0.76558 | 0.14971 | 1.6208 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-04 | 14 | 14.3612 | 7.003 | 21.3642 | 0.79398 | 0.76558 | 0.15882 | 1.7184 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-04 | 15 | 15.9538 | 7.6837 | 23.6376 | 0.97194 | 0.76558 | 0.17572 | 1.9132 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-04-04 | 16 | 17.5905 | 8.4932 | 26.0838 | 1.1835 | 0.76558 | 0.19391 | 2.143 | 8.216% | 8.742% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-04-04 | 17 | 19.512 | 9.5995 | 29.1115 | 1.4742 | 0.76558 | 0.21642 | 2.4562 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-04-04 | 18 | 21.3084 | 10.5033 | 31.8116 | 1.7604 | 0.76558 | 0.23649 | 2.7625 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-04-04 | 19 | 22.4299 | 10.7789 | 33.2088 | 1.9184 | 0.76558 | 0.24688 | 2.9309 | 8.826% | 9.39% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-04-04 | 20 | 22.8444 | 11.0496 | 33.894 | 1.9984 | 0.76558 | 0.25197 | 3.0159 | 8.898% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-04-04 | 21 | 23.7061 | 11.0976 | 34.8037 | 2.1071 | 0.76558 | 0.25873 | 3.1314 | 8.997% | 9.573% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-04-04 | 22 | 23.3313 | 11.1984 | 34.5297 | 2.0741 | 0.76558 | 0.2567 | 3.0963 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-04 | 23 | 22.7721 | 10.8082 | 33.5803 | 1.9616 | 0.76558 | 0.24964 | 2.9768 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-04-04 | 24 | 22.2418 | 10.5191 | 32.7609 | 1.867 | 0.76558 | 0.24355 | 2.8761 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-04-04 | 25 | 21.7378 | 10.4429 | 32.1808 | 1.8015 | 0.76558 | 0.23924 | 2.8063 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-04-04 | 26 | 21.3068 | 10.0088 | 31.3157 | 1.7059 | 0.76558 | 0.2328 | 2.7043 | 8.636% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-04-04 | 27 | 20.8337 | 9.9703 | 30.8041 | 1.6506 | 0.76558 | 0.229 | 2.6452 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-04-04 | 28 | 20.5895 | 9.6571 | 30.2466 | 1.5914 | 0.76558 | 0.22486 | 2.5819 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-04-04 | 29 | 20.0092 | 9.287 | 29.2962 | 1.493 | 0.76558 | 0.21779 | 2.4764 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-04-04 | 30 | 19.3768 | 9.026 | 28.4027 | 1.4033 | 0.76558 | 0.21115 | 2.38 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-04-04 | 31 | 19.4258 | 8.8655 | 28.2914 | 1.3923 | 0.76558 | 0.21032 | 2.3682 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-04-04 | 32 | 19.1532 | 8.9538 | 28.107 | 1.3742 | 0.76558 | 0.20895 | 2.3488 | 8.357% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-04-04 | 33 | 19.3414 | 9.1514 | 28.4928 | 1.4122 | 0.76558 | 0.21182 | 2.3896 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2010-04-04 | 34 | 19.7501 | 9.3305 | 29.0806 | 1.4711 | 0.76558 | 0.21619 | 2.4529 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-04-04 | 35 | 20.3239 | 9.8634 | 30.1873 | 1.5852 | 0.76558 | 0.22442 | 2.5752 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-04-04 | 36 | 20.9751 | 10.215 | 31.1902 | 1.6923 | 0.76558 | 0.23187 | 2.6897 | 8.624% | 9.176% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-04-04 | 37 | 21.8067 | 10.475 | 32.2817 | 1.8128 | 0.76558 | 0.23999 | 2.8184 | 8.731% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-04-04 | 38 | 21.923 | 10.5516 | 32.4746 | 1.8345 | 0.76558 | 0.24142 | 2.8415 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2010-04-04 | 39 | 22.0524 | 10.543 | 32.5954 | 1.8482 | 0.76558 | 0.24232 | 2.8561 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-04-04 | 40 | 23.2138 | 10.9611 | 34.1749 | 2.0317 | 0.76558 | 0.25406 | 3.0513 | 8.928% | 9.5% | 6.42% | 1.098 | 1.105 | 1.0686
2010-04-04 | 41 | 23.6648 | 10.6677 | 34.3324 | 2.0504 | 0.76558 | 0.25523 | 3.0712 | 8.946% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2010-04-04 | 42 | 23.0267 | 10.2334 | 33.2601 | 1.9243 | 0.76558 | 0.24726 | 2.9372 | 8.831% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2010-04-04 | 43 | 21.7403 | 9.6536 | 31.3938 | 1.7144 | 0.76558 | 0.23339 | 2.7134 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-04-04 | 44 | 20.7424 | 9.2458 | 29.9882 | 1.5644 | 0.76558 | 0.22294 | 2.5529 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-04-04 | 45 | 19.2979 | 8.8575 | 28.1554 | 1.379 | 0.76558 | 0.20931 | 2.3539 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-04-04 | 46 | 17.7816 | 8.3447 | 26.1263 | 1.1874 | 0.76558 | 0.19423 | 2.1472 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-04-04 | 47 | 17.1951 | 8.269 | 25.464 | 1.1279 | 0.76558 | 0.1893 | 2.0828 | 8.179% | 8.703% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-04-04 | 48 | 16.4184 | 8.349 | 24.7674 | 1.0671 | 0.76558 | 0.18412 | 2.0168 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2010-04-05 | 1 | 14.9168 | 7.5724 | 22.4892 | 0.8798 | 0.76558 | 0.16719 | 1.8126 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-04-05 | 2 | 14.4648 | 7.1651 | 21.6299 | 0.81385 | 0.76558 | 0.1608 | 1.7402 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-05 | 3 | 13.6624 | 6.6899 | 20.3523 | 0.72055 | 0.76558 | 0.1513 | 1.6374 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-05 | 4 | 13.1595 | 6.4618 | 19.6213 | 0.66972 | 0.76558 | 0.14587 | 1.5812 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-05 | 5 | 12.4696 | 6.402 | 18.8716 | 0.61952 | 0.76558 | 0.14029 | 1.5254 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-04-05 | 6 | 12.1535 | 6.2763 | 18.4299 | 0.59085 | 0.76558 | 0.13701 | 1.4934 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2010-04-05 | 7 | 12.0673 | 6.2126 | 18.2798 | 0.58127 | 0.76558 | 0.13589 | 1.4827 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-04-05 | 8 | 12.0953 | 6.2062 | 18.3015 | 0.58265 | 0.76558 | 0.13606 | 1.4843 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-04-05 | 9 | 11.866 | 6.2978 | 18.1638 | 0.57392 | 0.76558 | 0.13503 | 1.4745 | 8.118% | 8.637% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-04-05 | 10 | 11.8257 | 6.2714 | 18.0971 | 0.56971 | 0.76558 | 0.13454 | 1.4698 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-04-05 | 11 | 12.0692 | 6.2089 | 18.2781 | 0.58116 | 0.76558 | 0.13588 | 1.4826 | 8.111% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-04-05 | 12 | 12.2418 | 6.0984 | 18.3401 | 0.58511 | 0.76558 | 0.13634 | 1.487 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-04-05 | 13 | 12.6575 | 6.1843 | 18.8418 | 0.61756 | 0.76558 | 0.14007 | 1.5232 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-05 | 14 | 12.8599 | 6.474 | 19.3339 | 0.65024 | 0.76558 | 0.14373 | 1.5596 | 8.066% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-04-05 | 15 | 13.5915 | 6.5945 | 20.1861 | 0.70882 | 0.76558 | 0.15007 | 1.6245 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-05 | 16 | 14.5139 | 6.9671 | 21.481 | 0.80268 | 0.76558 | 0.15969 | 1.728 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-05 | 17 | 16.5863 | 7.7091 | 24.2954 | 1.0268 | 0.76558 | 0.18061 | 1.973 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-04-05 | 18 | 18.3285 | 8.7912 | 27.1197 | 1.2794 | 0.76558 | 0.20161 | 2.2466 | 8.284% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-04-05 | 19 | 19.6303 | 9.8469 | 29.4772 | 1.5115 | 0.76558 | 0.21914 | 2.4962 | 8.468% | 9.01% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-04-05 | 20 | 21.4432 | 10.5759 | 32.0191 | 1.7834 | 0.76558 | 0.23803 | 2.787 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-04-05 | 21 | 23.227 | 10.6352 | 33.8622 | 1.9946 | 0.76558 | 0.25174 | 3.012 | 8.895% | 9.464% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-04-05 | 22 | 23.7502 | 10.6557 | 34.4059 | 2.0592 | 0.76558 | 0.25578 | 3.0806 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-04-05 | 23 | 24.0302 | 10.6608 | 34.691 | 2.0935 | 0.76558 | 0.2579 | 3.117 | 8.985% | 9.56% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-04-05 | 24 | 23.4203 | 10.8056 | 34.2259 | 2.0377 | 0.76558 | 0.25444 | 3.0577 | 8.934% | 9.506% | 6.424% | 1.0981 | 1.105 | 1.0686
2010-04-05 | 25 | 22.6607 | 10.5849 | 33.2456 | 1.9227 | 0.76558 | 0.24715 | 2.9354 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-04-05 | 26 | 22.0289 | 10.4815 | 32.5104 | 1.8386 | 0.76558 | 0.24169 | 2.8458 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-04-05 | 27 | 21.2068 | 10.2024 | 31.4092 | 1.7161 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-04-05 | 28 | 20.4174 | 9.8406 | 30.258 | 1.5926 | 0.76558 | 0.22494 | 2.5832 | 8.537% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-04-05 | 29 | 20.1586 | 9.8808 | 30.0394 | 1.5697 | 0.76558 | 0.22332 | 2.5586 | 8.517% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-04-05 | 30 | 19.8281 | 9.8115 | 29.6396 | 1.5282 | 0.76558 | 0.22034 | 2.5141 | 8.482% | 9.025% | 6.099% | 1.0927 | 1.0992 | 1.0649
2010-04-05 | 31 | 19.238 | 9.5014 | 28.7394 | 1.4368 | 0.76558 | 0.21365 | 2.416 | 8.407% | 8.945% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-04-05 | 32 | 18.7539 | 9.3973 | 28.1513 | 1.3786 | 0.76558 | 0.20928 | 2.3534 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-04-05 | 33 | 18.8654 | 9.413 | 28.2783 | 1.3911 | 0.76558 | 0.21022 | 2.3669 | 8.37% | 8.906% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-04-05 | 34 | 18.4505 | 9.2334 | 27.684 | 1.3332 | 0.76558 | 0.20581 | 2.3046 | 8.325% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2010-04-05 | 35 | 18.7997 | 9.4624 | 28.262 | 1.3894 | 0.76558 | 0.2101 | 2.3651 | 8.369% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-04-05 | 36 | 19.5407 | 9.7627 | 29.3034 | 1.4937 | 0.76558 | 0.21785 | 2.4771 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-04-05 | 37 | 20.5724 | 10.1622 | 30.7346 | 1.6432 | 0.76558 | 0.22848 | 2.6373 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-04-05 | 38 | 21.7169 | 10.8607 | 32.5776 | 1.8462 | 0.76558 | 0.24219 | 2.8539 | 8.76% | 9.321% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-04-05 | 39 | 23.1509 | 11.3447 | 34.4956 | 2.07 | 0.76558 | 0.25644 | 3.092 | 8.963% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-04-05 | 40 | 24.5397 | 11.917 | 36.4568 | 2.312 | 0.76558 | 0.27102 | 3.3486 | 9.185% | 9.773% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-04-05 | 41 | 24.6814 | 11.7229 | 36.4044 | 2.3054 | 0.76558 | 0.27063 | 3.3416 | 9.179% | 9.767% | 6.6% | 1.1011 | 1.1082 | 1.0707
2010-04-05 | 42 | 24.0062 | 11.3164 | 35.3226 | 2.1704 | 0.76558 | 0.26259 | 3.1986 | 9.055% | 9.635% | 6.511% | 1.0996 | 1.1066 | 1.0696
2010-04-05 | 43 | 23.6898 | 10.9681 | 34.6579 | 2.0895 | 0.76558 | 0.25765 | 3.1127 | 8.981% | 9.556% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-04-05 | 44 | 22.7238 | 10.3562 | 33.08 | 1.9036 | 0.76558 | 0.24592 | 2.9151 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-04-05 | 45 | 21.2157 | 9.7526 | 30.9683 | 1.6683 | 0.76558 | 0.23022 | 2.6641 | 8.603% | 9.153% | 6.185% | 1.0941 | 1.1008 | 1.0659
2010-04-05 | 46 | 19.5845 | 9.1019 | 28.6864 | 1.4315 | 0.76558 | 0.21326 | 2.4103 | 8.402% | 8.94% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-04-05 | 47 | 18.0678 | 8.479 | 26.5468 | 1.2259 | 0.76558 | 0.19735 | 2.1888 | 8.245% | 8.773% | 5.928% | 1.0899 | 1.0962 | 1.063
2010-04-05 | 48 | 16.6752 | 7.8891 | 24.5642 | 1.0496 | 0.76558 | 0.18261 | 1.9978 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-04-06 | 1 | 13.3543 | 7.3954 | 20.7497 | 0.74896 | 0.76558 | 0.15426 | 1.6688 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-06 | 2 | 13.1509 | 6.9635 | 20.1144 | 0.7038 | 0.76558 | 0.14953 | 1.6189 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-06 | 3 | 12.491 | 6.7623 | 19.2533 | 0.64483 | 0.76558 | 0.14313 | 1.5535 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-06 | 4 | 11.9582 | 6.6381 | 18.5962 | 0.60157 | 0.76558 | 0.13825 | 1.5054 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2010-04-06 | 5 | 11.786 | 6.5204 | 18.3064 | 0.58296 | 0.76558 | 0.13609 | 1.4846 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-04-06 | 6 | 11.5423 | 6.4427 | 17.985 | 0.56267 | 0.76558 | 0.1337 | 1.462 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-04-06 | 7 | 11.8868 | 6.4239 | 18.3106 | 0.58323 | 0.76558 | 0.13612 | 1.4849 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-04-06 | 8 | 11.7176 | 6.4379 | 18.1556 | 0.5734 | 0.76558 | 0.13497 | 1.4739 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-04-06 | 9 | 11.6365 | 6.6943 | 18.3308 | 0.58452 | 0.76558 | 0.13627 | 1.4864 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-04-06 | 10 | 11.1821 | 6.7439 | 17.926 | 0.55899 | 0.76558 | 0.13326 | 1.4578 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-04-06 | 11 | 11.3655 | 6.7622 | 18.1277 | 0.57164 | 0.76558 | 0.13476 | 1.472 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-04-06 | 12 | 13.0583 | 7.0077 | 20.066 | 0.70042 | 0.76558 | 0.14917 | 1.6152 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-06 | 13 | 14.5961 | 6.8826 | 21.4786 | 0.8025 | 0.76558 | 0.15967 | 1.7278 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-06 | 14 | 17.1061 | 8.0097 | 25.1158 | 1.0973 | 0.76558 | 0.18671 | 2.0496 | 8.161% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-04-06 | 15 | 21.1298 | 10.4182 | 31.5481 | 1.7313 | 0.76558 | 0.23453 | 2.7314 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-04-06 | 16 | 23.4267 | 11.4345 | 34.8613 | 2.1141 | 0.76558 | 0.25916 | 3.1388 | 9.004% | 9.58% | 6.474% | 1.0989 | 1.1059 | 1.0692
2010-04-06 | 17 | 24.1497 | 11.9244 | 36.0741 | 2.2637 | 0.76558 | 0.26818 | 3.2975 | 9.141% | 9.726% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-04-06 | 18 | 24.0332 | 11.8945 | 35.9277 | 2.2454 | 0.76558 | 0.26709 | 3.2781 | 9.124% | 9.708% | 6.56% | 1.1004 | 1.1075 | 1.0702
2010-04-06 | 19 | 24.0061 | 11.8636 | 35.8697 | 2.2382 | 0.76558 | 0.26666 | 3.2704 | 9.117% | 9.701% | 6.555% | 1.1003 | 1.1074 | 1.0702
2010-04-06 | 20 | 23.3865 | 11.5695 | 34.956 | 2.1256 | 0.76558 | 0.25987 | 3.151 | 9.014% | 9.591% | 6.481% | 1.0991 | 1.1061 | 1.0693
2010-04-06 | 21 | 23.5546 | 11.1285 | 34.6831 | 2.0925 | 0.76558 | 0.25784 | 3.1159 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-04-06 | 22 | 23.2751 | 11.0637 | 34.3388 | 2.0512 | 0.76558 | 0.25528 | 3.072 | 8.946% | 9.519% | 6.432% | 1.0983 | 1.1052 | 1.0687
2010-04-06 | 23 | 23.1381 | 10.8417 | 33.9798 | 2.0085 | 0.76558 | 0.25261 | 3.0267 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-04-06 | 24 | 22.9383 | 10.8605 | 33.7988 | 1.9872 | 0.76558 | 0.25126 | 3.004 | 8.888% | 9.457% | 6.39% | 1.0975 | 1.1044 | 1.0683
2010-04-06 | 25 | 22.8687 | 10.7074 | 33.5761 | 1.9611 | 0.76558 | 0.24961 | 2.9763 | 8.864% | 9.432% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-04-06 | 26 | 22.8777 | 10.5531 | 33.4308 | 1.9441 | 0.76558 | 0.24853 | 2.9582 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-04-06 | 27 | 23.5184 | 11.1299 | 34.6483 | 2.0883 | 0.76558 | 0.25758 | 3.1115 | 8.98% | 9.555% | 6.457% | 1.0987 | 1.1056 | 1.069
2010-04-06 | 28 | 23.8628 | 11.1905 | 35.0534 | 2.1374 | 0.76558 | 0.26059 | 3.1636 | 9.025% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-04-06 | 29 | 24.0786 | 10.2525 | 34.3311 | 2.0503 | 0.76558 | 0.25522 | 3.0711 | 8.945% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2010-04-06 | 30 | 24.02 | 10.2967 | 34.3168 | 2.0486 | 0.76558 | 0.25512 | 3.0692 | 8.944% | 9.516% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-04-06 | 31 | 24.4373 | 10.5772 | 35.0145 | 2.1327 | 0.76558 | 0.2603 | 3.1586 | 9.021% | 9.598% | 6.486% | 1.0992 | 1.1062 | 1.0694
2010-04-06 | 32 | 24.5089 | 10.8669 | 35.3758 | 2.1769 | 0.76558 | 0.26299 | 3.2055 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-04-06 | 33 | 25.4694 | 11.1271 | 36.5965 | 2.3298 | 0.76558 | 0.27206 | 3.3674 | 9.201% | 9.79% | 6.616% | 1.1013 | 1.1085 | 1.0708
2010-04-06 | 34 | 26.6007 | 11.3026 | 37.9033 | 2.4991 | 0.76558 | 0.28178 | 3.5465 | 9.357% | 9.955% | 6.727% | 1.1032 | 1.1106 | 1.0721
2010-04-06 | 35 | 27.0911 | 11.975 | 39.0661 | 2.6548 | 0.76558 | 0.29042 | 3.7108 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-04-06 | 36 | 28.1236 | 12.692 | 40.8157 | 2.8979 | 0.76558 | 0.30343 | 3.9669 | 9.719% | 10.34% | 6.988% | 1.1077 | 1.1153 | 1.0751
2010-04-06 | 37 | 29.2878 | 12.8395 | 42.1273 | 3.0872 | 0.76558 | 0.31318 | 4.1659 | 9.889% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-04-06 | 38 | 29.3719 | 12.9068 | 42.2787 | 3.1094 | 0.76558 | 0.31431 | 4.1893 | 9.909% | 10.54% | 7.124% | 1.11 | 1.1179 | 1.0767
2010-04-06 | 39 | 28.7543 | 12.5071 | 41.2614 | 2.9616 | 0.76558 | 0.30674 | 4.0339 | 9.776% | 10.4% | 7.029% | 1.1084 | 1.1161 | 1.0756
2010-04-06 | 40 | 27.7206 | 12.0824 | 39.803 | 2.7559 | 0.76558 | 0.2959 | 3.8174 | 9.591% | 10.2% | 6.896% | 1.1061 | 1.1136 | 1.0741
2010-04-06 | 41 | 27.1305 | 11.2812 | 38.4117 | 2.5666 | 0.76558 | 0.28556 | 3.6178 | 9.418% | 10.02% | 6.772% | 1.104 | 1.1114 | 1.0726
2010-04-06 | 42 | 25.9088 | 10.7741 | 36.6829 | 2.3408 | 0.76558 | 0.27271 | 3.3791 | 9.212% | 9.801% | 6.623% | 1.1015 | 1.1087 | 1.0709
2010-04-06 | 43 | 24.1882 | 10.3317 | 34.5199 | 2.0729 | 0.76558 | 0.25663 | 3.0951 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-06 | 44 | 22.5508 | 9.7348 | 32.2856 | 1.8132 | 0.76558 | 0.24001 | 2.8188 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-04-06 | 45 | 20.4096 | 8.9674 | 29.377 | 1.5012 | 0.76558 | 0.21839 | 2.4852 | 8.46% | 9.001% | 6.083% | 1.0924 | 1.0989 | 1.0648
2010-04-06 | 46 | 18.4729 | 7.9661 | 26.4389 | 1.216 | 0.76558 | 0.19655 | 2.1781 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-04-06 | 47 | 17.1538 | 7.7049 | 24.8586 | 1.075 | 0.76558 | 0.1848 | 2.0253 | 8.147% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-04-06 | 48 | 16.0752 | 7.8368 | 23.912 | 0.99464 | 0.76558 | 0.17777 | 1.938 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-04-07 | 1 | 14.7948 | 7.2499 | 22.0447 | 0.84536 | 0.76558 | 0.16388 | 1.7748 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-07 | 2 | 14.6537 | 6.972 | 21.6257 | 0.81353 | 0.76558 | 0.16077 | 1.7399 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-07 | 3 | 13.9511 | 6.757 | 20.7081 | 0.74596 | 0.76558 | 0.15395 | 1.6655 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-07 | 4 | 13.177 | 6.5847 | 19.7617 | 0.67933 | 0.76558 | 0.14691 | 1.5918 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-04-07 | 5 | 12.7298 | 6.5034 | 19.2332 | 0.64349 | 0.76558 | 0.14298 | 1.552 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-07 | 6 | 12.4581 | 6.4942 | 18.9523 | 0.62483 | 0.76558 | 0.14089 | 1.5313 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-04-07 | 7 | 12.703 | 6.3422 | 19.0452 | 0.63097 | 0.76558 | 0.14158 | 1.5381 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2010-04-07 | 8 | 12.4001 | 6.372 | 18.7722 | 0.613 | 0.76558 | 0.13955 | 1.5181 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2010-04-07 | 9 | 12.4279 | 6.4552 | 18.8832 | 0.62028 | 0.76558 | 0.14038 | 1.5262 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-07 | 10 | 12.7309 | 6.3691 | 19.1 | 0.6346 | 0.76558 | 0.14199 | 1.5422 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-04-07 | 11 | 13.4791 | 6.5481 | 20.0272 | 0.69771 | 0.76558 | 0.14888 | 1.6122 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-07 | 12 | 14.5991 | 6.8673 | 21.4664 | 0.80159 | 0.76558 | 0.15958 | 1.7268 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-07 | 13 | 16.2356 | 7.6493 | 23.8849 | 0.99239 | 0.76558 | 0.17756 | 1.9355 | 8.104% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2010-04-07 | 14 | 18.8782 | 9.3058 | 28.184 | 1.3818 | 0.76558 | 0.20952 | 2.3569 | 8.362% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-04-07 | 15 | 22.8584 | 11.1856 | 34.044 | 2.0161 | 0.76558 | 0.25309 | 3.0348 | 8.914% | 9.485% | 6.409% | 1.0979 | 1.1048 | 1.0685
2010-04-07 | 16 | 25.6129 | 11.8964 | 37.5093 | 2.4474 | 0.76558 | 0.27885 | 3.4919 | 9.309% | 9.905% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-04-07 | 17 | 26.0267 | 11.8549 | 37.8816 | 2.4963 | 0.76558 | 0.28162 | 3.5435 | 9.354% | 9.953% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-04-07 | 18 | 25.8985 | 11.3585 | 37.257 | 2.4146 | 0.76558 | 0.27697 | 3.4572 | 9.279% | 9.873% | 6.672% | 1.1023 | 1.1095 | 1.0715
2010-04-07 | 19 | 25.2824 | 10.9411 | 36.2235 | 2.2825 | 0.76558 | 0.26929 | 3.3174 | 9.158% | 9.744% | 6.585% | 1.1008 | 1.108 | 1.0705
2010-04-07 | 20 | 24.4078 | 10.5762 | 34.984 | 2.129 | 0.76558 | 0.26008 | 3.1546 | 9.017% | 9.595% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-04-07 | 21 | 24.465 | 10.2999 | 34.7649 | 2.1024 | 0.76558 | 0.25845 | 3.1264 | 8.993% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-04-07 | 22 | 24.793 | 10.4492 | 35.2422 | 2.1605 | 0.76558 | 0.262 | 3.1881 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-04-07 | 23 | 24.8673 | 10.101 | 34.9683 | 2.1271 | 0.76558 | 0.25996 | 3.1526 | 9.016% | 9.593% | 6.482% | 1.0991 | 1.1061 | 1.0693
2010-04-07 | 24 | 24.1492 | 10.1618 | 34.311 | 2.0479 | 0.76558 | 0.25507 | 3.0685 | 8.943% | 9.516% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-04-07 | 25 | 23.3728 | 10.283 | 33.6558 | 1.9704 | 0.76558 | 0.2502 | 2.9862 | 8.873% | 9.441% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-04-07 | 26 | 22.7981 | 10.0109 | 32.809 | 1.8725 | 0.76558 | 0.24391 | 2.882 | 8.784% | 9.346% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-04-07 | 27 | 22.4558 | 9.9879 | 32.4437 | 1.831 | 0.76558 | 0.24119 | 2.8378 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-04-07 | 28 | 22.4967 | 10.011 | 32.5077 | 1.8383 | 0.76558 | 0.24167 | 2.8455 | 8.753% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-04-07 | 29 | 23.128 | 9.812 | 32.94 | 1.8875 | 0.76558 | 0.24488 | 2.8979 | 8.798% | 9.361% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-04-07 | 30 | 23.4994 | 9.7772 | 33.2766 | 1.9263 | 0.76558 | 0.24738 | 2.9392 | 8.833% | 9.398% | 6.351% | 1.0969 | 1.1037 | 1.0678
2010-04-07 | 31 | 24.3302 | 9.994 | 34.3242 | 2.0494 | 0.76558 | 0.25517 | 3.0702 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-04-07 | 32 | 24.9628 | 10.2562 | 35.219 | 2.1577 | 0.76558 | 0.26182 | 3.1851 | 9.044% | 9.622% | 6.502% | 1.0994 | 1.1065 | 1.0695
2010-04-07 | 33 | 25.2502 | 10.5694 | 35.8196 | 2.2319 | 0.76558 | 0.26629 | 3.2638 | 9.112% | 9.695% | 6.551% | 1.1003 | 1.1074 | 1.0701
2010-04-07 | 34 | 26.0688 | 11.024 | 37.0928 | 2.3934 | 0.76558 | 0.27575 | 3.4347 | 9.26% | 9.852% | 6.658% | 1.102 | 1.1093 | 1.0713
2010-04-07 | 35 | 26.8022 | 11.8616 | 38.6638 | 2.6004 | 0.76558 | 0.28743 | 3.6534 | 9.449% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-04-07 | 36 | 28.4684 | 12.6381 | 41.1065 | 2.9394 | 0.76558 | 0.30559 | 4.0105 | 9.756% | 10.38% | 7.015% | 1.1081 | 1.1158 | 1.0754
2010-04-07 | 37 | 30.7349 | 13.2637 | 43.9987 | 3.3675 | 0.76558 | 0.32709 | 4.4602 | 10.14% | 10.79% | 7.289% | 1.1128 | 1.1209 | 1.0786
2010-04-07 | 38 | 32.11 | 13.7727 | 45.8826 | 3.6621 | 0.76558 | 0.3411 | 4.7688 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-04-07 | 39 | 32.154 | 13.6837 | 45.8377 | 3.6549 | 0.76558 | 0.34076 | 4.7613 | 10.39% | 11.05% | 7.468% | 1.1159 | 1.1243 | 1.0807
2010-04-07 | 40 | 30.8394 | 13.094 | 43.9334 | 3.3576 | 0.76558 | 0.32661 | 4.4498 | 10.13% | 10.78% | 7.282% | 1.1127 | 1.1208 | 1.0785
2010-04-07 | 41 | 29.9635 | 12.4113 | 42.3748 | 3.1236 | 0.76558 | 0.31502 | 4.2042 | 9.921% | 10.56% | 7.133% | 1.1101 | 1.118 | 1.0768
2010-04-07 | 42 | 29.5345 | 11.9905 | 41.525 | 2.9995 | 0.76558 | 0.3087 | 4.0738 | 9.811% | 10.44% | 7.054% | 1.1088 | 1.1165 | 1.0759
2010-04-07 | 43 | 27.7831 | 11.329 | 39.1121 | 2.6611 | 0.76558 | 0.29076 | 3.7174 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2010-04-07 | 44 | 26.2323 | 10.7073 | 36.9396 | 2.3737 | 0.76558 | 0.27461 | 3.4139 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-04-07 | 45 | 23.6459 | 9.9294 | 33.5753 | 1.961 | 0.76558 | 0.2496 | 2.9762 | 8.864% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-04-07 | 46 | 21.2622 | 8.9885 | 30.2508 | 1.5919 | 0.76558 | 0.22489 | 2.5823 | 8.536% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-04-07 | 47 | 19.9137 | 8.6263 | 28.54 | 1.4169 | 0.76558 | 0.21217 | 2.3947 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-04-07 | 48 | 18.3918 | 8.346 | 26.7378 | 1.2436 | 0.76558 | 0.19877 | 2.208 | 8.258% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-04-08 | 1 | 16.6462 | 7.6622 | 24.3084 | 1.0279 | 0.76558 | 0.18071 | 1.9742 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-04-08 | 2 | 16.5227 | 7.1364 | 23.6591 | 0.97372 | 0.76558 | 0.17588 | 1.9152 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-04-08 | 3 | 15.6114 | 7.1045 | 22.7159 | 0.89763 | 0.76558 | 0.16887 | 1.8321 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-08 | 4 | 15.2311 | 6.8901 | 22.1212 | 0.85124 | 0.76558 | 0.16445 | 1.7813 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-04-08 | 5 | 14.6498 | 6.6884 | 21.3382 | 0.79205 | 0.76558 | 0.15863 | 1.7163 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 6 | 14.3201 | 6.5524 | 20.8725 | 0.75785 | 0.76558 | 0.15517 | 1.6786 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 7 | 14.4836 | 6.5813 | 21.0649 | 0.77189 | 0.76558 | 0.1566 | 1.6941 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 8 | 14.6278 | 6.6201 | 21.2479 | 0.78536 | 0.76558 | 0.15796 | 1.7089 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 9 | 14.7572 | 6.6014 | 21.3586 | 0.79356 | 0.76558 | 0.15878 | 1.7179 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 10 | 14.6134 | 6.7134 | 21.3269 | 0.7912 | 0.76558 | 0.15855 | 1.7153 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-08 | 11 | 15.1742 | 6.8525 | 22.0267 | 0.84398 | 0.76558 | 0.16375 | 1.7733 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-04-08 | 12 | 16.0067 | 7.3271 | 23.3338 | 0.94712 | 0.76558 | 0.17347 | 1.8862 | 8.083% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-04-08 | 13 | 18.2031 | 7.9659 | 26.169 | 1.1913 | 0.76558 | 0.19454 | 2.1514 | 8.221% | 8.747% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-04-08 | 14 | 21.3235 | 9.5685 | 30.892 | 1.6601 | 0.76558 | 0.22966 | 2.6553 | 8.595% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-04-08 | 15 | 25.5757 | 11.8833 | 37.459 | 2.4409 | 0.76558 | 0.27847 | 3.4849 | 9.303% | 9.899% | 6.689% | 1.1026 | 1.1099 | 1.0717
2010-04-08 | 16 | 28.663 | 12.8732 | 41.5361 | 3.0011 | 0.76558 | 0.30878 | 4.0755 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-04-08 | 17 | 29.8538 | 13.5121 | 43.3659 | 3.2714 | 0.76558 | 0.32239 | 4.3593 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-04-08 | 18 | 30.725 | 13.2942 | 44.0193 | 3.3707 | 0.76558 | 0.32724 | 4.4635 | 10.14% | 10.79% | 7.291% | 1.1128 | 1.1209 | 1.0786
2010-04-08 | 19 | 31.0721 | 12.9816 | 44.0537 | 3.376 | 0.76558 | 0.3275 | 4.4691 | 10.14% | 10.79% | 7.294% | 1.1129 | 1.121 | 1.0787
2010-04-08 | 20 | 30.3962 | 12.6337 | 43.0299 | 3.2209 | 0.76558 | 0.31989 | 4.3063 | 10.01% | 10.65% | 7.196% | 1.1112 | 1.1192 | 1.0775
2010-04-08 | 21 | 30.6535 | 12.5391 | 43.1927 | 3.2453 | 0.76558 | 0.3211 | 4.332 | 10.03% | 10.67% | 7.211% | 1.1115 | 1.1195 | 1.0777
2010-04-08 | 22 | 30.5539 | 12.5629 | 43.1167 | 3.2339 | 0.76558 | 0.32053 | 4.32 | 10.02% | 10.66% | 7.204% | 1.1113 | 1.1193 | 1.0776
2010-04-08 | 23 | 29.2172 | 12.1127 | 41.3298 | 2.9714 | 0.76558 | 0.30725 | 4.0442 | 9.785% | 10.41% | 7.036% | 1.1085 | 1.1162 | 1.0757
2010-04-08 | 24 | 27.8958 | 12.0487 | 39.9445 | 2.7755 | 0.76558 | 0.29695 | 3.8381 | 9.609% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-04-08 | 25 | 26.5041 | 11.7473 | 38.2515 | 2.5453 | 0.76558 | 0.28437 | 3.5952 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-04-08 | 26 | 25.6855 | 11.0246 | 36.7101 | 2.3443 | 0.76558 | 0.27291 | 3.3827 | 9.215% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.071
2010-04-08 | 27 | 25.5858 | 10.8466 | 36.4324 | 2.3089 | 0.76558 | 0.27084 | 3.3453 | 9.182% | 9.77% | 6.602% | 1.1011 | 1.1083 | 1.0707
2010-04-08 | 28 | 25.3279 | 10.8217 | 36.1496 | 2.2732 | 0.76558 | 0.26874 | 3.3075 | 9.15% | 9.735% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-04-08 | 29 | 24.94 | 10.5104 | 35.4504 | 2.1861 | 0.76558 | 0.26354 | 3.2153 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-04-08 | 30 | 24.5931 | 10.4543 | 35.0474 | 2.1367 | 0.76558 | 0.26055 | 3.1628 | 9.024% | 9.602% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-04-08 | 31 | 25.8575 | 10.3342 | 36.1917 | 2.2785 | 0.76558 | 0.26905 | 3.3132 | 9.154% | 9.74% | 6.582% | 1.1008 | 1.1079 | 1.0705
2010-04-08 | 32 | 27.2368 | 10.7671 | 38.0038 | 2.5124 | 0.76558 | 0.28253 | 3.5605 | 9.369% | 9.968% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-04-08 | 33 | 28.9878 | 11.6331 | 40.621 | 2.8704 | 0.76558 | 0.30198 | 3.9379 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2010-04-08 | 34 | 29.5907 | 11.6851 | 41.2758 | 2.9636 | 0.76558 | 0.30685 | 4.0361 | 9.778% | 10.4% | 7.031% | 1.1084 | 1.1161 | 1.0756
2010-04-08 | 35 | 30.0518 | 12.1426 | 42.1944 | 3.097 | 0.76558 | 0.31368 | 4.1763 | 9.898% | 10.53% | 7.116% | 1.1098 | 1.1177 | 1.0766
2010-04-08 | 36 | 31.7322 | 12.7041 | 44.4362 | 3.4349 | 0.76558 | 0.33034 | 4.5308 | 10.2% | 10.85% | 7.331% | 1.1135 | 1.1217 | 1.0791
2010-04-08 | 37 | 33.3399 | 13.463 | 46.8029 | 3.8105 | 0.76558 | 0.34794 | 4.924 | 10.52% | 11.19% | 7.564% | 1.1176 | 1.1261 | 1.0818
2010-04-08 | 38 | 35.0925 | 13.9814 | 49.0738 | 4.1892 | 0.76558 | 0.36482 | 5.3196 | 10.84% | 11.53% | 7.794% | 1.1216 | 1.1304 | 1.0845
2010-04-08 | 39 | 35.0353 | 13.7802 | 48.8155 | 4.1453 | 0.76558 | 0.3629 | 5.2737 | 10.8% | 11.49% | 7.768% | 1.1211 | 1.1299 | 1.0842
2010-04-08 | 40 | 34.1295 | 13.1874 | 47.3169 | 3.8946 | 0.76558 | 0.35176 | 5.012 | 10.59% | 11.27% | 7.616% | 1.1185 | 1.127 | 1.0824
2010-04-08 | 41 | 34.1726 | 12.767 | 46.9396 | 3.8328 | 0.76558 | 0.34895 | 4.9473 | 10.54% | 11.21% | 7.578% | 1.1178 | 1.1263 | 1.082
2010-04-08 | 42 | 33.5542 | 12.2997 | 45.8539 | 3.6575 | 0.76558 | 0.34088 | 4.764 | 10.39% | 11.05% | 7.47% | 1.1159 | 1.1243 | 1.0807
2010-04-08 | 43 | 31.5444 | 11.6626 | 43.207 | 3.2475 | 0.76558 | 0.32121 | 4.3342 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-04-08 | 44 | 30.0937 | 10.7354 | 40.8291 | 2.8998 | 0.76558 | 0.30353 | 3.969 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-04-08 | 45 | 27.3656 | 9.7136 | 37.0792 | 2.3916 | 0.76558 | 0.27565 | 3.4329 | 9.258% | 9.851% | 6.657% | 1.102 | 1.1093 | 1.0713
2010-04-08 | 46 | 24.5628 | 8.6284 | 33.1912 | 1.9164 | 0.76558 | 0.24675 | 2.9287 | 8.824% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-04-08 | 47 | 22.8255 | 8.1963 | 31.0217 | 1.674 | 0.76558 | 0.23062 | 2.6702 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-04-08 | 48 | 21.4766 | 8.2853 | 29.7619 | 1.5408 | 0.76558 | 0.22125 | 2.5277 | 8.493% | 9.037% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-04-09 | 1 | 20.3843 | 7.6025 | 27.9868 | 1.3625 | 0.76558 | 0.20806 | 2.3361 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0638
2010-04-09 | 2 | 20.2393 | 7.1309 | 27.3702 | 1.3031 | 0.76558 | 0.20347 | 2.2722 | 8.302% | 8.833% | 5.969% | 1.0905 | 1.0969 | 1.0635
2010-04-09 | 3 | 18.9624 | 6.7831 | 25.7454 | 1.153 | 0.76558 | 0.19139 | 2.11 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-04-09 | 4 | 18.2723 | 6.7625 | 25.0348 | 1.0902 | 0.76558 | 0.18611 | 2.0419 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-04-09 | 5 | 17.8847 | 6.5368 | 24.4215 | 1.0375 | 0.76558 | 0.18155 | 1.9846 | 8.126% | 8.647% | 5.843% | 1.0885 | 1.0946 | 1.0621
2010-04-09 | 6 | 17.7709 | 6.4635 | 24.2344 | 1.0216 | 0.76558 | 0.18016 | 1.9674 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-04-09 | 7 | 17.483 | 6.3775 | 23.8605 | 0.99036 | 0.76558 | 0.17738 | 1.9333 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-04-09 | 8 | 17.3244 | 6.5249 | 23.8493 | 0.98943 | 0.76558 | 0.1773 | 1.9323 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-04-09 | 9 | 17.5403 | 6.5803 | 24.1205 | 1.0121 | 0.76558 | 0.17931 | 1.957 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-04-09 | 10 | 17.8717 | 6.5937 | 24.4654 | 1.0412 | 0.76558 | 0.18188 | 1.9887 | 8.128% | 8.649% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-09 | 11 | 18.1733 | 6.7969 | 24.9702 | 1.0846 | 0.76558 | 0.18563 | 2.0358 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-04-09 | 12 | 18.9048 | 7.388 | 26.2928 | 1.2026 | 0.76558 | 0.19546 | 2.1636 | 8.229% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-04-09 | 13 | 21.0744 | 8.4471 | 29.5215 | 1.516 | 0.76558 | 0.21947 | 2.5011 | 8.472% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-04-09 | 14 | 24.2776 | 10.2781 | 34.5558 | 2.0772 | 0.76558 | 0.25689 | 3.0997 | 8.97% | 9.544% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-04-09 | 15 | 28.632 | 12.8091 | 41.4411 | 2.9874 | 0.76558 | 0.30808 | 4.0611 | 9.8% | 10.43% | 7.046% | 1.1086 | 1.1164 | 1.0758
2010-04-09 | 16 | 31.1998 | 14.2373 | 45.437 | 3.5913 | 0.76558 | 0.33778 | 4.6947 | 10.33% | 10.99% | 7.429% | 1.1152 | 1.1235 | 1.0803
2010-04-09 | 17 | 32.3344 | 14.3531 | 46.6874 | 3.7917 | 0.76558 | 0.34708 | 4.9044 | 10.5% | 11.18% | 7.553% | 1.1174 | 1.1258 | 1.0817
2010-04-09 | 18 | 32.707 | 13.9469 | 46.6539 | 3.7863 | 0.76558 | 0.34683 | 4.8987 | 10.5% | 11.17% | 7.55% | 1.1173 | 1.1258 | 1.0817
2010-04-09 | 19 | 31.8474 | 13.3654 | 45.2129 | 3.556 | 0.76558 | 0.33612 | 4.6577 | 10.3% | 10.96% | 7.407% | 1.1148 | 1.1231 | 1.08
2010-04-09 | 20 | 30.5828 | 12.3882 | 42.971 | 3.2121 | 0.76558 | 0.31945 | 4.2971 | 10% | 10.64% | 7.19% | 1.1111 | 1.1191 | 1.0775
2010-04-09 | 21 | 30.4685 | 11.8128 | 42.2813 | 3.1098 | 0.76558 | 0.31432 | 4.1897 | 9.909% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-04-09 | 22 | 29.4207 | 11.4854 | 40.9061 | 2.9108 | 0.76558 | 0.3041 | 3.9805 | 9.731% | 10.35% | 6.996% | 1.1078 | 1.1155 | 1.0752
2010-04-09 | 23 | 28.2287 | 10.9873 | 39.216 | 2.6752 | 0.76558 | 0.29154 | 3.7324 | 9.517% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-04-09 | 24 | 27.0794 | 10.6579 | 37.7374 | 2.4773 | 0.76558 | 0.28054 | 3.5234 | 9.337% | 9.934% | 6.713% | 1.103 | 1.1103 | 1.072
2010-04-09 | 25 | 25.571 | 10.5023 | 36.0734 | 2.2636 | 0.76558 | 0.26817 | 3.2974 | 9.141% | 9.726% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-04-09 | 26 | 24.9964 | 10.0835 | 35.0799 | 2.1407 | 0.76558 | 0.26079 | 3.167 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-04-09 | 27 | 25.1253 | 10.352 | 35.4773 | 2.1895 | 0.76558 | 0.26374 | 3.2188 | 9.073% | 9.653% | 6.523% | 1.0998 | 1.1068 | 1.0698
2010-04-09 | 28 | 25.2543 | 10.3882 | 35.6425 | 2.2099 | 0.76558 | 0.26497 | 3.2404 | 9.092% | 9.673% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-04-09 | 29 | 25.0391 | 10.0582 | 35.0972 | 2.1428 | 0.76558 | 0.26092 | 3.1693 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-04-09 | 30 | 24.6083 | 9.7775 | 34.3858 | 2.0568 | 0.76558 | 0.25563 | 3.078 | 8.951% | 9.524% | 6.436% | 1.0983 | 1.1053 | 1.0688
2010-04-09 | 31 | 24.8811 | 9.5251 | 34.4063 | 2.0593 | 0.76558 | 0.25578 | 3.0806 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-04-09 | 32 | 25.0384 | 9.481 | 34.5194 | 2.0728 | 0.76558 | 0.25662 | 3.095 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-09 | 33 | 25.2684 | 9.9076 | 35.176 | 2.1524 | 0.76558 | 0.2615 | 3.1795 | 9.039% | 9.617% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-04-09 | 34 | 25.8859 | 9.9198 | 35.8057 | 2.2302 | 0.76558 | 0.26618 | 3.2619 | 9.11% | 9.693% | 6.55% | 1.1002 | 1.1073 | 1.0701
2010-04-09 | 35 | 26.3021 | 9.9978 | 36.2998 | 2.2922 | 0.76558 | 0.26986 | 3.3276 | 9.167% | 9.754% | 6.591% | 1.1009 | 1.1081 | 1.0706
2010-04-09 | 36 | 27.7674 | 10.9617 | 38.7291 | 2.6092 | 0.76558 | 0.28792 | 3.6627 | 9.457% | 10.06% | 6.8% | 1.1045 | 1.1119 | 1.073
2010-04-09 | 37 | 30.3665 | 12.1411 | 42.5076 | 3.1432 | 0.76558 | 0.31601 | 4.2248 | 9.939% | 10.57% | 7.146% | 1.1104 | 1.1183 | 1.077
2010-04-09 | 38 | 32.7357 | 13.3671 | 46.1028 | 3.6973 | 0.76558 | 0.34273 | 4.8056 | 10.42% | 11.09% | 7.495% | 1.1164 | 1.1247 | 1.081
2010-04-09 | 39 | 33.0673 | 13.2572 | 46.3245 | 3.733 | 0.76558 | 0.34438 | 4.8429 | 10.45% | 11.12% | 7.517% | 1.1167 | 1.1252 | 1.0813
2010-04-09 | 40 | 32.7673 | 12.6907 | 45.458 | 3.5946 | 0.76558 | 0.33794 | 4.6982 | 10.34% | 11% | 7.431% | 1.1153 | 1.1236 | 1.0803
2010-04-09 | 41 | 32.8116 | 12.3907 | 45.2023 | 3.5543 | 0.76558 | 0.33604 | 4.6559 | 10.3% | 10.96% | 7.406% | 1.1148 | 1.1231 | 1.08
2010-04-09 | 42 | 32.3937 | 12.2202 | 44.6139 | 3.4624 | 0.76558 | 0.33166 | 4.5596 | 10.22% | 10.87% | 7.348% | 1.1138 | 1.122 | 1.0793
2010-04-09 | 43 | 30.7131 | 11.6636 | 42.3766 | 3.1238 | 0.76558 | 0.31503 | 4.2044 | 9.922% | 10.56% | 7.134% | 1.1101 | 1.118 | 1.0768
2010-04-09 | 44 | 29.3629 | 11.0816 | 40.4445 | 2.8455 | 0.76558 | 0.30067 | 3.9117 | 9.672% | 10.29% | 6.954% | 1.1071 | 1.1147 | 1.0747
2010-04-09 | 45 | 27.2816 | 10.3214 | 37.6029 | 2.4597 | 0.76558 | 0.27954 | 3.5048 | 9.321% | 9.917% | 6.701% | 1.1028 | 1.1101 | 1.0718
2010-04-09 | 46 | 24.8804 | 9.5293 | 34.4097 | 2.0597 | 0.76558 | 0.25581 | 3.081 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-04-09 | 47 | 23.3295 | 9.0793 | 32.4088 | 1.8271 | 0.76558 | 0.24093 | 2.8336 | 8.743% | 9.303% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-04-09 | 48 | 22.3669 | 9.0019 | 31.3688 | 1.7117 | 0.76558 | 0.2332 | 2.7105 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2010-04-10 | 1 | 20.9456 | 8.1463 | 29.0919 | 1.4722 | 0.76558 | 0.21627 | 2.4541 | 8.436% | 8.976% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-04-10 | 2 | 20.6589 | 7.5354 | 28.1942 | 1.3828 | 0.76558 | 0.2096 | 2.358 | 8.363% | 8.899% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-04-10 | 3 | 19.411 | 7.2528 | 26.6638 | 1.2367 | 0.76558 | 0.19822 | 2.2005 | 8.253% | 8.781% | 5.934% | 1.09 | 1.0963 | 1.0631
2010-04-10 | 4 | 18.5903 | 6.9926 | 25.5829 | 1.1385 | 0.76558 | 0.19019 | 2.0943 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-04-10 | 5 | 18.0875 | 6.8809 | 24.9685 | 1.0845 | 0.76558 | 0.18562 | 2.0357 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-04-10 | 6 | 18.1734 | 6.8692 | 25.0426 | 1.0909 | 0.76558 | 0.18617 | 2.0427 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-04-10 | 7 | 17.8865 | 6.7798 | 24.6663 | 1.0584 | 0.76558 | 0.18337 | 2.0073 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-04-10 | 8 | 17.5984 | 6.6989 | 24.2973 | 1.027 | 0.76558 | 0.18063 | 1.9732 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-04-10 | 9 | 17.9009 | 6.5473 | 24.4482 | 1.0397 | 0.76558 | 0.18175 | 1.9871 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-10 | 10 | 18.602 | 6.5601 | 25.1621 | 1.1014 | 0.76558 | 0.18706 | 2.054 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0624
2010-04-10 | 11 | 18.9479 | 6.9098 | 25.8577 | 1.1631 | 0.76558 | 0.19223 | 2.1209 | 8.202% | 8.727% | 5.897% | 1.0894 | 1.0956 | 1.0627
2010-04-10 | 12 | 19.4641 | 7.0395 | 26.5036 | 1.2219 | 0.76558 | 0.19703 | 2.1845 | 8.242% | 8.77% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-04-10 | 13 | 20.6996 | 7.3885 | 28.0881 | 1.3724 | 0.76558 | 0.20881 | 2.3468 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-04-10 | 14 | 21.8913 | 8.0487 | 29.94 | 1.5593 | 0.76558 | 0.22258 | 2.5475 | 8.509% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2010-04-10 | 15 | 24.0901 | 9.2329 | 33.323 | 1.9316 | 0.76558 | 0.24773 | 2.9449 | 8.838% | 9.403% | 6.354% | 1.0969 | 1.1038 | 1.0679
2010-04-10 | 16 | 25.7268 | 10.6173 | 36.3441 | 2.2977 | 0.76558 | 0.27019 | 3.3335 | 9.172% | 9.759% | 6.595% | 1.101 | 1.1081 | 1.0706
2010-04-10 | 17 | 28.2686 | 11.7319 | 40.0005 | 2.7833 | 0.76558 | 0.29737 | 3.8463 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-04-10 | 18 | 30.1523 | 12.4128 | 42.5651 | 3.1517 | 0.76558 | 0.31643 | 4.2337 | 9.946% | 10.58% | 7.151% | 1.1104 | 1.1184 | 1.077
2010-04-10 | 19 | 31.4603 | 12.3044 | 43.7647 | 3.3318 | 0.76558 | 0.32535 | 4.4228 | 10.11% | 10.75% | 7.266% | 1.1124 | 1.1205 | 1.0784
2010-04-10 | 20 | 30.9993 | 11.8901 | 42.8894 | 3.1999 | 0.76558 | 0.31885 | 4.2843 | 9.989% | 10.63% | 7.182% | 1.111 | 1.1189 | 1.0774
2010-04-10 | 21 | 31.3004 | 11.5647 | 42.8651 | 3.1963 | 0.76558 | 0.31866 | 4.2805 | 9.986% | 10.63% | 7.18% | 1.1109 | 1.1189 | 1.0774
2010-04-10 | 22 | 30.223 | 11.0801 | 41.303 | 2.9676 | 0.76558 | 0.30705 | 4.0402 | 9.782% | 10.41% | 7.033% | 1.1084 | 1.1162 | 1.0757
2010-04-10 | 23 | 28.7886 | 10.4328 | 39.2214 | 2.676 | 0.76558 | 0.29158 | 3.7331 | 9.518% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-04-10 | 24 | 27.2095 | 10.2219 | 37.4314 | 2.4373 | 0.76558 | 0.27827 | 3.4811 | 9.3% | 9.895% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-04-10 | 25 | 25.9002 | 9.9065 | 35.8068 | 2.2303 | 0.76558 | 0.26619 | 3.2621 | 9.11% | 9.693% | 6.55% | 1.1002 | 1.1073 | 1.0701
2010-04-10 | 26 | 24.4348 | 9.3441 | 33.7789 | 1.9848 | 0.76558 | 0.25112 | 3.0015 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0682
2010-04-10 | 27 | 24.1634 | 9.2561 | 33.4195 | 1.9428 | 0.76558 | 0.24844 | 2.9569 | 8.848% | 9.414% | 6.361% | 1.0971 | 1.1039 | 1.0679
2010-04-10 | 28 | 23.7606 | 9.2501 | 33.0108 | 1.8956 | 0.76558 | 0.24541 | 2.9066 | 8.805% | 9.368% | 6.331% | 1.0966 | 1.1034 | 1.0676
2010-04-10 | 29 | 23.0847 | 8.9404 | 32.0252 | 1.7841 | 0.76558 | 0.23808 | 2.7877 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2010-04-10 | 30 | 22.4401 | 8.6053 | 31.0454 | 1.6766 | 0.76558 | 0.2308 | 2.673 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1008 | 1.066
2010-04-10 | 31 | 23.2033 | 8.3175 | 31.5208 | 1.7283 | 0.76558 | 0.23433 | 2.7283 | 8.655% | 9.209% | 6.223% | 1.0948 | 1.1014 | 1.0664
2010-04-10 | 32 | 22.9597 | 8.2252 | 31.1848 | 1.6917 | 0.76558 | 0.23183 | 2.6891 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-04-10 | 33 | 23.6206 | 8.5458 | 32.1664 | 1.7999 | 0.76558 | 0.23913 | 2.8046 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-04-10 | 34 | 24.4956 | 8.5663 | 33.0618 | 1.9015 | 0.76558 | 0.24579 | 2.9128 | 8.81% | 9.374% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-04-10 | 35 | 25.845 | 9.1439 | 34.989 | 2.1296 | 0.76558 | 0.26011 | 3.1553 | 9.018% | 9.595% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-04-10 | 36 | 28.0024 | 10.3556 | 38.3579 | 2.5594 | 0.76558 | 0.28516 | 3.6102 | 9.412% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-04-10 | 37 | 30.4443 | 11.5077 | 41.952 | 3.0615 | 0.76558 | 0.31188 | 4.139 | 9.866% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-04-10 | 38 | 32.8509 | 12.1396 | 44.9905 | 3.5211 | 0.76558 | 0.33446 | 4.6211 | 10.27% | 10.93% | 7.385% | 1.1145 | 1.1227 | 1.0797
2010-04-10 | 39 | 33.3689 | 11.9182 | 45.2871 | 3.5677 | 0.76558 | 0.33667 | 4.6699 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-04-10 | 40 | 32.5644 | 11.298 | 43.8624 | 3.3467 | 0.76558 | 0.32608 | 4.4384 | 10.12% | 10.77% | 7.275% | 1.1126 | 1.1207 | 1.0785
2010-04-10 | 41 | 32.2494 | 11.0538 | 43.3032 | 3.2619 | 0.76558 | 0.32192 | 4.3494 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-04-10 | 42 | 31.6178 | 10.9227 | 42.5404 | 3.148 | 0.76558 | 0.31625 | 4.2299 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-04-10 | 43 | 30.3814 | 10.2668 | 40.6482 | 2.8742 | 0.76558 | 0.30218 | 3.942 | 9.698% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-04-10 | 44 | 28.8162 | 9.7705 | 38.5868 | 2.5901 | 0.76558 | 0.28686 | 3.6425 | 9.44% | 10.04% | 6.787% | 1.1042 | 1.1117 | 1.0728
2010-04-10 | 45 | 26.7346 | 8.8805 | 35.6152 | 2.2065 | 0.76558 | 0.26477 | 3.2369 | 9.088% | 9.67% | 6.535% | 1.1 | 1.1071 | 1.0699
2010-04-10 | 46 | 24.2916 | 7.7901 | 32.0818 | 1.7904 | 0.76558 | 0.2385 | 2.7945 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1021 | 1.0668
2010-04-10 | 47 | 23.0129 | 7.423 | 30.4359 | 1.6114 | 0.76558 | 0.22626 | 2.6033 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-04-10 | 48 | 21.6914 | 7.6094 | 29.3007 | 1.4935 | 0.76558 | 0.21783 | 2.4769 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-04-11 | 1 | 20.4275 | 6.9133 | 27.3408 | 1.3003 | 0.76558 | 0.20325 | 2.2692 | 8.3% | 8.831% | 5.967% | 1.0905 | 1.0969 | 1.0635
2010-04-11 | 2 | 20.3572 | 6.3671 | 26.7243 | 1.2424 | 0.76558 | 0.19867 | 2.2066 | 8.257% | 8.785% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-04-11 | 3 | 19.0763 | 6.2496 | 25.3259 | 1.1157 | 0.76558 | 0.18828 | 2.0696 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2010-04-11 | 4 | 18.0571 | 5.9699 | 24.027 | 1.0042 | 0.76558 | 0.17862 | 1.9484 | 8.109% | 8.628% | 5.831% | 1.0882 | 1.0944 | 1.0619
2010-04-11 | 5 | 17.6111 | 5.7732 | 23.3843 | 0.95123 | 0.76558 | 0.17384 | 1.8906 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-11 | 6 | 17.5684 | 5.7551 | 23.3235 | 0.94629 | 0.76558 | 0.17339 | 1.8853 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-04-11 | 7 | 17.2528 | 5.6396 | 22.8924 | 0.91163 | 0.76558 | 0.17019 | 1.8474 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-11 | 8 | 16.9798 | 5.7427 | 22.7225 | 0.89815 | 0.76558 | 0.16892 | 1.8326 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-11 | 9 | 17.0529 | 5.8572 | 22.9101 | 0.91304 | 0.76558 | 0.17032 | 1.8489 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-04-11 | 10 | 17.1958 | 5.9661 | 23.1619 | 0.93322 | 0.76558 | 0.17219 | 1.871 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-04-11 | 11 | 17.744 | 6.1037 | 23.8477 | 0.9893 | 0.76558 | 0.17729 | 1.9322 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-04-11 | 12 | 17.9869 | 6.3748 | 24.3617 | 1.0324 | 0.76558 | 0.18111 | 1.9791 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-04-11 | 13 | 18.9194 | 6.6831 | 25.6026 | 1.1403 | 0.76558 | 0.19033 | 2.0962 | 8.187% | 8.711% | 5.887% | 1.0892 | 1.0954 | 1.0625
2010-04-11 | 14 | 20.4551 | 7.3501 | 27.8052 | 1.3449 | 0.76558 | 0.20671 | 2.3172 | 8.334% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-04-11 | 15 | 22.5816 | 8.4876 | 31.0692 | 1.6792 | 0.76558 | 0.23097 | 2.6757 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-04-11 | 16 | 24.3614 | 10.0138 | 34.3751 | 2.0555 | 0.76558 | 0.25555 | 3.0767 | 8.95% | 9.523% | 6.435% | 1.0983 | 1.1053 | 1.0688
2010-04-11 | 17 | 27.2473 | 11.5508 | 38.798 | 2.6185 | 0.76558 | 0.28843 | 3.6725 | 9.466% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-04-11 | 18 | 29.6325 | 12.4162 | 42.0487 | 3.0757 | 0.76558 | 0.3126 | 4.1538 | 9.879% | 10.51% | 7.103% | 1.1096 | 1.1175 | 1.0765
2010-04-11 | 19 | 31.0324 | 13.0356 | 44.0679 | 3.3782 | 0.76558 | 0.32761 | 4.4713 | 10.15% | 10.8% | 7.295% | 1.1129 | 1.121 | 1.0787
2010-04-11 | 20 | 30.8297 | 12.9201 | 43.7498 | 3.3296 | 0.76558 | 0.32524 | 4.4204 | 10.1% | 10.75% | 7.265% | 1.1124 | 1.1205 | 1.0783
2010-04-11 | 21 | 31.2616 | 12.5417 | 43.8033 | 3.3377 | 0.76558 | 0.32564 | 4.4289 | 10.11% | 10.76% | 7.27% | 1.1125 | 1.1205 | 1.0784
2010-04-11 | 22 | 29.7216 | 11.5439 | 41.2656 | 2.9622 | 0.76558 | 0.30677 | 4.0345 | 9.777% | 10.4% | 7.03% | 1.1084 | 1.1161 | 1.0756
2010-04-11 | 23 | 27.7962 | 10.3529 | 38.149 | 2.5316 | 0.76558 | 0.2836 | 3.5808 | 9.386% | 9.987% | 6.749% | 1.1036 | 1.111 | 1.0724
2010-04-11 | 24 | 26.0581 | 9.8387 | 35.8968 | 2.2415 | 0.76558 | 0.26686 | 3.274 | 9.121% | 9.704% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-04-11 | 25 | 24.6795 | 9.4731 | 34.1526 | 2.029 | 0.76558 | 0.25389 | 3.0485 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-04-11 | 26 | 23.6156 | 9.1105 | 32.7261 | 1.863 | 0.76558 | 0.24329 | 2.8719 | 8.776% | 9.337% | 6.31% | 1.0962 | 1.103 | 1.0673
2010-04-11 | 27 | 23.4452 | 9.2075 | 32.6527 | 1.8547 | 0.76558 | 0.24274 | 2.863 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-04-11 | 28 | 23.3873 | 9.1738 | 32.5611 | 1.8443 | 0.76558 | 0.24206 | 2.8519 | 8.759% | 9.319% | 6.298% | 1.096 | 1.1028 | 1.0672
2010-04-11 | 29 | 22.7849 | 8.8215 | 31.6064 | 1.7377 | 0.76558 | 0.23497 | 2.7383 | 8.664% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-04-11 | 30 | 22.1823 | 8.1853 | 30.3677 | 1.6042 | 0.76558 | 0.22576 | 2.5955 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-04-11 | 31 | 22.9152 | 7.9062 | 30.8214 | 1.6525 | 0.76558 | 0.22913 | 2.6472 | 8.589% | 9.139% | 6.175% | 1.094 | 1.1006 | 1.0658
2010-04-11 | 32 | 23.1165 | 8.0704 | 31.1869 | 1.6919 | 0.76558 | 0.23185 | 2.6893 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-04-11 | 33 | 23.3481 | 8.4799 | 31.8279 | 1.7622 | 0.76558 | 0.23661 | 2.7644 | 8.685% | 9.241% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-04-11 | 34 | 23.8341 | 8.5133 | 32.3475 | 1.8202 | 0.76558 | 0.24048 | 2.8262 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-04-11 | 35 | 24.9823 | 9.1212 | 34.1035 | 2.0232 | 0.76558 | 0.25353 | 3.0423 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2010-04-11 | 36 | 26.5774 | 10.0731 | 36.6504 | 2.3366 | 0.76558 | 0.27246 | 3.3747 | 9.208% | 9.797% | 6.62% | 1.1014 | 1.1086 | 1.0709
2010-04-11 | 37 | 28.5586 | 10.9029 | 39.4615 | 2.7088 | 0.76558 | 0.29336 | 3.7678 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-04-11 | 38 | 30.5084 | 11.4172 | 41.9255 | 3.0577 | 0.76558 | 0.31168 | 4.1349 | 9.863% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-04-11 | 39 | 30.5528 | 11.0967 | 41.6495 | 3.0175 | 0.76558 | 0.30963 | 4.0927 | 9.827% | 10.46% | 7.065% | 1.109 | 1.1168 | 1.076
2010-04-11 | 40 | 29.8348 | 10.7849 | 40.6197 | 2.8702 | 0.76558 | 0.30197 | 3.9377 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2010-04-11 | 41 | 29.2194 | 10.0987 | 39.3181 | 2.6892 | 0.76558 | 0.2923 | 3.7471 | 9.53% | 10.14% | 6.852% | 1.1053 | 1.1128 | 1.0736
2010-04-11 | 42 | 28.6724 | 9.6708 | 38.3432 | 2.5575 | 0.76558 | 0.28505 | 3.6081 | 9.41% | 10.01% | 6.766% | 1.1039 | 1.1113 | 1.0726
2010-04-11 | 43 | 27.6506 | 9.2886 | 36.9392 | 2.3736 | 0.76558 | 0.27461 | 3.4138 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-04-11 | 44 | 26.1009 | 8.5867 | 34.6876 | 2.0931 | 0.76558 | 0.25787 | 3.1165 | 8.985% | 9.56% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-04-11 | 45 | 24.4911 | 7.9302 | 32.4214 | 1.8285 | 0.76558 | 0.24102 | 2.8351 | 8.745% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-04-11 | 46 | 22.624 | 7.1574 | 29.7814 | 1.5429 | 0.76558 | 0.2214 | 2.5298 | 8.495% | 9.038% | 6.108% | 1.0928 | 1.0994 | 1.065
2010-04-11 | 47 | 21.8074 | 7.1931 | 29.0004 | 1.463 | 0.76558 | 0.21559 | 2.4442 | 8.428% | 8.967% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-04-11 | 48 | 20.6596 | 7.269 | 27.9287 | 1.3569 | 0.76558 | 0.20763 | 2.3301 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-04-12 | 1 | 18.9772 | 6.2727 | 25.2498 | 1.1091 | 0.76558 | 0.18771 | 2.0623 | 8.168% | 8.69% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-04-12 | 2 | 18.9191 | 5.8782 | 24.7973 | 1.0697 | 0.76558 | 0.18435 | 2.0196 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-04-12 | 3 | 17.671 | 5.6913 | 23.3623 | 0.94944 | 0.76558 | 0.17368 | 1.8887 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-12 | 4 | 16.5352 | 5.3999 | 21.9351 | 0.83698 | 0.76558 | 0.16307 | 1.7656 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-12 | 5 | 16.0466 | 5.144 | 21.1906 | 0.78113 | 0.76558 | 0.15753 | 1.7042 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 6 | 15.8486 | 4.949 | 20.7976 | 0.75242 | 0.76558 | 0.15461 | 1.6726 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 7 | 15.8173 | 4.9692 | 20.7865 | 0.75162 | 0.76558 | 0.15453 | 1.6717 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 8 | 15.5282 | 5.0257 | 20.5538 | 0.73489 | 0.76558 | 0.1528 | 1.6533 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 9 | 15.5847 | 4.902 | 20.4867 | 0.7301 | 0.76558 | 0.1523 | 1.648 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 10 | 15.9727 | 4.9506 | 20.9232 | 0.76154 | 0.76558 | 0.15555 | 1.6827 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 11 | 16.4607 | 5.1839 | 21.6445 | 0.81495 | 0.76558 | 0.16091 | 1.7414 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-12 | 12 | 16.9207 | 5.2892 | 22.2099 | 0.85808 | 0.76558 | 0.16511 | 1.7888 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-12 | 13 | 17.8387 | 5.5534 | 23.3921 | 0.95186 | 0.76558 | 0.1739 | 1.8913 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-12 | 14 | 18.8587 | 5.9951 | 24.8538 | 1.0745 | 0.76558 | 0.18477 | 2.0249 | 8.147% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-04-12 | 15 | 20.8407 | 6.7408 | 27.5815 | 1.3233 | 0.76558 | 0.20504 | 2.294 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-04-12 | 16 | 22.4368 | 7.8942 | 30.3309 | 1.6003 | 0.76558 | 0.22548 | 2.5914 | 8.544% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-04-12 | 17 | 25.0368 | 9.3197 | 34.3565 | 2.0533 | 0.76558 | 0.25541 | 3.0743 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-04-12 | 18 | 26.8168 | 10.7764 | 37.5932 | 2.4584 | 0.76558 | 0.27947 | 3.5035 | 9.319% | 9.916% | 6.701% | 1.1028 | 1.1101 | 1.0718
2010-04-12 | 19 | 28.1388 | 11.3997 | 39.5384 | 2.7194 | 0.76558 | 0.29393 | 3.7789 | 9.558% | 10.17% | 6.872% | 1.1057 | 1.1132 | 1.0738
2010-04-12 | 20 | 28.0949 | 11.4776 | 39.5724 | 2.7241 | 0.76558 | 0.29419 | 3.7838 | 9.562% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-04-12 | 21 | 28.2688 | 11.1691 | 39.4379 | 2.7056 | 0.76558 | 0.29319 | 3.7644 | 9.545% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-04-12 | 22 | 27.2188 | 10.9878 | 38.2066 | 2.5393 | 0.76558 | 0.28403 | 3.5889 | 9.393% | 9.995% | 6.754% | 1.1037 | 1.111 | 1.0724
2010-04-12 | 23 | 25.7107 | 10.0645 | 35.7753 | 2.2264 | 0.76558 | 0.26596 | 3.2579 | 9.107% | 9.689% | 6.548% | 1.1002 | 1.1073 | 1.0701
2010-04-12 | 24 | 24.4188 | 9.3106 | 33.7294 | 1.979 | 0.76558 | 0.25075 | 2.9954 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1043 | 1.0682
2010-04-12 | 25 | 23.0968 | 8.6478 | 31.7446 | 1.753 | 0.76558 | 0.23599 | 2.7545 | 8.677% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-04-12 | 26 | 22.1928 | 7.7914 | 29.9842 | 1.5639 | 0.76558 | 0.22291 | 2.5524 | 8.513% | 9.057% | 6.121% | 1.093 | 1.0996 | 1.0652
2010-04-12 | 27 | 22.0047 | 8.1334 | 30.1382 | 1.58 | 0.76558 | 0.22405 | 2.5697 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-04-12 | 28 | 21.5307 | 8.0004 | 29.5311 | 1.517 | 0.76558 | 0.21954 | 2.5021 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-04-12 | 29 | 20.9706 | 7.5711 | 28.5417 | 1.4171 | 0.76558 | 0.21218 | 2.3948 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-04-12 | 30 | 20.6407 | 7.0631 | 27.7038 | 1.3351 | 0.76558 | 0.20595 | 2.3066 | 8.326% | 8.859% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-04-12 | 31 | 20.9264 | 6.8895 | 27.8159 | 1.3459 | 0.76558 | 0.20679 | 2.3183 | 8.334% | 8.868% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-04-12 | 32 | 20.6404 | 6.947 | 27.5874 | 1.3239 | 0.76558 | 0.20509 | 2.2946 | 8.317% | 8.85% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-04-12 | 33 | 20.5543 | 7.2097 | 27.7639 | 1.3409 | 0.76558 | 0.2064 | 2.3129 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-04-12 | 34 | 21.2722 | 7.2498 | 28.522 | 1.4151 | 0.76558 | 0.21204 | 2.3927 | 8.389% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-04-12 | 35 | 22.6083 | 7.7043 | 30.3125 | 1.5984 | 0.76558 | 0.22535 | 2.5893 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-04-12 | 36 | 24.6185 | 9.163 | 33.7815 | 1.9852 | 0.76558 | 0.25114 | 3.0019 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2010-04-12 | 37 | 26.7024 | 10.1089 | 36.8113 | 2.3572 | 0.76558 | 0.27366 | 3.3964 | 9.227% | 9.817% | 6.634% | 1.1016 | 1.1089 | 1.0711
2010-04-12 | 38 | 28.6264 | 10.8832 | 39.5096 | 2.7154 | 0.76558 | 0.29372 | 3.7747 | 9.554% | 10.17% | 6.869% | 1.1056 | 1.1132 | 1.0738
2010-04-12 | 39 | 28.5405 | 10.6881 | 39.2286 | 2.677 | 0.76558 | 0.29163 | 3.7342 | 9.519% | 10.13% | 6.844% | 1.1052 | 1.1127 | 1.0735
2010-04-12 | 40 | 27.2905 | 10.195 | 37.4854 | 2.4443 | 0.76558 | 0.27867 | 3.4886 | 9.306% | 9.902% | 6.691% | 1.1026 | 1.1099 | 1.0717
2010-04-12 | 41 | 26.9464 | 9.818 | 36.7645 | 2.3512 | 0.76558 | 0.27331 | 3.3901 | 9.221% | 9.811% | 6.63% | 1.1016 | 1.1088 | 1.071
2010-04-12 | 42 | 26.9024 | 9.4742 | 36.3767 | 2.3019 | 0.76558 | 0.27043 | 3.3379 | 9.176% | 9.763% | 6.597% | 1.101 | 1.1082 | 1.0706
2010-04-12 | 43 | 25.9985 | 9.0043 | 35.0027 | 2.1313 | 0.76558 | 0.26021 | 3.1571 | 9.019% | 9.597% | 6.485% | 1.0991 | 1.1062 | 1.0693
2010-04-12 | 44 | 24.3465 | 8.4435 | 32.79 | 1.8703 | 0.76558 | 0.24376 | 2.8797 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-04-12 | 45 | 22.4206 | 7.9285 | 30.3492 | 1.6022 | 0.76558 | 0.22562 | 2.5934 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-04-12 | 46 | 20.7846 | 7.1425 | 27.9272 | 1.3567 | 0.76558 | 0.20761 | 2.3299 | 8.343% | 8.877% | 5.998% | 1.091 | 1.0974 | 1.0638
2010-04-12 | 47 | 19.9785 | 7.0898 | 27.0683 | 1.2746 | 0.76558 | 0.20123 | 2.2414 | 8.28% | 8.81% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-04-12 | 48 | 18.8167 | 7.2936 | 26.1103 | 1.1859 | 0.76558 | 0.19411 | 2.1456 | 8.217% | 8.743% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-04-13 | 1 | 17.1066 | 6.3784 | 23.485 | 0.95944 | 0.76558 | 0.17459 | 1.8996 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-04-13 | 2 | 16.7765 | 6.0193 | 22.7958 | 0.90395 | 0.76558 | 0.16947 | 1.839 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-04-13 | 3 | 15.7704 | 5.6174 | 21.3878 | 0.79573 | 0.76558 | 0.159 | 1.7203 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-13 | 4 | 15.4684 | 5.2405 | 20.7089 | 0.74602 | 0.76558 | 0.15395 | 1.6655 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-13 | 5 | 14.6923 | 5.0668 | 19.7592 | 0.67916 | 0.76558 | 0.14689 | 1.5916 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-04-13 | 6 | 14.2622 | 5.0369 | 19.2991 | 0.6479 | 0.76558 | 0.14347 | 1.557 | 8.067% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-04-13 | 7 | 14.2762 | 5.0257 | 19.3019 | 0.64809 | 0.76558 | 0.14349 | 1.5572 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-04-13 | 8 | 14.3482 | 4.9465 | 19.2947 | 0.6476 | 0.76558 | 0.14344 | 1.5566 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-04-13 | 9 | 14.5504 | 5.0855 | 19.6359 | 0.67071 | 0.76558 | 0.14598 | 1.5823 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-13 | 10 | 14.4201 | 4.9227 | 19.3428 | 0.65084 | 0.76558 | 0.1438 | 1.5602 | 8.066% | 8.582% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-04-13 | 11 | 14.7801 | 5.0536 | 19.8336 | 0.68429 | 0.76558 | 0.14745 | 1.5973 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-13 | 12 | 15.5401 | 5.1558 | 20.6958 | 0.74508 | 0.76558 | 0.15386 | 1.6645 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-13 | 13 | 16.69 | 5.5235 | 22.2135 | 0.85836 | 0.76558 | 0.16514 | 1.7891 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-13 | 14 | 17.308 | 5.9676 | 23.2756 | 0.9424 | 0.76558 | 0.17303 | 1.881 | 8.081% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-13 | 15 | 18.9159 | 6.6626 | 25.5785 | 1.1381 | 0.76558 | 0.19015 | 2.0938 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-04-13 | 16 | 20.956 | 7.8235 | 28.7795 | 1.4408 | 0.76558 | 0.21395 | 2.4203 | 8.41% | 8.948% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-04-13 | 17 | 23.1399 | 9.1225 | 32.2624 | 1.8106 | 0.76558 | 0.23984 | 2.816 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-04-13 | 18 | 25.524 | 10.106 | 35.63 | 2.2083 | 0.76558 | 0.26488 | 3.2388 | 9.09% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-04-13 | 19 | 27.5482 | 10.587 | 38.1352 | 2.5298 | 0.76558 | 0.2835 | 3.5789 | 9.385% | 9.985% | 6.748% | 1.1036 | 1.1109 | 1.0724
2010-04-13 | 20 | 27.3622 | 10.7021 | 38.0643 | 2.5204 | 0.76558 | 0.28297 | 3.569 | 9.376% | 9.976% | 6.741% | 1.1035 | 1.1108 | 1.0723
2010-04-13 | 21 | 28.2683 | 10.4668 | 38.7351 | 2.61 | 0.76558 | 0.28796 | 3.6636 | 9.458% | 10.06% | 6.8% | 1.1045 | 1.1119 | 1.073
2010-04-13 | 22 | 27.7784 | 10.2469 | 38.0253 | 2.5152 | 0.76558 | 0.28269 | 3.5635 | 9.371% | 9.971% | 6.738% | 1.1034 | 1.1108 | 1.0722
2010-04-13 | 23 | 26.4427 | 9.8428 | 36.2855 | 2.2903 | 0.76558 | 0.26975 | 3.3257 | 9.165% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0705
2010-04-13 | 24 | 25.5107 | 9.533 | 35.0437 | 2.1363 | 0.76558 | 0.26052 | 3.1624 | 9.024% | 9.602% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-04-13 | 25 | 24.2306 | 9.4556 | 33.6862 | 1.974 | 0.76558 | 0.25043 | 2.99 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-04-13 | 26 | 23.1965 | 8.9783 | 32.1748 | 1.8008 | 0.76558 | 0.23919 | 2.8056 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-04-13 | 27 | 22.7524 | 8.9915 | 31.7439 | 1.7529 | 0.76558 | 0.23599 | 2.7545 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-04-13 | 28 | 22.2924 | 8.7154 | 31.0078 | 1.6725 | 0.76558 | 0.23052 | 2.6686 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-04-13 | 29 | 21.5304 | 8.2013 | 29.7317 | 1.5377 | 0.76558 | 0.22103 | 2.5243 | 8.49% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-04-13 | 30 | 20.9843 | 7.7999 | 28.7842 | 1.4413 | 0.76558 | 0.21398 | 2.4208 | 8.41% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-04-13 | 31 | 20.8703 | 7.6066 | 28.4769 | 1.4107 | 0.76558 | 0.2117 | 2.3879 | 8.386% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-04-13 | 32 | 20.8984 | 7.5621 | 28.4605 | 1.409 | 0.76558 | 0.21158 | 2.3862 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-04-13 | 33 | 21.0843 | 7.9339 | 29.0182 | 1.4648 | 0.76558 | 0.21573 | 2.4461 | 8.43% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-04-13 | 34 | 21.3582 | 8.0967 | 29.4549 | 1.5092 | 0.76558 | 0.21897 | 2.4938 | 8.466% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-04-13 | 35 | 22.1923 | 8.6316 | 30.8239 | 1.6528 | 0.76558 | 0.22915 | 2.6475 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-04-13 | 36 | 23.9004 | 9.8393 | 33.7397 | 1.9802 | 0.76558 | 0.25082 | 2.9966 | 8.882% | 9.45% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-04-13 | 37 | 25.8545 | 10.6744 | 36.5288 | 2.3212 | 0.76558 | 0.27156 | 3.3583 | 9.194% | 9.782% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-04-13 | 38 | 28.2385 | 11.0625 | 39.301 | 2.6868 | 0.76558 | 0.29217 | 3.7446 | 9.528% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0735
2010-04-13 | 39 | 28.2827 | 10.8257 | 39.1084 | 2.6606 | 0.76558 | 0.29074 | 3.7169 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-04-13 | 40 | 27.5928 | 10.3161 | 37.9088 | 2.4999 | 0.76558 | 0.28182 | 3.5473 | 9.357% | 9.956% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-04-13 | 41 | 27.2047 | 9.7657 | 36.9704 | 2.3776 | 0.76558 | 0.27484 | 3.418 | 9.245% | 9.837% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-04-13 | 42 | 26.5728 | 9.2386 | 35.8114 | 2.2309 | 0.76558 | 0.26623 | 3.2627 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1073 | 1.0701
2010-04-13 | 43 | 24.9648 | 8.7829 | 33.7477 | 1.9812 | 0.76558 | 0.25088 | 2.9976 | 8.882% | 9.451% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-04-13 | 44 | 23.8289 | 8.0804 | 31.9093 | 1.7712 | 0.76558 | 0.23722 | 2.774 | 8.693% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-04-13 | 45 | 22.0768 | 7.1813 | 29.2581 | 1.4891 | 0.76558 | 0.21751 | 2.4722 | 8.45% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-04-13 | 46 | 20.0948 | 6.5552 | 26.65 | 1.2355 | 0.76558 | 0.19812 | 2.1992 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0963 | 1.0631
2010-04-13 | 47 | 19.0747 | 6.4621 | 25.5368 | 1.1344 | 0.76558 | 0.18984 | 2.0898 | 8.184% | 8.707% | 5.884% | 1.0891 | 1.0954 | 1.0625
2010-04-13 | 48 | 17.6388 | 6.5461 | 24.1848 | 1.0175 | 0.76558 | 0.17979 | 1.9628 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-04-14 | 1 | 16.0869 | 5.7398 | 21.8267 | 0.82872 | 0.76558 | 0.16226 | 1.7566 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-14 | 2 | 15.9429 | 5.3006 | 21.2435 | 0.78503 | 0.76558 | 0.15793 | 1.7085 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-14 | 3 | 15.3409 | 5.1223 | 20.4632 | 0.72842 | 0.76558 | 0.15213 | 1.6461 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-14 | 4 | 14.443 | 4.9256 | 19.3686 | 0.65257 | 0.76558 | 0.14399 | 1.5621 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-14 | 5 | 13.811 | 4.8588 | 18.6698 | 0.60634 | 0.76558 | 0.13879 | 1.5107 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-04-14 | 6 | 13.653 | 4.6777 | 18.3307 | 0.58451 | 0.76558 | 0.13627 | 1.4864 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-04-14 | 7 | 13.911 | 4.77 | 18.681 | 0.60707 | 0.76558 | 0.13888 | 1.5115 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-04-14 | 8 | 13.703 | 4.7637 | 18.4667 | 0.59322 | 0.76558 | 0.13728 | 1.4961 | 8.101% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-04-14 | 9 | 13.8751 | 4.7443 | 18.6194 | 0.60307 | 0.76558 | 0.13842 | 1.5071 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-04-14 | 10 | 14.0471 | 4.7928 | 18.8399 | 0.61744 | 0.76558 | 0.14006 | 1.5231 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-14 | 11 | 14.6072 | 5.0183 | 19.6254 | 0.67 | 0.76558 | 0.1459 | 1.5815 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-14 | 12 | 15.6571 | 5.5231 | 21.1802 | 0.78036 | 0.76558 | 0.15746 | 1.7034 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-14 | 13 | 17.2792 | 6.2067 | 23.4859 | 0.95951 | 0.76558 | 0.1746 | 1.8997 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-04-14 | 14 | 19.3191 | 7.6475 | 26.9666 | 1.265 | 0.76558 | 0.20047 | 2.231 | 8.273% | 8.803% | 5.949% | 1.0902 | 1.0965 | 1.0632
2010-04-14 | 15 | 22.795 | 9.3776 | 32.1726 | 1.8006 | 0.76558 | 0.23918 | 2.8053 | 8.72% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-04-14 | 16 | 25.8549 | 10.5644 | 36.4194 | 2.3073 | 0.76558 | 0.27075 | 3.3436 | 9.181% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-04-14 | 17 | 27.865 | 11.5323 | 39.3974 | 2.7 | 0.76558 | 0.29288 | 3.7585 | 9.54% | 10.15% | 6.859% | 1.1055 | 1.113 | 1.0736
2010-04-14 | 18 | 28.929 | 11.5947 | 40.5237 | 2.8566 | 0.76558 | 0.30126 | 3.9235 | 9.682% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-04-14 | 19 | 28.813 | 11.4789 | 40.2919 | 2.824 | 0.76558 | 0.29953 | 3.8891 | 9.652% | 10.27% | 6.94% | 1.1068 | 1.1145 | 1.0746
2010-04-14 | 20 | 28.3389 | 10.9797 | 39.3186 | 2.6892 | 0.76558 | 0.2923 | 3.7471 | 9.53% | 10.14% | 6.852% | 1.1053 | 1.1128 | 1.0736
2010-04-14 | 21 | 28.0944 | 10.5398 | 38.6342 | 2.5964 | 0.76558 | 0.28721 | 3.6492 | 9.446% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-04-14 | 22 | 27.061 | 10.2786 | 37.3396 | 2.4253 | 0.76558 | 0.27759 | 3.4685 | 9.289% | 9.884% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-04-14 | 23 | 25.783 | 9.6976 | 35.4806 | 2.1899 | 0.76558 | 0.26377 | 3.2192 | 9.073% | 9.654% | 6.524% | 1.0998 | 1.1069 | 1.0698
2010-04-14 | 24 | 24.419 | 9.6873 | 34.1064 | 2.0235 | 0.76558 | 0.25355 | 3.0426 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2010-04-14 | 25 | 23.4795 | 9.4949 | 32.9744 | 1.8914 | 0.76558 | 0.24514 | 2.9021 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2010-04-14 | 26 | 22.6564 | 8.6162 | 31.2727 | 1.7012 | 0.76558 | 0.23248 | 2.6993 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-04-14 | 27 | 22.3124 | 8.4434 | 30.7558 | 1.6455 | 0.76558 | 0.22864 | 2.6397 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-04-14 | 28 | 22.1723 | 8.301 | 30.4732 | 1.6154 | 0.76558 | 0.22654 | 2.6075 | 8.557% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-04-14 | 29 | 21.5686 | 7.9976 | 29.5661 | 1.5206 | 0.76558 | 0.2198 | 2.506 | 8.476% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-04-14 | 30 | 21.1799 | 7.8332 | 29.0131 | 1.4643 | 0.76558 | 0.21569 | 2.4455 | 8.429% | 8.969% | 6.061% | 1.092 | 1.0985 | 1.0645
2010-04-14 | 31 | 21.5675 | 7.5711 | 29.1386 | 1.477 | 0.76558 | 0.21662 | 2.4592 | 8.44% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-04-14 | 32 | 21.8116 | 7.6278 | 29.4393 | 1.5076 | 0.76558 | 0.21886 | 2.4921 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-04-14 | 33 | 21.6829 | 7.9218 | 29.6046 | 1.5246 | 0.76558 | 0.22008 | 2.5103 | 8.479% | 9.022% | 6.097% | 1.0926 | 1.0992 | 1.0649
2010-04-14 | 34 | 22.2738 | 8.1879 | 30.4616 | 1.6141 | 0.76558 | 0.22646 | 2.6062 | 8.556% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2010-04-14 | 35 | 23.6238 | 8.7603 | 32.3841 | 1.8243 | 0.76558 | 0.24075 | 2.8306 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-04-14 | 36 | 25.3735 | 9.9967 | 35.3702 | 2.1763 | 0.76558 | 0.26295 | 3.2048 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-04-14 | 37 | 28.26 | 10.9308 | 39.1908 | 2.6718 | 0.76558 | 0.29135 | 3.7287 | 9.514% | 10.12% | 6.841% | 1.1051 | 1.1126 | 1.0734
2010-04-14 | 38 | 30.543 | 11.4097 | 41.9526 | 3.0616 | 0.76558 | 0.31188 | 4.1391 | 9.866% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-04-14 | 39 | 30.3416 | 11.0535 | 41.3951 | 2.9808 | 0.76558 | 0.30774 | 4.0541 | 9.794% | 10.42% | 7.042% | 1.1086 | 1.1163 | 1.0758
2010-04-14 | 40 | 29.4075 | 10.4709 | 39.8784 | 2.7664 | 0.76558 | 0.29646 | 3.8284 | 9.6% | 10.21% | 6.903% | 1.1062 | 1.1138 | 1.0741
2010-04-14 | 41 | 29.4386 | 9.8429 | 39.2815 | 2.6842 | 0.76558 | 0.29202 | 3.7418 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-04-14 | 42 | 28.8644 | 9.4913 | 38.3557 | 2.5591 | 0.76558 | 0.28514 | 3.6099 | 9.412% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-04-14 | 43 | 27.3255 | 9.141 | 36.4665 | 2.3132 | 0.76558 | 0.2711 | 3.3499 | 9.186% | 9.774% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-04-14 | 44 | 25.9311 | 8.5961 | 34.5272 | 2.0738 | 0.76558 | 0.25668 | 3.096 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-14 | 45 | 23.7902 | 8.0757 | 31.8658 | 1.7664 | 0.76558 | 0.23689 | 2.7689 | 8.689% | 9.245% | 6.247% | 1.0952 | 1.1019 | 1.0666
2010-04-14 | 46 | 21.5504 | 6.9954 | 28.5458 | 1.4175 | 0.76558 | 0.21221 | 2.3953 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-04-14 | 47 | 20.2293 | 6.5848 | 26.814 | 1.2507 | 0.76558 | 0.19934 | 2.2156 | 8.263% | 8.792% | 5.941% | 1.0901 | 1.0964 | 1.0632
2010-04-14 | 48 | 18.4639 | 6.5834 | 25.0473 | 1.0913 | 0.76558 | 0.1862 | 2.0431 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-04-15 | 1 | 16.6959 | 5.6477 | 22.3436 | 0.86844 | 0.76558 | 0.16611 | 1.8001 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-04-15 | 2 | 16.3947 | 5.243 | 21.6377 | 0.81444 | 0.76558 | 0.16086 | 1.7409 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-15 | 3 | 15.7195 | 5.0201 | 20.7396 | 0.74823 | 0.76558 | 0.15418 | 1.668 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-15 | 4 | 15.058 | 4.9556 | 20.0136 | 0.69676 | 0.76558 | 0.14878 | 1.6111 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-15 | 5 | 14.515 | 4.9116 | 19.4266 | 0.65649 | 0.76558 | 0.14442 | 1.5665 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-04-15 | 6 | 14.2124 | 4.7264 | 18.9389 | 0.62394 | 0.76558 | 0.14079 | 1.5303 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-04-15 | 7 | 14.542 | 4.6589 | 19.2008 | 0.64132 | 0.76558 | 0.14274 | 1.5496 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-04-15 | 8 | 14.529 | 4.6215 | 19.1505 | 0.63796 | 0.76558 | 0.14237 | 1.5459 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-04-15 | 9 | 14.341 | 4.5105 | 18.8515 | 0.6182 | 0.76558 | 0.14014 | 1.5239 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-04-15 | 10 | 14.4117 | 4.6153 | 19.027 | 0.62976 | 0.76558 | 0.14145 | 1.5368 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-04-15 | 11 | 14.7421 | 4.8382 | 19.5803 | 0.66692 | 0.76558 | 0.14556 | 1.5781 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-04-15 | 12 | 15.7929 | 5.2598 | 21.0527 | 0.77099 | 0.76558 | 0.15651 | 1.6931 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-15 | 13 | 17.4859 | 5.9837 | 23.4696 | 0.95818 | 0.76558 | 0.17448 | 1.8982 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-04-15 | 14 | 19.8279 | 7.2855 | 27.1134 | 1.2788 | 0.76558 | 0.20156 | 2.2459 | 8.284% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-04-15 | 15 | 22.8468 | 8.9774 | 31.8242 | 1.7618 | 0.76558 | 0.23659 | 2.7639 | 8.685% | 9.241% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-04-15 | 16 | 25.5321 | 10.3301 | 35.8622 | 2.2372 | 0.76558 | 0.2666 | 3.2694 | 9.117% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-04-15 | 17 | 27.9723 | 11.1684 | 39.1407 | 2.665 | 0.76558 | 0.29098 | 3.7215 | 9.508% | 10.12% | 6.836% | 1.1051 | 1.1126 | 1.0734
2010-04-15 | 18 | 29.0658 | 11.8063 | 40.8721 | 2.9059 | 0.76558 | 0.30385 | 3.9754 | 9.726% | 10.35% | 6.993% | 1.1077 | 1.1154 | 1.0752
2010-04-15 | 19 | 29.7965 | 12.0729 | 41.8694 | 3.0495 | 0.76558 | 0.31126 | 4.1263 | 9.855% | 10.49% | 7.086% | 1.1093 | 1.1171 | 1.0763
2010-04-15 | 20 | 29.3384 | 12.0798 | 41.4183 | 2.9841 | 0.76558 | 0.30791 | 4.0576 | 9.797% | 10.42% | 7.044% | 1.1086 | 1.1164 | 1.0758
2010-04-15 | 21 | 29.4257 | 11.8516 | 41.2774 | 2.9639 | 0.76558 | 0.30686 | 4.0363 | 9.778% | 10.4% | 7.031% | 1.1084 | 1.1161 | 1.0756
2010-04-15 | 22 | 28.7086 | 11.8085 | 40.5171 | 2.8557 | 0.76558 | 0.30121 | 3.9225 | 9.681% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-04-15 | 23 | 27.6318 | 11.5549 | 39.1867 | 2.6712 | 0.76558 | 0.29132 | 3.7281 | 9.514% | 10.12% | 6.84% | 1.1051 | 1.1126 | 1.0734
2010-04-15 | 24 | 26.9409 | 11.4956 | 38.4365 | 2.5699 | 0.76558 | 0.28574 | 3.6213 | 9.421% | 10.02% | 6.774% | 1.104 | 1.1114 | 1.0727
2010-04-15 | 25 | 25.7745 | 11.4349 | 37.2094 | 2.4085 | 0.76558 | 0.27662 | 3.4507 | 9.274% | 9.867% | 6.668% | 1.1022 | 1.1095 | 1.0714
2010-04-15 | 26 | 25.2011 | 11.0606 | 36.2616 | 2.2873 | 0.76558 | 0.26957 | 3.3225 | 9.163% | 9.749% | 6.588% | 1.1009 | 1.108 | 1.0705
2010-04-15 | 27 | 25.2445 | 11.2037 | 36.4483 | 2.3109 | 0.76558 | 0.27096 | 3.3475 | 9.184% | 9.772% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-04-15 | 28 | 24.8854 | 10.9244 | 35.8098 | 2.2307 | 0.76558 | 0.26621 | 3.2625 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1073 | 1.0701
2010-04-15 | 29 | 23.794 | 10.4302 | 34.2241 | 2.0375 | 0.76558 | 0.25443 | 3.0575 | 8.934% | 9.506% | 6.423% | 1.0981 | 1.105 | 1.0686
2010-04-15 | 30 | 23.1056 | 10.3405 | 33.4461 | 1.9459 | 0.76558 | 0.24864 | 2.9601 | 8.85% | 9.417% | 6.364% | 1.0971 | 1.104 | 1.068
2010-04-15 | 31 | 22.7738 | 10.2721 | 33.0459 | 1.8996 | 0.76558 | 0.24567 | 2.9109 | 8.809% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-04-15 | 32 | 22.3856 | 10.0715 | 32.4571 | 1.8325 | 0.76558 | 0.24129 | 2.8394 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-04-15 | 33 | 22.3846 | 10.3488 | 32.7333 | 1.8639 | 0.76558 | 0.24334 | 2.8728 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-04-15 | 34 | 22.6446 | 10.5384 | 33.183 | 1.9154 | 0.76558 | 0.24669 | 2.9277 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-04-15 | 35 | 23.3193 | 10.754 | 34.0733 | 2.0196 | 0.76558 | 0.2533 | 3.0385 | 8.917% | 9.488% | 6.412% | 1.0979 | 1.1048 | 1.0685
2010-04-15 | 36 | 25.5011 | 11.8724 | 37.3735 | 2.4298 | 0.76558 | 0.27784 | 3.4732 | 9.293% | 9.888% | 6.682% | 1.1025 | 1.1097 | 1.0716
2010-04-15 | 37 | 28.547 | 12.8654 | 41.4124 | 2.9833 | 0.76558 | 0.30786 | 4.0567 | 9.796% | 10.42% | 7.043% | 1.1086 | 1.1164 | 1.0758
2010-04-15 | 38 | 30.1393 | 12.9851 | 43.1244 | 3.235 | 0.76558 | 0.32059 | 4.3212 | 10.02% | 10.66% | 7.205% | 1.1114 | 1.1193 | 1.0776
2010-04-15 | 39 | 29.7939 | 12.4403 | 42.2342 | 3.1029 | 0.76558 | 0.31397 | 4.1824 | 9.903% | 10.54% | 7.12% | 1.1099 | 1.1178 | 1.0767
2010-04-15 | 40 | 28.9487 | 11.8241 | 40.7728 | 2.8918 | 0.76558 | 0.30311 | 3.9605 | 9.714% | 10.34% | 6.984% | 1.1076 | 1.1153 | 1.0751
2010-04-15 | 41 | 28.5163 | 11.1993 | 39.7156 | 2.7438 | 0.76558 | 0.29525 | 3.8047 | 9.58% | 10.19% | 6.888% | 1.1059 | 1.1135 | 1.074
2010-04-15 | 42 | 27.9289 | 10.614 | 38.5429 | 2.5842 | 0.76558 | 0.28653 | 3.6363 | 9.434% | 10.04% | 6.783% | 1.1042 | 1.1116 | 1.0728
2010-04-15 | 43 | 26.5635 | 9.8914 | 36.4549 | 2.3118 | 0.76558 | 0.27101 | 3.3484 | 9.185% | 9.773% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-04-15 | 44 | 25.086 | 9.1965 | 34.2825 | 2.0445 | 0.76558 | 0.25486 | 3.0649 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2010-04-15 | 45 | 22.887 | 8.4446 | 31.3316 | 1.7077 | 0.76558 | 0.23292 | 2.7062 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-04-15 | 46 | 20.5298 | 7.5701 | 28.0999 | 1.3735 | 0.76558 | 0.2089 | 2.348 | 8.356% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-04-15 | 47 | 19.3808 | 7.4197 | 26.8005 | 1.2495 | 0.76558 | 0.19924 | 2.2143 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2010-04-15 | 48 | 18.0896 | 7.3861 | 25.4757 | 1.129 | 0.76558 | 0.18939 | 2.0839 | 8.18% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-04-16 | 1 | 16.3653 | 6.484 | 22.8493 | 0.9082 | 0.76558 | 0.16986 | 1.8436 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-04-16 | 2 | 15.8331 | 6.0536 | 21.8867 | 0.83329 | 0.76558 | 0.16271 | 1.7616 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-16 | 3 | 14.6407 | 5.7996 | 20.4404 | 0.72679 | 0.76558 | 0.15196 | 1.6443 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-16 | 4 | 14.1969 | 5.6268 | 19.8237 | 0.6836 | 0.76558 | 0.14737 | 1.5966 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-16 | 5 | 13.7656 | 5.5357 | 19.3012 | 0.64805 | 0.76558 | 0.14349 | 1.5571 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-04-16 | 6 | 13.0915 | 5.5288 | 18.6203 | 0.60313 | 0.76558 | 0.13843 | 1.5071 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-04-16 | 7 | 12.9613 | 5.5262 | 18.4875 | 0.59456 | 0.76558 | 0.13744 | 1.4976 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-04-16 | 8 | 12.8165 | 5.4539 | 18.2704 | 0.58067 | 0.76558 | 0.13582 | 1.4821 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-04-16 | 9 | 13.177 | 5.4574 | 18.6344 | 0.60404 | 0.76558 | 0.13853 | 1.5081 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-04-16 | 10 | 13.148 | 5.3587 | 18.5068 | 0.59579 | 0.76558 | 0.13758 | 1.499 | 8.099% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-04-16 | 11 | 13.1919 | 5.494 | 18.6859 | 0.60738 | 0.76558 | 0.13891 | 1.5119 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-04-16 | 12 | 13.9514 | 5.7808 | 19.7321 | 0.6773 | 0.76558 | 0.14669 | 1.5896 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-04-16 | 13 | 15.5332 | 6.4293 | 21.9624 | 0.83906 | 0.76558 | 0.16327 | 1.7679 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-16 | 14 | 17.9905 | 7.6318 | 25.6223 | 1.142 | 0.76558 | 0.19048 | 2.0981 | 8.188% | 8.713% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-04-16 | 15 | 21.2803 | 9.0337 | 30.314 | 1.5985 | 0.76558 | 0.22536 | 2.5895 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-04-16 | 16 | 23.6491 | 9.9191 | 33.5682 | 1.9602 | 0.76558 | 0.24955 | 2.9753 | 8.863% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-04-16 | 17 | 25.3717 | 10.278 | 35.6497 | 2.2108 | 0.76558 | 0.26502 | 3.2414 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-04-16 | 18 | 26.5219 | 10.4559 | 36.9777 | 2.3786 | 0.76558 | 0.2749 | 3.419 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-04-16 | 19 | 26.2482 | 10.3573 | 36.6055 | 2.3309 | 0.76558 | 0.27213 | 3.3686 | 9.203% | 9.791% | 6.617% | 1.1014 | 1.1085 | 1.0709
2010-04-16 | 20 | 25.9635 | 10.4724 | 36.436 | 2.3094 | 0.76558 | 0.27087 | 3.3458 | 9.183% | 9.77% | 6.602% | 1.1011 | 1.1083 | 1.0707
2010-04-16 | 21 | 25.7773 | 10.583 | 36.3602 | 2.2998 | 0.76558 | 0.27031 | 3.3357 | 9.174% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-04-16 | 22 | 24.9731 | 10.9259 | 35.8989 | 2.2418 | 0.76558 | 0.26688 | 3.2743 | 9.121% | 9.705% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-04-16 | 23 | 24.0698 | 10.8076 | 34.8773 | 2.116 | 0.76558 | 0.25928 | 3.1409 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2010-04-16 | 24 | 23.3541 | 10.8272 | 34.1813 | 2.0324 | 0.76558 | 0.25411 | 3.0521 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2010-04-16 | 25 | 22.72 | 10.6551 | 33.3751 | 1.9377 | 0.76558 | 0.24811 | 2.9514 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-04-16 | 26 | 21.843 | 10.3293 | 32.1722 | 1.8005 | 0.76558 | 0.23917 | 2.8053 | 8.72% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-04-16 | 27 | 21.9551 | 10.5029 | 32.458 | 1.8326 | 0.76558 | 0.2413 | 2.8395 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-04-16 | 28 | 21.7411 | 10.4879 | 32.229 | 1.8069 | 0.76558 | 0.23959 | 2.812 | 8.725% | 9.284% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-04-16 | 29 | 21.2816 | 10.3433 | 31.625 | 1.7398 | 0.76558 | 0.2351 | 2.7405 | 8.666% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-04-16 | 30 | 21.0339 | 10.2438 | 31.2777 | 1.7018 | 0.76558 | 0.23252 | 2.6999 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-04-16 | 31 | 21.2775 | 9.9604 | 31.2379 | 1.6975 | 0.76558 | 0.23223 | 2.6953 | 8.628% | 9.18% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-04-16 | 32 | 20.9053 | 9.9158 | 30.8211 | 1.6525 | 0.76558 | 0.22913 | 2.6472 | 8.589% | 9.138% | 6.175% | 1.094 | 1.1006 | 1.0658
2010-04-16 | 33 | 20.9785 | 10.1923 | 31.1708 | 1.6902 | 0.76558 | 0.23173 | 2.6875 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2010-04-16 | 34 | 21.2507 | 10.3659 | 31.6166 | 1.7389 | 0.76558 | 0.23504 | 2.7395 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-04-16 | 35 | 21.8376 | 10.6985 | 32.5362 | 1.8415 | 0.76558 | 0.24188 | 2.8489 | 8.756% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-04-16 | 36 | 23.3471 | 11.4366 | 34.7838 | 2.1047 | 0.76558 | 0.25859 | 3.1289 | 8.995% | 9.571% | 6.468% | 1.0988 | 1.1058 | 1.0691
2010-04-16 | 37 | 25.7003 | 12.3019 | 38.0022 | 2.5122 | 0.76558 | 0.28251 | 3.5603 | 9.369% | 9.968% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-04-16 | 38 | 27.5813 | 12.9241 | 40.5055 | 2.8541 | 0.76558 | 0.30112 | 3.9208 | 9.68% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-04-16 | 39 | 27.3094 | 12.5408 | 39.8502 | 2.7625 | 0.76558 | 0.29625 | 3.8243 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-04-16 | 40 | 26.7772 | 12.0318 | 38.809 | 2.62 | 0.76558 | 0.28851 | 3.6741 | 9.467% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-04-16 | 41 | 25.7724 | 11.2983 | 37.0707 | 2.3905 | 0.76558 | 0.27559 | 3.4317 | 9.257% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-04-16 | 42 | 25.0703 | 10.9783 | 36.0486 | 2.2605 | 0.76558 | 0.26799 | 3.2941 | 9.138% | 9.723% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-04-16 | 43 | 23.905 | 10.3479 | 34.2529 | 2.0409 | 0.76558 | 0.25464 | 3.0612 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2010-04-16 | 44 | 22.5964 | 9.8275 | 32.4239 | 1.8288 | 0.76558 | 0.24104 | 2.8354 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-04-16 | 45 | 20.7152 | 8.9707 | 29.686 | 1.533 | 0.76558 | 0.22069 | 2.5192 | 8.486% | 9.029% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-04-16 | 46 | 18.8635 | 8.0966 | 26.9602 | 1.2644 | 0.76558 | 0.20043 | 2.2304 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-04-16 | 47 | 17.7442 | 7.6828 | 25.427 | 1.1247 | 0.76558 | 0.18903 | 2.0793 | 8.177% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-04-16 | 48 | 16.4637 | 7.7179 | 24.1816 | 1.0172 | 0.76558 | 0.17977 | 1.9625 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-04-17 | 1 | 14.9255 | 6.966 | 21.8915 | 0.83365 | 0.76558 | 0.16274 | 1.762 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-17 | 2 | 14.4635 | 6.4691 | 20.9326 | 0.76222 | 0.76558 | 0.15562 | 1.6834 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-17 | 3 | 13.717 | 6.1723 | 19.8893 | 0.68813 | 0.76558 | 0.14786 | 1.6016 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-04-17 | 4 | 13.1393 | 6.083 | 19.2223 | 0.64276 | 0.76558 | 0.1429 | 1.5512 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-17 | 5 | 12.394 | 5.822 | 18.216 | 0.57722 | 0.76558 | 0.13542 | 1.4782 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-04-17 | 6 | 11.9466 | 5.7867 | 17.7333 | 0.54703 | 0.76558 | 0.13183 | 1.4444 | 8.145% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-04-17 | 7 | 11.8733 | 5.7282 | 17.6015 | 0.53893 | 0.76558 | 0.13085 | 1.4354 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-04-17 | 8 | 12.0612 | 5.6996 | 17.7608 | 0.54873 | 0.76558 | 0.13204 | 1.4463 | 8.143% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-04-17 | 9 | 12.4626 | 5.7271 | 18.1897 | 0.57556 | 0.76558 | 0.13522 | 1.4764 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-04-17 | 10 | 12.3034 | 5.7791 | 18.0825 | 0.56879 | 0.76558 | 0.13443 | 1.4688 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-04-17 | 11 | 12.6468 | 5.9898 | 18.6367 | 0.60419 | 0.76558 | 0.13855 | 1.5083 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-04-17 | 12 | 13.3636 | 6.1267 | 19.4903 | 0.6608 | 0.76558 | 0.14489 | 1.5713 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-04-17 | 13 | 14.9581 | 6.83 | 21.7881 | 0.8258 | 0.76558 | 0.16198 | 1.7534 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-17 | 14 | 17.372 | 7.9473 | 25.3193 | 1.1152 | 0.76558 | 0.18823 | 2.069 | 8.172% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2010-04-17 | 15 | 20.5762 | 9.5283 | 30.1045 | 1.5765 | 0.76558 | 0.2238 | 2.5659 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-04-17 | 16 | 22.8002 | 10.6936 | 33.4938 | 1.9515 | 0.76558 | 0.249 | 2.9661 | 8.856% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2010-04-17 | 17 | 24.7223 | 11.3296 | 36.0519 | 2.261 | 0.76558 | 0.26801 | 3.2945 | 9.138% | 9.723% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-04-17 | 18 | 25.5744 | 11.9559 | 37.5303 | 2.4502 | 0.76558 | 0.279 | 3.4948 | 9.312% | 9.908% | 6.695% | 1.1027 | 1.11 | 1.0718
2010-04-17 | 19 | 25.5605 | 12.1334 | 37.6939 | 2.4716 | 0.76558 | 0.28022 | 3.5174 | 9.331% | 9.929% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-04-17 | 20 | 25.0867 | 11.9017 | 36.9884 | 2.3799 | 0.76558 | 0.27498 | 3.4205 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-04-17 | 21 | 25.2145 | 11.7142 | 36.9287 | 2.3723 | 0.76558 | 0.27453 | 3.4124 | 9.24% | 9.832% | 6.644% | 1.1018 | 1.109 | 1.0712
2010-04-17 | 22 | 24.3245 | 11.3296 | 35.6541 | 2.2113 | 0.76558 | 0.26506 | 3.242 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.07
2010-04-17 | 23 | 23.4347 | 10.919 | 34.3537 | 2.053 | 0.76558 | 0.25539 | 3.0739 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-04-17 | 24 | 22.5003 | 10.6541 | 33.1544 | 1.9121 | 0.76558 | 0.24647 | 2.9242 | 8.82% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2010-04-17 | 25 | 21.9262 | 10.5414 | 32.4676 | 1.8337 | 0.76558 | 0.24137 | 2.8407 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1026 | 1.0671
2010-04-17 | 26 | 21.3369 | 10.0796 | 31.4164 | 1.7169 | 0.76558 | 0.23355 | 2.716 | 8.645% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-04-17 | 27 | 21.4236 | 10.0383 | 31.4619 | 1.7219 | 0.76558 | 0.23389 | 2.7214 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-04-17 | 28 | 21.6121 | 10.0292 | 31.6412 | 1.7416 | 0.76558 | 0.23522 | 2.7424 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-04-17 | 29 | 21.2226 | 9.6874 | 30.91 | 1.662 | 0.76558 | 0.22979 | 2.6574 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-04-17 | 30 | 20.806 | 9.411 | 30.217 | 1.5883 | 0.76558 | 0.22464 | 2.5785 | 8.533% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-04-17 | 31 | 21.3822 | 9.2611 | 30.6432 | 1.6334 | 0.76558 | 0.22781 | 2.6268 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-04-17 | 32 | 21.0367 | 9.2325 | 30.2692 | 1.5938 | 0.76558 | 0.22502 | 2.5844 | 8.538% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-04-17 | 33 | 21.0217 | 9.6737 | 30.6954 | 1.639 | 0.76558 | 0.22819 | 2.6328 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-04-17 | 34 | 21.7253 | 9.9725 | 31.6978 | 1.7478 | 0.76558 | 0.23565 | 2.749 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-04-17 | 35 | 22.2997 | 10.3673 | 32.6669 | 1.8563 | 0.76558 | 0.24285 | 2.8647 | 8.77% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-04-17 | 36 | 23.6367 | 11.1789 | 34.8157 | 2.1086 | 0.76558 | 0.25882 | 3.133 | 8.999% | 9.575% | 6.47% | 1.0989 | 1.1059 | 1.0692
2010-04-17 | 37 | 25.8328 | 12.0018 | 37.8346 | 2.4901 | 0.76558 | 0.28127 | 3.5369 | 9.348% | 9.947% | 6.721% | 1.1031 | 1.1105 | 1.0721
2010-04-17 | 38 | 27.5272 | 12.2528 | 39.78 | 2.7527 | 0.76558 | 0.29573 | 3.814 | 9.588% | 10.2% | 6.894% | 1.106 | 1.1136 | 1.074
2010-04-17 | 39 | 27.0963 | 11.8535 | 38.9498 | 2.639 | 0.76558 | 0.28956 | 3.6942 | 9.484% | 10.09% | 6.819% | 1.1048 | 1.1122 | 1.0732
2010-04-17 | 40 | 25.9911 | 11.0796 | 37.0708 | 2.3906 | 0.76558 | 0.27559 | 3.4317 | 9.257% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-04-17 | 41 | 25.26 | 10.4519 | 35.7119 | 2.2185 | 0.76558 | 0.26549 | 3.2496 | 9.099% | 9.682% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-04-17 | 42 | 24.7127 | 10.3195 | 35.0322 | 2.1349 | 0.76558 | 0.26043 | 3.1609 | 9.023% | 9.6% | 6.487% | 1.0992 | 1.1062 | 1.0694
2010-04-17 | 43 | 23.6057 | 9.8426 | 33.4483 | 1.9462 | 0.76558 | 0.24866 | 2.9604 | 8.851% | 9.417% | 6.364% | 1.0971 | 1.104 | 1.068
2010-04-17 | 44 | 22.6133 | 9.5621 | 32.1755 | 1.8009 | 0.76558 | 0.2392 | 2.8057 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-04-17 | 45 | 20.8751 | 8.8029 | 29.678 | 1.5322 | 0.76558 | 0.22063 | 2.5184 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-04-17 | 46 | 19.3678 | 8.0247 | 27.3925 | 1.3053 | 0.76558 | 0.20364 | 2.2745 | 8.303% | 8.835% | 5.97% | 1.0906 | 1.0969 | 1.0635
2010-04-17 | 47 | 18.3483 | 7.8755 | 26.2238 | 1.1963 | 0.76558 | 0.19495 | 2.1568 | 8.225% | 8.751% | 5.913% | 1.0896 | 1.0959 | 1.0629
2010-04-17 | 48 | 17.0702 | 7.9084 | 24.9786 | 1.0854 | 0.76558 | 0.18569 | 2.0366 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-04-18 | 1 | 15.1165 | 7.1349 | 22.2514 | 0.86129 | 0.76558 | 0.16542 | 1.7923 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-18 | 2 | 14.615 | 6.5483 | 21.1633 | 0.77911 | 0.76558 | 0.15733 | 1.702 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-18 | 3 | 13.8668 | 6.1947 | 20.0614 | 0.7001 | 0.76558 | 0.14914 | 1.6148 | 8.049% | 8.565% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-18 | 4 | 13.3073 | 5.937 | 19.2443 | 0.64423 | 0.76558 | 0.14306 | 1.5529 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-18 | 5 | 12.6476 | 5.8019 | 18.4495 | 0.59211 | 0.76558 | 0.13716 | 1.4948 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-04-18 | 6 | 12.3455 | 5.7168 | 18.0622 | 0.56752 | 0.76558 | 0.13428 | 1.4674 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-04-18 | 7 | 12.1014 | 5.5897 | 17.6912 | 0.54444 | 0.76558 | 0.13152 | 1.4415 | 8.148% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-04-18 | 8 | 12.2591 | 5.6097 | 17.8688 | 0.55543 | 0.76558 | 0.13284 | 1.4538 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-04-18 | 9 | 12.4451 | 5.3918 | 17.8369 | 0.55345 | 0.76558 | 0.1326 | 1.4516 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0622
2010-04-18 | 10 | 12.4171 | 5.295 | 17.712 | 0.54572 | 0.76558 | 0.13167 | 1.443 | 8.147% | 8.668% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-04-18 | 11 | 12.3895 | 5.4171 | 17.8066 | 0.55156 | 0.76558 | 0.13238 | 1.4495 | 8.14% | 8.661% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-04-18 | 12 | 12.8059 | 5.641 | 18.447 | 0.59195 | 0.76558 | 0.13714 | 1.4947 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-04-18 | 13 | 14.1831 | 5.9968 | 20.1798 | 0.70839 | 0.76558 | 0.15002 | 1.624 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-18 | 14 | 15.3195 | 6.4262 | 21.7457 | 0.82259 | 0.76558 | 0.16166 | 1.7498 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-18 | 15 | 17.001 | 7.3421 | 24.3431 | 1.0308 | 0.76558 | 0.18097 | 1.9774 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-04-18 | 16 | 18.6814 | 8.2847 | 26.9661 | 1.2649 | 0.76558 | 0.20047 | 2.231 | 8.273% | 8.803% | 5.949% | 1.0902 | 1.0965 | 1.0632
2010-04-18 | 17 | 20.9632 | 9.1613 | 30.1245 | 1.5786 | 0.76558 | 0.22395 | 2.5681 | 8.525% | 9.071% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-04-18 | 18 | 22.6579 | 9.7471 | 32.405 | 1.8267 | 0.76558 | 0.2409 | 2.8331 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-04-18 | 19 | 23.88 | 9.8677 | 33.7477 | 1.9812 | 0.76558 | 0.25088 | 2.9976 | 8.882% | 9.451% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-04-18 | 20 | 24.3407 | 10.0009 | 34.3416 | 2.0515 | 0.76558 | 0.2553 | 3.0724 | 8.947% | 9.519% | 6.433% | 1.0983 | 1.1052 | 1.0687
2010-04-18 | 21 | 24.7022 | 10.1082 | 34.8104 | 2.1079 | 0.76558 | 0.25878 | 3.1323 | 8.998% | 9.574% | 6.47% | 1.0989 | 1.1059 | 1.0692
2010-04-18 | 22 | 24.3264 | 10.0006 | 34.327 | 2.0498 | 0.76558 | 0.25519 | 3.0705 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-04-18 | 23 | 23.4359 | 9.7483 | 33.1842 | 1.9156 | 0.76558 | 0.2467 | 2.9278 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-04-18 | 24 | 22.7601 | 9.638 | 32.3982 | 1.8259 | 0.76558 | 0.24085 | 2.8323 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-04-18 | 25 | 21.8395 | 9.3988 | 31.2382 | 1.6975 | 0.76558 | 0.23223 | 2.6953 | 8.628% | 9.18% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-04-18 | 26 | 20.8051 | 9.0533 | 29.8584 | 1.5508 | 0.76558 | 0.22197 | 2.5384 | 8.501% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-04-18 | 27 | 20.6344 | 9.0677 | 29.7021 | 1.5346 | 0.76558 | 0.22081 | 2.521 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2010-04-18 | 28 | 20.1027 | 8.8836 | 28.9863 | 1.4616 | 0.76558 | 0.21549 | 2.4426 | 8.427% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-04-18 | 29 | 19.3854 | 8.5319 | 27.9173 | 1.3558 | 0.76558 | 0.20754 | 2.3289 | 8.342% | 8.876% | 5.998% | 1.091 | 1.0974 | 1.0638
2010-04-18 | 30 | 18.9698 | 8.2072 | 27.177 | 1.2848 | 0.76558 | 0.20204 | 2.2524 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-04-18 | 31 | 19.344 | 8.1332 | 27.4772 | 1.3133 | 0.76558 | 0.20427 | 2.2832 | 8.309% | 8.841% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-04-18 | 32 | 19.2577 | 8.0668 | 27.3245 | 1.2988 | 0.76558 | 0.20313 | 2.2675 | 8.298% | 8.83% | 5.967% | 1.0905 | 1.0968 | 1.0635
2010-04-18 | 33 | 19.5288 | 8.3635 | 27.8923 | 1.3533 | 0.76558 | 0.20735 | 2.3263 | 8.34% | 8.874% | 5.997% | 1.091 | 1.0974 | 1.0638
2010-04-18 | 34 | 20.1025 | 8.4714 | 28.5738 | 1.4203 | 0.76558 | 0.21242 | 2.3983 | 8.393% | 8.93% | 6.035% | 1.0916 | 1.0981 | 1.0642
2010-04-18 | 35 | 21.1805 | 8.9434 | 30.1239 | 1.5785 | 0.76558 | 0.22394 | 2.5681 | 8.525% | 9.071% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-04-18 | 36 | 23.3767 | 9.9201 | 33.2968 | 1.9286 | 0.76558 | 0.24753 | 2.9417 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-04-18 | 37 | 25.4726 | 10.9747 | 36.4473 | 2.3108 | 0.76558 | 0.27095 | 3.3473 | 9.184% | 9.772% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-04-18 | 38 | 26.6201 | 11.3357 | 37.9558 | 2.5061 | 0.76558 | 0.28217 | 3.5538 | 9.363% | 9.962% | 6.732% | 1.1033 | 1.1106 | 1.0722
2010-04-18 | 39 | 25.9893 | 10.8426 | 36.8319 | 2.3598 | 0.76558 | 0.27381 | 3.3992 | 9.229% | 9.82% | 6.636% | 1.1017 | 1.1089 | 1.0711
2010-04-18 | 40 | 24.8106 | 10.4266 | 35.2372 | 2.1599 | 0.76558 | 0.26196 | 3.1875 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-04-18 | 41 | 23.9639 | 9.7164 | 33.6803 | 1.9733 | 0.76558 | 0.25038 | 2.9892 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-04-18 | 42 | 23.5478 | 9.2041 | 32.7519 | 1.866 | 0.76558 | 0.24348 | 2.875 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-04-18 | 43 | 22.2107 | 8.7699 | 30.9807 | 1.6696 | 0.76558 | 0.23031 | 2.6655 | 8.604% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-04-18 | 44 | 21.2346 | 8.2585 | 29.4931 | 1.5131 | 0.76558 | 0.21926 | 2.498 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-04-18 | 45 | 19.5553 | 7.7282 | 27.2834 | 1.2949 | 0.76558 | 0.20283 | 2.2633 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2010-04-18 | 46 | 18.1038 | 7.2633 | 25.3671 | 1.1194 | 0.76558 | 0.18858 | 2.0735 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2010-04-18 | 47 | 17.4298 | 7.2456 | 24.6754 | 1.0592 | 0.76558 | 0.18344 | 2.0082 | 8.138% | 8.659% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-04-18 | 48 | 16.64 | 7.3941 | 24.0341 | 1.0048 | 0.76558 | 0.17867 | 1.9491 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-04-19 | 1 | 14.8444 | 6.6048 | 21.4492 | 0.80031 | 0.76558 | 0.15946 | 1.7253 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-19 | 2 | 14.2125 | 6.0522 | 20.2647 | 0.71436 | 0.76558 | 0.15065 | 1.6306 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-19 | 3 | 13.2655 | 5.749 | 19.0145 | 0.62893 | 0.76558 | 0.14136 | 1.5359 | 8.077% | 8.594% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-04-19 | 4 | 12.9499 | 5.6093 | 18.5592 | 0.59917 | 0.76558 | 0.13797 | 1.5027 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-04-19 | 5 | 12.4755 | 5.5092 | 17.9847 | 0.56265 | 0.76558 | 0.1337 | 1.4619 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-04-19 | 6 | 12.0435 | 5.5126 | 17.5561 | 0.53616 | 0.76558 | 0.13051 | 1.4323 | 8.158% | 8.68% | 5.866% | 1.0888 | 1.0951 | 1.0623
2010-04-19 | 7 | 11.7409 | 5.3753 | 17.1163 | 0.50963 | 0.76558 | 0.12724 | 1.4024 | 8.194% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-04-19 | 8 | 11.8719 | 5.4139 | 17.2858 | 0.51977 | 0.76558 | 0.1285 | 1.4139 | 8.179% | 8.703% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-04-19 | 9 | 12.0739 | 5.4207 | 17.4946 | 0.53241 | 0.76558 | 0.13006 | 1.428 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2010-04-19 | 10 | 11.9427 | 5.2763 | 17.219 | 0.51576 | 0.76558 | 0.12801 | 1.4093 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-04-19 | 11 | 12.2013 | 5.3289 | 17.5302 | 0.53457 | 0.76558 | 0.13032 | 1.4305 | 8.16% | 8.682% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-04-19 | 12 | 12.6325 | 5.3709 | 18.0035 | 0.56383 | 0.76558 | 0.13384 | 1.4632 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-19 | 13 | 13.4786 | 5.6888 | 19.1674 | 0.63909 | 0.76558 | 0.14249 | 1.5472 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-04-19 | 14 | 14.3569 | 5.9868 | 20.3437 | 0.71994 | 0.76558 | 0.15124 | 1.6368 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-19 | 15 | 15.6951 | 6.6636 | 22.3587 | 0.86962 | 0.76558 | 0.16622 | 1.8014 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-04-19 | 16 | 17.0731 | 7.3679 | 24.4411 | 1.0391 | 0.76558 | 0.1817 | 1.9864 | 8.127% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-04-19 | 17 | 19.2837 | 8.3511 | 27.6347 | 1.3285 | 0.76558 | 0.20544 | 2.2995 | 8.321% | 8.853% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-04-19 | 18 | 21.3514 | 9.2415 | 30.5928 | 1.6281 | 0.76558 | 0.22743 | 2.6211 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-04-19 | 19 | 22.4576 | 9.652 | 32.1096 | 1.7935 | 0.76558 | 0.23871 | 2.7978 | 8.713% | 9.271% | 6.265% | 1.0954 | 1.1022 | 1.0668
2010-04-19 | 20 | 22.8745 | 9.913 | 32.7876 | 1.87 | 0.76558 | 0.24375 | 2.8794 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-04-19 | 21 | 23.6789 | 9.7568 | 33.4357 | 1.9447 | 0.76558 | 0.24856 | 2.9589 | 8.849% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2010-04-19 | 22 | 23.2053 | 9.8541 | 33.0593 | 1.9012 | 0.76558 | 0.24577 | 2.9125 | 8.81% | 9.374% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-04-19 | 23 | 22.6147 | 9.4321 | 32.0468 | 1.7865 | 0.76558 | 0.23824 | 2.7903 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-04-19 | 24 | 21.7243 | 9.3023 | 31.0266 | 1.6746 | 0.76558 | 0.23066 | 2.6708 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-04-19 | 25 | 21.4229 | 9.4707 | 30.8936 | 1.6602 | 0.76558 | 0.22967 | 2.6555 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-04-19 | 26 | 20.8049 | 9.3358 | 30.1407 | 1.5803 | 0.76558 | 0.22407 | 2.5699 | 8.527% | 9.072% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-04-19 | 27 | 20.7199 | 9.662 | 30.3819 | 1.6057 | 0.76558 | 0.22586 | 2.5971 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1001 | 1.0655
2010-04-19 | 28 | 20.506 | 9.6669 | 30.1728 | 1.5837 | 0.76558 | 0.22431 | 2.5736 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2010-04-19 | 29 | 19.9595 | 9.5372 | 29.4967 | 1.5135 | 0.76558 | 0.21928 | 2.4984 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-04-19 | 30 | 19.5849 | 9.2002 | 28.7851 | 1.4414 | 0.76558 | 0.21399 | 2.4209 | 8.41% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-04-19 | 31 | 19.0392 | 9.079 | 28.1182 | 1.3753 | 0.76558 | 0.20903 | 2.35 | 8.357% | 8.892% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-04-19 | 32 | 19.1838 | 8.7523 | 27.9362 | 1.3576 | 0.76558 | 0.20768 | 2.3309 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-04-19 | 33 | 19.7296 | 9.1547 | 28.8842 | 1.4513 | 0.76558 | 0.21473 | 2.4316 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-04-19 | 34 | 20.3169 | 9.3457 | 29.6626 | 1.5306 | 0.76558 | 0.22052 | 2.5167 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-04-19 | 35 | 21.0207 | 10.0009 | 31.0216 | 1.674 | 0.76558 | 0.23062 | 2.6702 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-04-19 | 36 | 22.6144 | 11.1668 | 33.7812 | 1.9851 | 0.76558 | 0.25113 | 3.0018 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2010-04-19 | 37 | 25.2713 | 12.1072 | 37.3785 | 2.4304 | 0.76558 | 0.27788 | 3.4739 | 9.294% | 9.889% | 6.682% | 1.1025 | 1.1097 | 1.0716
2010-04-19 | 38 | 26.9489 | 12.3349 | 39.2838 | 2.6845 | 0.76558 | 0.29204 | 3.7421 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-04-19 | 39 | 26.6326 | 11.911 | 38.5436 | 2.5843 | 0.76558 | 0.28654 | 3.6364 | 9.434% | 10.04% | 6.783% | 1.1042 | 1.1116 | 1.0728
2010-04-19 | 40 | 25.829 | 11.3531 | 37.1821 | 2.4049 | 0.76558 | 0.27642 | 3.4469 | 9.27% | 9.864% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-04-19 | 41 | 24.8537 | 11.0188 | 35.8725 | 2.2385 | 0.76558 | 0.26668 | 3.2708 | 9.118% | 9.701% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-04-19 | 42 | 23.9485 | 10.4913 | 34.4398 | 2.0633 | 0.76558 | 0.25603 | 3.0849 | 8.957% | 9.531% | 6.44% | 1.0984 | 1.1053 | 1.0688
2010-04-19 | 43 | 22.6705 | 9.7071 | 32.3776 | 1.8236 | 0.76558 | 0.2407 | 2.8299 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2010-04-19 | 44 | 21.5208 | 9.2389 | 30.7597 | 1.6459 | 0.76558 | 0.22867 | 2.6401 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-04-19 | 45 | 20.0298 | 8.3767 | 28.4065 | 1.4037 | 0.76558 | 0.21118 | 2.3804 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-04-19 | 46 | 18.3615 | 7.6646 | 26.0261 | 1.1783 | 0.76558 | 0.19348 | 2.1374 | 8.212% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-04-19 | 47 | 17.0419 | 7.5424 | 24.5843 | 1.0514 | 0.76558 | 0.18276 | 1.9997 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-04-19 | 48 | 16.15 | 7.5535 | 23.7035 | 0.97737 | 0.76558 | 0.17621 | 1.9192 | 8.097% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-04-20 | 1 | 14.8303 | 6.8206 | 21.651 | 0.81544 | 0.76558 | 0.16096 | 1.742 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-20 | 2 | 14.4121 | 6.3544 | 20.7665 | 0.75017 | 0.76558 | 0.15438 | 1.6701 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-20 | 3 | 13.378 | 6.1303 | 19.5083 | 0.66202 | 0.76558 | 0.14503 | 1.5726 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-04-20 | 4 | 12.9896 | 5.9918 | 18.9814 | 0.62675 | 0.76558 | 0.14111 | 1.5334 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-04-20 | 5 | 12.6462 | 5.8024 | 18.4486 | 0.59205 | 0.76558 | 0.13715 | 1.4948 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-04-20 | 6 | 12.6876 | 5.732 | 18.4196 | 0.59019 | 0.76558 | 0.13693 | 1.4927 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-04-20 | 7 | 12.5289 | 5.7546 | 18.2835 | 0.58151 | 0.76558 | 0.13592 | 1.483 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-04-20 | 8 | 12.3161 | 5.5428 | 17.859 | 0.55481 | 0.76558 | 0.13277 | 1.4532 | 8.137% | 8.658% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-04-20 | 9 | 12.5872 | 5.6621 | 18.2493 | 0.57933 | 0.76558 | 0.13567 | 1.4806 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-04-20 | 10 | 13.1628 | 5.6037 | 18.7665 | 0.61263 | 0.76558 | 0.13951 | 1.5177 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-04-20 | 11 | 13.5361 | 5.8389 | 19.375 | 0.65301 | 0.76558 | 0.14404 | 1.5626 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-20 | 12 | 13.9819 | 6.1302 | 20.112 | 0.70363 | 0.76558 | 0.14952 | 1.6187 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-20 | 13 | 15.4321 | 6.9444 | 22.3765 | 0.871 | 0.76558 | 0.16635 | 1.8029 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-04-20 | 14 | 17.7467 | 8.0622 | 25.8089 | 1.1587 | 0.76558 | 0.19187 | 2.1162 | 8.199% | 8.724% | 5.895% | 1.0893 | 1.0956 | 1.0626
2010-04-20 | 15 | 21.1935 | 9.9102 | 31.1037 | 1.6829 | 0.76558 | 0.23123 | 2.6797 | 8.615% | 9.167% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-04-20 | 16 | 23.9968 | 10.8729 | 34.8697 | 2.1151 | 0.76558 | 0.25923 | 3.1399 | 9.005% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2010-04-20 | 17 | 25.9925 | 11.3073 | 37.2997 | 2.4202 | 0.76558 | 0.27729 | 3.463 | 9.284% | 9.879% | 6.675% | 1.1023 | 1.1096 | 1.0715
2010-04-20 | 18 | 27.3721 | 11.5926 | 38.9647 | 2.6411 | 0.76558 | 0.28967 | 3.6963 | 9.486% | 10.09% | 6.821% | 1.1048 | 1.1123 | 1.0732
2010-04-20 | 19 | 27.6594 | 11.3595 | 39.0189 | 2.6484 | 0.76558 | 0.29007 | 3.7041 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-04-20 | 20 | 26.7959 | 11.1461 | 37.942 | 2.5042 | 0.76558 | 0.28207 | 3.5519 | 9.361% | 9.96% | 6.731% | 1.1033 | 1.1106 | 1.0722
2010-04-20 | 21 | 26.7087 | 10.9084 | 37.6171 | 2.4615 | 0.76558 | 0.27965 | 3.5068 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-04-20 | 22 | 26.0498 | 10.8881 | 36.9378 | 2.3734 | 0.76558 | 0.2746 | 3.4136 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-04-20 | 23 | 25.0147 | 10.544 | 35.5587 | 2.1995 | 0.76558 | 0.26435 | 3.2294 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-04-20 | 24 | 24.2537 | 10.4976 | 34.7513 | 2.1008 | 0.76558 | 0.25835 | 3.1247 | 8.992% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-04-20 | 25 | 23.2326 | 10.4552 | 33.6878 | 1.9741 | 0.76558 | 0.25044 | 2.9902 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-04-20 | 26 | 22.8024 | 9.6995 | 32.5019 | 1.8376 | 0.76558 | 0.24162 | 2.8448 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-04-20 | 27 | 22.2718 | 9.8659 | 32.1377 | 1.7966 | 0.76558 | 0.23892 | 2.8011 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-04-20 | 28 | 22.4572 | 10.0357 | 32.4929 | 1.8366 | 0.76558 | 0.24156 | 2.8437 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-04-20 | 29 | 22.027 | 9.7518 | 31.7788 | 1.7567 | 0.76558 | 0.23625 | 2.7586 | 8.681% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2010-04-20 | 30 | 21.7265 | 9.6543 | 31.3808 | 1.713 | 0.76558 | 0.23329 | 2.7119 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-04-20 | 31 | 22.1285 | 9.5936 | 31.7221 | 1.7505 | 0.76558 | 0.23583 | 2.7519 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-04-20 | 32 | 22.0556 | 9.6724 | 31.728 | 1.7511 | 0.76558 | 0.23587 | 2.7526 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-04-20 | 33 | 22.4153 | 9.9511 | 32.3663 | 1.8223 | 0.76558 | 0.24062 | 2.8285 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-04-20 | 34 | 23.3622 | 10.2257 | 33.5879 | 1.9625 | 0.76558 | 0.2497 | 2.9777 | 8.865% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2010-04-20 | 35 | 24.9116 | 11.0692 | 35.9808 | 2.252 | 0.76558 | 0.26749 | 3.2851 | 9.13% | 9.714% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-04-20 | 36 | 27.0832 | 12.4451 | 39.5284 | 2.718 | 0.76558 | 0.29386 | 3.7775 | 9.556% | 10.17% | 6.871% | 1.1057 | 1.1132 | 1.0738
2010-04-20 | 37 | 29.7952 | 13.6383 | 43.4335 | 3.2816 | 0.76558 | 0.32289 | 4.3701 | 10.06% | 10.71% | 7.234% | 1.1119 | 1.1199 | 1.078
2010-04-20 | 38 | 31.5039 | 13.6037 | 45.1077 | 3.5394 | 0.76558 | 0.33534 | 4.6404 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-04-20 | 39 | 31.2316 | 13.1778 | 44.4093 | 3.4307 | 0.76558 | 0.33014 | 4.5264 | 10.19% | 10.84% | 7.328% | 1.1135 | 1.1216 | 1.0791
2010-04-20 | 40 | 30.3247 | 12.4039 | 42.7285 | 3.1759 | 0.76558 | 0.31765 | 4.2592 | 9.968% | 10.61% | 7.167% | 1.1107 | 1.1186 | 1.0772
2010-04-20 | 41 | 30.283 | 11.8078 | 42.0908 | 3.0818 | 0.76558 | 0.31291 | 4.1603 | 9.884% | 10.52% | 7.107% | 1.1097 | 1.1175 | 1.0765
2010-04-20 | 42 | 29.5203 | 11.2799 | 40.8002 | 2.8957 | 0.76558 | 0.30331 | 3.9646 | 9.717% | 10.34% | 6.987% | 1.1076 | 1.1153 | 1.0751
2010-04-20 | 43 | 27.9818 | 10.7156 | 38.6973 | 2.6049 | 0.76558 | 0.28768 | 3.6582 | 9.453% | 10.06% | 6.797% | 1.1044 | 1.1118 | 1.0729
2010-04-20 | 44 | 26.2013 | 10.2485 | 36.4498 | 2.3111 | 0.76558 | 0.27097 | 3.3477 | 9.184% | 9.772% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-04-20 | 45 | 24.3072 | 9.2109 | 33.5181 | 1.9543 | 0.76558 | 0.24918 | 2.9691 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-04-20 | 46 | 22.2539 | 8.4186 | 30.6725 | 1.6366 | 0.76558 | 0.22802 | 2.6302 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-04-20 | 47 | 20.7743 | 8.1249 | 28.8992 | 1.4528 | 0.76558 | 0.21484 | 2.4332 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-04-20 | 48 | 19.1229 | 8.1849 | 27.3078 | 1.2972 | 0.76558 | 0.20301 | 2.2658 | 8.297% | 8.828% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-04-21 | 1 | 17.4718 | 7.5141 | 24.986 | 1.086 | 0.76558 | 0.18575 | 2.0373 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-04-21 | 2 | 17.2853 | 6.9811 | 24.2664 | 1.0243 | 0.76558 | 0.1804 | 1.9703 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-04-21 | 3 | 16.6229 | 6.6667 | 23.2895 | 0.94353 | 0.76558 | 0.17314 | 1.8822 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-21 | 4 | 16.1349 | 6.5071 | 22.6421 | 0.8918 | 0.76558 | 0.16832 | 1.8257 | 8.063% | 8.579% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-04-21 | 5 | 15.647 | 6.4342 | 22.0812 | 0.84816 | 0.76558 | 0.16415 | 1.7779 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-21 | 6 | 15.3166 | 6.3074 | 21.624 | 0.8134 | 0.76558 | 0.16076 | 1.7397 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-21 | 7 | 15.5887 | 6.2993 | 21.8879 | 0.83338 | 0.76558 | 0.16272 | 1.7617 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-21 | 8 | 15.4163 | 6.2626 | 21.6788 | 0.81754 | 0.76558 | 0.16116 | 1.7443 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-21 | 9 | 15.2728 | 6.4405 | 21.7133 | 0.82014 | 0.76558 | 0.16142 | 1.7471 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-21 | 10 | 15.6181 | 6.5949 | 22.2131 | 0.85832 | 0.76558 | 0.16513 | 1.789 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-21 | 11 | 16.0349 | 6.8821 | 22.9171 | 0.91359 | 0.76558 | 0.17037 | 1.8495 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-04-21 | 12 | 17.1826 | 7.4709 | 24.6535 | 1.0573 | 0.76558 | 0.18328 | 2.0061 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-04-21 | 13 | 18.9499 | 8.3782 | 27.3281 | 1.2991 | 0.76558 | 0.20316 | 2.2679 | 8.299% | 8.83% | 5.967% | 1.0905 | 1.0968 | 1.0635
2010-04-21 | 14 | 21.5791 | 9.6584 | 31.2375 | 1.6974 | 0.76558 | 0.23222 | 2.6952 | 8.628% | 9.18% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-04-21 | 15 | 25.6468 | 11.8469 | 37.4937 | 2.4454 | 0.76558 | 0.27873 | 3.4897 | 9.307% | 9.903% | 6.692% | 1.1026 | 1.1099 | 1.0717
2010-04-21 | 16 | 28.2478 | 13.5038 | 41.7516 | 3.0324 | 0.76558 | 0.31039 | 4.1083 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-04-21 | 17 | 30.5143 | 14.2503 | 44.7646 | 3.4858 | 0.76558 | 0.33279 | 4.5842 | 10.24% | 10.9% | 7.363% | 1.1141 | 1.1223 | 1.0795
2010-04-21 | 18 | 31.6783 | 14.2361 | 45.9145 | 3.6672 | 0.76558 | 0.34133 | 4.7741 | 10.4% | 11.06% | 7.476% | 1.116 | 1.1244 | 1.0808
2010-04-21 | 19 | 31.3761 | 13.6811 | 45.0573 | 3.5315 | 0.76558 | 0.33496 | 4.6321 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-04-21 | 20 | 30.501 | 12.8715 | 43.3725 | 3.2724 | 0.76558 | 0.32244 | 4.3604 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-04-21 | 21 | 29.8262 | 11.9278 | 41.7541 | 3.0327 | 0.76558 | 0.3104 | 4.1087 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-04-21 | 22 | 28.5269 | 11.5118 | 40.0387 | 2.7887 | 0.76558 | 0.29765 | 3.8519 | 9.62% | 10.24% | 6.917% | 1.1064 | 1.114 | 1.0743
2010-04-21 | 23 | 27.112 | 10.7587 | 37.8707 | 2.4948 | 0.76558 | 0.28154 | 3.5419 | 9.353% | 9.951% | 6.725% | 1.1032 | 1.1105 | 1.0721
2010-04-21 | 24 | 26.1282 | 10.3437 | 36.4719 | 2.3139 | 0.76558 | 0.27114 | 3.3506 | 9.187% | 9.775% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-04-21 | 25 | 25.0283 | 10.0734 | 35.1017 | 2.1433 | 0.76558 | 0.26095 | 3.1699 | 9.031% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-04-21 | 26 | 23.9869 | 9.6353 | 33.6222 | 1.9665 | 0.76558 | 0.24995 | 2.982 | 8.869% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-04-21 | 27 | 23.7871 | 9.6802 | 33.4673 | 1.9484 | 0.76558 | 0.2488 | 2.9628 | 8.853% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2010-04-21 | 28 | 23.3913 | 9.6381 | 33.0293 | 1.8977 | 0.76558 | 0.24554 | 2.9089 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-04-21 | 29 | 22.8946 | 9.2136 | 32.1083 | 1.7934 | 0.76558 | 0.2387 | 2.7976 | 8.713% | 9.271% | 6.265% | 1.0954 | 1.1022 | 1.0668
2010-04-21 | 30 | 22.4563 | 8.8494 | 31.3056 | 1.7048 | 0.76558 | 0.23273 | 2.7031 | 8.635% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-04-21 | 31 | 23.0521 | 8.8374 | 31.8896 | 1.769 | 0.76558 | 0.23707 | 2.7717 | 8.691% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-04-21 | 32 | 23.3757 | 8.9915 | 32.3672 | 1.8224 | 0.76558 | 0.24062 | 2.8286 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-04-21 | 33 | 24.0717 | 9.2648 | 33.3365 | 1.9332 | 0.76558 | 0.24783 | 2.9466 | 8.839% | 9.405% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-04-21 | 34 | 25.0696 | 9.4052 | 34.4748 | 2.0675 | 0.76558 | 0.25629 | 3.0893 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-04-21 | 35 | 26.3853 | 10.5003 | 36.8856 | 2.3667 | 0.76558 | 0.27421 | 3.4065 | 9.235% | 9.826% | 6.64% | 1.1018 | 1.109 | 1.0711
2010-04-21 | 36 | 28.8631 | 11.9348 | 40.7978 | 2.8954 | 0.76558 | 0.3033 | 3.9643 | 9.717% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-04-21 | 37 | 31.6837 | 13.249 | 44.9327 | 3.512 | 0.76558 | 0.33403 | 4.6117 | 10.26% | 10.92% | 7.379% | 1.1144 | 1.1226 | 1.0797
2010-04-21 | 38 | 33.277 | 13.4829 | 46.7598 | 3.8035 | 0.76558 | 0.34762 | 4.9167 | 10.51% | 11.19% | 7.56% | 1.1175 | 1.126 | 1.0818
2010-04-21 | 39 | 32.7808 | 13.2706 | 46.0513 | 3.6891 | 0.76558 | 0.34235 | 4.797 | 10.42% | 11.08% | 7.49% | 1.1163 | 1.1246 | 1.081
2010-04-21 | 40 | 31.76 | 12.6104 | 44.3703 | 3.4247 | 0.76558 | 0.32985 | 4.5201 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-04-21 | 41 | 31.5874 | 12.096 | 43.6834 | 3.3195 | 0.76558 | 0.32475 | 4.4098 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-04-21 | 42 | 30.842 | 11.4602 | 42.3022 | 3.1129 | 0.76558 | 0.31448 | 4.1929 | 9.912% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-04-21 | 43 | 29.5612 | 11.0059 | 40.567 | 2.8627 | 0.76558 | 0.30158 | 3.9299 | 9.687% | 10.31% | 6.965% | 1.1073 | 1.1149 | 1.0749
2010-04-21 | 44 | 27.8674 | 10.4276 | 38.2949 | 2.551 | 0.76558 | 0.28469 | 3.6013 | 9.404% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2010-04-21 | 45 | 25.4268 | 9.6524 | 35.0792 | 2.1406 | 0.76558 | 0.26078 | 3.167 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-04-21 | 46 | 23.6458 | 9.0598 | 32.7056 | 1.8607 | 0.76558 | 0.24314 | 2.8694 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-04-21 | 47 | 22.512 | 8.4344 | 30.9464 | 1.6659 | 0.76558 | 0.23006 | 2.6616 | 8.601% | 9.151% | 6.184% | 1.0941 | 1.1007 | 1.0659
2010-04-21 | 48 | 20.6018 | 8.3973 | 28.999 | 1.4629 | 0.76558 | 0.21558 | 2.444 | 8.428% | 8.967% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-04-22 | 1 | 18.5768 | 7.5989 | 26.1757 | 1.1919 | 0.76558 | 0.19459 | 2.152 | 8.222% | 8.748% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-04-22 | 2 | 18.318 | 7.0268 | 25.3448 | 1.1174 | 0.76558 | 0.18842 | 2.0714 | 8.173% | 8.696% | 5.876% | 1.089 | 1.0952 | 1.0624
2010-04-22 | 3 | 17.6566 | 6.7014 | 24.358 | 1.0321 | 0.76558 | 0.18108 | 1.9788 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-04-22 | 4 | 17.0681 | 6.4204 | 23.4885 | 0.95972 | 0.76558 | 0.17462 | 1.8999 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-04-22 | 5 | 16.4642 | 6.2171 | 22.6812 | 0.89489 | 0.76558 | 0.16862 | 1.8291 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-04-22 | 6 | 16.0932 | 6.0852 | 22.1783 | 0.85564 | 0.76558 | 0.16488 | 1.7861 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-04-22 | 7 | 16.0061 | 5.9815 | 21.9876 | 0.84099 | 0.76558 | 0.16346 | 1.77 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-22 | 8 | 16.0769 | 6.0331 | 22.11 | 0.85038 | 0.76558 | 0.16437 | 1.7803 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-04-22 | 9 | 16.2647 | 6.1473 | 22.412 | 0.87377 | 0.76558 | 0.16661 | 1.806 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-22 | 10 | 16.3069 | 6.2369 | 22.5438 | 0.88407 | 0.76558 | 0.16759 | 1.8172 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-04-22 | 11 | 16.653 | 6.57 | 23.2231 | 0.93815 | 0.76558 | 0.17264 | 1.8764 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-04-22 | 12 | 17.2276 | 7.0317 | 24.2593 | 1.0237 | 0.76558 | 0.18035 | 1.9697 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-04-22 | 13 | 19.4837 | 8.1105 | 27.5941 | 1.3245 | 0.76558 | 0.20514 | 2.2953 | 8.318% | 8.85% | 5.981% | 1.0907 | 1.0971 | 1.0636
2010-04-22 | 14 | 21.8539 | 9.64 | 31.4939 | 1.7254 | 0.76558 | 0.23413 | 2.7251 | 8.653% | 9.207% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-04-22 | 15 | 25.0281 | 11.5488 | 36.5769 | 2.3273 | 0.76558 | 0.27192 | 3.3648 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-04-22 | 16 | 27.6137 | 12.9093 | 40.523 | 2.8565 | 0.76558 | 0.30125 | 3.9234 | 9.682% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-04-22 | 17 | 30.0694 | 13.6472 | 43.7165 | 3.3245 | 0.76558 | 0.32499 | 4.4151 | 10.1% | 10.75% | 7.261% | 1.1123 | 1.1204 | 1.0783
2010-04-22 | 18 | 31.5507 | 13.5539 | 45.1046 | 3.539 | 0.76558 | 0.33531 | 4.6399 | 10.29% | 10.95% | 7.396% | 1.1147 | 1.1229 | 1.0799
2010-04-22 | 19 | 32.0667 | 13.0588 | 45.1255 | 3.5422 | 0.76558 | 0.33547 | 4.6433 | 10.29% | 10.95% | 7.398% | 1.1147 | 1.1229 | 1.0799
2010-04-22 | 20 | 31.622 | 12.2479 | 43.8699 | 3.3479 | 0.76558 | 0.32613 | 4.4396 | 10.12% | 10.77% | 7.276% | 1.1126 | 1.1207 | 1.0785
2010-04-22 | 21 | 31.4782 | 11.7043 | 43.1825 | 3.2438 | 0.76558 | 0.32102 | 4.3304 | 10.03% | 10.67% | 7.21% | 1.1115 | 1.1194 | 1.0777
2010-04-22 | 22 | 30.5298 | 11.4334 | 41.9632 | 3.0632 | 0.76558 | 0.31196 | 4.1407 | 9.867% | 10.5% | 7.095% | 1.1095 | 1.1173 | 1.0764
2010-04-22 | 23 | 28.8785 | 10.7648 | 39.6434 | 2.7339 | 0.76558 | 0.29471 | 3.7941 | 9.571% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-04-22 | 24 | 27.0952 | 10.5883 | 37.6835 | 2.4702 | 0.76558 | 0.28014 | 3.516 | 9.33% | 9.927% | 6.708% | 1.1029 | 1.1102 | 1.0719
2010-04-22 | 25 | 25.7892 | 10.4101 | 36.1993 | 2.2795 | 0.76558 | 0.26911 | 3.3142 | 9.155% | 9.741% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-04-22 | 26 | 24.4535 | 9.8428 | 34.2962 | 2.0461 | 0.76558 | 0.25496 | 3.0666 | 8.942% | 9.514% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-04-22 | 27 | 23.9356 | 10.037 | 33.9726 | 2.0077 | 0.76558 | 0.25256 | 3.0258 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-04-22 | 28 | 23.8492 | 9.9728 | 33.822 | 1.9899 | 0.76558 | 0.25144 | 3.0069 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-04-22 | 29 | 23.2309 | 9.5313 | 32.7622 | 1.8672 | 0.76558 | 0.24356 | 2.8763 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-04-22 | 30 | 22.9735 | 9.2917 | 32.2652 | 1.8109 | 0.76558 | 0.23986 | 2.8164 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-04-22 | 31 | 23.7183 | 9.2467 | 32.965 | 1.8903 | 0.76558 | 0.24507 | 2.901 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-04-22 | 32 | 23.8488 | 9.5188 | 33.3676 | 1.9368 | 0.76558 | 0.24806 | 2.9504 | 8.842% | 9.408% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-04-22 | 33 | 24.2091 | 9.7809 | 33.99 | 2.0097 | 0.76558 | 0.25269 | 3.028 | 8.908% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-04-22 | 34 | 24.8962 | 10.0215 | 34.9177 | 2.1209 | 0.76558 | 0.25958 | 3.1461 | 9.01% | 9.587% | 6.478% | 1.099 | 1.106 | 1.0693
2010-04-22 | 35 | 26.4471 | 10.8959 | 37.343 | 2.4258 | 0.76558 | 0.27761 | 3.469 | 9.29% | 9.884% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-04-22 | 36 | 28.0857 | 12.2234 | 40.3091 | 2.8264 | 0.76558 | 0.29966 | 3.8917 | 9.655% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-04-22 | 37 | 30.9151 | 13.1977 | 44.1128 | 3.385 | 0.76558 | 0.32794 | 4.4786 | 10.15% | 10.8% | 7.3% | 1.113 | 1.1211 | 1.0787
2010-04-22 | 38 | 32.8107 | 13.4448 | 46.2555 | 3.7219 | 0.76558 | 0.34387 | 4.8313 | 10.44% | 11.11% | 7.51% | 1.1166 | 1.125 | 1.0812
2010-04-22 | 39 | 32.4939 | 12.8427 | 45.3366 | 3.5755 | 0.76558 | 0.33704 | 4.6781 | 10.32% | 10.98% | 7.419% | 1.1151 | 1.1233 | 1.0801
2010-04-22 | 40 | 31.2441 | 12.1579 | 43.402 | 3.2768 | 0.76558 | 0.32266 | 4.3651 | 10.06% | 10.7% | 7.231% | 1.1118 | 1.1198 | 1.0779
2010-04-22 | 41 | 30.9564 | 11.8236 | 42.7799 | 3.1836 | 0.76558 | 0.31803 | 4.2672 | 9.975% | 10.61% | 7.172% | 1.1108 | 1.1187 | 1.0773
2010-04-22 | 42 | 30.2518 | 11.4149 | 41.6667 | 3.02 | 0.76558 | 0.30976 | 4.0954 | 9.829% | 10.46% | 7.067% | 1.109 | 1.1168 | 1.076
2010-04-22 | 43 | 28.5984 | 10.8271 | 39.4255 | 2.7039 | 0.76558 | 0.29309 | 3.7626 | 9.543% | 10.15% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-04-22 | 44 | 27.3789 | 9.9736 | 37.3525 | 2.427 | 0.76558 | 0.27768 | 3.4703 | 9.291% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-04-22 | 45 | 25.1353 | 9.0423 | 34.1776 | 2.032 | 0.76558 | 0.25408 | 3.0516 | 8.929% | 9.5% | 6.42% | 1.098 | 1.105 | 1.0686
2010-04-22 | 46 | 22.5357 | 6.2952 | 28.8309 | 1.4459 | 0.76558 | 0.21433 | 2.4258 | 8.414% | 8.953% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-04-22 | 47 | 21.1158 | 5.8276 | 26.9434 | 1.2628 | 0.76558 | 0.2003 | 2.2287 | 8.272% | 8.801% | 5.947% | 1.0902 | 1.0965 | 1.0632
2010-04-22 | 48 | 19.8954 | 5.9563 | 25.8516 | 1.1625 | 0.76558 | 0.19218 | 2.1203 | 8.202% | 8.727% | 5.897% | 1.0893 | 1.0956 | 1.0627
2010-04-23 | 1 | 18.6177 | 5.314 | 23.9317 | 0.99628 | 0.76558 | 0.17791 | 1.9398 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-04-23 | 2 | 18.5596 | 7.5514 | 26.111 | 1.186 | 0.76558 | 0.19411 | 2.1457 | 8.218% | 8.743% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-04-23 | 3 | 17.4247 | 7.0037 | 24.4283 | 1.0381 | 0.76558 | 0.1816 | 1.9852 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2010-04-23 | 4 | 16.5467 | 6.752 | 23.2986 | 0.94427 | 0.76558 | 0.1732 | 1.8831 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-23 | 5 | 16.1446 | 6.8126 | 22.9572 | 0.91679 | 0.76558 | 0.17067 | 1.853 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-04-23 | 6 | 16.0892 | 6.6387 | 22.7279 | 0.89857 | 0.76558 | 0.16896 | 1.8331 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-23 | 7 | 16.1612 | 6.6282 | 22.7894 | 0.90345 | 0.76558 | 0.16942 | 1.8384 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-04-23 | 8 | 15.5119 | 6.5336 | 22.0455 | 0.84542 | 0.76558 | 0.16389 | 1.7749 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-23 | 9 | 15.7859 | 6.7309 | 22.5167 | 0.88195 | 0.76558 | 0.16739 | 1.8149 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-04-23 | 10 | 15.8588 | 6.7689 | 22.6277 | 0.89067 | 0.76558 | 0.16822 | 1.8245 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-04-23 | 11 | 16.8201 | 6.9667 | 23.7867 | 0.98425 | 0.76558 | 0.17683 | 1.9267 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-04-23 | 12 | 17.6259 | 7.4339 | 25.0597 | 1.0924 | 0.76558 | 0.1863 | 2.0443 | 8.158% | 8.68% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-04-23 | 13 | 19.1778 | 8.5816 | 27.7594 | 1.3405 | 0.76558 | 0.20637 | 2.3124 | 8.33% | 8.863% | 5.989% | 1.0909 | 1.0973 | 1.0637
2010-04-23 | 14 | 21.5627 | 10.3187 | 31.8814 | 1.7681 | 0.76558 | 0.23701 | 2.7707 | 8.691% | 9.247% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-04-23 | 15 | 25.1557 | 11.2313 | 36.3871 | 2.3032 | 0.76558 | 0.27051 | 3.3393 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-04-23 | 16 | 28.0124 | 12.349 | 40.3614 | 2.8338 | 0.76558 | 0.30005 | 3.8994 | 9.661% | 10.28% | 6.946% | 1.1069 | 1.1146 | 1.0746
2010-04-23 | 17 | 29.9345 | 13.1838 | 43.1183 | 3.2341 | 0.76558 | 0.32055 | 4.3203 | 10.02% | 10.66% | 7.204% | 1.1114 | 1.1193 | 1.0776
2010-04-23 | 18 | 31.1414 | 13.4955 | 44.6368 | 3.4659 | 0.76558 | 0.33184 | 4.5634 | 10.22% | 10.88% | 7.351% | 1.1139 | 1.1221 | 1.0793
2010-04-23 | 19 | 31.1146 | 13.0121 | 44.1267 | 3.3872 | 0.76558 | 0.32804 | 4.4808 | 10.15% | 10.8% | 7.301% | 1.113 | 1.1211 | 1.0788
2010-04-23 | 20 | 30.2511 | 12.3236 | 42.5747 | 3.1531 | 0.76558 | 0.31651 | 4.2352 | 9.948% | 10.58% | 7.152% | 1.1105 | 1.1184 | 1.077
2010-04-23 | 21 | 29.5474 | 11.5853 | 41.1328 | 2.9431 | 0.76558 | 0.30579 | 4.0145 | 9.76% | 10.38% | 7.017% | 1.1082 | 1.1159 | 1.0755
2010-04-23 | 22 | 28.514 | 11.2943 | 39.8083 | 2.7567 | 0.76558 | 0.29594 | 3.8182 | 9.591% | 10.21% | 6.896% | 1.1061 | 1.1137 | 1.0741
2010-04-23 | 23 | 26.7484 | 10.5795 | 37.328 | 2.4238 | 0.76558 | 0.2775 | 3.4669 | 9.288% | 9.882% | 6.678% | 1.1024 | 1.1097 | 1.0716
2010-04-23 | 24 | 25.5255 | 10.3103 | 35.8358 | 2.2339 | 0.76558 | 0.26641 | 3.2659 | 9.114% | 9.697% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-04-23 | 25 | 24.4483 | 9.9695 | 34.4179 | 2.0606 | 0.76558 | 0.25587 | 3.0821 | 8.955% | 9.528% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-04-23 | 26 | 23.5143 | 9.4128 | 32.9271 | 1.886 | 0.76558 | 0.24478 | 2.8964 | 8.796% | 9.359% | 6.325% | 1.0964 | 1.1033 | 1.0675
2010-04-23 | 27 | 23.4287 | 9.4182 | 32.8468 | 1.8768 | 0.76558 | 0.24419 | 2.8866 | 8.788% | 9.35% | 6.319% | 1.0963 | 1.1031 | 1.0674
2010-04-23 | 28 | 23.2838 | 9.3402 | 32.624 | 1.8514 | 0.76558 | 0.24253 | 2.8595 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1029 | 1.0673
2010-04-23 | 29 | 22.6655 | 9.1343 | 31.7998 | 1.7591 | 0.76558 | 0.2364 | 2.7611 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-04-23 | 30 | 22.2202 | 8.8756 | 31.0958 | 1.682 | 0.76558 | 0.23117 | 2.6788 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-04-23 | 31 | 22.6788 | 8.7651 | 31.4439 | 1.7199 | 0.76558 | 0.23376 | 2.7193 | 8.648% | 9.201% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-04-23 | 32 | 22.8369 | 8.8231 | 31.66 | 1.7436 | 0.76558 | 0.23536 | 2.7446 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2010-04-23 | 33 | 23.5839 | 9.1143 | 32.6982 | 1.8599 | 0.76558 | 0.24308 | 2.8685 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-04-23 | 34 | 24.4018 | 9.2379 | 33.6397 | 1.9685 | 0.76558 | 0.25008 | 2.9842 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2010-04-23 | 35 | 25.1654 | 10.1091 | 35.2745 | 2.1645 | 0.76558 | 0.26224 | 3.1923 | 9.05% | 9.629% | 6.507% | 1.0995 | 1.1066 | 1.0696
2010-04-23 | 36 | 27.3464 | 11.2817 | 38.6282 | 2.5956 | 0.76558 | 0.28717 | 3.6484 | 9.445% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-04-23 | 37 | 30.8901 | 12.7927 | 43.6828 | 3.3194 | 0.76558 | 0.32474 | 4.4097 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-04-23 | 38 | 32.3689 | 13.1281 | 45.4969 | 3.6008 | 0.76558 | 0.33823 | 4.7046 | 10.34% | 11% | 7.435% | 1.1153 | 1.1236 | 1.0803
2010-04-23 | 39 | 32.0269 | 12.8115 | 44.8385 | 3.4973 | 0.76558 | 0.33333 | 4.5962 | 10.25% | 10.91% | 7.37% | 1.1142 | 1.1224 | 1.0796
2010-04-23 | 40 | 31.3088 | 12.1994 | 43.5082 | 3.2929 | 0.76558 | 0.32345 | 4.3819 | 10.07% | 10.72% | 7.241% | 1.112 | 1.12 | 1.0781
2010-04-23 | 41 | 31.0208 | 11.8296 | 42.8504 | 3.1941 | 0.76558 | 0.31855 | 4.2782 | 9.984% | 10.62% | 7.179% | 1.1109 | 1.1189 | 1.0773
2010-04-23 | 42 | 30.2578 | 11.4442 | 41.702 | 3.0252 | 0.76558 | 0.31002 | 4.1007 | 9.833% | 10.46% | 7.07% | 1.1091 | 1.1169 | 1.0761
2010-04-23 | 43 | 28.1755 | 10.6321 | 38.8076 | 2.6198 | 0.76558 | 0.2885 | 3.6739 | 9.467% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-04-23 | 44 | 26.8682 | 9.9304 | 36.7986 | 2.3556 | 0.76558 | 0.27357 | 3.3947 | 9.225% | 9.816% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-04-23 | 45 | 24.7144 | 9.0062 | 33.7207 | 1.978 | 0.76558 | 0.25068 | 2.9943 | 8.88% | 9.448% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-04-23 | 46 | 22.4026 | 8.0185 | 30.4211 | 1.6098 | 0.76558 | 0.22615 | 2.6016 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-04-23 | 47 | 20.9113 | 7.7902 | 28.7015 | 1.433 | 0.76558 | 0.21337 | 2.4119 | 8.404% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2010-04-23 | 48 | 20.1791 | 7.9068 | 28.086 | 1.3722 | 0.76558 | 0.20879 | 2.3466 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-04-24 | 1 | 18.8829 | 7.0533 | 25.9362 | 1.1702 | 0.76558 | 0.19281 | 2.1286 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-04-24 | 2 | 18.6846 | 6.4896 | 25.1742 | 1.1024 | 0.76558 | 0.18715 | 2.0551 | 8.164% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-04-24 | 3 | 17.4483 | 6.1702 | 23.6186 | 0.97038 | 0.76558 | 0.17558 | 1.9115 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-04-24 | 4 | 16.788 | 6.0706 | 22.8585 | 0.90893 | 0.76558 | 0.16993 | 1.8444 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-24 | 5 | 16.3412 | 5.9024 | 22.2436 | 0.86069 | 0.76558 | 0.16536 | 1.7916 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-24 | 6 | 16.2795 | 5.8121 | 22.0916 | 0.84896 | 0.76558 | 0.16423 | 1.7788 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-24 | 7 | 15.9898 | 5.8773 | 21.8671 | 0.8318 | 0.76558 | 0.16256 | 1.7599 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-24 | 8 | 15.8182 | 5.8733 | 21.6915 | 0.81849 | 0.76558 | 0.16126 | 1.7453 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-24 | 9 | 16.183 | 5.8621 | 22.0451 | 0.84539 | 0.76558 | 0.16389 | 1.7749 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-24 | 10 | 16.4408 | 5.9738 | 22.4146 | 0.87397 | 0.76558 | 0.16663 | 1.8062 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-04-24 | 11 | 17.2412 | 6.3297 | 23.5709 | 0.96646 | 0.76558 | 0.17523 | 1.9073 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-04-24 | 12 | 18.0945 | 6.8121 | 24.9066 | 1.0791 | 0.76558 | 0.18516 | 2.0298 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2010-04-24 | 13 | 19.4838 | 7.6969 | 27.1808 | 1.2852 | 0.76558 | 0.20207 | 2.2528 | 8.288% | 8.819% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-04-24 | 14 | 22.3125 | 9.3974 | 31.71 | 1.7491 | 0.76558 | 0.23574 | 2.7505 | 8.674% | 9.229% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-04-24 | 15 | 25.9188 | 11.1497 | 37.0685 | 2.3903 | 0.76558 | 0.27557 | 3.4314 | 9.257% | 9.849% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-04-24 | 16 | 28.1949 | 12.6173 | 40.8122 | 2.8974 | 0.76558 | 0.3034 | 3.9664 | 9.719% | 10.34% | 6.988% | 1.1076 | 1.1153 | 1.0751
2010-04-24 | 17 | 30.3074 | 13.611 | 43.9184 | 3.3553 | 0.76558 | 0.32649 | 4.4473 | 10.13% | 10.77% | 7.281% | 1.1127 | 1.1208 | 1.0785
2010-04-24 | 18 | 31.1011 | 13.9623 | 45.0634 | 3.5325 | 0.76558 | 0.33501 | 4.6331 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-04-24 | 19 | 31.4084 | 13.5995 | 45.008 | 3.5238 | 0.76558 | 0.33459 | 4.624 | 10.27% | 10.93% | 7.387% | 1.1145 | 1.1227 | 1.0798
2010-04-24 | 20 | 30.2315 | 12.6332 | 42.8647 | 3.1962 | 0.76558 | 0.31866 | 4.2804 | 9.986% | 10.63% | 7.18% | 1.1109 | 1.1189 | 1.0774
2010-04-24 | 21 | 29.8949 | 11.8493 | 41.7442 | 3.0313 | 0.76558 | 0.31033 | 4.1072 | 9.839% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-04-24 | 22 | 28.6667 | 11.4972 | 40.1639 | 2.8061 | 0.76558 | 0.29858 | 3.8703 | 9.636% | 10.25% | 6.928% | 1.1066 | 1.1142 | 1.0744
2010-04-24 | 23 | 27.6326 | 10.9795 | 38.6121 | 2.5935 | 0.76558 | 0.28705 | 3.6461 | 9.443% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-04-24 | 24 | 26.3546 | 10.8903 | 37.2449 | 2.4131 | 0.76558 | 0.27688 | 3.4555 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-04-24 | 25 | 25.0328 | 10.4974 | 35.5302 | 2.196 | 0.76558 | 0.26414 | 3.2257 | 9.079% | 9.66% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-04-24 | 26 | 23.8546 | 9.8316 | 33.6862 | 1.974 | 0.76558 | 0.25043 | 2.99 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-04-24 | 27 | 23.7977 | 9.8439 | 33.6416 | 1.9687 | 0.76558 | 0.2501 | 2.9844 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2010-04-24 | 28 | 23.6538 | 9.643 | 33.2968 | 1.9286 | 0.76558 | 0.24753 | 2.9417 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-04-24 | 29 | 23.2781 | 9.285 | 32.5631 | 1.8445 | 0.76558 | 0.24208 | 2.8522 | 8.759% | 9.32% | 6.298% | 1.096 | 1.1028 | 1.0672
2010-04-24 | 30 | 23.2339 | 8.9534 | 32.1873 | 1.8022 | 0.76558 | 0.23928 | 2.8071 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-04-24 | 31 | 24.1977 | 8.8542 | 33.0519 | 1.9003 | 0.76558 | 0.24571 | 2.9116 | 8.809% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-04-24 | 32 | 23.9961 | 9.0159 | 33.012 | 1.8957 | 0.76558 | 0.24542 | 2.9067 | 8.805% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2010-04-24 | 33 | 23.9974 | 9.3508 | 33.3483 | 1.9346 | 0.76558 | 0.24792 | 2.9481 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2010-04-24 | 34 | 24.5126 | 9.2501 | 33.7627 | 1.9829 | 0.76558 | 0.251 | 2.9995 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-04-24 | 35 | 25.3737 | 9.4286 | 34.8023 | 2.1069 | 0.76558 | 0.25872 | 3.1312 | 8.997% | 9.573% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-04-24 | 36 | 27.2126 | 10.6912 | 37.9038 | 2.4992 | 0.76558 | 0.28178 | 3.5466 | 9.357% | 9.956% | 6.727% | 1.1032 | 1.1106 | 1.0721
2010-04-24 | 37 | 29.5681 | 11.8125 | 41.3806 | 2.9787 | 0.76558 | 0.30763 | 4.0519 | 9.792% | 10.42% | 7.04% | 1.1085 | 1.1163 | 1.0757
2010-04-24 | 38 | 30.8884 | 12.0271 | 42.9155 | 3.2038 | 0.76558 | 0.31904 | 4.2884 | 9.993% | 10.63% | 7.185% | 1.111 | 1.119 | 1.0774
2010-04-24 | 39 | 30.4998 | 11.7105 | 42.2103 | 3.0994 | 0.76558 | 0.3138 | 4.1787 | 9.9% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-04-24 | 40 | 29.7806 | 10.8781 | 40.6587 | 2.8757 | 0.76558 | 0.30226 | 3.9435 | 9.699% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-04-24 | 41 | 29.4804 | 10.2376 | 39.718 | 2.7442 | 0.76558 | 0.29527 | 3.805 | 9.58% | 10.19% | 6.888% | 1.106 | 1.1135 | 1.074
2010-04-24 | 42 | 28.6178 | 9.7629 | 38.3807 | 2.5625 | 0.76558 | 0.28533 | 3.6134 | 9.415% | 10.02% | 6.769% | 1.1039 | 1.1113 | 1.0726
2010-04-24 | 43 | 26.9229 | 9.2976 | 36.2204 | 2.2821 | 0.76558 | 0.26927 | 3.317 | 9.158% | 9.744% | 6.584% | 1.1008 | 1.108 | 1.0705
2010-04-24 | 44 | 25.1694 | 8.9163 | 34.0858 | 2.0211 | 0.76558 | 0.2534 | 3.04 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1048 | 1.0685
2010-04-24 | 45 | 23.4607 | 8.3842 | 31.8449 | 1.7641 | 0.76558 | 0.23674 | 2.7664 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2010-04-24 | 46 | 21.7794 | 7.5657 | 29.3451 | 1.498 | 0.76558 | 0.21816 | 2.4817 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-04-24 | 47 | 20.7026 | 7.3965 | 28.0991 | 1.3735 | 0.76558 | 0.20889 | 2.3479 | 8.356% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-04-24 | 48 | 19.6672 | 7.6177 | 27.2848 | 1.295 | 0.76558 | 0.20284 | 2.2634 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-04-25 | 1 | 18.3891 | 6.7091 | 25.0983 | 1.0958 | 0.76558 | 0.18658 | 2.0479 | 8.16% | 8.682% | 5.867% | 1.0888 | 1.0951 | 1.0623
2010-04-25 | 2 | 18.233 | 6.2383 | 24.4713 | 1.0417 | 0.76558 | 0.18192 | 1.9892 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-04-25 | 3 | 17.2121 | 5.8302 | 23.0423 | 0.9236 | 0.76558 | 0.1713 | 1.8605 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-04-25 | 4 | 15.9344 | 5.4729 | 21.4073 | 0.79719 | 0.76558 | 0.15914 | 1.7219 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 5 | 15.3731 | 5.3251 | 20.6982 | 0.74524 | 0.76558 | 0.15387 | 1.6647 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 6 | 15.2294 | 5.2559 | 20.4853 | 0.72999 | 0.76558 | 0.15229 | 1.6479 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 7 | 15.4861 | 5.1412 | 20.6273 | 0.74015 | 0.76558 | 0.15335 | 1.6591 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 8 | 15.185 | 5.0051 | 20.1901 | 0.70911 | 0.76558 | 0.1501 | 1.6248 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 9 | 15.0427 | 5.0248 | 20.0675 | 0.70052 | 0.76558 | 0.14918 | 1.6153 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-04-25 | 10 | 15.328 | 4.9654 | 20.2933 | 0.71638 | 0.76558 | 0.15086 | 1.6328 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 11 | 15.8027 | 5.0991 | 20.9018 | 0.75998 | 0.76558 | 0.15539 | 1.6809 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 12 | 16.4341 | 5.2536 | 21.6877 | 0.8182 | 0.76558 | 0.16123 | 1.745 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-25 | 13 | 17.5262 | 5.6845 | 23.2107 | 0.93716 | 0.76558 | 0.17255 | 1.8753 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-04-25 | 14 | 18.272 | 6.1173 | 24.3893 | 1.0347 | 0.76558 | 0.18131 | 1.9816 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-04-25 | 15 | 19.2774 | 6.9334 | 26.2108 | 1.1951 | 0.76558 | 0.19485 | 2.1555 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-04-25 | 16 | 20.1858 | 7.9256 | 28.1114 | 1.3747 | 0.76558 | 0.20898 | 2.3492 | 8.357% | 8.892% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-04-25 | 17 | 22.5419 | 8.8477 | 31.3896 | 1.714 | 0.76558 | 0.23335 | 2.7129 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-04-25 | 18 | 24.3927 | 9.3725 | 33.7652 | 1.9832 | 0.76558 | 0.25101 | 2.9998 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-04-25 | 19 | 24.939 | 9.6647 | 34.6036 | 2.0829 | 0.76558 | 0.25725 | 3.1058 | 8.975% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-04-25 | 20 | 24.5659 | 9.7872 | 34.3531 | 2.0529 | 0.76558 | 0.25539 | 3.0739 | 8.948% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-04-25 | 21 | 25.5134 | 9.582 | 35.0954 | 2.1426 | 0.76558 | 0.2609 | 3.1691 | 9.03% | 9.608% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-04-25 | 22 | 25.1111 | 9.4133 | 34.5244 | 2.0734 | 0.76558 | 0.25666 | 3.0957 | 8.967% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-25 | 23 | 24.5102 | 9.0688 | 33.579 | 1.9614 | 0.76558 | 0.24963 | 2.9766 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-04-25 | 24 | 23.3457 | 8.9429 | 32.2885 | 1.8136 | 0.76558 | 0.24004 | 2.8192 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-04-25 | 25 | 22.484 | 8.9889 | 31.473 | 1.7231 | 0.76558 | 0.23397 | 2.7227 | 8.651% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-04-25 | 26 | 21.7799 | 8.6593 | 30.4393 | 1.6118 | 0.76558 | 0.22629 | 2.6036 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-04-25 | 27 | 21.4474 | 8.9984 | 30.4458 | 1.6125 | 0.76558 | 0.22634 | 2.6044 | 8.554% | 9.102% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-04-25 | 28 | 21.2173 | 8.9571 | 30.1744 | 1.5838 | 0.76558 | 0.22432 | 2.5737 | 8.53% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2010-04-25 | 29 | 20.5413 | 8.6193 | 29.1606 | 1.4792 | 0.76558 | 0.21678 | 2.4616 | 8.441% | 8.982% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-04-25 | 30 | 20.0979 | 8.1722 | 28.2701 | 1.3902 | 0.76558 | 0.21016 | 2.366 | 8.369% | 8.905% | 6.017% | 1.0913 | 1.0978 | 1.064
2010-04-25 | 31 | 20.5408 | 8.0697 | 28.6105 | 1.4239 | 0.76558 | 0.21269 | 2.4022 | 8.396% | 8.934% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-04-25 | 32 | 20.3407 | 8.0366 | 28.3774 | 1.4008 | 0.76558 | 0.21096 | 2.3773 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-04-25 | 33 | 20.5977 | 8.3965 | 28.9941 | 1.4624 | 0.76558 | 0.21555 | 2.4435 | 8.428% | 8.967% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-04-25 | 34 | 21.3596 | 8.5469 | 29.9065 | 1.5558 | 0.76558 | 0.22233 | 2.5437 | 8.506% | 9.05% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-04-25 | 35 | 22.6807 | 9.1921 | 31.8728 | 1.7672 | 0.76558 | 0.23695 | 2.7697 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-04-25 | 36 | 24.2912 | 10.3929 | 34.6841 | 2.0926 | 0.76558 | 0.25785 | 3.1161 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-04-25 | 37 | 26.5157 | 11.3798 | 37.8956 | 2.4981 | 0.76558 | 0.28172 | 3.5454 | 9.356% | 9.954% | 6.727% | 1.1032 | 1.1105 | 1.0721
2010-04-25 | 38 | 27.4199 | 11.346 | 38.7659 | 2.6142 | 0.76558 | 0.28819 | 3.6679 | 9.462% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2010-04-25 | 39 | 27.0032 | 10.5386 | 37.5417 | 2.4517 | 0.76558 | 0.27909 | 3.4963 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-04-25 | 40 | 25.567 | 9.9292 | 35.4963 | 2.1918 | 0.76558 | 0.26388 | 3.2213 | 9.075% | 9.656% | 6.525% | 1.0998 | 1.1069 | 1.0698
2010-04-25 | 41 | 24.6072 | 9.5563 | 34.1635 | 2.0303 | 0.76558 | 0.25398 | 3.0498 | 8.927% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-04-25 | 42 | 24.2111 | 9.3475 | 33.5586 | 1.959 | 0.76558 | 0.24948 | 2.9741 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-04-25 | 43 | 23.3666 | 8.9211 | 32.2877 | 1.8135 | 0.76558 | 0.24003 | 2.8191 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-04-25 | 44 | 22.2048 | 8.4479 | 30.6527 | 1.6345 | 0.76558 | 0.22788 | 2.6279 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-04-25 | 45 | 20.1379 | 7.8591 | 27.997 | 1.3635 | 0.76558 | 0.20813 | 2.3372 | 8.348% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2010-04-25 | 46 | 18.487 | 7.2605 | 25.7475 | 1.1532 | 0.76558 | 0.19141 | 2.1102 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-04-25 | 47 | 18.2313 | 7.3409 | 25.5721 | 1.1375 | 0.76558 | 0.19011 | 2.0932 | 8.186% | 8.709% | 5.885% | 1.0892 | 1.0954 | 1.0625
2010-04-25 | 48 | 17.6713 | 7.6052 | 25.2764 | 1.1114 | 0.76558 | 0.18791 | 2.0649 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-04-26 | 1 | 16.0177 | 4.8976 | 20.9153 | 0.76096 | 0.76558 | 0.15549 | 1.682 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-26 | 2 | 15.6165 | 4.3378 | 19.9543 | 0.69264 | 0.76558 | 0.14834 | 1.6066 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-26 | 3 | 14.7242 | 3.9378 | 18.662 | 0.60583 | 0.76558 | 0.13874 | 1.5101 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-04-26 | 4 | 14.194 | 3.6981 | 17.8922 | 0.55688 | 0.76558 | 0.13301 | 1.4555 | 8.135% | 8.655% | 5.849% | 1.0885 | 1.0948 | 1.0621
2010-04-26 | 5 | 13.6606 | 3.5835 | 17.2441 | 0.51727 | 0.76558 | 0.12819 | 1.411 | 8.183% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-04-26 | 6 | 13.0711 | 3.4997 | 16.5708 | 0.47766 | 0.76558 | 0.12319 | 1.3664 | 8.246% | 8.774% | 5.929% | 1.0899 | 1.0962 | 1.063
2010-04-26 | 7 | 13.1015 | 3.5889 | 16.6904 | 0.48458 | 0.76558 | 0.12408 | 1.3742 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-04-26 | 8 | 13.1868 | 3.6644 | 16.8512 | 0.49396 | 0.76558 | 0.12527 | 1.3848 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-04-26 | 9 | 13.2277 | 3.6641 | 16.8919 | 0.49635 | 0.76558 | 0.12558 | 1.3875 | 8.214% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2010-04-26 | 10 | 13.2871 | 3.674 | 16.961 | 0.50043 | 0.76558 | 0.12609 | 1.3921 | 8.208% | 8.733% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-04-26 | 11 | 13.303 | 3.6964 | 16.9994 | 0.50269 | 0.76558 | 0.12638 | 1.3946 | 8.204% | 8.729% | 5.899% | 1.0894 | 1.0956 | 1.0627
2010-04-26 | 12 | 13.5905 | 3.781 | 17.3715 | 0.52494 | 0.76558 | 0.12914 | 1.4197 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2010-04-26 | 13 | 14.6249 | 3.9572 | 18.5821 | 0.60065 | 0.76558 | 0.13814 | 1.5044 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-04-26 | 14 | 15.2706 | 4.2378 | 19.5084 | 0.66203 | 0.76558 | 0.14503 | 1.5726 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-04-26 | 15 | 16.3482 | 3.6408 | 19.989 | 0.69505 | 0.76558 | 0.1486 | 1.6092 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-04-26 | 16 | 17.3101 | 3.8367 | 21.1468 | 0.7779 | 0.76558 | 0.15721 | 1.7007 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-26 | 17 | 18.9358 | 4.5442 | 23.48 | 0.95903 | 0.76558 | 0.17455 | 1.8992 | 8.088% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-04-26 | 18 | 20.4708 | 5.1961 | 25.6669 | 1.146 | 0.76558 | 0.19081 | 2.1024 | 8.191% | 8.715% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-04-26 | 19 | 21.6783 | 5.8147 | 27.493 | 1.3149 | 0.76558 | 0.20439 | 2.2848 | 8.311% | 8.842% | 5.975% | 1.0906 | 1.097 | 1.0636
2010-04-26 | 20 | 22.2692 | 6.0256 | 28.2948 | 1.3927 | 0.76558 | 0.21035 | 2.3686 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-04-26 | 21 | 23.532 | 5.8968 | 29.4289 | 1.5065 | 0.76558 | 0.21878 | 2.4909 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-04-26 | 22 | 23.6048 | 6.0507 | 29.6555 | 1.5298 | 0.76558 | 0.22046 | 2.5159 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-04-26 | 23 | 22.9286 | 5.8281 | 28.7567 | 1.4385 | 0.76558 | 0.21378 | 2.4179 | 8.408% | 8.946% | 6.045% | 1.0918 | 1.0983 | 1.0643
2010-04-26 | 24 | 22.4131 | 5.6229 | 28.0359 | 1.3673 | 0.76558 | 0.20842 | 2.3413 | 8.351% | 8.886% | 6.004% | 1.0911 | 1.0975 | 1.0639
2010-04-26 | 25 | 21.7238 | 5.6664 | 27.3902 | 1.305 | 0.76558 | 0.20362 | 2.2742 | 8.303% | 8.835% | 5.97% | 1.0905 | 1.0969 | 1.0635
2010-04-26 | 26 | 20.5173 | 5.2383 | 25.7556 | 1.1539 | 0.76558 | 0.19147 | 2.111 | 8.196% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-04-26 | 27 | 20.8481 | 5.4783 | 26.3265 | 1.2056 | 0.76558 | 0.19571 | 2.1669 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2010-04-26 | 28 | 20.6451 | 5.5119 | 26.1569 | 1.1902 | 0.76558 | 0.19445 | 2.1502 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-04-26 | 29 | 20.07 | 5.0623 | 25.1323 | 1.0988 | 0.76558 | 0.18684 | 2.0512 | 8.161% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-04-26 | 30 | 19.7119 | 4.8552 | 24.5671 | 1.0499 | 0.76558 | 0.18263 | 1.9981 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-04-26 | 31 | 19.6682 | 4.7176 | 24.3858 | 1.0344 | 0.76558 | 0.18129 | 1.9813 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-04-26 | 32 | 19.4531 | 4.8252 | 24.2784 | 1.0254 | 0.76558 | 0.18049 | 1.9714 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-04-26 | 33 | 19.8842 | 5.0733 | 24.9575 | 1.0835 | 0.76558 | 0.18554 | 2.0346 | 8.152% | 8.674% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-04-26 | 34 | 20.5155 | 5.2614 | 25.7769 | 1.1558 | 0.76558 | 0.19163 | 2.113 | 8.197% | 8.722% | 5.894% | 1.0893 | 1.0956 | 1.0626
2010-04-26 | 35 | 21.7499 | 5.8771 | 27.6271 | 1.3277 | 0.76558 | 0.20538 | 2.2987 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2010-04-26 | 36 | 23.604 | 6.8955 | 30.4995 | 1.6182 | 0.76558 | 0.22674 | 2.6105 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-04-26 | 37 | 25.9566 | 7.9489 | 33.9055 | 1.9997 | 0.76558 | 0.25206 | 3.0174 | 8.899% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-04-26 | 38 | 26.6451 | 8.0874 | 34.7325 | 2.0985 | 0.76558 | 0.25821 | 3.1223 | 8.989% | 9.565% | 6.463% | 1.0988 | 1.1058 | 1.0691
2010-04-26 | 39 | 25.8412 | 7.6866 | 33.5278 | 1.9554 | 0.76558 | 0.24925 | 2.9703 | 8.859% | 9.426% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-04-26 | 40 | 24.8508 | 7.1679 | 32.0187 | 1.7834 | 0.76558 | 0.23803 | 2.787 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-04-26 | 41 | 24.117 | 6.7591 | 30.8761 | 1.6584 | 0.76558 | 0.22954 | 2.6535 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-04-26 | 42 | 23.6003 | 6.3859 | 29.9862 | 1.5642 | 0.76558 | 0.22292 | 2.5526 | 8.513% | 9.058% | 6.121% | 1.093 | 1.0996 | 1.0652
2010-04-26 | 43 | 22.2652 | 5.6402 | 27.9053 | 1.3546 | 0.76558 | 0.20745 | 2.3276 | 8.341% | 8.875% | 5.997% | 1.091 | 1.0974 | 1.0638
2010-04-26 | 44 | 20.569 | 5.0311 | 25.6001 | 1.14 | 0.76558 | 0.19031 | 2.0959 | 8.187% | 8.711% | 5.887% | 1.0892 | 1.0954 | 1.0625
2010-04-26 | 45 | 18.8895 | 4.4677 | 23.3572 | 0.94902 | 0.76558 | 0.17364 | 1.8882 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-26 | 46 | 17.0224 | 4.6285 | 21.6509 | 0.81543 | 0.76558 | 0.16096 | 1.742 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-26 | 47 | 16.4781 | 4.7059 | 21.184 | 0.78064 | 0.76558 | 0.15748 | 1.7037 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-26 | 48 | 15.616 | 4.8469 | 20.4629 | 0.7284 | 0.76558 | 0.15212 | 1.6461 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-04-27 | 1 | 14.2088 | 3.9446 | 18.1534 | 0.57326 | 0.76558 | 0.13495 | 1.4738 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-04-27 | 2 | 13.8622 | 3.5713 | 17.4335 | 0.5287 | 0.76558 | 0.1296 | 1.4239 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-04-27 | 3 | 13.173 | 3.3571 | 16.5301 | 0.47532 | 0.76558 | 0.12289 | 1.3638 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2010-04-27 | 4 | 13.0431 | 3.2797 | 16.3228 | 0.46347 | 0.76558 | 0.12135 | 1.3504 | 8.273% | 8.803% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-04-27 | 5 | 12.6989 | 3.2262 | 15.9251 | 0.44116 | 0.76558 | 0.11839 | 1.3251 | 8.321% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-04-27 | 6 | 12.367 | 3.1343 | 15.5013 | 0.41799 | 0.76558 | 0.11524 | 1.2988 | 8.379% | 8.915% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-04-27 | 7 | 12.0811 | 3.1517 | 15.2328 | 0.40364 | 0.76558 | 0.11324 | 1.2825 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-04-27 | 8 | 12.203 | 3.1679 | 15.3708 | 0.41099 | 0.76558 | 0.11427 | 1.2908 | 8.398% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2010-04-27 | 9 | 12.3521 | 3.3168 | 15.6688 | 0.42708 | 0.76558 | 0.11648 | 1.3091 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-04-27 | 10 | 12.4535 | 3.3633 | 15.8168 | 0.43518 | 0.76558 | 0.11758 | 1.3183 | 8.335% | 8.869% | 5.993% | 1.0909 | 1.0973 | 1.0637
2010-04-27 | 11 | 12.6635 | 3.3726 | 16.0362 | 0.44734 | 0.76558 | 0.11921 | 1.3321 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-04-27 | 12 | 13.2161 | 3.7233 | 16.9395 | 0.49915 | 0.76558 | 0.12593 | 1.3907 | 8.21% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-04-27 | 13 | 15.0978 | 4.5003 | 19.5982 | 0.66814 | 0.76558 | 0.1457 | 1.5794 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-04-27 | 14 | 17.2158 | 5.9662 | 23.182 | 0.93484 | 0.76558 | 0.17234 | 1.8728 | 8.078% | 8.596% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-04-27 | 15 | 20.8791 | 6.9047 | 27.7839 | 1.3428 | 0.76558 | 0.20655 | 2.315 | 8.332% | 8.865% | 5.991% | 1.0909 | 1.0973 | 1.0637
2010-04-27 | 16 | 23.6733 | 7.6047 | 31.278 | 1.7018 | 0.76558 | 0.23252 | 2.6999 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-04-27 | 17 | 25.1732 | 7.5952 | 32.7684 | 1.8679 | 0.76558 | 0.2436 | 2.877 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.103 | 1.0674
2010-04-27 | 18 | 25.1907 | 7.9836 | 33.1743 | 1.9144 | 0.76558 | 0.24662 | 2.9266 | 8.822% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-04-27 | 19 | 25.1181 | 7.6633 | 32.7814 | 1.8693 | 0.76558 | 0.2437 | 2.8786 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-04-27 | 20 | 24.9879 | 7.307 | 32.2948 | 1.8143 | 0.76558 | 0.24008 | 2.8199 | 8.732% | 9.291% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-04-27 | 21 | 25.4978 | 7.359 | 32.8569 | 1.878 | 0.76558 | 0.24426 | 2.8878 | 8.789% | 9.352% | 6.319% | 1.0964 | 1.1032 | 1.0675
2010-04-27 | 22 | 23.575 | 7.7154 | 31.2904 | 1.7032 | 0.76558 | 0.23262 | 2.7014 | 8.633% | 9.186% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-04-27 | 23 | 21.7214 | 7.4154 | 29.1368 | 1.4768 | 0.76558 | 0.21661 | 2.459 | 8.439% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-04-27 | 24 | 21.8568 | 7.6056 | 29.4624 | 1.51 | 0.76558 | 0.21903 | 2.4946 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-04-27 | 25 | 21.6487 | 7.4314 | 29.0801 | 1.471 | 0.76558 | 0.21618 | 2.4528 | 8.435% | 8.974% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-04-27 | 26 | 21.6921 | 7.1411 | 28.8333 | 1.4462 | 0.76558 | 0.21435 | 2.4261 | 8.414% | 8.953% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-04-27 | 27 | 22.2093 | 7.1264 | 29.3356 | 1.497 | 0.76558 | 0.21808 | 2.4807 | 8.456% | 8.997% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-04-27 | 28 | 21.9278 | 7.2056 | 29.1334 | 1.4764 | 0.76558 | 0.21658 | 2.4586 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-04-27 | 29 | 21.5481 | 7.001 | 28.5491 | 1.4178 | 0.76558 | 0.21224 | 2.3956 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-04-27 | 30 | 26.5609 | 6.7581 | 33.319 | 1.9312 | 0.76558 | 0.2477 | 2.9444 | 8.837% | 9.403% | 6.354% | 1.0969 | 1.1038 | 1.0678
2010-04-27 | 31 | 26.6621 | 6.6473 | 33.3095 | 1.9301 | 0.76558 | 0.24763 | 2.9433 | 8.836% | 9.402% | 6.353% | 1.0969 | 1.1038 | 1.0678
2010-04-27 | 32 | 24.7593 | 6.6465 | 31.4058 | 1.7157 | 0.76558 | 0.23347 | 2.7148 | 8.644% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-04-27 | 33 | 24.1994 | 7.2014 | 31.4008 | 1.7152 | 0.76558 | 0.23344 | 2.7142 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-04-27 | 34 | 24.177 | 7.5464 | 31.7234 | 1.7506 | 0.76558 | 0.23584 | 2.752 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-04-27 | 35 | 24.6012 | 7.97 | 32.5712 | 1.8454 | 0.76558 | 0.24214 | 2.8532 | 8.76% | 9.32% | 6.298% | 1.096 | 1.1028 | 1.0672
2010-04-27 | 36 | 25.9608 | 8.6951 | 34.6559 | 2.0892 | 0.76558 | 0.25764 | 3.1125 | 8.981% | 9.556% | 6.457% | 1.0987 | 1.1057 | 1.069
2010-04-27 | 37 | 28.549 | 9.3585 | 37.9075 | 2.4997 | 0.76558 | 0.28181 | 3.5471 | 9.357% | 9.956% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-04-27 | 38 | 28.9451 | 9.0877 | 38.0328 | 2.5162 | 0.76558 | 0.28274 | 3.5646 | 9.372% | 9.972% | 6.739% | 1.1034 | 1.1108 | 1.0723
2010-04-27 | 39 | 28.5002 | 8.5272 | 37.0274 | 2.385 | 0.76558 | 0.27527 | 3.4258 | 9.252% | 9.844% | 6.652% | 1.102 | 1.1092 | 1.0713
2010-04-27 | 40 | 27.6739 | 7.9568 | 35.6308 | 2.2084 | 0.76558 | 0.26488 | 3.2389 | 9.09% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-04-27 | 41 | 27.4305 | 7.557 | 34.9875 | 2.1294 | 0.76558 | 0.2601 | 3.1551 | 9.018% | 9.595% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-04-27 | 42 | 26.2389 | 7.1107 | 33.3496 | 1.9347 | 0.76558 | 0.24792 | 2.9482 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2010-04-27 | 43 | 24.7723 | 6.6127 | 31.385 | 1.7135 | 0.76558 | 0.23332 | 2.7124 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-04-27 | 44 | 23.6011 | 6.2492 | 29.8503 | 1.55 | 0.76558 | 0.22191 | 2.5375 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2010-04-27 | 45 | 21.6341 | 5.5143 | 27.1484 | 1.2821 | 0.76558 | 0.20182 | 2.2495 | 8.286% | 8.816% | 5.958% | 1.0903 | 1.0967 | 1.0634
2010-04-27 | 46 | 19.4754 | 7.1954 | 26.6709 | 1.2374 | 0.76558 | 0.19827 | 2.2012 | 8.253% | 8.782% | 5.934% | 1.09 | 1.0963 | 1.0631
2010-04-27 | 47 | 18.1886 | 7.0932 | 25.2818 | 1.1119 | 0.76558 | 0.18795 | 2.0654 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-04-27 | 48 | 17.0693 | 7.2558 | 24.3251 | 1.0293 | 0.76558 | 0.18084 | 1.9757 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-04-28 | 1 | 15.7761 | 6.2128 | 21.9889 | 0.84109 | 0.76558 | 0.16347 | 1.7701 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-04-28 | 2 | 15.776 | 3.1244 | 18.9004 | 0.62141 | 0.76558 | 0.14051 | 1.5275 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-04-28 | 3 | 15.1582 | 3.2339 | 18.3922 | 0.58844 | 0.76558 | 0.13673 | 1.4907 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-04-28 | 4 | 14.2519 | 3.1722 | 17.4241 | 0.52813 | 0.76558 | 0.12953 | 1.4232 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-04-28 | 5 | 13.7213 | 3.0711 | 16.7923 | 0.49052 | 0.76558 | 0.12484 | 1.3809 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-04-28 | 6 | 13.5481 | 3.0006 | 16.5487 | 0.47639 | 0.76558 | 0.12303 | 1.365 | 8.248% | 8.776% | 5.931% | 1.0899 | 1.0962 | 1.063
2010-04-28 | 7 | 13.8505 | 2.984 | 16.8346 | 0.49299 | 0.76558 | 0.12515 | 1.3837 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-04-28 | 8 | 13.6206 | 2.8373 | 16.4579 | 0.47117 | 0.76558 | 0.12235 | 1.3591 | 8.258% | 8.787% | 5.938% | 1.09 | 1.0963 | 1.0631
2010-04-28 | 9 | 13.5481 | 2.8885 | 16.4366 | 0.46996 | 0.76558 | 0.12219 | 1.3577 | 8.26% | 8.789% | 5.939% | 1.09 | 1.0964 | 1.0631
2010-04-28 | 10 | 13.692 | 2.9159 | 16.608 | 0.47981 | 0.76558 | 0.12347 | 1.3689 | 8.242% | 8.77% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-04-28 | 11 | 14.3525 | 3.0819 | 17.4344 | 0.52875 | 0.76558 | 0.12961 | 1.4239 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-04-28 | 12 | 15.3315 | 3.4953 | 18.8267 | 0.61657 | 0.76558 | 0.13996 | 1.5221 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-28 | 13 | 17.0416 | 4.1583 | 21.2 | 0.78182 | 0.76558 | 0.1576 | 1.705 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-28 | 14 | 19.3804 | 5.2696 | 24.65 | 1.057 | 0.76558 | 0.18325 | 2.0058 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-04-28 | 15 | 23.1802 | 7.2356 | 30.4158 | 1.6093 | 0.76558 | 0.22611 | 2.601 | 8.551% | 9.099% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-04-28 | 16 | 25.7945 | 7.961 | 33.7555 | 1.9821 | 0.76558 | 0.25094 | 2.9986 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-04-28 | 17 | 27.1218 | 7.7382 | 34.86 | 2.1139 | 0.76558 | 0.25915 | 3.1387 | 9.004% | 9.58% | 6.474% | 1.0989 | 1.1059 | 1.0692
2010-04-28 | 18 | 27.1745 | 6.8357 | 34.0102 | 2.0121 | 0.76558 | 0.25284 | 3.0305 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2010-04-28 | 19 | 26.2733 | 6.7976 | 33.0709 | 1.9025 | 0.76558 | 0.24585 | 2.9139 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-04-28 | 20 | 25.0368 | 6.7636 | 31.8004 | 1.7591 | 0.76558 | 0.23641 | 2.7611 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-04-28 | 21 | 25.0583 | 6.404 | 31.4624 | 1.7219 | 0.76558 | 0.2339 | 2.7214 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-04-28 | 22 | 24.2458 | 6.4112 | 30.6571 | 1.6349 | 0.76558 | 0.22791 | 2.6284 | 8.574% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-04-28 | 23 | 23.2766 | 5.9895 | 29.2662 | 1.4899 | 0.76558 | 0.21757 | 2.4731 | 8.45% | 8.991% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-04-28 | 24 | 22.6384 | 5.7995 | 28.4379 | 1.4068 | 0.76558 | 0.21141 | 2.3838 | 8.382% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2010-04-28 | 25 | 21.9852 | 5.8959 | 27.8811 | 1.3522 | 0.76558 | 0.20727 | 2.3251 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-04-28 | 26 | 21.3524 | 5.4857 | 26.8381 | 1.253 | 0.76558 | 0.19952 | 2.2181 | 8.265% | 8.794% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-04-28 | 27 | 21.238 | 5.7235 | 26.9615 | 1.2645 | 0.76558 | 0.20043 | 2.2305 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-04-28 | 28 | 21.2539 | 5.6815 | 26.9354 | 1.2621 | 0.76558 | 0.20024 | 2.2279 | 8.271% | 8.801% | 5.947% | 1.0902 | 1.0965 | 1.0632
2010-04-28 | 29 | 20.9294 | 5.405 | 26.3344 | 1.2064 | 0.76558 | 0.19577 | 2.1677 | 8.232% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2010-04-28 | 30 | 20.7126 | 5.1765 | 25.8891 | 1.1659 | 0.76558 | 0.19246 | 2.124 | 8.204% | 8.729% | 5.899% | 1.0894 | 1.0956 | 1.0627
2010-04-28 | 31 | 21.1952 | 5.3099 | 26.5051 | 1.2221 | 0.76558 | 0.19704 | 2.1847 | 8.243% | 8.77% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-04-28 | 32 | 21.0153 | 5.4999 | 26.5152 | 1.223 | 0.76558 | 0.19712 | 2.1857 | 8.243% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2010-04-28 | 33 | 21.4033 | 5.949 | 27.3524 | 1.3014 | 0.76558 | 0.20334 | 2.2704 | 8.3% | 8.832% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-04-28 | 34 | 21.8761 | 6.11 | 27.9861 | 1.3624 | 0.76558 | 0.20805 | 2.3361 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0638
2010-04-28 | 35 | 23.2397 | 6.5453 | 29.785 | 1.5432 | 0.76558 | 0.22143 | 2.5302 | 8.495% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2010-04-28 | 36 | 25.3152 | 7.8838 | 33.199 | 1.9173 | 0.76558 | 0.24681 | 2.9297 | 8.825% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-04-28 | 37 | 28.2794 | 9.1273 | 37.4066 | 2.4341 | 0.76558 | 0.27809 | 3.4777 | 9.297% | 9.892% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-04-28 | 38 | 29.6651 | 9.0494 | 38.7145 | 2.6073 | 0.76558 | 0.28781 | 3.6606 | 9.455% | 10.06% | 6.798% | 1.1044 | 1.1119 | 1.0729
2010-04-28 | 39 | 29.343 | 8.4209 | 37.7639 | 2.4808 | 0.76558 | 0.28074 | 3.5271 | 9.34% | 9.938% | 6.715% | 1.103 | 1.1103 | 1.072
2010-04-28 | 40 | 28.9189 | 7.7521 | 36.671 | 2.3393 | 0.76558 | 0.27262 | 3.3775 | 9.21% | 9.8% | 6.622% | 1.1014 | 1.1086 | 1.0709
2010-04-28 | 41 | 28.6255 | 7.2849 | 35.9104 | 2.2432 | 0.76558 | 0.26696 | 3.2758 | 9.122% | 9.706% | 6.559% | 1.1004 | 1.1075 | 1.0702
2010-04-28 | 42 | 27.5708 | 6.7856 | 34.3564 | 2.0533 | 0.76558 | 0.25541 | 3.0743 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-04-28 | 43 | 26.0326 | 6.2463 | 32.2789 | 1.8125 | 0.76558 | 0.23997 | 2.818 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-04-28 | 44 | 24.6054 | 5.9571 | 30.5626 | 1.6249 | 0.76558 | 0.22721 | 2.6176 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-04-28 | 45 | 22.738 | 5.5245 | 28.2625 | 1.3895 | 0.76558 | 0.21011 | 2.3652 | 8.369% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-04-28 | 46 | 20.5662 | 5.4136 | 25.9798 | 1.1741 | 0.76558 | 0.19314 | 2.1328 | 8.21% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-04-28 | 47 | 19.564 | 5.2133 | 24.7773 | 1.0679 | 0.76558 | 0.1842 | 2.0177 | 8.143% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-04-28 | 48 | 18.2136 | 5.2124 | 23.426 | 0.95462 | 0.76558 | 0.17415 | 1.8943 | 8.087% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-04-29 | 1 | 16.9343 | 4.1857 | 21.12 | 0.77593 | 0.76558 | 0.15701 | 1.6985 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-04-29 | 2 | 16.8613 | 3.7958 | 20.6571 | 0.74229 | 0.76558 | 0.15357 | 1.6614 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-29 | 3 | 15.8999 | 3.5197 | 19.4196 | 0.65602 | 0.76558 | 0.14437 | 1.566 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2010-04-29 | 4 | 15.2407 | 3.3183 | 18.559 | 0.59916 | 0.76558 | 0.13797 | 1.5027 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-04-29 | 5 | 14.6498 | 3.4134 | 18.0633 | 0.56758 | 0.76558 | 0.13428 | 1.4674 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-04-29 | 6 | 14.5635 | 3.3647 | 17.9282 | 0.55912 | 0.76558 | 0.13328 | 1.458 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-04-29 | 7 | 14.8438 | 3.2881 | 18.1318 | 0.5719 | 0.76558 | 0.13479 | 1.4723 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-04-29 | 8 | 14.9151 | 3.253 | 18.1681 | 0.57419 | 0.76558 | 0.13506 | 1.4748 | 8.118% | 8.637% | 5.837% | 1.0883 | 1.0945 | 1.062
2010-04-29 | 9 | 14.8945 | 3.3385 | 18.233 | 0.5783 | 0.76558 | 0.13555 | 1.4794 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-04-29 | 10 | 15.0949 | 3.5382 | 18.6331 | 0.60395 | 0.76558 | 0.13852 | 1.5081 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-04-29 | 11 | 15.3118 | 3.8077 | 19.1195 | 0.6359 | 0.76558 | 0.14214 | 1.5436 | 8.074% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-04-29 | 12 | 15.7512 | 4.187 | 19.9382 | 0.69152 | 0.76558 | 0.14822 | 1.6053 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-29 | 13 | 17.7447 | 5.1461 | 22.8909 | 0.9115 | 0.76558 | 0.17017 | 1.8473 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-04-29 | 14 | 20.2677 | 6.4561 | 26.7239 | 1.2423 | 0.76558 | 0.19867 | 2.2066 | 8.257% | 8.785% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-04-29 | 15 | 24.2601 | 7.5236 | 31.7836 | 1.7573 | 0.76558 | 0.23628 | 2.7591 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2010-04-29 | 16 | 26.6437 | 8.4071 | 35.0507 | 2.1371 | 0.76558 | 0.26057 | 3.1633 | 9.025% | 9.602% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-04-29 | 17 | 28.2946 | 8.8228 | 37.1173 | 2.3966 | 0.76558 | 0.27593 | 3.4381 | 9.263% | 9.856% | 6.66% | 1.1021 | 1.1093 | 1.0714
2010-04-29 | 18 | 28.9485 | 8.6385 | 37.587 | 2.4576 | 0.76558 | 0.27943 | 3.5026 | 9.319% | 9.915% | 6.7% | 1.1028 | 1.1101 | 1.0718
2010-04-29 | 19 | 28.8349 | 8.3899 | 37.2249 | 2.4105 | 0.76558 | 0.27673 | 3.4528 | 9.275% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2010-04-29 | 20 | 28.2401 | 8.1817 | 36.4218 | 2.3076 | 0.76558 | 0.27076 | 3.3439 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-04-29 | 21 | 28.3842 | 8.0634 | 36.4476 | 2.3108 | 0.76558 | 0.27096 | 3.3474 | 9.184% | 9.772% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-04-29 | 22 | 27.6145 | 8.1333 | 35.7478 | 2.223 | 0.76558 | 0.26575 | 3.2543 | 9.104% | 9.686% | 6.545% | 1.1002 | 1.1072 | 1.07
2010-04-29 | 23 | 26.1864 | 8.067 | 34.2534 | 2.041 | 0.76558 | 0.25464 | 3.0612 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2010-04-29 | 24 | 25.7263 | 8.1235 | 33.8498 | 1.9932 | 0.76558 | 0.25164 | 3.0104 | 8.893% | 9.463% | 6.394% | 1.0976 | 1.1045 | 1.0683
2010-04-29 | 25 | 25.1578 | 7.8732 | 33.031 | 1.8979 | 0.76558 | 0.24556 | 2.9091 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-04-29 | 26 | 24.6772 | 7.3732 | 32.0504 | 1.7869 | 0.76558 | 0.23827 | 2.7908 | 8.707% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-04-29 | 27 | 24.9343 | 7.6071 | 32.5414 | 1.8421 | 0.76558 | 0.24192 | 2.8496 | 8.757% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-04-29 | 28 | 24.6904 | 7.5873 | 32.2777 | 1.8123 | 0.76558 | 0.23996 | 2.8179 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-04-29 | 29 | 24.331 | 7.3493 | 31.6803 | 1.7459 | 0.76558 | 0.23552 | 2.747 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-04-29 | 30 | 24.1866 | 7.0537 | 31.2403 | 1.6977 | 0.76558 | 0.23224 | 2.6955 | 8.628% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-04-29 | 31 | 24.7757 | 6.9514 | 31.7271 | 1.751 | 0.76558 | 0.23586 | 2.7525 | 8.675% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-04-29 | 32 | 25.0207 | 7.1796 | 32.2003 | 1.8037 | 0.76558 | 0.23938 | 2.8086 | 8.722% | 9.281% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-04-29 | 33 | 25.4099 | 7.5903 | 33.0002 | 1.8944 | 0.76558 | 0.24533 | 2.9053 | 8.804% | 9.367% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-04-29 | 34 | 26.2565 | 8.3751 | 34.6316 | 2.0863 | 0.76558 | 0.25746 | 3.1093 | 8.978% | 9.553% | 6.455% | 1.0986 | 1.1056 | 1.069
2010-04-29 | 35 | 27.4901 | 9.3715 | 36.8616 | 2.3636 | 0.76558 | 0.27403 | 3.4033 | 9.233% | 9.823% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-04-29 | 36 | 29.819 | 10.2656 | 40.0846 | 2.7951 | 0.76558 | 0.29799 | 3.8586 | 9.626% | 10.24% | 6.921% | 1.1065 | 1.1141 | 1.0744
2010-04-29 | 37 | 31.5412 | 10.5355 | 42.0768 | 3.0798 | 0.76558 | 0.3128 | 4.1582 | 9.882% | 10.51% | 7.105% | 1.1097 | 1.1175 | 1.0765
2010-04-29 | 38 | 32.0873 | 10.1895 | 42.2767 | 3.1091 | 0.76558 | 0.31429 | 4.189 | 9.908% | 10.54% | 7.124% | 1.11 | 1.1179 | 1.0767
2010-04-29 | 39 | 31.6555 | 9.5008 | 41.1562 | 2.9465 | 0.76558 | 0.30596 | 4.018 | 9.763% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-04-29 | 40 | 30.765 | 9.0811 | 39.8461 | 2.7619 | 0.76558 | 0.29622 | 3.8237 | 9.596% | 10.21% | 6.9% | 1.1061 | 1.1137 | 1.0741
2010-04-29 | 41 | 30.3469 | 8.9899 | 39.3368 | 2.6917 | 0.76558 | 0.29243 | 3.7497 | 9.532% | 10.14% | 6.854% | 1.1054 | 1.1129 | 1.0736
2010-04-29 | 42 | 29.3713 | 8.3307 | 37.702 | 2.4727 | 0.76558 | 0.28028 | 3.5185 | 9.332% | 9.93% | 6.71% | 1.1029 | 1.1102 | 1.0719
2010-04-29 | 43 | 27.6612 | 7.7479 | 35.4091 | 2.181 | 0.76558 | 0.26324 | 3.2099 | 9.065% | 9.645% | 6.518% | 1.0997 | 1.1067 | 1.0697
2010-04-29 | 44 | 26.0795 | 7.393 | 33.4725 | 1.949 | 0.76558 | 0.24884 | 2.9634 | 8.853% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-04-29 | 45 | 23.7118 | 6.8179 | 30.5297 | 1.6214 | 0.76558 | 0.22696 | 2.6139 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-04-29 | 46 | 20.8686 | 6.5941 | 27.4628 | 1.312 | 0.76558 | 0.20416 | 2.2817 | 8.308% | 8.84% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-04-29 | 47 | 19.6491 | 6.6107 | 26.2598 | 1.1995 | 0.76558 | 0.19522 | 2.1603 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-04-29 | 48 | 18.599 | 6.6519 | 25.2509 | 1.1091 | 0.76558 | 0.18772 | 2.0624 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-04-30 | 1 | 17.2497 | 5.5857 | 22.8354 | 0.90709 | 0.76558 | 0.16976 | 1.8424 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-04-30 | 2 | 17.1081 | 5.1604 | 22.2685 | 0.86262 | 0.76558 | 0.16555 | 1.7937 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-04-30 | 3 | 16.0448 | 4.6997 | 20.7445 | 0.74858 | 0.76558 | 0.15422 | 1.6684 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-30 | 4 | 15.3857 | 4.3989 | 19.7846 | 0.68091 | 0.76558 | 0.14708 | 1.5936 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-04-30 | 5 | 14.9674 | 4.3835 | 19.3508 | 0.65138 | 0.76558 | 0.14386 | 1.5608 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-30 | 6 | 14.7808 | 4.2184 | 18.9992 | 0.62792 | 0.76558 | 0.14124 | 1.5347 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-04-30 | 7 | 14.6513 | 4.1827 | 18.834 | 0.61705 | 0.76558 | 0.14001 | 1.5226 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-04-30 | 8 | 14.5874 | 4.2769 | 18.8643 | 0.61903 | 0.76558 | 0.14024 | 1.5249 | 8.083% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-04-30 | 9 | 15.0895 | 4.2621 | 19.3516 | 0.65143 | 0.76558 | 0.14386 | 1.5609 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-04-30 | 10 | 15.5805 | 4.3505 | 19.931 | 0.69102 | 0.76558 | 0.14817 | 1.6048 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-04-30 | 11 | 16.1529 | 4.5376 | 20.6905 | 0.74469 | 0.76558 | 0.15382 | 1.6641 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-04-30 | 12 | 16.6351 | 4.9722 | 21.6072 | 0.81214 | 0.76558 | 0.16063 | 1.7384 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-04-30 | 13 | 18.2292 | 5.8113 | 24.0405 | 1.0054 | 0.76558 | 0.17872 | 1.9497 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-04-30 | 14 | 20.2833 | 7.3728 | 27.6562 | 1.3305 | 0.76558 | 0.2056 | 2.3017 | 8.323% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-04-30 | 15 | 24.5713 | 8.5067 | 33.078 | 1.9033 | 0.76558 | 0.24591 | 2.9148 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-04-30 | 16 | 27.0991 | 9.4494 | 36.5485 | 2.3237 | 0.76558 | 0.27171 | 3.361 | 9.196% | 9.784% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-04-30 | 17 | 28.2901 | 10.079 | 38.3691 | 2.5609 | 0.76558 | 0.28524 | 3.6118 | 9.413% | 10.02% | 6.768% | 1.1039 | 1.1113 | 1.0726
2010-04-30 | 18 | 28.9361 | 10.015 | 38.9511 | 2.6392 | 0.76558 | 0.28957 | 3.6944 | 9.485% | 10.09% | 6.819% | 1.1048 | 1.1122 | 1.0732
2010-04-30 | 19 | 28.5703 | 9.7582 | 38.3285 | 2.5555 | 0.76558 | 0.28494 | 3.606 | 9.408% | 10.01% | 6.765% | 1.1039 | 1.1112 | 1.0726
2010-04-30 | 20 | 27.9159 | 9.4854 | 37.4013 | 2.4334 | 0.76558 | 0.27805 | 3.477 | 9.296% | 9.891% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-04-30 | 21 | 28.3173 | 9.4328 | 37.7501 | 2.479 | 0.76558 | 0.28064 | 3.5252 | 9.338% | 9.936% | 6.714% | 1.103 | 1.1103 | 1.072
2010-04-30 | 22 | 27.9021 | 9.2172 | 37.1192 | 2.3968 | 0.76558 | 0.27595 | 3.4383 | 9.263% | 9.856% | 6.66% | 1.1021 | 1.1093 | 1.0714
2010-04-30 | 23 | 27.0637 | 8.7959 | 35.8596 | 2.2369 | 0.76558 | 0.26658 | 3.2691 | 9.116% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-04-30 | 24 | 26.783 | 8.342 | 35.1249 | 2.1462 | 0.76558 | 0.26112 | 3.1729 | 9.033% | 9.611% | 6.495% | 1.0993 | 1.1063 | 1.0695
2010-04-30 | 25 | 25.9555 | 7.7261 | 33.6816 | 1.9734 | 0.76558 | 0.25039 | 2.9894 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-04-30 | 26 | 25.0088 | 6.9211 | 31.93 | 1.7735 | 0.76558 | 0.23737 | 2.7765 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-04-30 | 27 | 24.6497 | 6.9636 | 31.6133 | 1.7385 | 0.76558 | 0.23502 | 2.7391 | 8.664% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-04-30 | 28 | 24.7212 | 7.012 | 31.7332 | 1.7517 | 0.76558 | 0.23591 | 2.7532 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-04-30 | 29 | 24.5911 | 6.7089 | 31.3 | 1.7042 | 0.76558 | 0.23269 | 2.7025 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-04-30 | 30 | 24.2611 | 6.4057 | 30.6667 | 1.6359 | 0.76558 | 0.22798 | 2.6295 | 8.574% | 9.123% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-04-30 | 31 | 25.0814 | 6.3645 | 31.4459 | 1.7201 | 0.76558 | 0.23377 | 2.7195 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-04-30 | 32 | 25.3809 | 6.6156 | 31.9965 | 1.7809 | 0.76558 | 0.23787 | 2.7843 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2010-04-30 | 33 | 26.1696 | 7.0785 | 33.2481 | 1.9229 | 0.76558 | 0.24717 | 2.9357 | 8.83% | 9.395% | 6.349% | 1.0968 | 1.1037 | 1.0678
2010-04-30 | 34 | 27.0036 | 7.522 | 34.5256 | 2.0736 | 0.76558 | 0.25667 | 3.0958 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-04-30 | 35 | 28.0891 | 8.3635 | 36.4526 | 2.3115 | 0.76558 | 0.27099 | 3.3481 | 9.185% | 9.773% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-04-30 | 36 | 30.459 | 9.5708 | 40.0298 | 2.7874 | 0.76558 | 0.29759 | 3.8506 | 9.619% | 10.23% | 6.916% | 1.1064 | 1.114 | 1.0743
2010-04-30 | 37 | 32.4673 | 10.4224 | 42.8897 | 3.1999 | 0.76558 | 0.31885 | 4.2844 | 9.989% | 10.63% | 7.182% | 1.111 | 1.1189 | 1.0774
2010-04-30 | 38 | 33.1362 | 10.2753 | 43.4115 | 3.2783 | 0.76558 | 0.32273 | 4.3666 | 10.06% | 10.7% | 7.232% | 1.1118 | 1.1198 | 1.078
2010-04-30 | 39 | 32.9132 | 9.7343 | 42.6475 | 3.1639 | 0.76558 | 0.31705 | 4.2465 | 9.957% | 10.59% | 7.159% | 1.1106 | 1.1185 | 1.0771
2010-04-30 | 40 | 32.0026 | 9.1756 | 41.1783 | 2.9497 | 0.76558 | 0.30612 | 4.0214 | 9.766% | 10.39% | 7.022% | 1.1082 | 1.116 | 1.0755
2010-04-30 | 41 | 31.529 | 8.7165 | 40.2455 | 2.8175 | 0.76558 | 0.29919 | 3.8823 | 9.647% | 10.26% | 6.936% | 1.1068 | 1.1144 | 1.0745
2010-04-30 | 42 | 30.7541 | 8.2676 | 39.0218 | 2.6488 | 0.76558 | 0.29009 | 3.7045 | 9.493% | 10.1% | 6.826% | 1.1049 | 1.1124 | 1.0733
2010-04-30 | 43 | 29.6121 | 7.4463 | 37.0585 | 2.389 | 0.76558 | 0.2755 | 3.43 | 9.256% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-04-30 | 44 | 28.0336 | 7.0095 | 35.0431 | 2.1362 | 0.76558 | 0.26051 | 3.1623 | 9.024% | 9.602% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-04-30 | 45 | 25.4694 | 6.3945 | 31.8639 | 1.7662 | 0.76558 | 0.23688 | 2.7686 | 8.689% | 9.245% | 6.247% | 1.0952 | 1.1019 | 1.0666
2010-04-30 | 46 | 22.9241 | 6.0916 | 29.0156 | 1.4645 | 0.76558 | 0.21571 | 2.4458 | 8.429% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-04-30 | 47 | 21.7625 | 5.9642 | 27.7267 | 1.3373 | 0.76558 | 0.20612 | 2.309 | 8.328% | 8.861% | 5.988% | 1.0908 | 1.0972 | 1.0637
2010-04-30 | 48 | 20.6972 | 5.9756 | 26.6728 | 1.2376 | 0.76558 | 0.19829 | 2.2014 | 8.254% | 8.782% | 5.934% | 1.09 | 1.0963 | 1.0631
2010-05-01 | 1 | 19.3477 | 6.8053 | 26.1529 | 1.1898 | 0.76558 | 0.19442 | 2.1498 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-05-01 | 2 | 19.2756 | 6.4106 | 25.6862 | 1.1477 | 0.76558 | 0.19095 | 2.1042 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-05-01 | 3 | 17.9246 | 6.054 | 23.9786 | 1.0002 | 0.76558 | 0.17826 | 1.944 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-05-01 | 4 | 17.1201 | 5.8534 | 22.9735 | 0.9181 | 0.76558 | 0.17079 | 1.8545 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-05-01 | 5 | 16.8027 | 5.8323 | 22.635 | 0.89124 | 0.76558 | 0.16827 | 1.8251 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-05-01 | 6 | 16.478 | 5.756 | 22.234 | 0.85995 | 0.76558 | 0.16529 | 1.7908 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-05-01 | 7 | 16.3132 | 5.8045 | 22.1177 | 0.85097 | 0.76558 | 0.16443 | 1.781 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-05-01 | 8 | 16.3933 | 5.6848 | 22.0781 | 0.84793 | 0.76558 | 0.16413 | 1.7776 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-05-01 | 9 | 16.5713 | 5.7153 | 22.2867 | 0.86402 | 0.76558 | 0.16568 | 1.7953 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-05-01 | 10 | 17.1304 | 5.8632 | 22.9936 | 0.91971 | 0.76558 | 0.17094 | 1.8562 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-05-01 | 11 | 17.7831 | 6.2365 | 24.0196 | 1.0036 | 0.76558 | 0.17856 | 1.9478 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-05-01 | 12 | 18.5593 | 6.5619 | 25.1212 | 1.0978 | 0.76558 | 0.18675 | 2.0501 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-05-01 | 13 | 20.2615 | 7.4353 | 27.6968 | 1.3344 | 0.76558 | 0.2059 | 2.3059 | 8.326% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-05-01 | 14 | 23.4766 | 8.832 | 32.3086 | 1.8158 | 0.76558 | 0.24019 | 2.8216 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-05-01 | 15 | 27.5361 | 11.217 | 38.753 | 2.6124 | 0.76558 | 0.28809 | 3.6661 | 9.46% | 10.07% | 6.802% | 1.1045 | 1.1119 | 1.073
2010-05-01 | 16 | 30.4286 | 12.9867 | 43.4153 | 3.2788 | 0.76558 | 0.32275 | 4.3672 | 10.06% | 10.7% | 7.232% | 1.1118 | 1.1199 | 1.078
2010-05-01 | 17 | 32.0633 | 13.6331 | 45.6964 | 3.6324 | 0.76558 | 0.33971 | 4.7377 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-05-01 | 18 | 32.1239 | 13.1921 | 45.316 | 3.5722 | 0.76558 | 0.33688 | 4.6747 | 10.32% | 10.98% | 7.417% | 1.115 | 1.1233 | 1.0801
2010-05-01 | 19 | 31.7321 | 12.5951 | 44.3273 | 3.418 | 0.76558 | 0.32953 | 4.5131 | 10.18% | 10.83% | 7.32% | 1.1134 | 1.1215 | 1.079
2010-05-01 | 20 | 30.4758 | 12.0778 | 42.5536 | 3.15 | 0.76558 | 0.31635 | 4.2319 | 9.945% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-05-01 | 21 | 30.1161 | 11.4731 | 41.5892 | 3.0088 | 0.76558 | 0.30918 | 4.0836 | 9.819% | 10.45% | 7.06% | 1.1089 | 1.1167 | 1.076
2010-05-01 | 22 | 28.5449 | 11.0796 | 39.6245 | 2.7313 | 0.76558 | 0.29457 | 3.7914 | 9.568% | 10.18% | 6.88% | 1.1058 | 1.1133 | 1.0739
2010-05-01 | 23 | 26.9833 | 10.4987 | 37.482 | 2.4439 | 0.76558 | 0.27865 | 3.4881 | 9.306% | 9.902% | 6.691% | 1.1026 | 1.1099 | 1.0717
2010-05-01 | 24 | 26.3013 | 10.0587 | 36.36 | 2.2998 | 0.76558 | 0.2703 | 3.3356 | 9.174% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-05-01 | 25 | 25.1887 | 9.67 | 34.8586 | 2.1138 | 0.76558 | 0.25914 | 3.1385 | 9.003% | 9.58% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-05-01 | 26 | 24.3557 | 9.3569 | 33.7126 | 1.9771 | 0.76558 | 0.25062 | 2.9933 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-05-01 | 27 | 23.9607 | 9.6175 | 33.5782 | 1.9613 | 0.76558 | 0.24962 | 2.9765 | 8.864% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-05-01 | 28 | 24.2344 | 9.7584 | 33.9928 | 2.0101 | 0.76558 | 0.25271 | 3.0283 | 8.909% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-05-01 | 29 | 23.8823 | 9.2948 | 33.1771 | 1.9147 | 0.76558 | 0.24664 | 2.927 | 8.822% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-05-01 | 30 | 23.4576 | 9.0021 | 32.4597 | 1.8328 | 0.76558 | 0.24131 | 2.8397 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-05-01 | 31 | 23.9125 | 8.7872 | 32.6996 | 1.86 | 0.76558 | 0.24309 | 2.8687 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-05-01 | 32 | 24.3439 | 8.8802 | 33.2241 | 1.9202 | 0.76558 | 0.24699 | 2.9327 | 8.827% | 9.392% | 6.347% | 1.0968 | 1.1037 | 1.0678
2010-05-01 | 33 | 25.0758 | 9.1929 | 34.2688 | 2.0428 | 0.76558 | 0.25476 | 3.0632 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-05-01 | 34 | 26.0818 | 9.5282 | 35.61 | 2.2059 | 0.76558 | 0.26473 | 3.2362 | 9.088% | 9.669% | 6.534% | 1.1 | 1.107 | 1.0699
2010-05-01 | 35 | 27.1739 | 10.2556 | 37.4295 | 2.437 | 0.76558 | 0.27826 | 3.4809 | 9.3% | 9.895% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-05-01 | 36 | 29.4579 | 11.3696 | 40.8275 | 2.8996 | 0.76558 | 0.30352 | 3.9687 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-05-01 | 37 | 32.1578 | 12.4932 | 44.651 | 3.4681 | 0.76558 | 0.33194 | 4.5657 | 10.23% | 10.88% | 7.352% | 1.1139 | 1.1221 | 1.0794
2010-05-01 | 38 | 32.9478 | 12.4198 | 45.3676 | 3.5804 | 0.76558 | 0.33727 | 4.6832 | 10.32% | 10.98% | 7.422% | 1.1151 | 1.1234 | 1.0802
2010-05-01 | 39 | 32.4159 | 12.215 | 44.6309 | 3.465 | 0.76558 | 0.33179 | 4.5624 | 10.22% | 10.88% | 7.35% | 1.1139 | 1.122 | 1.0793
2010-05-01 | 40 | 31.6699 | 11.7795 | 43.4494 | 3.284 | 0.76558 | 0.32301 | 4.3726 | 10.06% | 10.71% | 7.236% | 1.1119 | 1.1199 | 1.078
2010-05-01 | 41 | 31.2959 | 11.4227 | 42.7186 | 3.1744 | 0.76558 | 0.31757 | 4.2576 | 9.967% | 10.6% | 7.166% | 1.1107 | 1.1186 | 1.0772
2010-05-01 | 42 | 31.1099 | 10.8036 | 41.9135 | 3.0559 | 0.76558 | 0.31159 | 4.1331 | 9.861% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-05-01 | 43 | 30.0898 | 10.2753 | 40.3651 | 2.8343 | 0.76558 | 0.30008 | 3.9 | 9.662% | 10.28% | 6.947% | 1.107 | 1.1146 | 1.0747
2010-05-01 | 44 | 28.9678 | 9.8437 | 38.8116 | 2.6203 | 0.76558 | 0.28853 | 3.6744 | 9.467% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-05-01 | 45 | 26.2978 | 9.1381 | 35.436 | 2.1844 | 0.76558 | 0.26344 | 3.2134 | 9.068% | 9.648% | 6.52% | 1.0997 | 1.1068 | 1.0697
2010-05-01 | 46 | 24.2859 | 8.3243 | 32.6101 | 1.8499 | 0.76558 | 0.24243 | 2.8579 | 8.764% | 9.325% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-05-01 | 47 | 23.7838 | 8.0707 | 31.8545 | 1.7651 | 0.76558 | 0.23681 | 2.7675 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-05-01 | 48 | 22.8361 | 8.1569 | 30.9929 | 1.6709 | 0.76558 | 0.23041 | 2.6669 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.0659
2010-05-02 | 1 | 20.9678 | 7.3284 | 28.2963 | 1.3928 | 0.76558 | 0.21036 | 2.3687 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-05-02 | 2 | 21.1397 | 6.8592 | 27.9989 | 1.3637 | 0.76558 | 0.20815 | 2.3374 | 8.348% | 8.883% | 6.002% | 1.0911 | 1.0975 | 1.0639
2010-05-02 | 3 | 20.3358 | 6.6304 | 26.9662 | 1.265 | 0.76558 | 0.20047 | 2.231 | 8.273% | 8.803% | 5.949% | 1.0902 | 1.0965 | 1.0632
2010-05-02 | 4 | 19.5897 | 6.3773 | 25.967 | 1.173 | 0.76558 | 0.19304 | 2.1316 | 8.209% | 8.734% | 5.902% | 1.0894 | 1.0957 | 1.0627
2010-05-02 | 5 | 18.8557 | 6.3123 | 25.1681 | 1.1019 | 0.76558 | 0.1871 | 2.0546 | 8.163% | 8.686% | 5.869% | 1.0889 | 1.0951 | 1.0624
2010-05-02 | 6 | 18.5397 | 6.0862 | 24.6259 | 1.0549 | 0.76558 | 0.18307 | 2.0036 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-05-02 | 7 | 18.6837 | 5.9748 | 24.6585 | 1.0577 | 0.76558 | 0.18331 | 2.0066 | 8.138% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-05-02 | 8 | 18.8136 | 5.9488 | 24.7624 | 1.0666 | 0.76558 | 0.18409 | 2.0163 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2010-05-02 | 9 | 19.0435 | 6.0667 | 25.1102 | 1.0968 | 0.76558 | 0.18667 | 2.0491 | 8.16% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-05-02 | 10 | 19.1576 | 6.1403 | 25.2979 | 1.1133 | 0.76558 | 0.18807 | 2.0669 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-05-02 | 11 | 19.0435 | 6.4484 | 25.4919 | 1.1304 | 0.76558 | 0.18951 | 2.0855 | 8.181% | 8.705% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-05-02 | 12 | 19.9475 | 6.9339 | 26.8814 | 1.257 | 0.76558 | 0.19984 | 2.2224 | 8.268% | 8.797% | 5.944% | 1.0901 | 1.0965 | 1.0632
2010-05-02 | 13 | 21.2555 | 7.4725 | 28.728 | 1.4356 | 0.76558 | 0.21357 | 2.4148 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-05-02 | 14 | 22.3615 | 7.8461 | 30.2076 | 1.5873 | 0.76558 | 0.22457 | 2.5775 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-05-02 | 15 | 23.7535 | 8.5403 | 32.2938 | 1.8141 | 0.76558 | 0.24008 | 2.8198 | 8.732% | 9.291% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-05-02 | 16 | 25.1335 | 9.7338 | 34.8673 | 2.1148 | 0.76558 | 0.25921 | 3.1396 | 9.004% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2010-05-02 | 17 | 27.8195 | 11.134 | 38.9535 | 2.6395 | 0.76558 | 0.28958 | 3.6947 | 9.485% | 10.09% | 6.82% | 1.1048 | 1.1122 | 1.0732
2010-05-02 | 18 | 29.8154 | 11.9134 | 41.7288 | 3.0291 | 0.76558 | 0.31022 | 4.1049 | 9.837% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-05-02 | 19 | 31.0654 | 12.2417 | 43.3071 | 3.2625 | 0.76558 | 0.32195 | 4.35 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-05-02 | 20 | 30.8794 | 12.0484 | 42.9279 | 3.2056 | 0.76558 | 0.31913 | 4.2903 | 9.994% | 10.63% | 7.186% | 1.111 | 1.119 | 1.0774
2010-05-02 | 21 | 31.5834 | 11.9845 | 43.5679 | 3.3019 | 0.76558 | 0.32389 | 4.3914 | 10.08% | 10.72% | 7.247% | 1.1121 | 1.1201 | 1.0781
2010-05-02 | 22 | 30.8434 | 11.3935 | 42.2369 | 3.1033 | 0.76558 | 0.31399 | 4.1828 | 9.903% | 10.54% | 7.12% | 1.1099 | 1.1178 | 1.0767
2010-05-02 | 23 | 29.5794 | 10.6013 | 40.1807 | 2.8085 | 0.76558 | 0.29871 | 3.8728 | 9.638% | 10.26% | 6.93% | 1.1067 | 1.1143 | 1.0745
2010-05-02 | 24 | 28.0354 | 10.0499 | 38.0852 | 2.5232 | 0.76558 | 0.28313 | 3.5719 | 9.379% | 9.979% | 6.743% | 1.1035 | 1.1109 | 1.0723
2010-05-02 | 25 | 26.3835 | 9.5806 | 35.9641 | 2.2499 | 0.76558 | 0.26736 | 3.2829 | 9.128% | 9.712% | 6.563% | 1.1005 | 1.1076 | 1.0702
2010-05-02 | 26 | 25.1835 | 8.9839 | 34.1674 | 2.0308 | 0.76558 | 0.254 | 3.0503 | 8.928% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-05-02 | 27 | 25.2695 | 9.0577 | 34.3272 | 2.0498 | 0.76558 | 0.25519 | 3.0706 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-05-02 | 28 | 25.0894 | 8.8326 | 33.922 | 2.0017 | 0.76558 | 0.25218 | 3.0194 | 8.901% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-05-02 | 29 | 24.1353 | 8.2644 | 32.3998 | 1.8261 | 0.76558 | 0.24086 | 2.8325 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-05-02 | 30 | 23.6313 | 8.0137 | 31.645 | 1.742 | 0.76558 | 0.23525 | 2.7428 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-05-02 | 31 | 24.2213 | 7.9507 | 32.172 | 1.8005 | 0.76558 | 0.23917 | 2.8052 | 8.72% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-05-02 | 32 | 24.1554 | 8.0057 | 32.1611 | 1.7993 | 0.76558 | 0.23909 | 2.8039 | 8.718% | 9.276% | 6.269% | 1.0955 | 1.1022 | 1.0669
2010-05-02 | 33 | 25.0693 | 8.4254 | 33.4947 | 1.9516 | 0.76558 | 0.249 | 2.9662 | 8.856% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2010-05-02 | 34 | 26.2173 | 8.8849 | 35.1021 | 2.1434 | 0.76558 | 0.26095 | 3.1699 | 9.031% | 9.609% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-05-02 | 35 | 27.7474 | 9.7704 | 37.5178 | 2.4486 | 0.76558 | 0.27891 | 3.493 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.11 | 1.0717
2010-05-02 | 36 | 29.8013 | 11.4435 | 41.2448 | 2.9592 | 0.76558 | 0.30662 | 4.0314 | 9.774% | 10.4% | 7.028% | 1.1083 | 1.1161 | 1.0756
2010-05-02 | 37 | 32.5873 | 12.3038 | 44.8911 | 3.5055 | 0.76558 | 0.33373 | 4.6048 | 10.26% | 10.91% | 7.375% | 1.1143 | 1.1225 | 1.0796
2010-05-02 | 38 | 33.2552 | 12.4103 | 45.6656 | 3.6275 | 0.76558 | 0.33948 | 4.7326 | 10.36% | 11.03% | 7.451% | 1.1156 | 1.1239 | 1.0805
2010-05-02 | 39 | 32.6733 | 12.0154 | 44.6887 | 3.474 | 0.76558 | 0.33222 | 4.5718 | 10.23% | 10.89% | 7.356% | 1.114 | 1.1221 | 1.0794
2010-05-02 | 40 | 31.4532 | 11.4623 | 42.9155 | 3.2038 | 0.76558 | 0.31904 | 4.2884 | 9.993% | 10.63% | 7.185% | 1.111 | 1.119 | 1.0774
2010-05-02 | 41 | 31.0153 | 10.9584 | 41.9736 | 3.0647 | 0.76558 | 0.31204 | 4.1423 | 9.869% | 10.5% | 7.096% | 1.1095 | 1.1173 | 1.0764
2010-05-02 | 42 | 30.3333 | 10.5805 | 40.9138 | 2.9119 | 0.76558 | 0.30416 | 3.9816 | 9.732% | 10.35% | 6.997% | 1.1078 | 1.1155 | 1.0752
2010-05-02 | 43 | 29.2334 | 10.0526 | 39.286 | 2.6848 | 0.76558 | 0.29206 | 3.7424 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-05-02 | 44 | 27.8253 | 9.6147 | 37.44 | 2.4384 | 0.76558 | 0.27833 | 3.4823 | 9.301% | 9.896% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-05-02 | 45 | 25.9154 | 8.9969 | 34.9122 | 2.1203 | 0.76558 | 0.25954 | 3.1454 | 9.009% | 9.586% | 6.478% | 1.099 | 1.106 | 1.0693
2010-05-02 | 46 | 23.6814 | 8.4472 | 32.1286 | 1.7956 | 0.76558 | 0.23885 | 2.8001 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2010-05-02 | 47 | 23.3094 | 8.5335 | 31.8429 | 1.7638 | 0.76558 | 0.23672 | 2.7661 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2010-05-02 | 48 | 22.7334 | 8.7321 | 31.4655 | 1.7223 | 0.76558 | 0.23392 | 2.7218 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-05-03 | 1 | 21.3973 | 7.8034 | 29.2007 | 1.4833 | 0.76558 | 0.21708 | 2.4659 | 8.445% | 8.985% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-05-03 | 2 | 21.0113 | 7.1685 | 28.1798 | 1.3814 | 0.76558 | 0.20949 | 2.3564 | 8.362% | 8.897% | 6.012% | 1.0913 | 1.0977 | 1.064
2010-05-03 | 3 | 20.2214 | 6.7334 | 26.9547 | 1.2639 | 0.76558 | 0.20038 | 2.2298 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-05-03 | 4 | 19.5013 | 6.4899 | 25.9912 | 1.1751 | 0.76558 | 0.19322 | 2.1339 | 8.21% | 8.736% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-05-03 | 5 | 19.0134 | 6.3691 | 25.3825 | 1.1207 | 0.76558 | 0.1887 | 2.075 | 8.175% | 8.698% | 5.878% | 1.089 | 1.0953 | 1.0624
2010-05-03 | 6 | 18.5833 | 6.2696 | 24.8529 | 1.0745 | 0.76558 | 0.18476 | 2.0248 | 8.147% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-05-03 | 7 | 18.3673 | 6.2205 | 24.5878 | 1.0517 | 0.76558 | 0.18279 | 2 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-05-03 | 8 | 18.1952 | 6.1769 | 24.3721 | 1.0333 | 0.76558 | 0.18119 | 1.9801 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-05-03 | 9 | 18.7272 | 6.2044 | 24.9316 | 1.0813 | 0.76558 | 0.18534 | 2.0322 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2010-05-03 | 10 | 18.8272 | 6.0373 | 24.8645 | 1.0755 | 0.76558 | 0.18485 | 2.0259 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-05-03 | 11 | 18.8272 | 6.1594 | 24.9866 | 1.086 | 0.76558 | 0.18575 | 2.0374 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-05-03 | 12 | 19.3433 | 6.4359 | 25.7792 | 1.156 | 0.76558 | 0.19165 | 2.1133 | 8.198% | 8.722% | 5.894% | 1.0893 | 1.0956 | 1.0626
2010-05-03 | 13 | 20.4354 | 6.8409 | 27.2763 | 1.2942 | 0.76558 | 0.20278 | 2.2626 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2010-05-03 | 14 | 21.5713 | 7.0717 | 28.643 | 1.4272 | 0.76558 | 0.21294 | 2.4057 | 8.399% | 8.936% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-05-03 | 15 | 22.6193 | 7.5794 | 30.1987 | 1.5864 | 0.76558 | 0.2245 | 2.5765 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-05-03 | 16 | 23.5672 | 8.4749 | 32.0421 | 1.786 | 0.76558 | 0.2382 | 2.7898 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-05-03 | 17 | 26.0232 | 9.9778 | 36.001 | 2.2546 | 0.76558 | 0.26764 | 3.2878 | 9.132% | 9.717% | 6.566% | 1.1005 | 1.1076 | 1.0703
2010-05-03 | 18 | 27.8192 | 11.121 | 38.9402 | 2.6377 | 0.76558 | 0.28949 | 3.6928 | 9.483% | 10.09% | 6.818% | 1.1048 | 1.1122 | 1.0732
2010-05-03 | 19 | 29.4411 | 11.7402 | 41.1813 | 2.9501 | 0.76558 | 0.30615 | 4.0218 | 9.766% | 10.39% | 7.022% | 1.1082 | 1.116 | 1.0755
2010-05-03 | 20 | 29.5991 | 11.8249 | 41.424 | 2.985 | 0.76558 | 0.30795 | 4.0585 | 9.797% | 10.42% | 7.044% | 1.1086 | 1.1164 | 1.0758
2010-05-03 | 21 | 30.6192 | 11.6775 | 42.2967 | 3.1121 | 0.76558 | 0.31444 | 4.1921 | 9.911% | 10.55% | 7.126% | 1.11 | 1.1179 | 1.0767
2010-05-03 | 22 | 30.1171 | 11.3384 | 41.4555 | 2.9895 | 0.76558 | 0.30819 | 4.0633 | 9.802% | 10.43% | 7.047% | 1.1087 | 1.1164 | 1.0758
2010-05-03 | 23 | 28.7092 | 10.8013 | 39.5106 | 2.7156 | 0.76558 | 0.29373 | 3.7749 | 9.554% | 10.17% | 6.869% | 1.1056 | 1.1132 | 1.0738
2010-05-03 | 24 | 27.3452 | 10.3105 | 37.6557 | 2.4666 | 0.76558 | 0.27994 | 3.5121 | 9.327% | 9.924% | 6.706% | 1.1029 | 1.1102 | 1.0719
2010-05-03 | 25 | 25.6933 | 9.9589 | 35.6522 | 2.2111 | 0.76558 | 0.26504 | 3.2417 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.0699
2010-05-03 | 26 | 24.3132 | 9.4203 | 33.7336 | 1.9795 | 0.76558 | 0.25078 | 2.9959 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1044 | 1.0682
2010-05-03 | 27 | 24.1993 | 9.2296 | 33.4289 | 1.9439 | 0.76558 | 0.24851 | 2.958 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-05-03 | 28 | 24.0272 | 9.2435 | 33.2707 | 1.9256 | 0.76558 | 0.24734 | 2.9385 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-05-03 | 29 | 23.5092 | 8.7747 | 32.2839 | 1.813 | 0.76558 | 0.24 | 2.8186 | 8.731% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-05-03 | 30 | 22.8912 | 8.5576 | 31.4488 | 1.7205 | 0.76558 | 0.23379 | 2.7198 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-05-03 | 31 | 23.9433 | 8.2658 | 32.2091 | 1.8046 | 0.76558 | 0.23945 | 2.8097 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-05-03 | 32 | 24.5432 | 8.0632 | 32.6064 | 1.8494 | 0.76558 | 0.2424 | 2.8574 | 8.763% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-05-03 | 33 | 25.2331 | 8.4292 | 33.6623 | 1.9712 | 0.76558 | 0.25025 | 2.987 | 8.873% | 9.441% | 6.38% | 1.0974 | 1.1043 | 1.0681
2010-05-03 | 34 | 26.5472 | 8.8017 | 35.3489 | 2.1736 | 0.76558 | 0.26279 | 3.202 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-05-03 | 35 | 28.0131 | 9.9101 | 37.9232 | 2.5018 | 0.76558 | 0.28193 | 3.5493 | 9.359% | 9.958% | 6.729% | 1.1033 | 1.1106 | 1.0721
2010-05-03 | 36 | 30.2392 | 11.5565 | 41.7957 | 3.0388 | 0.76558 | 0.31071 | 4.1151 | 9.846% | 10.48% | 7.079% | 1.1092 | 1.117 | 1.0762
2010-05-03 | 37 | 32.6391 | 12.4752 | 45.1143 | 3.5405 | 0.76558 | 0.33539 | 4.6415 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-05-03 | 38 | 33.0691 | 12.392 | 45.4612 | 3.5951 | 0.76558 | 0.33796 | 4.6987 | 10.34% | 11% | 7.431% | 1.1153 | 1.1236 | 1.0803
2010-05-03 | 39 | 32.7613 | 12.067 | 44.8283 | 3.4957 | 0.76558 | 0.33326 | 4.5946 | 10.25% | 10.91% | 7.369% | 1.1142 | 1.1224 | 1.0796
2010-05-03 | 40 | 31.8992 | 11.5854 | 43.4846 | 3.2893 | 0.76558 | 0.32327 | 4.3782 | 10.07% | 10.71% | 7.239% | 1.112 | 1.12 | 1.078
2010-05-03 | 41 | 31.7413 | 11.3735 | 43.1148 | 3.2336 | 0.76558 | 0.32052 | 4.3197 | 10.02% | 10.66% | 7.204% | 1.1113 | 1.1193 | 1.0776
2010-05-03 | 42 | 30.7413 | 10.8065 | 41.5478 | 3.0028 | 0.76558 | 0.30887 | 4.0773 | 9.813% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-05-03 | 43 | 29.2414 | 10.213 | 39.4544 | 2.7079 | 0.76558 | 0.29331 | 3.7667 | 9.547% | 10.16% | 6.864% | 1.1055 | 1.1131 | 1.0737
2010-05-03 | 44 | 27.5174 | 9.4713 | 36.9887 | 2.38 | 0.76558 | 0.27498 | 3.4205 | 9.248% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-05-03 | 45 | 24.8673 | 8.5034 | 33.3708 | 1.9372 | 0.76558 | 0.24808 | 2.9508 | 8.843% | 9.408% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-05-03 | 46 | 22.4693 | 7.5992 | 30.0685 | 1.5727 | 0.76558 | 0.22353 | 2.5619 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-05-03 | 47 | 21.8873 | 7.5898 | 29.4771 | 1.5115 | 0.76558 | 0.21914 | 2.4962 | 8.468% | 9.01% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-05-03 | 48 | 20.8673 | 7.8665 | 28.7338 | 1.4362 | 0.76558 | 0.21361 | 2.4154 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-05-04 | 1 | 20.0055 | 7.1544 | 27.1598 | 1.2832 | 0.76558 | 0.20191 | 2.2507 | 8.287% | 8.817% | 5.958% | 1.0904 | 1.0967 | 1.0634
2010-05-04 | 2 | 20.3073 | 6.9222 | 27.2294 | 1.2898 | 0.76558 | 0.20243 | 2.2578 | 8.292% | 8.822% | 5.962% | 1.0904 | 1.0968 | 1.0634
2010-05-04 | 3 | 19.1852 | 6.7543 | 25.9395 | 1.1705 | 0.76558 | 0.19284 | 2.1289 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-05-04 | 4 | 18.3392 | 6.4402 | 24.7794 | 1.0681 | 0.76558 | 0.18421 | 2.0179 | 8.143% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-05-04 | 5 | 18.2092 | 6.3377 | 24.5468 | 1.0482 | 0.76558 | 0.18248 | 1.9962 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-05-04 | 6 | 17.8652 | 6.2687 | 24.134 | 1.0132 | 0.76558 | 0.17941 | 1.9582 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-05-04 | 7 | 17.7631 | 6.1743 | 23.9374 | 0.99676 | 0.76558 | 0.17795 | 1.9403 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-05-04 | 8 | 17.5632 | 6.1973 | 23.7605 | 0.98208 | 0.76558 | 0.17664 | 1.9243 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-05-04 | 9 | 17.8072 | 6.4099 | 24.2171 | 1.0202 | 0.76558 | 0.18003 | 1.9658 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-05-04 | 10 | 18.3251 | 6.4958 | 24.8209 | 1.0717 | 0.76558 | 0.18452 | 2.0218 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-05-04 | 11 | 18.8989 | 6.7654 | 25.6643 | 1.1458 | 0.76558 | 0.19079 | 2.1021 | 8.191% | 8.715% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-05-04 | 12 | 19.5891 | 7.1451 | 26.7342 | 1.2433 | 0.76558 | 0.19875 | 2.2076 | 8.258% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-05-04 | 13 | 21.5552 | 8.0991 | 29.6543 | 1.5297 | 0.76558 | 0.22045 | 2.5157 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-05-04 | 14 | 24.6455 | 9.7826 | 34.4281 | 2.0619 | 0.76558 | 0.25594 | 3.0834 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-05-04 | 15 | 28.9395 | 12.2131 | 41.1526 | 2.946 | 0.76558 | 0.30593 | 4.0175 | 9.762% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-05-04 | 16 | 31.5834 | 13.8877 | 45.471 | 3.5967 | 0.76558 | 0.33804 | 4.7003 | 10.34% | 11% | 7.432% | 1.1153 | 1.1236 | 1.0803
2010-05-04 | 17 | 33.2774 | 14.3671 | 47.6445 | 3.9488 | 0.76558 | 0.3542 | 5.0685 | 10.64% | 11.32% | 7.649% | 1.119 | 1.1276 | 1.0828
2010-05-04 | 18 | 33.8953 | 14.2759 | 48.1712 | 4.0366 | 0.76558 | 0.35811 | 5.1602 | 10.71% | 11.4% | 7.702% | 1.12 | 1.1286 | 1.0834
2010-05-04 | 19 | 33.5512 | 14.1059 | 47.657 | 3.9508 | 0.76558 | 0.35429 | 5.0707 | 10.64% | 11.32% | 7.65% | 1.1191 | 1.1277 | 1.0828
2010-05-04 | 20 | 31.9411 | 13.2897 | 45.2308 | 3.5588 | 0.76558 | 0.33625 | 4.6606 | 10.3% | 10.96% | 7.409% | 1.1149 | 1.1231 | 1.08
2010-05-04 | 21 | 31.999 | 12.8145 | 44.8135 | 3.4934 | 0.76558 | 0.33315 | 4.5922 | 10.25% | 10.9% | 7.368% | 1.1142 | 1.1224 | 1.0795
2010-05-04 | 22 | 30.721 | 12.8591 | 43.5801 | 3.3038 | 0.76558 | 0.32398 | 4.3933 | 10.08% | 10.73% | 7.248% | 1.1121 | 1.1202 | 1.0781
2010-05-04 | 23 | 29.097 | 12.1058 | 41.2028 | 2.9532 | 0.76558 | 0.30631 | 4.0251 | 9.769% | 10.39% | 7.024% | 1.1083 | 1.116 | 1.0755
2010-05-04 | 24 | 27.919 | 11.4533 | 39.3723 | 2.6966 | 0.76558 | 0.2927 | 3.7549 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-05-04 | 25 | 26.325 | 11.116 | 37.441 | 2.4385 | 0.76558 | 0.27834 | 3.4825 | 9.301% | 9.896% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-05-04 | 26 | 25.621 | 10.2022 | 35.8232 | 2.2324 | 0.76558 | 0.26631 | 3.2642 | 9.112% | 9.695% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-05-04 | 27 | 25.4769 | 10.3594 | 35.8363 | 2.234 | 0.76558 | 0.26641 | 3.266 | 9.114% | 9.697% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-05-04 | 28 | 25.3629 | 10.1271 | 35.4901 | 2.191 | 0.76558 | 0.26384 | 3.2204 | 9.074% | 9.655% | 6.524% | 1.0998 | 1.1069 | 1.0698
2010-05-04 | 29 | 25.0469 | 9.6121 | 34.659 | 2.0896 | 0.76558 | 0.25766 | 3.1128 | 8.981% | 9.556% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-05-04 | 30 | 24.2129 | 9.226 | 33.4389 | 1.9451 | 0.76558 | 0.24859 | 2.9592 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2010-05-04 | 31 | 25.1469 | 9.377 | 34.5239 | 2.0734 | 0.76558 | 0.25665 | 3.0956 | 8.967% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-05-04 | 32 | 25.7648 | 9.4446 | 35.2094 | 2.1565 | 0.76558 | 0.26175 | 3.1838 | 9.043% | 9.621% | 6.502% | 1.0994 | 1.1065 | 1.0695
2010-05-04 | 33 | 26.3688 | 9.6576 | 36.0264 | 2.2577 | 0.76558 | 0.26782 | 3.2912 | 9.135% | 9.72% | 6.568% | 1.1005 | 1.1077 | 1.0703
2010-05-04 | 34 | 27.0007 | 10.1786 | 37.1794 | 2.4046 | 0.76558 | 0.2764 | 3.4465 | 9.27% | 9.863% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-05-04 | 35 | 28.7667 | 11.4667 | 40.2334 | 2.8158 | 0.76558 | 0.2991 | 3.8805 | 9.645% | 10.26% | 6.935% | 1.1067 | 1.1144 | 1.0745
2010-05-04 | 36 | 31.8827 | 13.1311 | 45.0138 | 3.5247 | 0.76558 | 0.33464 | 4.625 | 10.27% | 10.93% | 7.387% | 1.1145 | 1.1227 | 1.0798
2010-05-04 | 37 | 33.8507 | 13.7517 | 47.6024 | 3.9418 | 0.76558 | 0.35388 | 5.0612 | 10.63% | 11.31% | 7.645% | 1.119 | 1.1276 | 1.0828
2010-05-04 | 38 | 34.1827 | 13.4805 | 47.6631 | 3.9518 | 0.76558 | 0.35433 | 5.0718 | 10.64% | 11.32% | 7.651% | 1.1191 | 1.1277 | 1.0828
2010-05-04 | 39 | 33.2187 | 12.9498 | 46.1685 | 3.7079 | 0.76558 | 0.34322 | 4.8167 | 10.43% | 11.1% | 7.501% | 1.1165 | 1.1249 | 1.0811
2010-05-04 | 40 | 32.4867 | 12.3354 | 44.8221 | 3.4948 | 0.76558 | 0.33321 | 4.5936 | 10.25% | 10.9% | 7.369% | 1.1142 | 1.1224 | 1.0795
2010-05-04 | 41 | 32.2707 | 11.9806 | 44.2513 | 3.4063 | 0.76558 | 0.32897 | 4.5009 | 10.17% | 10.82% | 7.313% | 1.1132 | 1.1214 | 1.0789
2010-05-04 | 42 | 31.6687 | 11.2863 | 42.955 | 3.2097 | 0.76558 | 0.31933 | 4.2946 | 9.998% | 10.64% | 7.188% | 1.1111 | 1.119 | 1.0775
2010-05-04 | 43 | 29.6867 | 10.5569 | 40.2435 | 2.8173 | 0.76558 | 0.29918 | 3.882 | 9.646% | 10.26% | 6.936% | 1.1068 | 1.1144 | 1.0745
2010-05-04 | 44 | 27.7186 | 9.8137 | 37.5323 | 2.4504 | 0.76558 | 0.27902 | 3.495 | 9.312% | 9.908% | 6.695% | 1.1027 | 1.11 | 1.0718
2010-05-04 | 45 | 25.5346 | 9.0043 | 34.5389 | 2.0752 | 0.76558 | 0.25677 | 3.0975 | 8.968% | 9.542% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-05-04 | 46 | 23.0346 | 7.9739 | 31.0084 | 1.6726 | 0.76558 | 0.23052 | 2.6687 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-05-04 | 47 | 22.0005 | 7.712 | 29.7125 | 1.5357 | 0.76558 | 0.22089 | 2.5222 | 8.489% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-05-04 | 48 | 20.9525 | 7.9826 | 28.9351 | 1.4564 | 0.76558 | 0.21511 | 2.4371 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-05-05 | 1 | 19.5585 | 7.1089 | 26.6673 | 1.2371 | 0.76558 | 0.19825 | 2.2009 | 8.253% | 8.781% | 5.934% | 1.09 | 1.0963 | 1.0631
2010-05-05 | 2 | 19.5884 | 6.6998 | 26.2882 | 1.2021 | 0.76558 | 0.19543 | 2.1631 | 8.229% | 8.755% | 5.916% | 1.0897 | 1.096 | 1.0629
2010-05-05 | 3 | 18.4664 | 6.399 | 24.8653 | 1.0755 | 0.76558 | 0.18485 | 2.026 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-05-05 | 4 | 17.5182 | 6.1826 | 23.7007 | 0.97714 | 0.76558 | 0.17619 | 1.9189 | 8.096% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-05-05 | 5 | 17.1462 | 6.1199 | 23.2661 | 0.94164 | 0.76558 | 0.17296 | 1.8802 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-05-05 | 6 | 17.0581 | 6.0177 | 23.0758 | 0.92629 | 0.76558 | 0.17155 | 1.8634 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-05-05 | 7 | 16.8141 | 5.9009 | 22.7151 | 0.89756 | 0.76558 | 0.16887 | 1.832 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-05-05 | 8 | 16.6141 | 5.8938 | 22.5079 | 0.88126 | 0.76558 | 0.16733 | 1.8142 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-05-05 | 9 | 16.7 | 6.0433 | 22.7433 | 0.89979 | 0.76558 | 0.16908 | 1.8344 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-05-05 | 10 | 17.2741 | 6.0658 | 23.3398 | 0.94761 | 0.76558 | 0.17351 | 1.8867 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-05-05 | 11 | 17.7063 | 6.3314 | 24.0377 | 1.0051 | 0.76558 | 0.1787 | 1.9494 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-05-05 | 12 | 18.3667 | 6.755 | 25.1218 | 1.0978 | 0.76558 | 0.18676 | 2.0502 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-05-05 | 13 | 20.2491 | 7.7175 | 27.9666 | 1.3606 | 0.76558 | 0.20791 | 2.334 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-05-05 | 14 | 22.9931 | 9.5342 | 32.5273 | 1.8405 | 0.76558 | 0.24181 | 2.8479 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-05-05 | 15 | 27.087 | 11.7361 | 38.8231 | 2.6219 | 0.76558 | 0.28862 | 3.6761 | 9.469% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-05-05 | 16 | 29.5708 | 13.299 | 42.8698 | 3.197 | 0.76558 | 0.3187 | 4.2812 | 9.987% | 10.63% | 7.18% | 1.1109 | 1.1189 | 1.0774
2010-05-05 | 17 | 31.3528 | 14.3164 | 45.6692 | 3.6281 | 0.76558 | 0.33951 | 4.7332 | 10.36% | 11.03% | 7.452% | 1.1156 | 1.1239 | 1.0805
2010-05-05 | 18 | 31.6107 | 14.0632 | 45.6739 | 3.6289 | 0.76558 | 0.33955 | 4.734 | 10.36% | 11.03% | 7.452% | 1.1156 | 1.124 | 1.0805
2010-05-05 | 19 | 31.2667 | 13.535 | 44.8017 | 3.4916 | 0.76558 | 0.33306 | 4.5902 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-05-05 | 20 | 30.6905 | 12.898 | 43.5885 | 3.3051 | 0.76558 | 0.32404 | 4.3947 | 10.08% | 10.73% | 7.249% | 1.1121 | 1.1202 | 1.0782
2010-05-05 | 21 | 30.1445 | 12.0557 | 42.2002 | 3.0979 | 0.76558 | 0.31372 | 4.1772 | 9.898% | 10.53% | 7.117% | 1.1099 | 1.1177 | 1.0766
2010-05-05 | 22 | 28.9526 | 11.5983 | 40.5509 | 2.8605 | 0.76558 | 0.30146 | 3.9275 | 9.685% | 10.31% | 6.964% | 1.1072 | 1.1149 | 1.0749
2010-05-05 | 23 | 27.7605 | 10.5218 | 38.2823 | 2.5494 | 0.76558 | 0.28459 | 3.5995 | 9.403% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-05-05 | 24 | 26.4245 | 10.3614 | 36.7859 | 2.3539 | 0.76558 | 0.27347 | 3.393 | 9.224% | 9.814% | 6.632% | 1.1016 | 1.1088 | 1.071
2010-05-05 | 25 | 25.2464 | 10.0922 | 35.3386 | 2.1724 | 0.76558 | 0.26271 | 3.2007 | 9.057% | 9.637% | 6.512% | 1.0996 | 1.1066 | 1.0697
2010-05-05 | 26 | 25.4045 | 9.3771 | 34.7816 | 2.1044 | 0.76558 | 0.25857 | 3.1286 | 8.995% | 9.571% | 6.467% | 1.0988 | 1.1058 | 1.0691
2010-05-05 | 27 | 25.6067 | 9.5839 | 35.1906 | 2.1542 | 0.76558 | 0.26161 | 3.1814 | 9.04% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2010-05-05 | 28 | 26.1386 | 9.4094 | 35.548 | 2.1982 | 0.76558 | 0.26427 | 3.228 | 9.081% | 9.662% | 6.529% | 1.0999 | 1.107 | 1.0699
2010-05-05 | 29 | 25.7506 | 8.9347 | 34.6853 | 2.0928 | 0.76558 | 0.25785 | 3.1162 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-05-05 | 30 | 25.8067 | 8.8545 | 34.6612 | 2.0899 | 0.76558 | 0.25768 | 3.1131 | 8.982% | 9.556% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-05-05 | 31 | 27.1726 | 8.7986 | 35.9712 | 2.2508 | 0.76558 | 0.26741 | 3.2838 | 9.129% | 9.713% | 6.564% | 1.1005 | 1.1076 | 1.0702
2010-05-05 | 32 | 27.8186 | 9.1192 | 36.9378 | 2.3734 | 0.76558 | 0.2746 | 3.4136 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-05-05 | 33 | 28.9384 | 10.387 | 39.3254 | 2.6902 | 0.76558 | 0.29235 | 3.7481 | 9.531% | 10.14% | 6.853% | 1.1054 | 1.1129 | 1.0736
2010-05-05 | 34 | 30.2605 | 11.0062 | 41.2668 | 2.9623 | 0.76558 | 0.30678 | 4.0347 | 9.777% | 10.4% | 7.03% | 1.1084 | 1.1161 | 1.0756
2010-05-05 | 35 | 31.6385 | 12.2763 | 43.9148 | 3.3547 | 0.76558 | 0.32647 | 4.4468 | 10.13% | 10.77% | 7.281% | 1.1127 | 1.1207 | 1.0785
2010-05-05 | 36 | 33.8366 | 13.6795 | 47.516 | 3.9275 | 0.76558 | 0.35324 | 5.0463 | 10.62% | 11.3% | 7.636% | 1.1188 | 1.1274 | 1.0827
2010-05-05 | 37 | 35.5886 | 13.7171 | 49.3057 | 4.2289 | 0.76558 | 0.36654 | 5.361 | 10.87% | 11.57% | 7.818% | 1.122 | 1.1308 | 1.0848
2010-05-05 | 38 | 35.7467 | 13.1351 | 48.8818 | 4.1565 | 0.76558 | 0.36339 | 5.2855 | 10.81% | 11.5% | 7.774% | 1.1212 | 1.13 | 1.0843
2010-05-05 | 39 | 34.3746 | 12.5956 | 46.9703 | 3.8378 | 0.76558 | 0.34918 | 4.9525 | 10.54% | 11.22% | 7.581% | 1.1179 | 1.1264 | 1.082
2010-05-05 | 40 | 33.5649 | 11.9847 | 45.5496 | 3.6091 | 0.76558 | 0.33862 | 4.7133 | 10.35% | 11.01% | 7.44% | 1.1154 | 1.1237 | 1.0804
2010-05-05 | 41 | 33.3048 | 11.5349 | 44.8397 | 3.4975 | 0.76558 | 0.33334 | 4.5964 | 10.25% | 10.91% | 7.37% | 1.1142 | 1.1224 | 1.0796
2010-05-05 | 42 | 32.5149 | 10.9268 | 43.4417 | 3.2828 | 0.76558 | 0.32295 | 4.3714 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-05-05 | 43 | 30.9929 | 10.2983 | 41.2912 | 2.9659 | 0.76558 | 0.30696 | 4.0384 | 9.78% | 10.41% | 7.032% | 1.1084 | 1.1161 | 1.0756
2010-05-05 | 44 | 29.3989 | 9.7319 | 39.1307 | 2.6636 | 0.76558 | 0.2909 | 3.7201 | 9.507% | 10.12% | 6.835% | 1.1051 | 1.1125 | 1.0734
2010-05-05 | 45 | 26.4249 | 8.8885 | 35.3134 | 2.1693 | 0.76558 | 0.26252 | 3.1974 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-05-05 | 46 | 23.5809 | 7.7745 | 31.3554 | 1.7102 | 0.76558 | 0.2331 | 2.7089 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-05-05 | 47 | 23.0649 | 7.7342 | 30.7991 | 1.6501 | 0.76558 | 0.22896 | 2.6446 | 8.587% | 9.136% | 6.174% | 1.0939 | 1.1005 | 1.0658
2010-05-05 | 48 | 21.8009 | 7.8856 | 29.6865 | 1.533 | 0.76558 | 0.22069 | 2.5193 | 8.486% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-05-06 | 1 | 20.149 | 7.112 | 27.2609 | 1.2928 | 0.76558 | 0.20266 | 2.261 | 8.294% | 8.825% | 5.963% | 1.0904 | 1.0968 | 1.0634
2010-05-06 | 2 | 20.2347 | 6.7634 | 26.9981 | 1.2679 | 0.76558 | 0.20071 | 2.2342 | 8.276% | 8.805% | 5.95% | 1.0902 | 1.0966 | 1.0633
2010-05-06 | 3 | 19.0569 | 6.4422 | 25.4991 | 1.1311 | 0.76558 | 0.18956 | 2.0862 | 8.181% | 8.705% | 5.882% | 1.0891 | 1.0954 | 1.0625
2010-05-06 | 4 | 18.539 | 6.1252 | 24.6642 | 1.0582 | 0.76558 | 0.18336 | 2.0071 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-05-06 | 5 | 17.937 | 6.086 | 24.023 | 1.0039 | 0.76558 | 0.17859 | 1.9481 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-05-06 | 6 | 17.305 | 5.8297 | 23.1348 | 0.93103 | 0.76558 | 0.17199 | 1.8686 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-05-06 | 7 | 17.075 | 5.6517 | 22.7267 | 0.89848 | 0.76558 | 0.16895 | 1.833 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-05-06 | 8 | 17.305 | 5.7169 | 23.0219 | 0.92197 | 0.76558 | 0.17115 | 1.8587 | 8.074% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-05-06 | 9 | 17.577 | 5.7245 | 23.3015 | 0.9445 | 0.76558 | 0.17323 | 1.8833 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-05-06 | 10 | 17.591 | 5.7115 | 23.3025 | 0.94459 | 0.76558 | 0.17323 | 1.8834 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-05-06 | 11 | 18.223 | 5.944 | 24.167 | 1.016 | 0.76558 | 0.17966 | 1.9612 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-05-06 | 12 | 18.9991 | 6.2544 | 25.2534 | 1.1094 | 0.76558 | 0.18774 | 2.0627 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-05-06 | 13 | 21.081 | 7.1559 | 28.2369 | 1.387 | 0.76558 | 0.20992 | 2.3625 | 8.367% | 8.902% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-05-06 | 14 | 24.013 | 8.8149 | 32.8279 | 1.8746 | 0.76558 | 0.24405 | 2.8843 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-05-06 | 15 | 27.949 | 11.0687 | 39.0177 | 2.6482 | 0.76558 | 0.29006 | 3.7039 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-05-06 | 16 | 30.6349 | 12.3909 | 43.0259 | 3.2203 | 0.76558 | 0.31986 | 4.3057 | 10.01% | 10.65% | 7.195% | 1.1112 | 1.1192 | 1.0775
2010-05-06 | 17 | 31.639 | 12.9067 | 44.5458 | 3.4518 | 0.76558 | 0.33116 | 4.5486 | 10.21% | 10.86% | 7.342% | 1.1137 | 1.1219 | 1.0792
2010-05-06 | 18 | 31.639 | 12.8935 | 44.5325 | 3.4498 | 0.76558 | 0.33106 | 4.5464 | 10.21% | 10.86% | 7.34% | 1.1137 | 1.1219 | 1.0792
2010-05-06 | 19 | 31.467 | 12.6927 | 44.1597 | 3.3922 | 0.76558 | 0.32829 | 4.4861 | 10.16% | 10.81% | 7.304% | 1.1131 | 1.1212 | 1.0788
2010-05-06 | 20 | 30.8791 | 12.3287 | 43.2077 | 3.2476 | 0.76558 | 0.32121 | 4.3344 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-05-06 | 21 | 30.8211 | 11.9962 | 42.8173 | 3.1891 | 0.76558 | 0.31831 | 4.273 | 9.98% | 10.62% | 7.175% | 1.1109 | 1.1188 | 1.0773
2010-05-06 | 22 | 29.9591 | 11.7978 | 41.757 | 3.0331 | 0.76558 | 0.31043 | 4.1091 | 9.841% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-05-06 | 23 | 28.7951 | 11.1903 | 39.9854 | 2.7812 | 0.76558 | 0.29726 | 3.8441 | 9.614% | 10.23% | 6.912% | 1.1064 | 1.1139 | 1.0743
2010-05-06 | 24 | 27.6332 | 10.959 | 38.5922 | 2.5908 | 0.76558 | 0.2869 | 3.6433 | 9.44% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-05-06 | 25 | 25.9811 | 10.5174 | 36.4985 | 2.3173 | 0.76558 | 0.27133 | 3.3542 | 9.19% | 9.778% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-05-06 | 26 | 25.2772 | 9.9354 | 35.2127 | 2.1569 | 0.76558 | 0.26178 | 3.1843 | 9.043% | 9.622% | 6.502% | 1.0994 | 1.1065 | 1.0695
2010-05-06 | 27 | 25.3632 | 10.1657 | 35.5289 | 2.1958 | 0.76558 | 0.26413 | 3.2255 | 9.079% | 9.66% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-05-06 | 28 | 25.2912 | 10.2667 | 35.5579 | 2.1994 | 0.76558 | 0.26434 | 3.2293 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-05-06 | 29 | 24.7171 | 9.8661 | 34.5832 | 2.0805 | 0.76558 | 0.2571 | 3.1032 | 8.973% | 9.547% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-05-06 | 30 | 24.1411 | 9.5723 | 33.7134 | 1.9772 | 0.76558 | 0.25063 | 2.9934 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-05-06 | 31 | 25.4051 | 9.4581 | 34.8633 | 2.1143 | 0.76558 | 0.25918 | 3.1391 | 9.004% | 9.58% | 6.474% | 1.0989 | 1.106 | 1.0692
2010-05-06 | 32 | 25.6652 | 9.4147 | 35.0799 | 2.1407 | 0.76558 | 0.26079 | 3.167 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-05-06 | 33 | 25.9813 | 9.5979 | 35.5791 | 2.202 | 0.76558 | 0.2645 | 3.2321 | 9.084% | 9.666% | 6.532% | 1.0999 | 1.107 | 1.0699
2010-05-06 | 34 | 26.6693 | 9.9093 | 36.5786 | 2.3275 | 0.76558 | 0.27193 | 3.365 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-05-06 | 35 | 27.7193 | 10.9242 | 38.6435 | 2.5977 | 0.76558 | 0.28728 | 3.6506 | 9.447% | 10.05% | 6.792% | 1.1043 | 1.1117 | 1.0729
2010-05-06 | 36 | 30.3192 | 12.6063 | 42.9255 | 3.2053 | 0.76558 | 0.31911 | 4.29 | 9.994% | 10.63% | 7.186% | 1.111 | 1.119 | 1.0774
2010-05-06 | 37 | 32.7454 | 13.2521 | 45.9974 | 3.6805 | 0.76558 | 0.34195 | 4.788 | 10.41% | 11.08% | 7.484% | 1.1162 | 1.1245 | 1.0809
2010-05-06 | 38 | 33.6514 | 12.8676 | 46.519 | 3.7644 | 0.76558 | 0.34583 | 4.8758 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-05-06 | 39 | 32.8755 | 12.411 | 45.2865 | 3.5676 | 0.76558 | 0.33667 | 4.6698 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-05-06 | 40 | 32.3574 | 11.8489 | 44.2062 | 3.3994 | 0.76558 | 0.32863 | 4.4936 | 10.17% | 10.82% | 7.309% | 1.1132 | 1.1213 | 1.0788
2010-05-06 | 41 | 31.9713 | 11.3683 | 43.3396 | 3.2674 | 0.76558 | 0.32219 | 4.3552 | 10.05% | 10.69% | 7.225% | 1.1117 | 1.1197 | 1.0779
2010-05-06 | 42 | 31.2673 | 11.016 | 42.2833 | 3.1101 | 0.76558 | 0.31434 | 4.19 | 9.909% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-05-06 | 43 | 29.6292 | 10.2273 | 39.8565 | 2.7633 | 0.76558 | 0.2963 | 3.8252 | 9.597% | 10.21% | 6.901% | 1.1062 | 1.1137 | 1.0741
2010-05-06 | 44 | 28.1073 | 9.6224 | 37.7297 | 2.4763 | 0.76558 | 0.28049 | 3.5224 | 9.336% | 9.933% | 6.712% | 1.103 | 1.1103 | 1.072
2010-05-06 | 45 | 25.679 | 8.7192 | 34.3982 | 2.0583 | 0.76558 | 0.25572 | 3.0796 | 8.953% | 9.526% | 6.437% | 1.0983 | 1.1053 | 1.0688
2010-05-06 | 46 | 23.1788 | 7.8333 | 31.012 | 1.673 | 0.76558 | 0.23055 | 2.6691 | 8.607% | 9.158% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-05-06 | 47 | 22.5047 | 7.6843 | 30.189 | 1.5854 | 0.76558 | 0.22443 | 2.5754 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-05-06 | 48 | 21.5407 | 7.8992 | 29.4399 | 1.5077 | 0.76558 | 0.21886 | 2.4921 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-05-07 | 1 | 20.2347 | 7.0354 | 27.2701 | 1.2936 | 0.76558 | 0.20273 | 2.2619 | 8.295% | 8.825% | 5.964% | 1.0904 | 1.0968 | 1.0634
2010-05-07 | 2 | 20.4346 | 6.6326 | 27.0671 | 1.2744 | 0.76558 | 0.20122 | 2.2412 | 8.28% | 8.81% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-05-07 | 3 | 19.4145 | 6.341 | 25.7556 | 1.1539 | 0.76558 | 0.19147 | 2.111 | 8.196% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-05-07 | 4 | 18.4825 | 6.0806 | 24.5631 | 1.0495 | 0.76558 | 0.1826 | 1.9977 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-05-07 | 5 | 18.1085 | 5.9948 | 24.1033 | 1.0106 | 0.76558 | 0.17919 | 1.9554 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-05-07 | 6 | 17.6205 | 5.8552 | 23.4757 | 0.95868 | 0.76558 | 0.17452 | 1.8988 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-05-07 | 7 | 17.6905 | 5.9598 | 23.6502 | 0.97298 | 0.76558 | 0.17582 | 1.9144 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-05-07 | 8 | 17.7204 | 5.824 | 23.5444 | 0.96429 | 0.76558 | 0.17503 | 1.9049 | 8.091% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-05-07 | 9 | 17.9924 | 5.9073 | 23.8997 | 0.99362 | 0.76558 | 0.17767 | 1.9369 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-05-07 | 10 | 18.2084 | 6.0644 | 24.2728 | 1.0249 | 0.76558 | 0.18045 | 1.9709 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-05-07 | 11 | 18.9263 | 6.5594 | 25.4857 | 1.1299 | 0.76558 | 0.18946 | 2.0849 | 8.181% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-05-07 | 12 | 19.6583 | 6.9985 | 26.6568 | 1.2361 | 0.76558 | 0.19817 | 2.1998 | 8.252% | 8.781% | 5.934% | 1.0899 | 1.0963 | 1.0631
2010-05-07 | 13 | 21.9283 | 7.9409 | 29.8693 | 1.552 | 0.76558 | 0.22205 | 2.5396 | 8.502% | 9.047% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-05-07 | 14 | 25.1024 | 9.6943 | 34.7967 | 2.1062 | 0.76558 | 0.25868 | 3.1305 | 8.997% | 9.572% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-05-07 | 15 | 29.1823 | 11.9971 | 41.1794 | 2.9498 | 0.76558 | 0.30613 | 4.0215 | 9.766% | 10.39% | 7.022% | 1.1082 | 1.116 | 1.0755
2010-05-07 | 16 | 31.5822 | 13.7117 | 45.2939 | 3.5687 | 0.76558 | 0.33672 | 4.671 | 10.31% | 10.97% | 7.415% | 1.115 | 1.1233 | 1.0801
2010-05-07 | 17 | 32.9022 | 14.4651 | 47.3673 | 3.9029 | 0.76558 | 0.35213 | 5.0207 | 10.6% | 11.28% | 7.621% | 1.1186 | 1.1271 | 1.0825
2010-05-07 | 18 | 33.0601 | 14.0746 | 47.1347 | 3.8647 | 0.76558 | 0.35041 | 4.9807 | 10.57% | 11.24% | 7.598% | 1.1182 | 1.1267 | 1.0822
2010-05-07 | 19 | 32.8162 | 13.3884 | 46.2046 | 3.7137 | 0.76558 | 0.34349 | 4.8228 | 10.44% | 11.11% | 7.505% | 1.1165 | 1.1249 | 1.0811
2010-05-07 | 20 | 32.0842 | 12.557 | 44.6412 | 3.4666 | 0.76558 | 0.33187 | 4.5641 | 10.22% | 10.88% | 7.351% | 1.1139 | 1.1221 | 1.0793
2010-05-07 | 21 | 32.1562 | 11.9747 | 44.1309 | 3.3878 | 0.76558 | 0.32807 | 4.4815 | 10.15% | 10.8% | 7.301% | 1.113 | 1.1211 | 1.0788
2010-05-07 | 22 | 31.2801 | 11.2163 | 42.4965 | 3.1415 | 0.76558 | 0.31592 | 4.223 | 9.937% | 10.57% | 7.145% | 1.1103 | 1.1182 | 1.0769
2010-05-07 | 23 | 30.2881 | 10.4657 | 40.7538 | 2.8892 | 0.76558 | 0.30297 | 3.9577 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2010-05-07 | 24 | 29.4561 | 10.2267 | 39.6829 | 2.7393 | 0.76558 | 0.29501 | 3.7999 | 9.576% | 10.19% | 6.885% | 1.1059 | 1.1134 | 1.0739
2010-05-07 | 25 | 28.4641 | 10.1671 | 38.6312 | 2.596 | 0.76558 | 0.28719 | 3.6488 | 9.445% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-05-07 | 26 | 27.4879 | 9.8929 | 37.3808 | 2.4307 | 0.76558 | 0.27789 | 3.4742 | 9.294% | 9.889% | 6.682% | 1.1025 | 1.1097 | 1.0716
2010-05-07 | 27 | 27.372 | 10.2068 | 37.5788 | 2.4565 | 0.76558 | 0.27937 | 3.5015 | 9.318% | 9.914% | 6.699% | 1.1028 | 1.1101 | 1.0718
2010-05-07 | 28 | 27.0558 | 10.4861 | 37.5419 | 2.4517 | 0.76558 | 0.27909 | 3.4964 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-05-07 | 29 | 26.8559 | 10.1847 | 37.0406 | 2.3867 | 0.76558 | 0.27536 | 3.4276 | 9.254% | 9.846% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-05-07 | 30 | 26.7539 | 9.9186 | 36.6725 | 2.3395 | 0.76558 | 0.27263 | 3.3777 | 9.21% | 9.8% | 6.622% | 1.1014 | 1.1086 | 1.0709
2010-05-07 | 31 | 28.522 | 9.7281 | 38.2501 | 2.5451 | 0.76558 | 0.28436 | 3.595 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-05-07 | 32 | 29.7722 | 9.7141 | 39.4863 | 2.7122 | 0.76558 | 0.29355 | 3.7714 | 9.551% | 10.16% | 6.867% | 1.1056 | 1.1131 | 1.0737
2010-05-07 | 33 | 30.1023 | 10.2017 | 40.304 | 2.8257 | 0.76558 | 0.29963 | 3.8909 | 9.654% | 10.27% | 6.941% | 1.1069 | 1.1145 | 1.0746
2010-05-07 | 34 | 30.9208 | 10.8409 | 41.7617 | 3.0338 | 0.76558 | 0.31046 | 4.1099 | 9.841% | 10.47% | 7.076% | 1.1092 | 1.117 | 1.0761
2010-05-07 | 35 | 31.9271 | 12.0483 | 43.9754 | 3.364 | 0.76558 | 0.32692 | 4.4565 | 10.13% | 10.78% | 7.286% | 1.1128 | 1.1209 | 1.0786
2010-05-07 | 36 | 33.895 | 13.2385 | 47.1336 | 3.8645 | 0.76558 | 0.3504 | 4.9805 | 10.57% | 11.24% | 7.598% | 1.1182 | 1.1267 | 1.0822
2010-05-07 | 37 | 34.857 | 13.4098 | 48.2668 | 4.0526 | 0.76558 | 0.35882 | 5.177 | 10.73% | 11.41% | 7.712% | 1.1201 | 1.1288 | 1.0836
2010-05-07 | 38 | 34.9011 | 13.0661 | 47.9672 | 4.0024 | 0.76558 | 0.35659 | 5.1246 | 10.68% | 11.37% | 7.681% | 1.1196 | 1.1283 | 1.0832
2010-05-07 | 39 | 33.7652 | 12.4882 | 46.2534 | 3.7215 | 0.76558 | 0.34385 | 4.831 | 10.44% | 11.11% | 7.51% | 1.1166 | 1.125 | 1.0812
2010-05-07 | 40 | 33.0472 | 12.0028 | 45.05 | 3.5304 | 0.76558 | 0.33491 | 4.6309 | 10.28% | 10.94% | 7.391% | 1.1146 | 1.1228 | 1.0798
2010-05-07 | 41 | 32.761 | 11.4535 | 44.2145 | 3.4007 | 0.76558 | 0.3287 | 4.4949 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-05-07 | 42 | 32.3731 | 11.146 | 43.5191 | 3.2945 | 0.76558 | 0.32353 | 4.3836 | 10.07% | 10.72% | 7.242% | 1.112 | 1.12 | 1.0781
2010-05-07 | 43 | 30.6051 | 10.5603 | 41.1653 | 2.9478 | 0.76558 | 0.30603 | 4.0194 | 9.764% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-05-07 | 44 | 28.667 | 9.9343 | 38.6014 | 2.592 | 0.76558 | 0.28697 | 3.6446 | 9.442% | 10.05% | 6.788% | 1.1043 | 1.1117 | 1.0728
2010-05-07 | 45 | 26.181 | 8.96 | 35.141 | 2.1481 | 0.76558 | 0.26124 | 3.175 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-05-07 | 46 | 23.711 | 7.8801 | 31.5911 | 1.7361 | 0.76558 | 0.23485 | 2.7365 | 8.662% | 9.217% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-05-07 | 47 | 23.3949 | 7.9306 | 31.3256 | 1.707 | 0.76558 | 0.23288 | 2.7055 | 8.637% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-05-07 | 48 | 22.347 | 8.2249 | 30.5719 | 1.6258 | 0.76558 | 0.22728 | 2.6187 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2010-05-08 | 1 | 20.9089 | 7.3519 | 28.2608 | 1.3893 | 0.76558 | 0.21009 | 2.365 | 8.368% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-05-08 | 2 | 21.1249 | 6.9554 | 28.0803 | 1.3716 | 0.76558 | 0.20875 | 2.346 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-05-08 | 3 | 20.2488 | 6.592 | 26.8408 | 1.2532 | 0.76558 | 0.19954 | 2.2183 | 8.265% | 8.794% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-05-08 | 4 | 19.4148 | 6.2276 | 25.6424 | 1.1438 | 0.76558 | 0.19063 | 2.1 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-05-08 | 5 | 18.4389 | 6.0368 | 24.4756 | 1.0421 | 0.76558 | 0.18195 | 1.9896 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-05-08 | 6 | 17.9069 | 5.8546 | 23.7615 | 0.98216 | 0.76558 | 0.17665 | 1.9244 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-05-08 | 7 | 17.7928 | 5.8005 | 23.5933 | 0.9683 | 0.76558 | 0.1754 | 1.9093 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-05-08 | 8 | 17.9208 | 5.6887 | 23.6095 | 0.96963 | 0.76558 | 0.17552 | 1.9107 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-05-08 | 9 | 18.3668 | 5.7251 | 24.0919 | 1.0097 | 0.76558 | 0.1791 | 1.9543 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-05-08 | 10 | 18.4667 | 5.8491 | 24.3158 | 1.0285 | 0.76558 | 0.18077 | 1.9749 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-05-08 | 11 | 18.5248 | 6.1604 | 24.6852 | 1.06 | 0.76558 | 0.18351 | 2.0091 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-05-08 | 12 | 19.1708 | 6.4748 | 25.6456 | 1.1441 | 0.76558 | 0.19065 | 2.1003 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-05-08 | 13 | 21.3548 | 7.4696 | 28.8244 | 1.4453 | 0.76558 | 0.21428 | 2.4252 | 8.414% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-05-08 | 14 | 24.1708 | 9.2046 | 33.3754 | 1.9377 | 0.76558 | 0.24812 | 2.9514 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-05-08 | 15 | 28.3207 | 11.5012 | 39.822 | 2.7585 | 0.76558 | 0.29604 | 3.8202 | 9.593% | 10.21% | 6.897% | 1.1061 | 1.1137 | 1.0741
2010-05-08 | 16 | 31.0647 | 12.9131 | 43.9778 | 3.3644 | 0.76558 | 0.32694 | 4.4569 | 10.13% | 10.78% | 7.287% | 1.1128 | 1.1209 | 1.0786
2010-05-08 | 17 | 32.7887 | 13.6751 | 46.4638 | 3.7555 | 0.76558 | 0.34542 | 4.8665 | 10.47% | 11.14% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-05-08 | 18 | 33.0908 | 13.5353 | 46.6262 | 3.7818 | 0.76558 | 0.34662 | 4.894 | 10.5% | 11.17% | 7.547% | 1.1173 | 1.1257 | 1.0816
2010-05-08 | 19 | 32.8308 | 13.148 | 45.9788 | 3.6775 | 0.76558 | 0.34181 | 4.7849 | 10.41% | 11.07% | 7.482% | 1.1162 | 1.1245 | 1.0809
2010-05-08 | 20 | 32.4589 | 12.2281 | 44.6869 | 3.4737 | 0.76558 | 0.33221 | 4.5715 | 10.23% | 10.88% | 7.355% | 1.114 | 1.1221 | 1.0794
2010-05-08 | 21 | 32.3868 | 11.5112 | 43.898 | 3.3522 | 0.76558 | 0.32634 | 4.4441 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-05-08 | 22 | 31.2809 | 10.9342 | 42.215 | 3.1 | 0.76558 | 0.31383 | 4.1795 | 9.9% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-05-08 | 23 | 30.5628 | 10.2914 | 40.8543 | 2.9034 | 0.76558 | 0.30372 | 3.9727 | 9.724% | 10.35% | 6.992% | 1.1077 | 1.1154 | 1.0752
2010-05-08 | 24 | 29.3128 | 9.9979 | 39.3107 | 2.6882 | 0.76558 | 0.29224 | 3.746 | 9.529% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0736
2010-05-08 | 25 | 28.4068 | 10.0893 | 38.4961 | 2.5779 | 0.76558 | 0.28619 | 3.6297 | 9.429% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-05-08 | 26 | 27.5608 | 9.5625 | 37.1233 | 2.3973 | 0.76558 | 0.27598 | 3.4389 | 9.263% | 9.856% | 6.66% | 1.1021 | 1.1093 | 1.0714
2010-05-08 | 27 | 27.8188 | 9.8616 | 37.6804 | 2.4698 | 0.76558 | 0.28012 | 3.5155 | 9.33% | 9.927% | 6.708% | 1.1029 | 1.1102 | 1.0719
2010-05-08 | 28 | 28.1628 | 10.0935 | 38.2563 | 2.5459 | 0.76558 | 0.2844 | 3.5959 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-05-08 | 29 | 27.6328 | 9.9114 | 37.5442 | 2.452 | 0.76558 | 0.27911 | 3.4967 | 9.314% | 9.91% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-05-08 | 30 | 27.2288 | 9.5454 | 36.7741 | 2.3524 | 0.76558 | 0.27338 | 3.3914 | 9.222% | 9.812% | 6.631% | 1.1016 | 1.1088 | 1.071
2010-05-08 | 31 | 28.3208 | 9.7614 | 38.0822 | 2.5228 | 0.76558 | 0.28311 | 3.5715 | 9.378% | 9.979% | 6.743% | 1.1035 | 1.1108 | 1.0723
2010-05-08 | 32 | 28.2208 | 10.069 | 38.2899 | 2.5504 | 0.76558 | 0.28465 | 3.6006 | 9.404% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-05-08 | 33 | 28.9668 | 10.3489 | 39.3157 | 2.6889 | 0.76558 | 0.29228 | 3.7467 | 9.53% | 10.14% | 6.852% | 1.1053 | 1.1128 | 1.0736
2010-05-08 | 34 | 30.159 | 10.4682 | 40.6271 | 2.8712 | 0.76558 | 0.30203 | 3.9388 | 9.695% | 10.32% | 6.971% | 1.1074 | 1.115 | 1.0749
2010-05-08 | 35 | 31.1288 | 11.3836 | 42.5124 | 3.1439 | 0.76558 | 0.31604 | 4.2255 | 9.939% | 10.58% | 7.146% | 1.1104 | 1.1183 | 1.077
2010-05-08 | 36 | 33.1469 | 12.5539 | 45.7007 | 3.6331 | 0.76558 | 0.33974 | 4.7385 | 10.37% | 11.03% | 7.455% | 1.1157 | 1.124 | 1.0806
2010-05-08 | 37 | 34.4548 | 12.7244 | 47.1792 | 3.872 | 0.76558 | 0.35074 | 4.9883 | 10.57% | 11.25% | 7.602% | 1.1182 | 1.1268 | 1.0823
2010-05-08 | 38 | 34.7288 | 12.7194 | 47.4482 | 3.9163 | 0.76558 | 0.35274 | 5.0346 | 10.61% | 11.29% | 7.629% | 1.1187 | 1.1273 | 1.0826
2010-05-08 | 39 | 34.3248 | 12.2018 | 46.5266 | 3.7656 | 0.76558 | 0.34588 | 4.8771 | 10.48% | 11.15% | 7.537% | 1.1171 | 1.1255 | 1.0815
2010-05-08 | 40 | 33.6728 | 11.6526 | 45.3254 | 3.5737 | 0.76558 | 0.33695 | 4.6762 | 10.32% | 10.98% | 7.418% | 1.115 | 1.1233 | 1.0801
2010-05-08 | 41 | 33.2709 | 11.2963 | 44.5672 | 3.4551 | 0.76558 | 0.33132 | 4.552 | 10.21% | 10.87% | 7.344% | 1.1138 | 1.1219 | 1.0793
2010-05-08 | 42 | 32.8889 | 10.9013 | 43.7902 | 3.3357 | 0.76558 | 0.32554 | 4.4268 | 10.11% | 10.76% | 7.269% | 1.1125 | 1.1205 | 1.0784
2010-05-08 | 43 | 30.9928 | 10.5224 | 41.5152 | 2.9981 | 0.76558 | 0.30863 | 4.0723 | 9.809% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-05-08 | 44 | 29.8588 | 9.898 | 39.7568 | 2.7495 | 0.76558 | 0.29556 | 3.8107 | 9.585% | 10.2% | 6.892% | 1.106 | 1.1136 | 1.074
2010-05-08 | 45 | 27.5308 | 9.1874 | 36.7181 | 2.3453 | 0.76558 | 0.27297 | 3.3838 | 9.216% | 9.806% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-05-08 | 46 | 25.4268 | 8.3696 | 33.7964 | 1.9869 | 0.76558 | 0.25125 | 3.0037 | 8.888% | 9.457% | 6.39% | 1.0975 | 1.1044 | 1.0683
2010-05-08 | 47 | 24.8087 | 8.3593 | 33.168 | 1.9137 | 0.76558 | 0.24658 | 2.9259 | 8.821% | 9.386% | 6.343% | 1.0967 | 1.1036 | 1.0677
2010-05-08 | 48 | 23.9327 | 8.6595 | 32.5923 | 1.8478 | 0.76558 | 0.24229 | 2.8557 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-05-09 | 1 | 22.6328 | 7.7309 | 30.3637 | 1.6038 | 0.76558 | 0.22573 | 2.5951 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-05-09 | 2 | 23.0346 | 7.3634 | 30.398 | 1.6074 | 0.76558 | 0.22598 | 2.599 | 8.55% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-05-09 | 3 | 21.7847 | 7.0205 | 28.8052 | 1.4434 | 0.76558 | 0.21414 | 2.4231 | 8.412% | 8.95% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-05-09 | 4 | 20.8226 | 6.6811 | 27.5037 | 1.3159 | 0.76558 | 0.20447 | 2.2859 | 8.311% | 8.843% | 5.976% | 1.0906 | 1.097 | 1.0636
2010-05-09 | 5 | 20.4345 | 6.5622 | 26.9968 | 1.2678 | 0.76558 | 0.2007 | 2.2341 | 8.275% | 8.805% | 5.95% | 1.0902 | 1.0966 | 1.0633
2010-05-09 | 6 | 20.2905 | 6.437 | 26.7275 | 1.2427 | 0.76558 | 0.1987 | 2.2069 | 8.257% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-05-09 | 7 | 19.9605 | 6.4107 | 26.3711 | 1.2097 | 0.76558 | 0.19605 | 2.1714 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-05-09 | 8 | 19.6884 | 6.3881 | 26.0765 | 1.1829 | 0.76558 | 0.19386 | 2.1423 | 8.215% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-05-09 | 9 | 19.9183 | 6.4248 | 26.3431 | 1.2072 | 0.76558 | 0.19584 | 2.1686 | 8.232% | 8.759% | 5.919% | 1.0897 | 1.096 | 1.0629
2010-05-09 | 10 | 20.3923 | 6.5081 | 26.9004 | 1.2588 | 0.76558 | 0.19998 | 2.2243 | 8.269% | 8.798% | 5.945% | 1.0901 | 1.0965 | 1.0632
2010-05-09 | 11 | 20.5642 | 6.6731 | 27.2373 | 1.2905 | 0.76558 | 0.20249 | 2.2586 | 8.292% | 8.823% | 5.962% | 1.0904 | 1.0968 | 1.0634
2010-05-09 | 12 | 20.8221 | 6.7687 | 27.5908 | 1.3242 | 0.76558 | 0.20511 | 2.2949 | 8.318% | 8.85% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-05-09 | 13 | 21.8001 | 7.2457 | 29.0458 | 1.4676 | 0.76558 | 0.21593 | 2.4491 | 8.432% | 8.971% | 6.062% | 1.0921 | 1.0986 | 1.0645
2010-05-09 | 14 | 23.1781 | 7.8185 | 30.9966 | 1.6713 | 0.76558 | 0.23043 | 2.6673 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2010-05-09 | 15 | 24.528 | 8.6387 | 33.1667 | 1.9135 | 0.76558 | 0.24657 | 2.9257 | 8.821% | 9.386% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-05-09 | 16 | 25.332 | 9.7705 | 35.1025 | 2.1434 | 0.76558 | 0.26096 | 3.17 | 9.031% | 9.609% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-05-09 | 17 | 27.2859 | 10.96 | 38.2459 | 2.5445 | 0.76558 | 0.28432 | 3.5944 | 9.398% | 10% | 6.757% | 1.1037 | 1.1111 | 1.0725
2010-05-09 | 18 | 29.8719 | 12.023 | 41.8949 | 3.0532 | 0.76558 | 0.31145 | 4.1302 | 9.859% | 10.49% | 7.088% | 1.1094 | 1.1172 | 1.0763
2010-05-09 | 19 | 32.5578 | 12.7128 | 45.2706 | 3.5651 | 0.76558 | 0.33655 | 4.6672 | 10.31% | 10.97% | 7.413% | 1.1149 | 1.1232 | 1.0801
2010-05-09 | 20 | 33.7077 | 12.8584 | 46.5661 | 3.772 | 0.76558 | 0.34618 | 4.8838 | 10.49% | 11.16% | 7.541% | 1.1172 | 1.1256 | 1.0816
2010-05-09 | 21 | 35.1437 | 13.1222 | 48.266 | 4.0524 | 0.76558 | 0.35882 | 5.1768 | 10.73% | 11.41% | 7.712% | 1.1201 | 1.1288 | 1.0836
2010-05-09 | 22 | 35.0138 | 13.2335 | 48.2473 | 4.0493 | 0.76558 | 0.35868 | 5.1736 | 10.72% | 11.41% | 7.71% | 1.1201 | 1.1288 | 1.0835
2010-05-09 | 23 | 33.6057 | 13.0014 | 46.6071 | 3.7787 | 0.76558 | 0.34648 | 4.8907 | 10.49% | 11.17% | 7.545% | 1.1172 | 1.1257 | 1.0816
2010-05-09 | 24 | 32.7876 | 12.7351 | 45.5227 | 3.6049 | 0.76558 | 0.33842 | 4.7089 | 10.34% | 11.01% | 7.437% | 1.1154 | 1.1237 | 1.0803
2010-05-09 | 25 | 31.1936 | 12.3982 | 43.5918 | 3.3056 | 0.76558 | 0.32407 | 4.3952 | 10.08% | 10.73% | 7.249% | 1.1121 | 1.1202 | 1.0782
2010-05-09 | 26 | 29.7716 | 11.3883 | 41.1599 | 2.947 | 0.76558 | 0.30599 | 4.0186 | 9.763% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-05-09 | 27 | 29.0956 | 10.9613 | 40.0568 | 2.7912 | 0.76558 | 0.29779 | 3.8545 | 9.623% | 10.24% | 6.919% | 1.1065 | 1.1141 | 1.0743
2010-05-09 | 28 | 28.8376 | 10.8719 | 39.7094 | 2.743 | 0.76558 | 0.2952 | 3.8038 | 9.579% | 10.19% | 6.887% | 1.1059 | 1.1135 | 1.074
2010-05-09 | 29 | 28.5796 | 10.4882 | 39.0677 | 2.655 | 0.76558 | 0.29043 | 3.7111 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-05-09 | 30 | 28.3196 | 10.1518 | 38.4715 | 2.5746 | 0.76558 | 0.286 | 3.6262 | 9.426% | 10.03% | 6.777% | 1.1041 | 1.1115 | 1.0727
2010-05-09 | 31 | 29.4695 | 10.4285 | 39.898 | 2.7691 | 0.76558 | 0.29661 | 3.8313 | 9.603% | 10.22% | 6.904% | 1.1062 | 1.1138 | 1.0742
2010-05-09 | 32 | 29.8996 | 10.4785 | 40.3781 | 2.8361 | 0.76558 | 0.30018 | 3.9019 | 9.663% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-05-09 | 33 | 29.8995 | 10.6454 | 40.5449 | 2.8596 | 0.76558 | 0.30142 | 3.9266 | 9.685% | 10.3% | 6.963% | 1.1072 | 1.1149 | 1.0748
2010-05-09 | 34 | 30.6335 | 10.7853 | 41.4188 | 2.9842 | 0.76558 | 0.30791 | 4.0577 | 9.797% | 10.42% | 7.044% | 1.1086 | 1.1164 | 1.0758
2010-05-09 | 35 | 31.7955 | 11.839 | 43.6345 | 3.312 | 0.76558 | 0.32438 | 4.402 | 10.09% | 10.73% | 7.254% | 1.1122 | 1.1202 | 1.0782
2010-05-09 | 36 | 34.1374 | 13.0817 | 47.2191 | 3.8786 | 0.76558 | 0.35103 | 4.9952 | 10.58% | 11.26% | 7.606% | 1.1183 | 1.1268 | 1.0823
2010-05-09 | 37 | 35.3874 | 13.2014 | 48.5888 | 4.1068 | 0.76558 | 0.36121 | 5.2336 | 10.77% | 11.46% | 7.745% | 1.1207 | 1.1294 | 1.0839
2010-05-09 | 38 | 35.3153 | 12.7301 | 48.0454 | 4.0155 | 0.76558 | 0.35718 | 5.1382 | 10.69% | 11.38% | 7.689% | 1.1198 | 1.1284 | 1.0833
2010-05-09 | 39 | 34.7974 | 12.0524 | 46.8497 | 3.8181 | 0.76558 | 0.34829 | 4.932 | 10.53% | 11.2% | 7.569% | 1.1177 | 1.1261 | 1.0819
2010-05-09 | 40 | 33.9073 | 11.6219 | 45.5292 | 3.6059 | 0.76558 | 0.33847 | 4.71 | 10.34% | 11.01% | 7.438% | 1.1154 | 1.1237 | 1.0804
2010-05-09 | 41 | 33.8073 | 11.1958 | 45.0031 | 3.5231 | 0.76558 | 0.33456 | 4.6232 | 10.27% | 10.93% | 7.386% | 1.1145 | 1.1227 | 1.0798
2010-05-09 | 42 | 33.5493 | 10.7376 | 44.2869 | 3.4118 | 0.76558 | 0.32923 | 4.5066 | 10.18% | 10.83% | 7.317% | 1.1133 | 1.1214 | 1.0789
2010-05-09 | 43 | 32.1412 | 10.2932 | 42.4344 | 3.1324 | 0.76558 | 0.31546 | 4.2134 | 9.929% | 10.56% | 7.139% | 1.1102 | 1.1181 | 1.0769
2010-05-09 | 44 | 30.5172 | 9.7601 | 40.2773 | 2.822 | 0.76558 | 0.29943 | 3.887 | 9.651% | 10.27% | 6.939% | 1.1068 | 1.1144 | 1.0746
2010-05-09 | 45 | 28.3772 | 8.9729 | 37.3501 | 2.4267 | 0.76558 | 0.27767 | 3.47 | 9.29% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-05-09 | 46 | 26.3812 | 8.2706 | 34.6518 | 2.0888 | 0.76558 | 0.25761 | 3.1119 | 8.981% | 9.555% | 6.457% | 1.0987 | 1.1056 | 1.069
2010-05-09 | 47 | 26.1651 | 8.4309 | 34.596 | 2.082 | 0.76558 | 0.25719 | 3.1048 | 8.974% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-05-09 | 48 | 25.5192 | 8.7902 | 34.3094 | 2.0477 | 0.76558 | 0.25506 | 3.0683 | 8.943% | 9.515% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-05-10 | 1 | 23.9252 | 8.0171 | 31.9423 | 1.7749 | 0.76558 | 0.23746 | 2.7779 | 8.697% | 9.253% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-05-10 | 2 | 24.4412 | 7.5791 | 32.0204 | 1.7836 | 0.76558 | 0.23804 | 2.7872 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-05-10 | 3 | 23.4513 | 7.1296 | 30.5809 | 1.6268 | 0.76558 | 0.22734 | 2.6197 | 8.567% | 9.115% | 6.159% | 1.0937 | 1.1003 | 1.0656
2010-05-10 | 4 | 22.4153 | 6.7181 | 29.1334 | 1.4764 | 0.76558 | 0.21658 | 2.4586 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-05-10 | 5 | 21.6114 | 6.5162 | 28.1276 | 1.3763 | 0.76558 | 0.2091 | 2.3509 | 8.358% | 8.893% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-05-10 | 6 | 20.7494 | 6.426 | 27.1753 | 1.2846 | 0.76558 | 0.20202 | 2.2523 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-05-10 | 7 | 20.7354 | 6.3677 | 27.1032 | 1.2778 | 0.76558 | 0.20149 | 2.2449 | 8.283% | 8.813% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-05-10 | 8 | 20.7355 | 6.3347 | 27.0701 | 1.2747 | 0.76558 | 0.20124 | 2.2415 | 8.281% | 8.81% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-05-10 | 9 | 20.3914 | 6.34 | 26.7314 | 1.243 | 0.76558 | 0.19872 | 2.2073 | 8.257% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-05-10 | 10 | 20.3334 | 6.3517 | 26.6851 | 1.2387 | 0.76558 | 0.19838 | 2.2027 | 8.254% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-05-10 | 11 | 20.8075 | 6.404 | 27.2116 | 1.2881 | 0.76558 | 0.20229 | 2.2559 | 8.29% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2010-05-10 | 12 | 21.5536 | 6.4676 | 28.0212 | 1.3659 | 0.76558 | 0.20831 | 2.3398 | 8.35% | 8.884% | 6.004% | 1.0911 | 1.0975 | 1.0639
2010-05-10 | 13 | 22.5596 | 6.7922 | 29.3518 | 1.4987 | 0.76558 | 0.2182 | 2.4824 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-05-10 | 14 | 23.1357 | 7.1528 | 30.2885 | 1.5958 | 0.76558 | 0.22517 | 2.5866 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-05-10 | 15 | 23.9097 | 7.5043 | 31.414 | 1.7166 | 0.76558 | 0.23354 | 2.7158 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-05-10 | 16 | 24.3837 | 8.359 | 32.7428 | 1.8649 | 0.76558 | 0.24341 | 2.8739 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-05-10 | 17 | 26.6538 | 9.7768 | 36.4305 | 2.3087 | 0.76558 | 0.27083 | 3.3451 | 9.182% | 9.77% | 6.602% | 1.1011 | 1.1083 | 1.0707
2010-05-10 | 18 | 28.8378 | 11.1262 | 39.964 | 2.7783 | 0.76558 | 0.2971 | 3.8409 | 9.611% | 10.23% | 6.91% | 1.1063 | 1.1139 | 1.0742
2010-05-10 | 19 | 31.3377 | 12.0778 | 43.4156 | 3.2789 | 0.76558 | 0.32276 | 4.3672 | 10.06% | 10.7% | 7.232% | 1.1118 | 1.1199 | 1.078
2010-05-10 | 20 | 33.0898 | 12.5362 | 45.6259 | 3.6212 | 0.76558 | 0.33919 | 4.726 | 10.36% | 11.02% | 7.448% | 1.1156 | 1.1239 | 1.0805
2010-05-10 | 21 | 35.4739 | 12.8353 | 48.3091 | 4.0597 | 0.76558 | 0.35914 | 5.1844 | 10.73% | 11.42% | 7.716% | 1.1202 | 1.1289 | 1.0836
2010-05-10 | 22 | 35.4299 | 12.913 | 48.3429 | 4.0654 | 0.76558 | 0.35939 | 5.1903 | 10.74% | 11.42% | 7.72% | 1.1203 | 1.129 | 1.0837
2010-05-10 | 23 | 34.8559 | 12.6558 | 47.5117 | 3.9268 | 0.76558 | 0.35321 | 5.0456 | 10.62% | 11.3% | 7.636% | 1.1188 | 1.1274 | 1.0827
2010-05-10 | 24 | 34.024 | 12.5177 | 46.5416 | 3.7681 | 0.76558 | 0.346 | 4.8796 | 10.48% | 11.16% | 7.538% | 1.1171 | 1.1256 | 1.0815
2010-05-10 | 25 | 32.184 | 12.1897 | 44.3737 | 3.4252 | 0.76558 | 0.32988 | 4.5207 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-05-10 | 26 | 30.7761 | 11.2981 | 42.0742 | 3.0794 | 0.76558 | 0.31278 | 4.1578 | 9.882% | 10.51% | 7.105% | 1.1097 | 1.1175 | 1.0765
2010-05-10 | 27 | 31.0641 | 11.2053 | 42.2694 | 3.108 | 0.76558 | 0.31424 | 4.1878 | 9.908% | 10.54% | 7.124% | 1.11 | 1.1178 | 1.0767
2010-05-10 | 28 | 31.3941 | 11.1996 | 42.5937 | 3.1559 | 0.76558 | 0.31665 | 4.2381 | 9.95% | 10.59% | 7.154% | 1.1105 | 1.1184 | 1.0771
2010-05-10 | 29 | 30.6622 | 10.7184 | 41.3806 | 2.9787 | 0.76558 | 0.30763 | 4.0519 | 9.792% | 10.42% | 7.04% | 1.1085 | 1.1163 | 1.0757
2010-05-10 | 30 | 30.0302 | 10.4218 | 40.452 | 2.8465 | 0.76558 | 0.30072 | 3.9128 | 9.673% | 10.29% | 6.955% | 1.1071 | 1.1147 | 1.0747
2010-05-10 | 31 | 31.3522 | 10.5562 | 41.9084 | 3.0552 | 0.76558 | 0.31155 | 4.1323 | 9.86% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-05-10 | 32 | 32.1704 | 10.6199 | 42.7904 | 3.1851 | 0.76558 | 0.31811 | 4.2688 | 9.976% | 10.61% | 7.173% | 1.1108 | 1.1188 | 1.0773
2010-05-10 | 33 | 32.5863 | 10.892 | 43.4783 | 3.2884 | 0.76558 | 0.32322 | 4.3772 | 10.07% | 10.71% | 7.239% | 1.1119 | 1.12 | 1.078
2010-05-10 | 34 | 33.5643 | 11.1597 | 44.724 | 3.4795 | 0.76558 | 0.33248 | 4.5776 | 10.24% | 10.89% | 7.359% | 1.114 | 1.1222 | 1.0794
2010-05-10 | 35 | 33.9222 | 11.7835 | 45.7057 | 3.6339 | 0.76558 | 0.33978 | 4.7393 | 10.37% | 11.03% | 7.455% | 1.1157 | 1.124 | 1.0806
2010-05-10 | 36 | 35.4602 | 13.1207 | 48.5809 | 4.1055 | 0.76558 | 0.36116 | 5.2322 | 10.77% | 11.46% | 7.744% | 1.1207 | 1.1294 | 1.0839
2010-05-10 | 37 | 36.4362 | 13.3631 | 49.7993 | 4.314 | 0.76558 | 0.37021 | 5.4498 | 10.94% | 11.64% | 7.868% | 1.1229 | 1.1318 | 1.0854
2010-05-10 | 38 | 36.3363 | 13.1284 | 49.4647 | 4.2562 | 0.76558 | 0.36773 | 5.3895 | 10.9% | 11.59% | 7.834% | 1.1223 | 1.1311 | 1.085
2010-05-10 | 39 | 35.5183 | 12.6192 | 48.1375 | 4.0309 | 0.76558 | 0.35786 | 5.1543 | 10.71% | 11.39% | 7.699% | 1.1199 | 1.1286 | 1.0834
2010-05-10 | 40 | 34.6844 | 12.1125 | 46.7969 | 3.8095 | 0.76558 | 0.34789 | 4.923 | 10.52% | 11.19% | 7.564% | 1.1176 | 1.126 | 1.0818
2010-05-10 | 41 | 35.1003 | 11.8503 | 46.9506 | 3.8346 | 0.76558 | 0.34904 | 4.9492 | 10.54% | 11.22% | 7.579% | 1.1178 | 1.1263 | 1.082
2010-05-10 | 42 | 34.5263 | 11.3891 | 45.9154 | 3.6673 | 0.76558 | 0.34134 | 4.7743 | 10.4% | 11.06% | 7.476% | 1.116 | 1.1244 | 1.0808
2010-05-10 | 43 | 32.8464 | 10.6121 | 43.4585 | 3.2854 | 0.76558 | 0.32308 | 4.374 | 10.06% | 10.71% | 7.237% | 1.1119 | 1.1199 | 1.078
2010-05-10 | 44 | 31.2663 | 9.8739 | 41.1402 | 2.9442 | 0.76558 | 0.30584 | 4.0156 | 9.761% | 10.39% | 7.018% | 1.1082 | 1.1159 | 1.0755
2010-05-10 | 45 | 28.1623 | 9.1599 | 37.3222 | 2.4231 | 0.76558 | 0.27746 | 3.4661 | 9.287% | 9.881% | 6.677% | 1.1024 | 1.1096 | 1.0716
2010-05-10 | 46 | 25.3323 | 8.0607 | 33.393 | 1.9398 | 0.76558 | 0.24825 | 2.9536 | 8.845% | 9.411% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-05-10 | 47 | 24.7864 | 8.2054 | 32.9918 | 1.8934 | 0.76558 | 0.24526 | 2.9043 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-05-10 | 48 | 24.0683 | 8.6169 | 32.6852 | 1.8584 | 0.76558 | 0.24299 | 2.867 | 8.771% | 9.333% | 6.307% | 1.0961 | 1.1029 | 1.0673
2010-05-11 | 1 | 22.7624 | 7.8508 | 30.6132 | 1.6302 | 0.76558 | 0.22758 | 2.6234 | 8.57% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-05-11 | 2 | 23.6103 | 7.6013 | 31.2116 | 1.6946 | 0.76558 | 0.23203 | 2.6922 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-05-11 | 3 | 22.7904 | 7.2588 | 30.0492 | 1.5707 | 0.76558 | 0.22339 | 2.5597 | 8.518% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2010-05-11 | 4 | 21.7423 | 6.9596 | 28.7019 | 1.433 | 0.76558 | 0.21337 | 2.412 | 8.404% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2010-05-11 | 5 | 21.2383 | 6.7333 | 27.9716 | 1.361 | 0.76558 | 0.20794 | 2.3346 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-05-11 | 6 | 20.8363 | 6.4406 | 27.277 | 1.2943 | 0.76558 | 0.20278 | 2.2626 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2010-05-11 | 7 | 20.4203 | 6.4205 | 26.8408 | 1.2532 | 0.76558 | 0.19954 | 2.2183 | 8.265% | 8.794% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-05-11 | 8 | 20.3626 | 6.3231 | 26.6857 | 1.2388 | 0.76558 | 0.19838 | 2.2027 | 8.254% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-05-11 | 9 | 20.4926 | 6.398 | 26.8907 | 1.2579 | 0.76558 | 0.19991 | 2.2234 | 8.268% | 8.797% | 5.945% | 1.0901 | 1.0965 | 1.0632
2010-05-11 | 10 | 20.6226 | 6.4791 | 27.1017 | 1.2777 | 0.76558 | 0.20148 | 2.2448 | 8.283% | 8.813% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-05-11 | 11 | 21.1828 | 6.8076 | 27.9904 | 1.3629 | 0.76558 | 0.20808 | 2.3365 | 8.348% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2010-05-11 | 12 | 21.8145 | 7.215 | 29.0295 | 1.4659 | 0.76558 | 0.21581 | 2.4473 | 8.43% | 8.97% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-05-11 | 13 | 23.7526 | 8.0104 | 31.7629 | 1.755 | 0.76558 | 0.23613 | 2.7567 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-05-11 | 14 | 26.7845 | 9.5716 | 36.3562 | 2.2993 | 0.76558 | 0.27028 | 3.3351 | 9.173% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-05-11 | 15 | 31.0065 | 11.8995 | 42.906 | 3.2024 | 0.76558 | 0.31897 | 4.2869 | 9.991% | 10.63% | 7.184% | 1.111 | 1.119 | 1.0774
2010-05-11 | 16 | 33.5205 | 13.3576 | 46.8782 | 3.8228 | 0.76558 | 0.3485 | 4.9368 | 10.53% | 11.21% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-05-11 | 17 | 35.5185 | 14.5174 | 50.036 | 4.3551 | 0.76558 | 0.37197 | 5.4927 | 10.98% | 11.68% | 7.893% | 1.1233 | 1.1322 | 1.0857
2010-05-11 | 18 | 36.5945 | 14.6761 | 51.2706 | 4.5727 | 0.76558 | 0.38115 | 5.7194 | 11.16% | 11.87% | 8.021% | 1.1256 | 1.1347 | 1.0872
2010-05-11 | 19 | 37.0985 | 14.4882 | 51.5867 | 4.6292 | 0.76558 | 0.3835 | 5.7783 | 11.2% | 11.92% | 8.054% | 1.1261 | 1.1353 | 1.0876
2010-05-11 | 20 | 36.8106 | 14.224 | 51.0346 | 4.5307 | 0.76558 | 0.3794 | 5.6757 | 11.12% | 11.83% | 7.996% | 1.1251 | 1.1342 | 1.0869
2010-05-11 | 21 | 37.9025 | 13.8841 | 51.7866 | 4.6652 | 0.76558 | 0.38499 | 5.8158 | 11.23% | 11.95% | 8.075% | 1.1265 | 1.1357 | 1.0878
2010-05-11 | 22 | 37.3265 | 13.8269 | 51.1534 | 4.5518 | 0.76558 | 0.38028 | 5.6977 | 11.14% | 11.85% | 8.008% | 1.1253 | 1.1344 | 1.0871
2010-05-11 | 23 | 36.2365 | 13.5893 | 49.8258 | 4.3186 | 0.76558 | 0.37041 | 5.4546 | 10.95% | 11.65% | 7.871% | 1.1229 | 1.1318 | 1.0854
2010-05-11 | 24 | 35.7184 | 13.3667 | 49.0851 | 4.1912 | 0.76558 | 0.3649 | 5.3216 | 10.84% | 11.54% | 7.795% | 1.1216 | 1.1304 | 1.0845
2010-05-11 | 25 | 34.8704 | 12.9909 | 47.8613 | 3.9848 | 0.76558 | 0.35581 | 5.1062 | 10.67% | 11.35% | 7.671% | 1.1194 | 1.1281 | 1.0831
2010-05-11 | 26 | 33.6505 | 12.4528 | 46.1033 | 3.6974 | 0.76558 | 0.34274 | 4.8057 | 10.42% | 11.09% | 7.495% | 1.1164 | 1.1247 | 1.081
2010-05-11 | 27 | 33.4924 | 12.6786 | 46.171 | 3.7083 | 0.76558 | 0.34324 | 4.8171 | 10.43% | 11.1% | 7.501% | 1.1165 | 1.1249 | 1.0811
2010-05-11 | 28 | 33.7365 | 12.5114 | 46.2479 | 3.7207 | 0.76558 | 0.34381 | 4.83 | 10.44% | 11.11% | 7.509% | 1.1166 | 1.125 | 1.0812
2010-05-11 | 29 | 32.8745 | 11.9767 | 44.8512 | 3.4993 | 0.76558 | 0.33343 | 4.5983 | 10.25% | 10.91% | 7.371% | 1.1142 | 1.1224 | 1.0796
2010-05-11 | 30 | 31.8265 | 11.7938 | 43.6203 | 3.3099 | 0.76558 | 0.32428 | 4.3997 | 10.09% | 10.73% | 7.252% | 1.1122 | 1.1202 | 1.0782
2010-05-11 | 31 | 33.5205 | 11.7463 | 45.2668 | 3.5645 | 0.76558 | 0.33652 | 4.6666 | 10.31% | 10.97% | 7.412% | 1.1149 | 1.1232 | 1.0801
2010-05-11 | 32 | 34.2827 | 12.0117 | 46.2944 | 3.7281 | 0.76558 | 0.34416 | 4.8379 | 10.45% | 11.12% | 7.514% | 1.1167 | 1.1251 | 1.0812
2010-05-11 | 33 | 34.5626 | 12.5219 | 47.0845 | 3.8565 | 0.76558 | 0.35003 | 4.9721 | 10.56% | 11.24% | 7.593% | 1.1181 | 1.1266 | 1.0822
2010-05-11 | 34 | 35.1142 | 12.8747 | 47.9889 | 4.006 | 0.76558 | 0.35676 | 5.1284 | 10.69% | 11.37% | 7.684% | 1.1197 | 1.1283 | 1.0832
2010-05-11 | 35 | 35.3334 | 13.7104 | 49.0438 | 4.1841 | 0.76558 | 0.3646 | 5.3143 | 10.84% | 11.53% | 7.791% | 1.1215 | 1.1303 | 1.0845
2010-05-11 | 36 | 36.9492 | 14.6398 | 51.5891 | 4.6297 | 0.76558 | 0.38352 | 5.7788 | 11.2% | 11.92% | 8.054% | 1.1261 | 1.1353 | 1.0876
2010-05-11 | 37 | 37.8165 | 14.5436 | 52.3601 | 4.7691 | 0.76558 | 0.38925 | 5.9239 | 11.31% | 12.04% | 8.135% | 1.1276 | 1.1369 | 1.0885
2010-05-11 | 38 | 38.3185 | 13.7481 | 52.0667 | 4.7158 | 0.76558 | 0.38707 | 5.8684 | 11.27% | 11.99% | 8.104% | 1.127 | 1.1363 | 1.0882
2010-05-11 | 39 | 37.6426 | 13.1321 | 50.7747 | 4.4847 | 0.76558 | 0.37747 | 5.6277 | 11.08% | 11.79% | 7.969% | 1.1247 | 1.1337 | 1.0866
2010-05-11 | 40 | 36.6526 | 12.5003 | 49.1528 | 4.2027 | 0.76558 | 0.36541 | 5.3337 | 10.85% | 11.55% | 7.802% | 1.1217 | 1.1305 | 1.0846
2010-05-11 | 41 | 36.9546 | 12.1687 | 49.1233 | 4.1977 | 0.76558 | 0.36519 | 5.3285 | 10.85% | 11.54% | 7.799% | 1.1217 | 1.1305 | 1.0846
2010-05-11 | 42 | 36.6246 | 11.5887 | 48.2133 | 4.0436 | 0.76558 | 0.35842 | 5.1676 | 10.72% | 11.4% | 7.706% | 1.12 | 1.1287 | 1.0835
2010-05-11 | 43 | 34.7706 | 10.922 | 45.6926 | 3.6318 | 0.76558 | 0.33968 | 4.7371 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-05-11 | 44 | 32.8886 | 10.2343 | 43.1228 | 3.2348 | 0.76558 | 0.32058 | 4.321 | 10.02% | 10.66% | 7.204% | 1.1114 | 1.1193 | 1.0776
2010-05-11 | 45 | 29.6866 | 9.1401 | 38.8268 | 2.6224 | 0.76558 | 0.28864 | 3.6766 | 9.469% | 10.08% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-05-11 | 46 | 26.7986 | 8.0709 | 34.8695 | 2.1151 | 0.76558 | 0.25922 | 3.1399 | 9.005% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2010-05-11 | 47 | 25.9506 | 8.2074 | 34.1581 | 2.0296 | 0.76558 | 0.25394 | 3.0492 | 8.927% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-05-11 | 48 | 24.3127 | 8.5572 | 32.8699 | 1.8795 | 0.76558 | 0.24436 | 2.8894 | 8.79% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-05-12 | 1 | 22.7188 | 7.8438 | 30.5626 | 1.6249 | 0.76558 | 0.22721 | 2.6176 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-05-12 | 2 | 23.4526 | 7.574 | 31.0266 | 1.6746 | 0.76558 | 0.23066 | 2.6708 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-05-12 | 3 | 22.2747 | 7.1965 | 29.4712 | 1.5109 | 0.76558 | 0.21909 | 2.4956 | 8.468% | 9.01% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-05-12 | 4 | 21.4127 | 6.7429 | 28.1555 | 1.379 | 0.76558 | 0.20931 | 2.3539 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-05-12 | 5 | 20.7947 | 6.5706 | 27.3653 | 1.3027 | 0.76558 | 0.20344 | 2.2717 | 8.301% | 8.833% | 5.969% | 1.0905 | 1.0969 | 1.0635
2010-05-12 | 6 | 20.4648 | 6.3889 | 26.8536 | 1.2544 | 0.76558 | 0.19963 | 2.2196 | 8.266% | 8.795% | 5.943% | 1.0901 | 1.0964 | 1.0632
2010-05-12 | 7 | 20.3628 | 6.3504 | 26.7132 | 1.2413 | 0.76558 | 0.19859 | 2.2055 | 8.256% | 8.785% | 5.936% | 1.09 | 1.0963 | 1.0631
2010-05-12 | 8 | 19.9907 | 6.2706 | 26.2614 | 1.1997 | 0.76558 | 0.19523 | 2.1605 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-05-12 | 9 | 20.2627 | 6.4679 | 26.7306 | 1.2429 | 0.76558 | 0.19872 | 2.2072 | 8.257% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-05-12 | 10 | 20.4927 | 6.466 | 26.9587 | 1.2643 | 0.76558 | 0.20041 | 2.2302 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-05-12 | 11 | 21.0238 | 6.7707 | 27.7945 | 1.3439 | 0.76558 | 0.20663 | 2.3161 | 8.333% | 8.866% | 5.991% | 1.0909 | 1.0973 | 1.0637
2010-05-12 | 12 | 21.8147 | 7.1259 | 28.9406 | 1.457 | 0.76558 | 0.21515 | 2.4377 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-05-12 | 13 | 23.9107 | 8.0194 | 31.9301 | 1.7735 | 0.76558 | 0.23737 | 2.7765 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-05-12 | 14 | 26.7986 | 9.6901 | 36.4886 | 2.3161 | 0.76558 | 0.27126 | 3.3529 | 9.189% | 9.777% | 6.607% | 1.1012 | 1.1084 | 1.0707
2010-05-12 | 15 | 30.5486 | 11.8023 | 42.351 | 3.12 | 0.76558 | 0.31484 | 4.2005 | 9.918% | 10.55% | 7.131% | 1.1101 | 1.118 | 1.0768
2010-05-12 | 16 | 32.7647 | 13.3621 | 46.1268 | 3.7012 | 0.76558 | 0.34291 | 4.8097 | 10.43% | 11.09% | 7.497% | 1.1164 | 1.1248 | 1.081
2010-05-12 | 17 | 34.2306 | 14.2948 | 48.5254 | 4.0961 | 0.76558 | 0.36074 | 5.2224 | 10.76% | 11.45% | 7.738% | 1.1206 | 1.1293 | 1.0839
2010-05-12 | 18 | 35.0066 | 14.0419 | 49.0485 | 4.1849 | 0.76558 | 0.36463 | 5.3151 | 10.84% | 11.53% | 7.791% | 1.1215 | 1.1303 | 1.0845
2010-05-12 | 19 | 35.6825 | 13.7635 | 49.446 | 4.253 | 0.76558 | 0.36759 | 5.3862 | 10.89% | 11.59% | 7.832% | 1.1222 | 1.1311 | 1.085
2010-05-12 | 20 | 35.1506 | 13.7009 | 48.8515 | 4.1514 | 0.76558 | 0.36317 | 5.2801 | 10.81% | 11.5% | 7.771% | 1.1212 | 1.1299 | 1.0843
2010-05-12 | 21 | 36.2144 | 13.5379 | 49.7524 | 4.3059 | 0.76558 | 0.36987 | 5.4413 | 10.94% | 11.64% | 7.864% | 1.1228 | 1.1317 | 1.0853
2010-05-12 | 22 | 35.8124 | 13.4126 | 49.2251 | 4.2151 | 0.76558 | 0.36595 | 5.3466 | 10.86% | 11.56% | 7.809% | 1.1219 | 1.1307 | 1.0847
2010-05-12 | 23 | 34.8344 | 12.87 | 47.7044 | 3.9587 | 0.76558 | 0.35464 | 5.0789 | 10.65% | 11.33% | 7.655% | 1.1192 | 1.1278 | 1.0829
2010-05-12 | 24 | 34.2304 | 12.5472 | 46.7776 | 3.8064 | 0.76558 | 0.34775 | 4.9197 | 10.52% | 11.19% | 7.562% | 1.1175 | 1.126 | 1.0818
2010-05-12 | 25 | 33.5124 | 12.367 | 45.8793 | 3.6616 | 0.76558 | 0.34107 | 4.7682 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-05-12 | 26 | 31.9464 | 11.7345 | 43.6809 | 3.3191 | 0.76558 | 0.32473 | 4.4094 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-05-12 | 27 | 32.2344 | 12.1366 | 44.371 | 3.4248 | 0.76558 | 0.32986 | 4.5202 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-05-12 | 28 | 32.5224 | 12.3929 | 44.9153 | 3.5093 | 0.76558 | 0.33391 | 4.6088 | 10.26% | 10.92% | 7.378% | 1.1143 | 1.1226 | 1.0797
2010-05-12 | 29 | 31.9044 | 12.0548 | 43.9592 | 3.3615 | 0.76558 | 0.3268 | 4.4539 | 10.13% | 10.78% | 7.285% | 1.1127 | 1.1208 | 1.0786
2010-05-12 | 30 | 31.2963 | 11.7503 | 43.0466 | 3.2234 | 0.76558 | 0.32001 | 4.309 | 10.01% | 10.65% | 7.197% | 1.1112 | 1.1192 | 1.0776
2010-05-12 | 31 | 32.9183 | 11.7047 | 44.6229 | 3.4638 | 0.76558 | 0.33173 | 4.5611 | 10.22% | 10.88% | 7.349% | 1.1139 | 1.122 | 1.0793
2010-05-12 | 32 | 33.6643 | 11.8988 | 45.5631 | 3.6113 | 0.76558 | 0.33872 | 4.7156 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-05-12 | 33 | 34.3683 | 12.4389 | 46.8072 | 3.8112 | 0.76558 | 0.34797 | 4.9247 | 10.52% | 11.19% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-05-12 | 34 | 34.8423 | 12.8345 | 47.6768 | 3.9541 | 0.76558 | 0.35444 | 5.0741 | 10.64% | 11.32% | 7.652% | 1.1191 | 1.1277 | 1.0829
2010-05-12 | 35 | 34.4683 | 13.5602 | 48.0285 | 4.0127 | 0.76558 | 0.35705 | 5.1353 | 10.69% | 11.38% | 7.688% | 1.1197 | 1.1284 | 1.0833
2010-05-12 | 36 | 36.6803 | 14.6132 | 51.2935 | 4.5768 | 0.76558 | 0.38132 | 5.7237 | 11.16% | 11.87% | 8.023% | 1.1256 | 1.1347 | 1.0872
2010-05-12 | 37 | 37.9022 | 14.512 | 52.4142 | 4.7789 | 0.76558 | 0.38965 | 5.9342 | 11.32% | 12.05% | 8.14% | 1.1277 | 1.137 | 1.0886
2010-05-12 | 38 | 38.6922 | 13.8294 | 52.5216 | 4.7986 | 0.76558 | 0.39045 | 5.9546 | 11.34% | 12.06% | 8.152% | 1.1279 | 1.1372 | 1.0888
2010-05-12 | 39 | 38.0023 | 13.261 | 51.2633 | 4.5714 | 0.76558 | 0.3811 | 5.7181 | 11.15% | 11.87% | 8.02% | 1.1255 | 1.1347 | 1.0872
2010-05-12 | 40 | 37.0404 | 12.741 | 49.7814 | 4.3109 | 0.76558 | 0.37008 | 5.4466 | 10.94% | 11.64% | 7.867% | 1.1229 | 1.1317 | 1.0854
2010-05-12 | 41 | 37.1125 | 12.0565 | 49.169 | 4.2055 | 0.76558 | 0.36553 | 5.3366 | 10.85% | 11.55% | 7.804% | 1.1218 | 1.1306 | 1.0846
2010-05-12 | 42 | 36.6246 | 11.708 | 48.3326 | 4.0636 | 0.76558 | 0.35931 | 5.1885 | 10.74% | 11.42% | 7.718% | 1.1203 | 1.1289 | 1.0836
2010-05-12 | 43 | 34.5705 | 11.1367 | 45.7072 | 3.6342 | 0.76558 | 0.33979 | 4.7395 | 10.37% | 11.03% | 7.456% | 1.1157 | 1.124 | 1.0806
2010-05-12 | 44 | 32.8745 | 10.337 | 43.2115 | 3.2481 | 0.76558 | 0.32124 | 4.3349 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-05-12 | 45 | 29.6565 | 9.3853 | 39.0418 | 2.6515 | 0.76558 | 0.29024 | 3.7073 | 9.496% | 10.1% | 6.827% | 1.1049 | 1.1124 | 1.0733
2010-05-12 | 46 | 26.8266 | 8.312 | 35.1385 | 2.1478 | 0.76558 | 0.26122 | 3.1746 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-05-12 | 47 | 26.3244 | 8.6921 | 35.0165 | 2.1329 | 0.76558 | 0.26032 | 3.1588 | 9.021% | 9.598% | 6.486% | 1.0992 | 1.1062 | 1.0694
2010-05-12 | 48 | 25.2046 | 8.9816 | 34.1861 | 2.033 | 0.76558 | 0.25414 | 3.0527 | 8.93% | 9.501% | 6.42% | 1.0981 | 1.105 | 1.0686
2010-05-13 | 1 | 23.4806 | 7.9126 | 31.3932 | 1.7144 | 0.76558 | 0.23338 | 2.7133 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-05-13 | 2 | 23.9406 | 7.492 | 31.4326 | 1.7187 | 0.76558 | 0.23367 | 2.7179 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2010-05-13 | 3 | 22.9786 | 7.1348 | 30.1133 | 1.5774 | 0.76558 | 0.22387 | 2.5669 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-05-13 | 4 | 22.1726 | 6.7867 | 28.9593 | 1.4588 | 0.76558 | 0.21529 | 2.4397 | 8.425% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-05-13 | 5 | 21.4405 | 6.6403 | 28.0808 | 1.3717 | 0.76558 | 0.20876 | 2.346 | 8.355% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-05-13 | 6 | 21.0665 | 6.5158 | 27.5822 | 1.3234 | 0.76558 | 0.20505 | 2.294 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-05-13 | 7 | 21.0105 | 6.4973 | 27.5078 | 1.3163 | 0.76558 | 0.2045 | 2.2863 | 8.312% | 8.844% | 5.976% | 1.0907 | 1.097 | 1.0636
2010-05-13 | 8 | 20.5785 | 6.3793 | 26.9578 | 1.2642 | 0.76558 | 0.20041 | 2.2302 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-05-13 | 9 | 20.4484 | 6.3096 | 26.758 | 1.2455 | 0.76558 | 0.19892 | 2.21 | 8.259% | 8.788% | 5.938% | 1.09 | 1.0963 | 1.0631
2010-05-13 | 10 | 20.7224 | 6.414 | 27.1365 | 1.281 | 0.76558 | 0.20174 | 2.2483 | 8.285% | 8.815% | 5.957% | 1.0903 | 1.0967 | 1.0633
2010-05-13 | 11 | 20.9524 | 6.6945 | 27.647 | 1.3296 | 0.76558 | 0.20553 | 2.3007 | 8.322% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-05-13 | 12 | 21.3684 | 6.9222 | 28.2906 | 1.3923 | 0.76558 | 0.21032 | 2.3682 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-05-13 | 13 | 23.4944 | 7.971 | 31.4653 | 1.7223 | 0.76558 | 0.23392 | 2.7218 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-05-13 | 14 | 26.5103 | 9.5871 | 36.0974 | 2.2667 | 0.76558 | 0.26835 | 3.3006 | 9.144% | 9.729% | 6.574% | 1.1006 | 1.1078 | 1.0704
2010-05-13 | 15 | 30.2883 | 11.6446 | 41.9329 | 3.0587 | 0.76558 | 0.31173 | 4.1361 | 9.864% | 10.49% | 7.092% | 1.1094 | 1.1173 | 1.0763
2010-05-13 | 16 | 32.6102 | 12.6782 | 45.2884 | 3.5679 | 0.76558 | 0.33668 | 4.6701 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-05-13 | 17 | 33.5862 | 13.6085 | 47.1947 | 3.8746 | 0.76558 | 0.35085 | 4.991 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-05-13 | 18 | 34.4322 | 13.6633 | 48.0956 | 4.0239 | 0.76558 | 0.35755 | 5.147 | 10.7% | 11.39% | 7.694% | 1.1198 | 1.1285 | 1.0834
2010-05-13 | 19 | 34.2883 | 13.3322 | 47.6205 | 3.9448 | 0.76558 | 0.35402 | 5.0644 | 10.63% | 11.32% | 7.646% | 1.119 | 1.1276 | 1.0828
2010-05-13 | 20 | 33.7582 | 13.056 | 46.8142 | 3.8123 | 0.76558 | 0.34802 | 4.9259 | 10.52% | 11.2% | 7.566% | 1.1176 | 1.1261 | 1.0818
2010-05-13 | 21 | 34.4462 | 12.663 | 47.1092 | 3.8605 | 0.76558 | 0.35022 | 4.9763 | 10.56% | 11.24% | 7.595% | 1.1181 | 1.1266 | 1.0822
2010-05-13 | 22 | 33.8443 | 12.5454 | 46.3897 | 3.7435 | 0.76558 | 0.34487 | 4.8539 | 10.46% | 11.13% | 7.523% | 1.1169 | 1.1253 | 1.0814
2010-05-13 | 23 | 32.2923 | 12.2908 | 44.5831 | 3.4576 | 0.76558 | 0.33144 | 4.5546 | 10.22% | 10.87% | 7.345% | 1.1138 | 1.122 | 1.0793
2010-05-13 | 24 | 30.9723 | 12.0727 | 43.045 | 3.2231 | 0.76558 | 0.32 | 4.3087 | 10.01% | 10.65% | 7.197% | 1.1112 | 1.1192 | 1.0776
2010-05-13 | 25 | 29.4782 | 11.5213 | 40.9995 | 2.9241 | 0.76558 | 0.3048 | 3.9945 | 9.743% | 10.37% | 7.005% | 1.1079 | 1.1157 | 1.0753
2010-05-13 | 26 | 28.0042 | 10.8242 | 38.8284 | 2.6226 | 0.76558 | 0.28865 | 3.6768 | 9.469% | 10.08% | 6.809% | 1.1046 | 1.112 | 1.0731
2010-05-13 | 27 | 28.1802 | 11.0564 | 39.2366 | 2.678 | 0.76558 | 0.29169 | 3.7353 | 9.52% | 10.13% | 6.845% | 1.1052 | 1.1127 | 1.0735
2010-05-13 | 28 | 27.8663 | 11.1826 | 39.0489 | 2.6525 | 0.76558 | 0.29029 | 3.7083 | 9.497% | 10.1% | 6.828% | 1.1049 | 1.1124 | 1.0733
2010-05-13 | 29 | 27.2344 | 10.649 | 37.8834 | 2.4965 | 0.76558 | 0.28163 | 3.5437 | 9.354% | 9.953% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-05-13 | 30 | 26.9183 | 10.1931 | 37.1115 | 2.3958 | 0.76558 | 0.27589 | 3.4373 | 9.262% | 9.855% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-05-13 | 31 | 28.0943 | 10.1893 | 38.2835 | 2.5495 | 0.76558 | 0.2846 | 3.5997 | 9.403% | 10% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-05-13 | 32 | 28.0044 | 10.1532 | 38.1575 | 2.5328 | 0.76558 | 0.28367 | 3.582 | 9.387% | 9.988% | 6.75% | 1.1036 | 1.111 | 1.0724
2010-05-13 | 33 | 27.8766 | 10.3003 | 38.1769 | 2.5353 | 0.76558 | 0.28381 | 3.5847 | 9.39% | 9.991% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-05-13 | 34 | 28.8246 | 10.4583 | 39.2829 | 2.6844 | 0.76558 | 0.29203 | 3.742 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-05-13 | 35 | 29.9867 | 11.472 | 41.4587 | 2.99 | 0.76558 | 0.30821 | 4.0638 | 9.802% | 10.43% | 7.048% | 1.1087 | 1.1164 | 1.0758
2010-05-13 | 36 | 32.4006 | 13.2181 | 45.6188 | 3.6201 | 0.76558 | 0.33914 | 4.7248 | 10.36% | 11.02% | 7.447% | 1.1155 | 1.1238 | 1.0805
2010-05-13 | 37 | 33.9226 | 13.4853 | 47.4079 | 3.9096 | 0.76558 | 0.35244 | 5.0276 | 10.61% | 11.28% | 7.625% | 1.1186 | 1.1272 | 1.0825
2010-05-13 | 38 | 34.0248 | 13.0582 | 47.083 | 3.8562 | 0.76558 | 0.35002 | 4.9718 | 10.56% | 11.24% | 7.592% | 1.1181 | 1.1266 | 1.0822
2010-05-13 | 39 | 33.4788 | 12.4757 | 45.9545 | 3.6736 | 0.76558 | 0.34163 | 4.7808 | 10.4% | 11.07% | 7.48% | 1.1161 | 1.1245 | 1.0808
2010-05-13 | 40 | 32.8747 | 11.8835 | 44.7582 | 3.4848 | 0.76558 | 0.33274 | 4.5831 | 10.24% | 10.9% | 7.362% | 1.1141 | 1.1223 | 1.0795
2010-05-13 | 41 | 32.8607 | 11.6838 | 44.5445 | 3.4516 | 0.76558 | 0.33115 | 4.5483 | 10.21% | 10.86% | 7.342% | 1.1137 | 1.1219 | 1.0792
2010-05-13 | 42 | 32.1126 | 11.2188 | 43.3315 | 3.2662 | 0.76558 | 0.32213 | 4.3539 | 10.05% | 10.69% | 7.224% | 1.1117 | 1.1197 | 1.0779
2010-05-13 | 43 | 30.3187 | 10.5446 | 40.8634 | 2.9047 | 0.76558 | 0.30378 | 3.9741 | 9.725% | 10.35% | 6.992% | 1.1077 | 1.1154 | 1.0752
2010-05-13 | 44 | 29.2268 | 9.9553 | 39.1821 | 2.6706 | 0.76558 | 0.29128 | 3.7275 | 9.513% | 10.12% | 6.84% | 1.1051 | 1.1126 | 1.0734
2010-05-13 | 45 | 26.4247 | 9.0006 | 35.4253 | 2.183 | 0.76558 | 0.26336 | 3.212 | 9.067% | 9.647% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-05-13 | 46 | 23.8247 | 8.0293 | 31.854 | 1.7651 | 0.76558 | 0.23681 | 2.7675 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-05-13 | 47 | 23.3947 | 8.2195 | 31.6142 | 1.7386 | 0.76558 | 0.23502 | 2.7392 | 8.664% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-05-13 | 48 | 22.6627 | 8.5874 | 31.2501 | 1.6988 | 0.76558 | 0.23232 | 2.6967 | 8.629% | 9.182% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-05-14 | 1 | 21.4686 | 7.8139 | 29.2825 | 1.4916 | 0.76558 | 0.21769 | 2.4749 | 8.452% | 8.993% | 6.077% | 1.0923 | 1.0988 | 1.0647
2010-05-14 | 2 | 22.3026 | 7.5085 | 29.811 | 1.5459 | 0.76558 | 0.22162 | 2.5331 | 8.497% | 9.041% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-05-14 | 3 | 21.0526 | 6.966 | 28.0185 | 1.3656 | 0.76558 | 0.20829 | 2.3395 | 8.35% | 8.884% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-05-14 | 4 | 19.9606 | 6.6097 | 26.5703 | 1.2281 | 0.76558 | 0.19753 | 2.1912 | 8.247% | 8.775% | 5.929% | 1.0899 | 1.0962 | 1.063
2010-05-14 | 5 | 19.2566 | 6.5199 | 25.7765 | 1.1558 | 0.76558 | 0.19163 | 2.113 | 8.197% | 8.722% | 5.894% | 1.0893 | 1.0956 | 1.0626
2010-05-14 | 6 | 19.1146 | 6.3946 | 25.5092 | 1.1319 | 0.76558 | 0.18964 | 2.0872 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-05-14 | 7 | 19.0706 | 6.3761 | 25.4467 | 1.1264 | 0.76558 | 0.18917 | 2.0812 | 8.179% | 8.702% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-05-14 | 8 | 18.8986 | 6.3234 | 25.222 | 1.1066 | 0.76558 | 0.1875 | 2.0597 | 8.166% | 8.689% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-05-14 | 9 | 18.9125 | 6.5072 | 25.4196 | 1.124 | 0.76558 | 0.18897 | 2.0786 | 8.177% | 8.7% | 5.879% | 1.0891 | 1.0953 | 1.0625
2010-05-14 | 10 | 19.0565 | 6.4491 | 25.5056 | 1.1316 | 0.76558 | 0.18961 | 2.0868 | 8.182% | 8.705% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-05-14 | 11 | 20.0325 | 6.6583 | 26.6908 | 1.2392 | 0.76558 | 0.19842 | 2.2032 | 8.255% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-05-14 | 12 | 20.8225 | 7.0073 | 27.8298 | 1.3473 | 0.76558 | 0.20689 | 2.3197 | 8.335% | 8.869% | 5.993% | 1.0909 | 1.0973 | 1.0638
2010-05-14 | 13 | 22.5745 | 7.8595 | 30.434 | 1.6112 | 0.76558 | 0.22625 | 2.603 | 8.553% | 9.1% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-05-14 | 14 | 25.4344 | 9.3694 | 34.8037 | 2.1071 | 0.76558 | 0.25874 | 3.1314 | 8.997% | 9.573% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-05-14 | 15 | 29.4124 | 11.4979 | 40.9103 | 2.9114 | 0.76558 | 0.30413 | 3.9811 | 9.731% | 10.35% | 6.997% | 1.1078 | 1.1155 | 1.0752
2010-05-14 | 16 | 31.5105 | 12.6788 | 44.1893 | 3.3968 | 0.76558 | 0.32851 | 4.4909 | 10.16% | 10.81% | 7.307% | 1.1131 | 1.1212 | 1.0788
2010-05-14 | 17 | 32.8303 | 13.2733 | 46.1036 | 3.6975 | 0.76558 | 0.34274 | 4.8058 | 10.42% | 11.09% | 7.495% | 1.1164 | 1.1247 | 1.081
2010-05-14 | 18 | 32.9183 | 12.8687 | 45.787 | 3.6469 | 0.76558 | 0.34039 | 4.7528 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0807
2010-05-14 | 19 | 32.6022 | 12.2032 | 44.8054 | 3.4922 | 0.76558 | 0.33309 | 4.5908 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-05-14 | 20 | 31.9122 | 11.4635 | 43.3757 | 3.2729 | 0.76558 | 0.32246 | 4.3609 | 10.05% | 10.7% | 7.229% | 1.1118 | 1.1198 | 1.0779
2010-05-14 | 21 | 32.0841 | 11.265 | 43.3492 | 3.2689 | 0.76558 | 0.32226 | 4.3567 | 10.05% | 10.69% | 7.226% | 1.1117 | 1.1197 | 1.0779
2010-05-14 | 22 | 31.1941 | 10.8554 | 42.0495 | 3.0758 | 0.76558 | 0.3126 | 4.154 | 9.879% | 10.51% | 7.103% | 1.1096 | 1.1175 | 1.0765
2010-05-14 | 23 | 29.0819 | 10.582 | 39.6639 | 2.7367 | 0.76558 | 0.29487 | 3.7971 | 9.573% | 10.19% | 6.883% | 1.1059 | 1.1134 | 1.0739
2010-05-14 | 24 | 27.8893 | 10.3808 | 38.2701 | 2.5477 | 0.76558 | 0.2845 | 3.5978 | 9.401% | 10% | 6.759% | 1.1038 | 1.1111 | 1.0725
2010-05-14 | 25 | 26.5254 | 10.1071 | 36.6324 | 2.3343 | 0.76558 | 0.27233 | 3.3723 | 9.206% | 9.795% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-05-14 | 26 | 25.0154 | 9.7233 | 34.7387 | 2.0992 | 0.76558 | 0.25825 | 3.1231 | 8.99% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-05-14 | 27 | 25.6196 | 10.0886 | 35.7082 | 2.218 | 0.76558 | 0.26546 | 3.2491 | 9.099% | 9.681% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-05-14 | 28 | 25.6774 | 9.876 | 35.5534 | 2.1989 | 0.76558 | 0.26431 | 3.2287 | 9.081% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-05-14 | 29 | 25.0875 | 9.3513 | 34.4388 | 2.0631 | 0.76558 | 0.25602 | 3.0847 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2010-05-14 | 30 | 24.9294 | 9.051 | 33.9805 | 2.0086 | 0.76558 | 0.25261 | 3.0268 | 8.907% | 9.478% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-05-14 | 31 | 26.5535 | 9.0969 | 35.6504 | 2.2109 | 0.76558 | 0.26503 | 3.2415 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-05-14 | 32 | 26.8414 | 8.9894 | 35.8308 | 2.2333 | 0.76558 | 0.26637 | 3.2652 | 9.113% | 9.696% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-05-14 | 33 | 27.1576 | 9.2861 | 36.4437 | 2.3104 | 0.76558 | 0.27093 | 3.3469 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-05-14 | 34 | 28.4917 | 9.686 | 38.1777 | 2.5354 | 0.76558 | 0.28382 | 3.5848 | 9.39% | 9.991% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-05-14 | 35 | 29.8137 | 10.723 | 40.5367 | 2.8585 | 0.76558 | 0.30135 | 3.9254 | 9.684% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-05-14 | 36 | 32.1557 | 12.3444 | 44.5001 | 3.4447 | 0.76558 | 0.33082 | 4.5411 | 10.2% | 10.86% | 7.337% | 1.1136 | 1.1218 | 1.0792
2010-05-14 | 37 | 33.6498 | 12.7519 | 46.4017 | 3.7454 | 0.76558 | 0.34496 | 4.856 | 10.47% | 11.13% | 7.524% | 1.1169 | 1.1253 | 1.0814
2010-05-14 | 38 | 33.9939 | 12.5798 | 46.5737 | 3.7733 | 0.76558 | 0.34623 | 4.8851 | 10.49% | 11.16% | 7.542% | 1.1172 | 1.1256 | 1.0816
2010-05-14 | 39 | 33.204 | 12.0856 | 45.2896 | 3.568 | 0.76558 | 0.33669 | 4.6703 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-05-14 | 40 | 32.63 | 11.5721 | 44.2021 | 3.3988 | 0.76558 | 0.3286 | 4.4929 | 10.16% | 10.82% | 7.308% | 1.1131 | 1.1213 | 1.0788
2010-05-14 | 41 | 32.386 | 11.0921 | 43.4781 | 3.2883 | 0.76558 | 0.32322 | 4.3771 | 10.07% | 10.71% | 7.238% | 1.1119 | 1.12 | 1.078
2010-05-14 | 42 | 31.6101 | 10.834 | 42.4441 | 3.1338 | 0.76558 | 0.31553 | 4.2149 | 9.93% | 10.57% | 7.14% | 1.1103 | 1.1181 | 1.0769
2010-05-14 | 43 | 29.6419 | 10.1802 | 39.8221 | 2.7586 | 0.76558 | 0.29604 | 3.8202 | 9.593% | 10.21% | 6.897% | 1.1061 | 1.1137 | 1.0741
2010-05-14 | 44 | 28.2905 | 9.5408 | 37.8313 | 2.4896 | 0.76558 | 0.28124 | 3.5365 | 9.348% | 9.946% | 6.721% | 1.1031 | 1.1104 | 1.0721
2010-05-14 | 45 | 25.7327 | 8.8315 | 34.5642 | 2.0782 | 0.76558 | 0.25695 | 3.1007 | 8.971% | 9.545% | 6.45% | 1.0986 | 1.1055 | 1.0689
2010-05-14 | 46 | 23.4926 | 7.7657 | 31.2583 | 1.6997 | 0.76558 | 0.23238 | 2.6976 | 8.63% | 9.182% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-05-14 | 47 | 22.9465 | 7.786 | 30.7325 | 1.643 | 0.76558 | 0.22847 | 2.637 | 8.581% | 9.13% | 6.169% | 1.0939 | 1.1005 | 1.0658
2010-05-14 | 48 | 22.1426 | 8.222 | 30.3646 | 1.6039 | 0.76558 | 0.22573 | 2.5952 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-05-15 | 1 | 20.7787 | 7.2971 | 28.0758 | 1.3712 | 0.76558 | 0.20872 | 2.3455 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-05-15 | 2 | 21.2528 | 7.0456 | 28.2984 | 1.393 | 0.76558 | 0.21037 | 2.369 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-05-15 | 3 | 20.1311 | 6.6483 | 26.7794 | 1.2475 | 0.76558 | 0.19908 | 2.2121 | 8.261% | 8.789% | 5.939% | 1.09 | 1.0964 | 1.0631
2010-05-15 | 4 | 19.4132 | 6.4008 | 25.8141 | 1.1592 | 0.76558 | 0.1919 | 2.1167 | 8.2% | 8.724% | 5.896% | 1.0893 | 1.0956 | 1.0626
2010-05-15 | 5 | 18.7676 | 6.1872 | 24.9548 | 1.0833 | 0.76558 | 0.18552 | 2.0344 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2010-05-15 | 6 | 18.3658 | 5.981 | 24.3467 | 1.0311 | 0.76558 | 0.181 | 1.9777 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-05-15 | 7 | 18.3378 | 5.9161 | 24.2539 | 1.0233 | 0.76558 | 0.18031 | 1.9692 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-05-15 | 8 | 18.1799 | 5.8607 | 24.0406 | 1.0054 | 0.76558 | 0.17872 | 1.9497 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-05-15 | 9 | 18.0942 | 5.889 | 23.9832 | 1.0006 | 0.76558 | 0.17829 | 1.9444 | 8.108% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-05-15 | 10 | 18.366 | 5.9306 | 24.2966 | 1.0269 | 0.76558 | 0.18062 | 1.9731 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-05-15 | 11 | 18.8401 | 6.2527 | 25.0928 | 1.0953 | 0.76558 | 0.18654 | 2.0474 | 8.159% | 8.682% | 5.867% | 1.0888 | 1.0951 | 1.0623
2010-05-15 | 12 | 19.4859 | 6.5185 | 26.0043 | 1.1763 | 0.76558 | 0.19332 | 2.1352 | 8.211% | 8.737% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-05-15 | 13 | 21.3098 | 7.2947 | 28.6045 | 1.4233 | 0.76558 | 0.21265 | 2.4016 | 8.396% | 8.933% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-05-15 | 14 | 24.2559 | 8.7948 | 33.0508 | 1.9002 | 0.76558 | 0.2457 | 2.9115 | 8.809% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-05-15 | 15 | 28.018 | 10.7367 | 38.7547 | 2.6127 | 0.76558 | 0.28811 | 3.6663 | 9.46% | 10.07% | 6.802% | 1.1045 | 1.1119 | 1.073
2010-05-15 | 16 | 30.6042 | 12.0373 | 42.6415 | 3.163 | 0.76558 | 0.317 | 4.2456 | 9.956% | 10.59% | 7.159% | 1.1106 | 1.1185 | 1.0771
2010-05-15 | 17 | 32.1703 | 12.8892 | 45.0595 | 3.5319 | 0.76558 | 0.33498 | 4.6324 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-05-15 | 18 | 32.8161 | 12.9148 | 45.7309 | 3.6379 | 0.76558 | 0.33997 | 4.7435 | 10.37% | 11.04% | 7.458% | 1.1157 | 1.1241 | 1.0806
2010-05-15 | 19 | 32.4142 | 12.7494 | 45.1636 | 3.5482 | 0.76558 | 0.33575 | 4.6496 | 10.29% | 10.95% | 7.402% | 1.1148 | 1.123 | 1.0799
2010-05-15 | 20 | 31.8822 | 11.8003 | 43.6825 | 3.3193 | 0.76558 | 0.32474 | 4.4096 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-05-15 | 21 | 32.3002 | 11.1801 | 43.4803 | 3.2887 | 0.76558 | 0.32324 | 4.3775 | 10.07% | 10.71% | 7.239% | 1.1119 | 1.12 | 1.078
2010-05-15 | 22 | 31.4961 | 10.7974 | 42.2935 | 3.1116 | 0.76558 | 0.31442 | 4.1916 | 9.911% | 10.54% | 7.126% | 1.11 | 1.1179 | 1.0767
2010-05-15 | 23 | 29.3543 | 10.4168 | 39.7711 | 2.7515 | 0.76558 | 0.29566 | 3.8127 | 9.587% | 10.2% | 6.893% | 1.106 | 1.1136 | 1.074
2010-05-15 | 24 | 27.8603 | 10.4133 | 38.2736 | 2.5482 | 0.76558 | 0.28453 | 3.5983 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-05-15 | 25 | 26.2963 | 9.9962 | 36.2926 | 2.2912 | 0.76558 | 0.2698 | 3.3266 | 9.166% | 9.753% | 6.59% | 1.1009 | 1.1081 | 1.0706
2010-05-15 | 26 | 25.5484 | 9.2913 | 34.8397 | 2.1115 | 0.76558 | 0.259 | 3.136 | 9.001% | 9.577% | 6.472% | 1.0989 | 1.1059 | 1.0692
2010-05-15 | 27 | 26.1526 | 9.3265 | 35.4791 | 2.1897 | 0.76558 | 0.26376 | 3.219 | 9.073% | 9.654% | 6.523% | 1.0998 | 1.1069 | 1.0698
2010-05-15 | 28 | 26.5404 | 9.3844 | 35.9248 | 2.245 | 0.76558 | 0.26707 | 3.2777 | 9.124% | 9.708% | 6.56% | 1.1004 | 1.1075 | 1.0702
2010-05-15 | 29 | 26.2105 | 8.9616 | 35.1721 | 2.1519 | 0.76558 | 0.26147 | 3.179 | 9.038% | 9.617% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-05-15 | 30 | 25.9505 | 8.6383 | 34.5888 | 2.0812 | 0.76558 | 0.25714 | 3.1039 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-05-15 | 31 | 26.4244 | 8.5967 | 35.0211 | 2.1335 | 0.76558 | 0.26035 | 3.1594 | 9.022% | 9.599% | 6.486% | 1.0992 | 1.1062 | 1.0694
2010-05-15 | 32 | 26.9287 | 8.6284 | 35.5571 | 2.1993 | 0.76558 | 0.26434 | 3.2292 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-05-15 | 33 | 27.0705 | 8.9971 | 36.0676 | 2.2629 | 0.76558 | 0.26813 | 3.2966 | 9.14% | 9.725% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-05-15 | 34 | 27.8185 | 9.1611 | 36.9796 | 2.3788 | 0.76558 | 0.27491 | 3.4193 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-05-15 | 35 | 28.6365 | 10.0163 | 38.6529 | 2.599 | 0.76558 | 0.28735 | 3.6519 | 9.448% | 10.05% | 6.793% | 1.1043 | 1.1118 | 1.0729
2010-05-15 | 36 | 31.2365 | 11.6896 | 42.9261 | 3.2054 | 0.76558 | 0.31912 | 4.2901 | 9.994% | 10.63% | 7.186% | 1.111 | 1.119 | 1.0774
2010-05-15 | 37 | 33.0904 | 11.9949 | 45.0853 | 3.5359 | 0.76558 | 0.33517 | 4.6367 | 10.28% | 10.94% | 7.394% | 1.1146 | 1.1229 | 1.0798
2010-05-15 | 38 | 33.3624 | 11.8805 | 45.2428 | 3.5607 | 0.76558 | 0.33634 | 4.6626 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-05-15 | 39 | 32.8601 | 11.4423 | 44.3024 | 3.4142 | 0.76558 | 0.32935 | 4.5091 | 10.18% | 10.83% | 7.318% | 1.1133 | 1.1214 | 1.079
2010-05-15 | 40 | 32.1283 | 10.8876 | 43.0158 | 3.2188 | 0.76558 | 0.31979 | 4.3041 | 10.01% | 10.65% | 7.194% | 1.1112 | 1.1191 | 1.0775
2010-05-15 | 41 | 32.1843 | 10.6318 | 42.8161 | 3.189 | 0.76558 | 0.3183 | 4.2728 | 9.98% | 10.62% | 7.175% | 1.1109 | 1.1188 | 1.0773
2010-05-15 | 42 | 31.6382 | 10.227 | 41.8652 | 3.0489 | 0.76558 | 0.31123 | 4.1257 | 9.855% | 10.49% | 7.086% | 1.1093 | 1.1171 | 1.0763
2010-05-15 | 43 | 30.3024 | 9.6053 | 39.9077 | 2.7704 | 0.76558 | 0.29668 | 3.8327 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-05-15 | 44 | 28.9664 | 9.1892 | 38.1556 | 2.5325 | 0.76558 | 0.28365 | 3.5817 | 9.387% | 9.988% | 6.749% | 1.1036 | 1.111 | 1.0724
2010-05-15 | 45 | 26.3964 | 8.4601 | 34.8565 | 2.1135 | 0.76558 | 0.25913 | 3.1382 | 9.003% | 9.579% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-05-15 | 46 | 24.4004 | 7.638 | 32.0384 | 1.7856 | 0.76558 | 0.23818 | 2.7893 | 8.706% | 9.263% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-05-15 | 47 | 24.0984 | 7.893 | 31.9914 | 1.7803 | 0.76558 | 0.23783 | 2.7837 | 8.702% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-05-15 | 48 | 23.3944 | 8.2759 | 31.6704 | 1.7448 | 0.76558 | 0.23544 | 2.7458 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-05-16 | 1 | 21.7565 | 7.322 | 29.0785 | 1.4709 | 0.76558 | 0.21617 | 2.4526 | 8.435% | 8.974% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-05-16 | 2 | 22.1167 | 7.0428 | 29.1595 | 1.4791 | 0.76558 | 0.21677 | 2.4614 | 8.441% | 8.982% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-05-16 | 3 | 20.8232 | 6.6828 | 27.506 | 1.3161 | 0.76558 | 0.20448 | 2.2862 | 8.312% | 8.843% | 5.976% | 1.0906 | 1.097 | 1.0636
2010-05-16 | 4 | 19.9918 | 6.2155 | 26.2073 | 1.1948 | 0.76558 | 0.19483 | 2.1552 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-05-16 | 5 | 19.0766 | 6.1093 | 25.1859 | 1.1034 | 0.76558 | 0.18724 | 2.0563 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-05-16 | 6 | 18.874 | 5.9894 | 24.8634 | 1.0754 | 0.76558 | 0.18484 | 2.0258 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-05-16 | 7 | 18.588 | 5.9305 | 24.5185 | 1.0457 | 0.76558 | 0.18227 | 1.9936 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-05-16 | 8 | 18.114 | 5.8513 | 23.9653 | 0.99908 | 0.76558 | 0.17816 | 1.9428 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-05-16 | 9 | 18.186 | 5.8837 | 24.0697 | 1.0078 | 0.76558 | 0.17894 | 1.9523 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-05-16 | 10 | 18.602 | 5.8752 | 24.4772 | 1.0422 | 0.76558 | 0.18197 | 1.9898 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-05-16 | 11 | 18.788 | 5.9285 | 24.7165 | 1.0627 | 0.76558 | 0.18375 | 2.012 | 8.14% | 8.661% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-05-16 | 12 | 18.976 | 5.9855 | 24.9615 | 1.0839 | 0.76558 | 0.18557 | 2.035 | 8.153% | 8.674% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-05-16 | 13 | 19.952 | 6.3322 | 26.2842 | 1.2018 | 0.76558 | 0.1954 | 2.1628 | 8.228% | 8.755% | 5.916% | 1.0897 | 1.096 | 1.0629
2010-05-16 | 14 | 21.418 | 6.8244 | 28.2424 | 1.3875 | 0.76558 | 0.20996 | 2.3631 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-05-16 | 15 | 22.366 | 7.4328 | 29.7988 | 1.5447 | 0.76558 | 0.22153 | 2.5318 | 8.496% | 9.04% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-05-16 | 16 | 22.524 | 8.2364 | 30.7604 | 1.646 | 0.76558 | 0.22868 | 2.6402 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-05-16 | 17 | 24.2921 | 9.3337 | 33.6258 | 1.9669 | 0.76558 | 0.24998 | 2.9824 | 8.87% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-05-16 | 18 | 26.358 | 10.0603 | 36.4183 | 2.3071 | 0.76558 | 0.27074 | 3.3435 | 9.181% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-05-16 | 19 | 28.758 | 10.5698 | 39.3278 | 2.6905 | 0.76558 | 0.29237 | 3.7485 | 9.531% | 10.14% | 6.853% | 1.1054 | 1.1129 | 1.0736
2010-05-16 | 20 | 29.892 | 10.7031 | 40.5951 | 2.8667 | 0.76558 | 0.30179 | 3.9341 | 9.691% | 10.31% | 6.968% | 1.1073 | 1.115 | 1.0749
2010-05-16 | 21 | 32.234 | 11.1053 | 43.3393 | 3.2674 | 0.76558 | 0.32219 | 4.3551 | 10.05% | 10.69% | 7.225% | 1.1117 | 1.1197 | 1.0779
2010-05-16 | 22 | 32.176 | 10.9278 | 43.1038 | 3.232 | 0.76558 | 0.32044 | 4.318 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-05-16 | 23 | 31.458 | 10.4421 | 41.9001 | 3.054 | 0.76558 | 0.31149 | 4.131 | 9.859% | 10.49% | 7.089% | 1.1094 | 1.1172 | 1.0763
2010-05-16 | 24 | 30.884 | 9.9306 | 40.8146 | 2.8978 | 0.76558 | 0.30342 | 3.9668 | 9.719% | 10.34% | 6.988% | 1.1077 | 1.1153 | 1.0751
2010-05-16 | 25 | 29.92 | 9.4679 | 39.3879 | 2.6987 | 0.76558 | 0.29281 | 3.7571 | 9.539% | 10.15% | 6.858% | 1.1054 | 1.113 | 1.0736
2010-05-16 | 26 | 29.174 | 9.114 | 38.288 | 2.5501 | 0.76558 | 0.28464 | 3.6003 | 9.403% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-05-16 | 27 | 29.532 | 9.6127 | 39.1447 | 2.6655 | 0.76558 | 0.29101 | 3.7221 | 9.509% | 10.12% | 6.837% | 1.1051 | 1.1126 | 1.0734
2010-05-16 | 28 | 30.078 | 9.7732 | 39.8512 | 2.7626 | 0.76558 | 0.29626 | 3.8244 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-05-16 | 29 | 29.95 | 9.4132 | 39.3632 | 2.6953 | 0.76558 | 0.29263 | 3.7536 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-05-16 | 30 | 29.82 | 9.2427 | 39.0627 | 2.6544 | 0.76558 | 0.2904 | 3.7103 | 9.498% | 10.11% | 6.829% | 1.105 | 1.1124 | 1.0733
2010-05-16 | 31 | 30.998 | 9.2905 | 40.2885 | 2.8236 | 0.76558 | 0.29951 | 3.8887 | 9.652% | 10.27% | 6.94% | 1.1068 | 1.1145 | 1.0746
2010-05-16 | 32 | 30.984 | 9.3332 | 40.3172 | 2.8276 | 0.76558 | 0.29972 | 3.8929 | 9.656% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-05-16 | 33 | 30.898 | 9.4908 | 40.3888 | 2.8376 | 0.76558 | 0.30026 | 3.9035 | 9.665% | 10.28% | 6.949% | 1.107 | 1.1146 | 1.0747
2010-05-16 | 34 | 31.372 | 9.6888 | 41.0608 | 2.9328 | 0.76558 | 0.30525 | 4.0037 | 9.751% | 10.37% | 7.011% | 1.108 | 1.1158 | 1.0754
2010-05-16 | 35 | 32.046 | 10.6441 | 42.6901 | 3.1702 | 0.76558 | 0.31736 | 4.2532 | 9.963% | 10.6% | 7.163% | 1.1107 | 1.1186 | 1.0772
2010-05-16 | 36 | 33.304 | 11.7986 | 45.1026 | 3.5386 | 0.76558 | 0.3353 | 4.6395 | 10.29% | 10.94% | 7.396% | 1.1147 | 1.1229 | 1.0799
2010-05-16 | 37 | 33.204 | 11.9127 | 45.1167 | 3.5409 | 0.76558 | 0.3354 | 4.6419 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-05-16 | 38 | 33.31 | 11.3691 | 44.6791 | 3.4725 | 0.76558 | 0.33215 | 4.5702 | 10.23% | 10.88% | 7.355% | 1.1139 | 1.1221 | 1.0794
2010-05-16 | 39 | 32.176 | 10.8011 | 42.9771 | 3.213 | 0.76558 | 0.3195 | 4.2981 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-05-16 | 40 | 31.156 | 10.3343 | 41.4903 | 2.9945 | 0.76558 | 0.30844 | 4.0685 | 9.806% | 10.43% | 7.051% | 1.1087 | 1.1165 | 1.0759
2010-05-16 | 41 | 30.912 | 9.9037 | 40.8157 | 2.8979 | 0.76558 | 0.30343 | 3.967 | 9.719% | 10.34% | 6.988% | 1.1077 | 1.1153 | 1.0751
2010-05-16 | 42 | 30.208 | 9.5552 | 39.7632 | 2.7504 | 0.76558 | 0.2956 | 3.8116 | 9.586% | 10.2% | 6.892% | 1.106 | 1.1136 | 1.074
2010-05-16 | 43 | 28.836 | 9.182 | 38.018 | 2.5143 | 0.76558 | 0.28263 | 3.5625 | 9.371% | 9.97% | 6.737% | 1.1034 | 1.1107 | 1.0722
2010-05-16 | 44 | 27.508 | 8.8227 | 36.3307 | 2.296 | 0.76558 | 0.27009 | 3.3317 | 9.171% | 9.757% | 6.594% | 1.101 | 1.1081 | 1.0706
2010-05-16 | 45 | 25.36 | 8.2129 | 33.5729 | 1.9607 | 0.76558 | 0.24958 | 2.9759 | 8.864% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-05-16 | 46 | 23.414 | 7.6063 | 31.0203 | 1.6739 | 0.76558 | 0.23061 | 2.6701 | 8.608% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-05-16 | 47 | 23.73 | 7.8436 | 31.5736 | 1.7341 | 0.76558 | 0.23472 | 2.7344 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-05-16 | 48 | 22.904 | 8.2421 | 31.1461 | 1.6875 | 0.76558 | 0.23154 | 2.6846 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-05-17 | 1 | 21.446 | 7.4106 | 28.8566 | 1.4485 | 0.76558 | 0.21452 | 2.4286 | 8.416% | 8.955% | 6.051% | 1.0919 | 1.0984 | 1.0644
2010-05-17 | 2 | 22.1 | 6.9707 | 29.0707 | 1.4701 | 0.76558 | 0.21612 | 2.4518 | 8.434% | 8.974% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-05-17 | 3 | 20.692 | 6.461 | 27.153 | 1.2825 | 0.76558 | 0.20186 | 2.25 | 8.286% | 8.817% | 5.958% | 1.0903 | 1.0967 | 1.0634
2010-05-17 | 4 | 19.198 | 6.2559 | 25.4539 | 1.127 | 0.76558 | 0.18923 | 2.0819 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-05-17 | 5 | 18.63 | 6.0896 | 24.7196 | 1.063 | 0.76558 | 0.18377 | 2.0123 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-05-17 | 6 | 18.444 | 5.7742 | 24.2182 | 1.0203 | 0.76558 | 0.18004 | 1.9659 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-05-17 | 7 | 18.53 | 5.7467 | 24.2767 | 1.0252 | 0.76558 | 0.18048 | 1.9713 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-05-17 | 8 | 18.258 | 5.5896 | 23.8476 | 0.98929 | 0.76558 | 0.17729 | 1.9322 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-05-17 | 9 | 18.028 | 5.6534 | 23.6814 | 0.97555 | 0.76558 | 0.17605 | 1.9172 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-05-17 | 10 | 18.2 | 5.7015 | 23.9015 | 0.99377 | 0.76558 | 0.17769 | 1.937 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-05-17 | 11 | 18.802 | 5.8376 | 24.6396 | 1.0561 | 0.76558 | 0.18317 | 2.0048 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-05-17 | 12 | 18.976 | 5.8108 | 24.7868 | 1.0687 | 0.76558 | 0.18427 | 2.0186 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-05-17 | 13 | 19.852 | 5.863 | 25.715 | 1.1503 | 0.76558 | 0.19117 | 2.107 | 8.194% | 8.718% | 5.891% | 1.0893 | 1.0955 | 1.0626
2010-05-17 | 14 | 20.67 | 6.2359 | 26.9059 | 1.2593 | 0.76558 | 0.20002 | 2.2249 | 8.269% | 8.798% | 5.946% | 1.0901 | 1.0965 | 1.0632
2010-05-17 | 15 | 21.488 | 6.5407 | 28.0287 | 1.3666 | 0.76558 | 0.20837 | 2.3405 | 8.351% | 8.885% | 6.004% | 1.0911 | 1.0975 | 1.0639
2010-05-17 | 16 | 21.776 | 7.0319 | 28.8079 | 1.4436 | 0.76558 | 0.21416 | 2.4234 | 8.412% | 8.951% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-05-17 | 17 | 23.73 | 8.2099 | 31.9399 | 1.7746 | 0.76558 | 0.23745 | 2.7776 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-05-17 | 18 | 25.712 | 9.3407 | 35.0527 | 2.1374 | 0.76558 | 0.26059 | 3.1635 | 9.025% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-05-17 | 19 | 28.226 | 9.7813 | 38.0073 | 2.5129 | 0.76558 | 0.28255 | 3.561 | 9.369% | 9.969% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-05-17 | 20 | 30.122 | 10.1343 | 40.2563 | 2.819 | 0.76558 | 0.29927 | 3.8839 | 9.648% | 10.27% | 6.937% | 1.1068 | 1.1144 | 1.0745
2010-05-17 | 21 | 31.486 | 10.4314 | 41.9174 | 3.0565 | 0.76558 | 0.31162 | 4.1337 | 9.862% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-05-17 | 22 | 31.558 | 10.3677 | 41.9257 | 3.0577 | 0.76558 | 0.31168 | 4.135 | 9.863% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-05-17 | 23 | 31.056 | 9.9055 | 40.9615 | 2.9187 | 0.76558 | 0.30451 | 3.9888 | 9.738% | 10.36% | 7.002% | 1.1079 | 1.1156 | 1.0753
2010-05-17 | 24 | 30.51 | 9.6866 | 40.1966 | 2.8107 | 0.76558 | 0.29883 | 3.8751 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-05-17 | 25 | 29.562 | 9.3192 | 38.8812 | 2.6297 | 0.76558 | 0.28905 | 3.6844 | 9.476% | 10.08% | 6.813% | 1.1047 | 1.1121 | 1.0731
2010-05-17 | 26 | 28.484 | 8.6866 | 37.1706 | 2.4034 | 0.76558 | 0.27633 | 3.4454 | 9.269% | 9.862% | 6.664% | 1.1022 | 1.1094 | 1.0714
2010-05-17 | 27 | 28.858 | 8.7878 | 37.6458 | 2.4653 | 0.76558 | 0.27986 | 3.5107 | 9.326% | 9.923% | 6.705% | 1.1028 | 1.1102 | 1.0719
2010-05-17 | 28 | 28.6 | 8.8099 | 37.4099 | 2.4345 | 0.76558 | 0.27811 | 3.4782 | 9.297% | 9.893% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-05-17 | 29 | 27.192 | 8.3358 | 35.5278 | 2.1957 | 0.76558 | 0.26412 | 3.2254 | 9.078% | 9.66% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-05-17 | 30 | 26.402 | 7.8311 | 34.2331 | 2.0386 | 0.76558 | 0.25449 | 3.0586 | 8.935% | 9.507% | 6.424% | 1.0981 | 1.1051 | 1.0687
2010-05-17 | 31 | 27.494 | 7.8509 | 35.3449 | 2.1731 | 0.76558 | 0.26276 | 3.2015 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-05-17 | 32 | 27.55 | 7.7744 | 35.3244 | 2.1706 | 0.76558 | 0.26261 | 3.1988 | 9.056% | 9.635% | 6.511% | 1.0996 | 1.1066 | 1.0696
2010-05-17 | 33 | 27.536 | 8.125 | 35.661 | 2.2122 | 0.76558 | 0.26511 | 3.2429 | 9.094% | 9.676% | 6.538% | 1.1 | 1.1071 | 1.07
2010-05-17 | 34 | 27.896 | 8.6549 | 36.5509 | 2.324 | 0.76558 | 0.27172 | 3.3613 | 9.196% | 9.785% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-05-17 | 35 | 29.462 | 9.8834 | 39.3454 | 2.6929 | 0.76558 | 0.2925 | 3.751 | 9.533% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-05-17 | 36 | 32.55 | 11.6924 | 44.2424 | 3.405 | 0.76558 | 0.3289 | 4.4994 | 10.17% | 10.82% | 7.312% | 1.1132 | 1.1213 | 1.0789
2010-05-17 | 37 | 33.77 | 11.9939 | 45.7639 | 3.6432 | 0.76558 | 0.34021 | 4.749 | 10.38% | 11.04% | 7.461% | 1.1158 | 1.1241 | 1.0806
2010-05-17 | 38 | 33.856 | 11.6653 | 45.5213 | 3.6047 | 0.76558 | 0.33841 | 4.7086 | 10.34% | 11.01% | 7.437% | 1.1154 | 1.1237 | 1.0803
2010-05-17 | 39 | 33.11 | 11.31 | 44.42 | 3.4323 | 0.76558 | 0.33022 | 4.5281 | 10.19% | 10.85% | 7.329% | 1.1135 | 1.1217 | 1.0791
2010-05-17 | 40 | 32.306 | 10.775 | 43.081 | 3.2285 | 0.76558 | 0.32027 | 4.3144 | 10.01% | 10.66% | 7.2% | 1.1113 | 1.1193 | 1.0776
2010-05-17 | 41 | 32.506 | 10.4819 | 42.9879 | 3.2146 | 0.76558 | 0.31958 | 4.2998 | 10% | 10.64% | 7.192% | 1.1111 | 1.1191 | 1.0775
2010-05-17 | 42 | 31.904 | 10.1463 | 42.0503 | 3.0759 | 0.76558 | 0.31261 | 4.1541 | 9.879% | 10.51% | 7.103% | 1.1096 | 1.1175 | 1.0765
2010-05-17 | 43 | 30.108 | 9.515 | 39.623 | 2.731 | 0.76558 | 0.29456 | 3.7912 | 9.568% | 10.18% | 6.88% | 1.1058 | 1.1133 | 1.0739
2010-05-17 | 44 | 28.356 | 8.8651 | 37.2211 | 2.41 | 0.76558 | 0.27671 | 3.4523 | 9.275% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2010-05-17 | 45 | 25.654 | 7.9171 | 33.5711 | 1.9605 | 0.76558 | 0.24957 | 2.9757 | 8.864% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-05-17 | 46 | 23.544 | 7.0665 | 30.6105 | 1.63 | 0.76558 | 0.22756 | 2.6231 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-05-17 | 47 | 23.242 | 7.4188 | 30.6608 | 1.6353 | 0.76558 | 0.22794 | 2.6288 | 8.574% | 9.123% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-05-17 | 48 | 22.508 | 7.8951 | 30.4031 | 1.6079 | 0.76558 | 0.22602 | 2.5995 | 8.55% | 9.097% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-05-18 | 1 | 21.244 | 7.2969 | 28.5409 | 1.417 | 0.76558 | 0.21218 | 2.3948 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-05-18 | 2 | 21.934 | 7.0892 | 29.0232 | 1.4653 | 0.76558 | 0.21576 | 2.4466 | 8.43% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-05-18 | 3 | 20.986 | 6.6381 | 27.6241 | 1.3274 | 0.76558 | 0.20536 | 2.2984 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2010-05-18 | 4 | 20.066 | 6.3268 | 26.3928 | 1.2117 | 0.76558 | 0.19621 | 2.1735 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-05-18 | 5 | 19.09 | 6.1888 | 25.2788 | 1.1116 | 0.76558 | 0.18793 | 2.0651 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-05-18 | 6 | 18.616 | 5.9895 | 24.6055 | 1.0532 | 0.76558 | 0.18292 | 2.0017 | 8.135% | 8.656% | 5.849% | 1.0886 | 1.0948 | 1.0621
2010-05-18 | 7 | 18.932 | 5.8719 | 24.8039 | 1.0702 | 0.76558 | 0.1844 | 2.0202 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-05-18 | 8 | 18.716 | 5.8078 | 24.5238 | 1.0462 | 0.76558 | 0.18231 | 1.9941 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-05-18 | 9 | 18.918 | 5.8966 | 24.8146 | 1.0711 | 0.76558 | 0.18447 | 2.0212 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-05-18 | 10 | 18.874 | 5.9778 | 24.8518 | 1.0744 | 0.76558 | 0.18475 | 2.0247 | 8.147% | 8.668% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-05-18 | 11 | 19.048 | 6.004 | 25.052 | 1.0917 | 0.76558 | 0.18624 | 2.0436 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-05-18 | 12 | 19.88 | 6.3119 | 26.1919 | 1.1934 | 0.76558 | 0.19471 | 2.1536 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-05-18 | 13 | 21.92 | 7.1677 | 29.0877 | 1.4718 | 0.76558 | 0.21624 | 2.4536 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-05-18 | 14 | 24.894 | 8.6747 | 33.5687 | 1.9602 | 0.76558 | 0.24955 | 2.9753 | 8.863% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-05-18 | 15 | 28.34 | 10.4712 | 38.8112 | 2.6203 | 0.76558 | 0.28853 | 3.6744 | 9.467% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-05-18 | 16 | 30.568 | 11.5742 | 42.1422 | 3.0894 | 0.76558 | 0.31329 | 4.1682 | 9.891% | 10.52% | 7.112% | 1.1098 | 1.1176 | 1.0766
2010-05-18 | 17 | 32.836 | 12.6608 | 45.4968 | 3.6008 | 0.76558 | 0.33823 | 4.7046 | 10.34% | 11% | 7.435% | 1.1153 | 1.1236 | 1.0803
2010-05-18 | 18 | 33.712 | 12.7294 | 46.4414 | 3.7518 | 0.76558 | 0.34525 | 4.8627 | 10.47% | 11.14% | 7.528% | 1.117 | 1.1254 | 1.0814
2010-05-18 | 19 | 33.8 | 12.6562 | 46.4562 | 3.7542 | 0.76558 | 0.34536 | 4.8652 | 10.47% | 11.14% | 7.53% | 1.117 | 1.1254 | 1.0814
2010-05-18 | 20 | 33.8 | 12.5447 | 46.3447 | 3.7362 | 0.76558 | 0.34453 | 4.8464 | 10.46% | 11.13% | 7.519% | 1.1168 | 1.1252 | 1.0813
2010-05-18 | 21 | 34.82 | 12.1325 | 46.9525 | 3.8349 | 0.76558 | 0.34905 | 4.9495 | 10.54% | 11.22% | 7.579% | 1.1178 | 1.1263 | 1.082
2010-05-18 | 22 | 34.1581 | 11.8233 | 45.9814 | 3.6779 | 0.76558 | 0.34183 | 4.7853 | 10.41% | 11.07% | 7.483% | 1.1162 | 1.1245 | 1.0809
2010-05-18 | 23 | 32.9521 | 11.2862 | 44.2382 | 3.4043 | 0.76558 | 0.32887 | 4.4988 | 10.17% | 10.82% | 7.312% | 1.1132 | 1.1213 | 1.0789
2010-05-18 | 24 | 32.29 | 11.1103 | 43.4003 | 3.2766 | 0.76558 | 0.32264 | 4.3648 | 10.06% | 10.7% | 7.231% | 1.1118 | 1.1198 | 1.0779
2010-05-18 | 25 | 30.926 | 10.824 | 41.75 | 3.0321 | 0.76558 | 0.31037 | 4.1081 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-05-18 | 26 | 29.734 | 10.5004 | 40.2344 | 2.816 | 0.76558 | 0.29911 | 3.8807 | 9.645% | 10.26% | 6.935% | 1.1067 | 1.1144 | 1.0745
2010-05-18 | 27 | 30.036 | 10.7947 | 40.8307 | 2.9001 | 0.76558 | 0.30354 | 3.9692 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-05-18 | 28 | 30.108 | 10.7761 | 40.8841 | 2.9077 | 0.76558 | 0.30394 | 3.9772 | 9.728% | 10.35% | 6.994% | 1.1078 | 1.1155 | 1.0752
2010-05-18 | 29 | 29.446 | 10.3353 | 39.7813 | 2.7529 | 0.76558 | 0.29574 | 3.8142 | 9.588% | 10.2% | 6.894% | 1.106 | 1.1136 | 1.074
2010-05-18 | 30 | 28.57 | 9.9646 | 38.5346 | 2.5831 | 0.76558 | 0.28647 | 3.6351 | 9.433% | 10.04% | 6.783% | 1.1042 | 1.1116 | 1.0728
2010-05-18 | 31 | 29.246 | 10.0392 | 39.2852 | 2.6847 | 0.76558 | 0.29205 | 3.7423 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-05-18 | 32 | 29.074 | 9.8505 | 38.9245 | 2.6356 | 0.76558 | 0.28937 | 3.6906 | 9.481% | 10.09% | 6.817% | 1.1047 | 1.1122 | 1.0732
2010-05-18 | 33 | 29.532 | 10.2249 | 39.7569 | 2.7495 | 0.76558 | 0.29556 | 3.8107 | 9.585% | 10.2% | 6.892% | 1.106 | 1.1136 | 1.074
2010-05-18 | 34 | 30.338 | 10.8306 | 41.1686 | 2.9483 | 0.76558 | 0.30605 | 4.0199 | 9.764% | 10.39% | 7.021% | 1.1082 | 1.1159 | 1.0755
2010-05-18 | 35 | 31.342 | 11.9102 | 43.2522 | 3.2543 | 0.76558 | 0.32154 | 4.3414 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-05-18 | 36 | 33.942 | 13.3516 | 47.2936 | 3.8908 | 0.76558 | 0.35159 | 5.008 | 10.59% | 11.27% | 7.614% | 1.1184 | 1.127 | 1.0824
2010-05-18 | 37 | 35.752 | 13.6897 | 49.4417 | 4.2523 | 0.76558 | 0.36756 | 5.3854 | 10.89% | 11.59% | 7.832% | 1.1222 | 1.1311 | 1.085
2010-05-18 | 38 | 36.284 | 13.1282 | 49.4122 | 4.2472 | 0.76558 | 0.36734 | 5.3801 | 10.89% | 11.59% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-05-18 | 39 | 35.452 | 12.3013 | 47.7533 | 3.9668 | 0.76558 | 0.355 | 5.0874 | 10.65% | 11.34% | 7.66% | 1.1192 | 1.1278 | 1.083
2010-05-18 | 40 | 34.618 | 11.7268 | 46.3448 | 3.7363 | 0.76558 | 0.34453 | 4.8464 | 10.46% | 11.13% | 7.519% | 1.1168 | 1.1252 | 1.0813
2010-05-18 | 41 | 34.718 | 11.3765 | 46.0945 | 3.696 | 0.76558 | 0.34267 | 4.8043 | 10.42% | 11.09% | 7.494% | 1.1164 | 1.1247 | 1.081
2010-05-18 | 42 | 34 | 10.9547 | 44.9547 | 3.5155 | 0.76558 | 0.3342 | 4.6153 | 10.27% | 10.92% | 7.382% | 1.1144 | 1.1226 | 1.0797
2010-05-18 | 43 | 32.19 | 10.4195 | 42.6095 | 3.1583 | 0.76558 | 0.31676 | 4.2406 | 9.952% | 10.59% | 7.156% | 1.1105 | 1.1184 | 1.0771
2010-05-18 | 44 | 30.64 | 9.7866 | 40.4266 | 2.843 | 0.76558 | 0.30054 | 3.9091 | 9.67% | 10.29% | 6.952% | 1.107 | 1.1147 | 1.0747
2010-05-18 | 45 | 27.738 | 8.74 | 36.478 | 2.3147 | 0.76558 | 0.27118 | 3.3515 | 9.188% | 9.776% | 6.606% | 1.1012 | 1.1083 | 1.0707
2010-05-18 | 46 | 25.138 | 7.8019 | 32.9399 | 1.8875 | 0.76558 | 0.24488 | 2.8979 | 8.798% | 9.361% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-05-18 | 47 | 24.534 | 7.8903 | 32.4243 | 1.8288 | 0.76558 | 0.24105 | 2.8355 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-05-18 | 48 | 23.874 | 8.343 | 32.217 | 1.8055 | 0.76558 | 0.23951 | 2.8106 | 8.724% | 9.282% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-05-19 | 1 | 22.466 | 7.4593 | 29.9253 | 1.5578 | 0.76558 | 0.22247 | 2.5459 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-05-19 | 2 | 23.112 | 7.2381 | 30.3501 | 1.6023 | 0.76558 | 0.22563 | 2.5935 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-05-19 | 3 | 21.79 | 6.804 | 28.594 | 1.4223 | 0.76558 | 0.21257 | 2.4004 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-05-19 | 4 | 20.828 | 6.4869 | 27.3149 | 1.2979 | 0.76558 | 0.20306 | 2.2665 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-05-19 | 5 | 20.47 | 6.3248 | 26.7948 | 1.2489 | 0.76558 | 0.1992 | 2.2137 | 8.262% | 8.79% | 5.94% | 1.0901 | 1.0964 | 1.0632
2010-05-19 | 6 | 19.98 | 6.0438 | 26.0238 | 1.1781 | 0.76558 | 0.19346 | 2.1371 | 8.212% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-05-19 | 7 | 19.65 | 5.9929 | 25.6429 | 1.1438 | 0.76558 | 0.19063 | 2.1001 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-05-19 | 8 | 19.522 | 5.9535 | 25.4755 | 1.129 | 0.76558 | 0.18939 | 2.0839 | 8.18% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-05-19 | 9 | 19.808 | 6.0843 | 25.8923 | 1.1662 | 0.76558 | 0.19249 | 2.1243 | 8.204% | 8.729% | 5.899% | 1.0894 | 1.0956 | 1.0627
2010-05-19 | 10 | 20.11 | 6.0913 | 26.2013 | 1.1942 | 0.76558 | 0.19478 | 2.1546 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-05-19 | 11 | 20.254 | 6.3886 | 26.6426 | 1.2348 | 0.76558 | 0.19806 | 2.1984 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0962 | 1.0631
2010-05-19 | 12 | 21 | 6.7687 | 27.7687 | 1.3414 | 0.76558 | 0.20644 | 2.3134 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-05-19 | 13 | 23.284 | 7.7954 | 31.0794 | 1.6803 | 0.76558 | 0.23105 | 2.6769 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-05-19 | 14 | 26.358 | 9.4734 | 35.8314 | 2.2334 | 0.76558 | 0.26638 | 3.2653 | 9.113% | 9.696% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-05-19 | 15 | 30.294 | 11.7858 | 42.0799 | 3.0802 | 0.76558 | 0.31283 | 4.1586 | 9.883% | 10.52% | 7.106% | 1.1097 | 1.1175 | 1.0765
2010-05-19 | 16 | 32.492 | 12.9236 | 45.4156 | 3.5879 | 0.76558 | 0.33762 | 4.6911 | 10.33% | 10.99% | 7.427% | 1.1152 | 1.1235 | 1.0802
2010-05-19 | 17 | 33.656 | 13.8384 | 47.4944 | 3.9239 | 0.76558 | 0.35308 | 5.0426 | 10.62% | 11.3% | 7.634% | 1.1188 | 1.1274 | 1.0826
2010-05-19 | 18 | 34.346 | 13.6552 | 48.0012 | 4.0081 | 0.76558 | 0.35685 | 5.1305 | 10.69% | 11.37% | 7.685% | 1.1197 | 1.1283 | 1.0832
2010-05-19 | 19 | 34.488 | 13.4658 | 47.9538 | 4.0002 | 0.76558 | 0.35649 | 5.1223 | 10.68% | 11.37% | 7.68% | 1.1196 | 1.1282 | 1.0832
2010-05-19 | 20 | 34.1 | 12.6707 | 46.7707 | 3.8052 | 0.76558 | 0.3477 | 4.9185 | 10.52% | 11.19% | 7.561% | 1.1175 | 1.126 | 1.0818
2010-05-19 | 21 | 34.474 | 11.8259 | 46.2999 | 3.729 | 0.76558 | 0.3442 | 4.8388 | 10.45% | 11.12% | 7.514% | 1.1167 | 1.1251 | 1.0812
2010-05-19 | 22 | 34.33 | 11.7437 | 46.0737 | 3.6927 | 0.76558 | 0.34252 | 4.8008 | 10.42% | 11.09% | 7.492% | 1.1163 | 1.1247 | 1.081
2010-05-19 | 23 | 34.144 | 11.4065 | 45.5505 | 3.6093 | 0.76558 | 0.33863 | 4.7135 | 10.35% | 11.01% | 7.44% | 1.1154 | 1.1237 | 1.0804
2010-05-19 | 24 | 33.828 | 11.5365 | 45.3645 | 3.5799 | 0.76558 | 0.33724 | 4.6827 | 10.32% | 10.98% | 7.422% | 1.1151 | 1.1234 | 1.0802
2010-05-19 | 25 | 33.224 | 11.6573 | 44.8813 | 3.504 | 0.76558 | 0.33365 | 4.6032 | 10.26% | 10.91% | 7.374% | 1.1143 | 1.1225 | 1.0796
2010-05-19 | 26 | 31.99 | 11.538 | 43.528 | 3.2959 | 0.76558 | 0.32359 | 4.3851 | 10.07% | 10.72% | 7.243% | 1.112 | 1.1201 | 1.0781
2010-05-19 | 27 | 32.722 | 11.8532 | 44.5752 | 3.4564 | 0.76558 | 0.33138 | 4.5533 | 10.21% | 10.87% | 7.345% | 1.1138 | 1.1219 | 1.0793
2010-05-19 | 28 | 33.828 | 12.1494 | 45.9774 | 3.6773 | 0.76558 | 0.3418 | 4.7846 | 10.41% | 11.07% | 7.482% | 1.1162 | 1.1245 | 1.0809
2010-05-19 | 29 | 33.728 | 11.8581 | 45.5862 | 3.6149 | 0.76558 | 0.33889 | 4.7194 | 10.35% | 11.02% | 7.444% | 1.1155 | 1.1238 | 1.0804
2010-05-19 | 30 | 33.742 | 11.5888 | 45.3308 | 3.5745 | 0.76558 | 0.33699 | 4.6771 | 10.32% | 10.98% | 7.418% | 1.115 | 1.1233 | 1.0801
2010-05-19 | 31 | 35.278 | 12.2093 | 47.4873 | 3.9227 | 0.76558 | 0.35303 | 5.0413 | 10.62% | 11.3% | 7.633% | 1.1188 | 1.1273 | 1.0826
2010-05-19 | 32 | 36.154 | 12.5443 | 48.6983 | 4.1254 | 0.76558 | 0.36203 | 5.253 | 10.79% | 11.48% | 7.756% | 1.1209 | 1.1297 | 1.0841
2010-05-19 | 33 | 36.284 | 12.7107 | 48.9947 | 4.1757 | 0.76558 | 0.36423 | 5.3055 | 10.83% | 11.52% | 7.786% | 1.1214 | 1.1302 | 1.0844
2010-05-19 | 34 | 36.858 | 13.1342 | 49.9922 | 4.3475 | 0.76558 | 0.37165 | 5.4847 | 10.97% | 11.67% | 7.888% | 1.1232 | 1.1322 | 1.0856
2010-05-19 | 35 | 37.132 | 13.5208 | 50.6528 | 4.4632 | 0.76558 | 0.37656 | 5.6053 | 11.07% | 11.77% | 7.957% | 1.1244 | 1.1335 | 1.0864
2010-05-19 | 36 | 38.28 | 14.5923 | 52.8723 | 4.8628 | 0.76558 | 0.39306 | 6.0215 | 11.39% | 12.12% | 8.189% | 1.1285 | 1.1379 | 1.0892
2010-05-19 | 37 | 39.07 | 14.3302 | 53.4002 | 4.9604 | 0.76558 | 0.39698 | 6.123 | 11.47% | 12.2% | 8.244% | 1.1295 | 1.139 | 1.0898
2010-05-19 | 38 | 39.028 | 13.92 | 52.948 | 4.8768 | 0.76558 | 0.39362 | 6.036 | 11.4% | 12.13% | 8.196% | 1.1287 | 1.138 | 1.0893
2010-05-19 | 39 | 37.864 | 13.5187 | 51.3827 | 4.5927 | 0.76558 | 0.38198 | 5.7403 | 11.17% | 11.89% | 8.032% | 1.1258 | 1.1349 | 1.0873
2010-05-19 | 40 | 37.016 | 12.7902 | 49.8062 | 4.3152 | 0.76558 | 0.37027 | 5.451 | 10.94% | 11.64% | 7.869% | 1.1229 | 1.1318 | 1.0854
2010-05-19 | 41 | 36.916 | 12.451 | 49.367 | 4.2394 | 0.76558 | 0.367 | 5.372 | 10.88% | 11.58% | 7.824% | 1.1221 | 1.1309 | 1.0849
2010-05-19 | 42 | 36.686 | 11.9924 | 48.6784 | 4.122 | 0.76558 | 0.36188 | 5.2495 | 10.78% | 11.47% | 7.754% | 1.1209 | 1.1296 | 1.0841
2010-05-19 | 43 | 35.164 | 11.238 | 46.402 | 3.7455 | 0.76558 | 0.34496 | 4.856 | 10.47% | 11.13% | 7.524% | 1.1169 | 1.1253 | 1.0814
2010-05-19 | 44 | 33.238 | 10.536 | 43.774 | 3.3332 | 0.76558 | 0.32542 | 4.4242 | 10.11% | 10.75% | 7.267% | 1.1124 | 1.1205 | 1.0784
2010-05-19 | 45 | 30.094 | 9.4963 | 39.5903 | 2.7265 | 0.76558 | 0.29432 | 3.7864 | 9.564% | 10.18% | 6.877% | 1.1058 | 1.1133 | 1.0738
2010-05-19 | 46 | 27.162 | 8.273 | 35.435 | 2.1842 | 0.76558 | 0.26343 | 3.2132 | 9.068% | 9.648% | 6.52% | 1.0997 | 1.1068 | 1.0697
2010-05-19 | 47 | 26.56 | 8.5813 | 35.1413 | 2.1482 | 0.76558 | 0.26124 | 3.175 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-05-19 | 48 | 25.54 | 8.8797 | 34.4197 | 2.0609 | 0.76558 | 0.25588 | 3.0823 | 8.955% | 9.528% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-05-20 | 1 | 24.06 | 8.1627 | 32.2227 | 1.8062 | 0.76558 | 0.23955 | 2.8113 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-05-20 | 2 | 24.98 | 7.8736 | 32.8536 | 1.8776 | 0.76558 | 0.24424 | 2.8874 | 8.789% | 9.351% | 6.319% | 1.0964 | 1.1032 | 1.0675
2010-05-20 | 3 | 23.988 | 7.5256 | 31.5136 | 1.7275 | 0.76558 | 0.23428 | 2.7274 | 8.655% | 9.209% | 6.223% | 1.0947 | 1.1014 | 1.0664
2010-05-20 | 4 | 22.796 | 7.2701 | 30.0661 | 1.5725 | 0.76558 | 0.22351 | 2.5616 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-05-20 | 5 | 22.524 | 7.1215 | 29.6455 | 1.5288 | 0.76558 | 0.22039 | 2.5148 | 8.483% | 9.026% | 6.099% | 1.0927 | 1.0992 | 1.065
2010-05-20 | 6 | 22.092 | 6.9872 | 29.0792 | 1.471 | 0.76558 | 0.21618 | 2.4527 | 8.435% | 8.974% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-05-20 | 7 | 22.064 | 6.908 | 28.972 | 1.4601 | 0.76558 | 0.21538 | 2.4411 | 8.426% | 8.965% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-05-20 | 8 | 21.402 | 6.8226 | 28.2246 | 1.3858 | 0.76558 | 0.20983 | 2.3612 | 8.366% | 8.901% | 6.015% | 1.0913 | 1.0977 | 1.064
2010-05-20 | 9 | 21.374 | 6.8789 | 28.2529 | 1.3885 | 0.76558 | 0.21004 | 2.3642 | 8.368% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-05-20 | 10 | 21.646 | 6.9599 | 28.6059 | 1.4235 | 0.76558 | 0.21266 | 2.4017 | 8.396% | 8.933% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-05-20 | 11 | 22.294 | 7.0493 | 29.3433 | 1.4978 | 0.76558 | 0.21814 | 2.4815 | 8.457% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-05-20 | 12 | 23.07 | 7.4396 | 30.5096 | 1.6192 | 0.76558 | 0.22681 | 2.6116 | 8.56% | 9.108% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-05-20 | 13 | 24.922 | 8.6713 | 33.5933 | 1.9631 | 0.76558 | 0.24974 | 2.9784 | 8.866% | 9.433% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-05-20 | 14 | 28.356 | 10.3473 | 38.7033 | 2.6057 | 0.76558 | 0.28772 | 3.659 | 9.454% | 10.06% | 6.797% | 1.1044 | 1.1118 | 1.0729
2010-05-20 | 15 | 32.452 | 12.4618 | 44.9138 | 3.5091 | 0.76558 | 0.33389 | 4.6086 | 10.26% | 10.92% | 7.378% | 1.1143 | 1.1226 | 1.0797
2010-05-20 | 16 | 34.33 | 13.7505 | 48.0805 | 4.0214 | 0.76558 | 0.35744 | 5.1444 | 10.7% | 11.38% | 7.693% | 1.1198 | 1.1285 | 1.0833
2010-05-20 | 17 | 36.132 | 14.6759 | 50.808 | 4.4905 | 0.76558 | 0.37771 | 5.6338 | 11.09% | 11.8% | 7.973% | 1.1247 | 1.1338 | 1.0866
2010-05-20 | 18 | 36.65 | 14.6206 | 51.2706 | 4.5727 | 0.76558 | 0.38115 | 5.7194 | 11.16% | 11.87% | 8.021% | 1.1256 | 1.1347 | 1.0872
2010-05-20 | 19 | 36.85 | 14.4015 | 51.2515 | 4.5693 | 0.76558 | 0.38101 | 5.7159 | 11.15% | 11.87% | 8.019% | 1.1255 | 1.1346 | 1.0872
2010-05-20 | 20 | 36.492 | 13.9069 | 50.3989 | 4.4185 | 0.76558 | 0.37467 | 5.5588 | 11.03% | 11.74% | 7.93% | 1.124 | 1.133 | 1.0861
2010-05-20 | 21 | 37.712 | 13.6748 | 51.3868 | 4.5934 | 0.76558 | 0.38202 | 5.741 | 11.17% | 11.89% | 8.033% | 1.1258 | 1.1349 | 1.0873
2010-05-20 | 22 | 37.124 | 13.4504 | 50.5744 | 4.4493 | 0.76558 | 0.37598 | 5.5909 | 11.05% | 11.76% | 7.948% | 1.1243 | 1.1333 | 1.0863
2010-05-20 | 23 | 35.616 | 12.6717 | 48.2877 | 4.0561 | 0.76558 | 0.35898 | 5.1806 | 10.73% | 11.42% | 7.714% | 1.1202 | 1.1289 | 1.0836
2010-05-20 | 24 | 34.554 | 12.6516 | 47.2056 | 3.8763 | 0.76558 | 0.35093 | 4.9929 | 10.58% | 11.25% | 7.605% | 1.1183 | 1.1268 | 1.0823
2010-05-20 | 25 | 32.894 | 12.3552 | 45.2492 | 3.5617 | 0.76558 | 0.33639 | 4.6637 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-05-20 | 26 | 31.738 | 11.5668 | 43.3048 | 3.2622 | 0.76558 | 0.32193 | 4.3497 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-05-20 | 27 | 31.904 | 11.7343 | 43.6384 | 3.3126 | 0.76558 | 0.32441 | 4.4026 | 10.09% | 10.73% | 7.254% | 1.1122 | 1.1203 | 1.0782
2010-05-20 | 28 | 31.868 | 11.7911 | 43.6591 | 3.3158 | 0.76558 | 0.32457 | 4.4059 | 10.09% | 10.74% | 7.256% | 1.1122 | 1.1203 | 1.0782
2010-05-20 | 29 | 31.264 | 11.5225 | 42.7865 | 3.1846 | 0.76558 | 0.31808 | 4.2682 | 9.976% | 10.61% | 7.172% | 1.1108 | 1.1187 | 1.0773
2010-05-20 | 30 | 30.89 | 11.0672 | 41.9572 | 3.0623 | 0.76558 | 0.31192 | 4.1398 | 9.867% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-05-20 | 31 | 33.0161 | 11.2621 | 44.2781 | 3.4105 | 0.76558 | 0.32917 | 4.5052 | 10.17% | 10.83% | 7.316% | 1.1133 | 1.1214 | 1.0789
2010-05-20 | 32 | 33.418 | 11.6867 | 45.1048 | 3.539 | 0.76558 | 0.33531 | 4.6399 | 10.29% | 10.95% | 7.396% | 1.1147 | 1.1229 | 1.0799
2010-05-20 | 33 | 33.936 | 12.22 | 46.1561 | 3.7059 | 0.76558 | 0.34313 | 4.8146 | 10.43% | 11.1% | 7.5% | 1.1165 | 1.1248 | 1.0811
2010-05-20 | 34 | 34.244 | 12.8495 | 47.0935 | 3.8579 | 0.76558 | 0.3501 | 4.9736 | 10.56% | 11.24% | 7.593% | 1.1181 | 1.1266 | 1.0822
2010-05-20 | 35 | 35.078 | 13.4281 | 48.5061 | 4.0929 | 0.76558 | 0.3606 | 5.219 | 10.76% | 11.45% | 7.736% | 1.1206 | 1.1293 | 1.0838
2010-05-20 | 36 | 37.454 | 14.7618 | 52.2158 | 4.7428 | 0.76558 | 0.38818 | 5.8966 | 11.29% | 12.02% | 8.119% | 1.1273 | 1.1366 | 1.0884
2010-05-20 | 37 | 38.934 | 14.7167 | 53.6507 | 5.0071 | 0.76558 | 0.39885 | 6.1715 | 11.5% | 12.24% | 8.271% | 1.13 | 1.1395 | 1.0902
2010-05-20 | 38 | 38.948 | 14.5236 | 53.4716 | 4.9737 | 0.76558 | 0.39751 | 6.1368 | 11.48% | 12.21% | 8.252% | 1.1296 | 1.1391 | 1.0899
2010-05-20 | 39 | 37.874 | 13.6905 | 51.5645 | 4.6253 | 0.76558 | 0.38334 | 5.7742 | 11.2% | 11.91% | 8.051% | 1.1261 | 1.1353 | 1.0876
2010-05-20 | 40 | 36.802 | 13.0834 | 49.8854 | 4.3289 | 0.76558 | 0.37085 | 5.4654 | 10.96% | 11.66% | 7.877% | 1.123 | 1.132 | 1.0855
2010-05-20 | 41 | 37.304 | 12.8198 | 50.1238 | 4.3704 | 0.76558 | 0.37263 | 5.5086 | 10.99% | 11.69% | 7.902% | 1.1235 | 1.1324 | 1.0858
2010-05-20 | 42 | 36.73 | 12.379 | 49.109 | 4.1952 | 0.76558 | 0.36508 | 5.3259 | 10.85% | 11.54% | 7.798% | 1.1216 | 1.1304 | 1.0846
2010-05-20 | 43 | 34.906 | 11.6488 | 46.5548 | 3.7702 | 0.76558 | 0.34609 | 4.8819 | 10.49% | 11.16% | 7.54% | 1.1171 | 1.1256 | 1.0815
2010-05-20 | 44 | 33.224 | 10.8845 | 44.1085 | 3.3844 | 0.76558 | 0.32791 | 4.4779 | 10.15% | 10.8% | 7.299% | 1.113 | 1.1211 | 1.0787
2010-05-20 | 45 | 29.59 | 9.5869 | 39.1769 | 2.6699 | 0.76558 | 0.29125 | 3.7267 | 9.513% | 10.12% | 6.84% | 1.1051 | 1.1126 | 1.0734
2010-05-20 | 46 | 26.646 | 8.4472 | 35.0932 | 2.1423 | 0.76558 | 0.26089 | 3.1688 | 9.03% | 9.607% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-05-20 | 47 | 26.028 | 8.5405 | 34.5685 | 2.0787 | 0.76558 | 0.25699 | 3.1013 | 8.971% | 9.546% | 6.45% | 1.0986 | 1.1055 | 1.069
2010-05-20 | 48 | 25.382 | 9.0091 | 34.3911 | 2.0574 | 0.76558 | 0.25567 | 3.0787 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2010-05-21 | 1 | 24.16 | 8.1299 | 32.2899 | 1.8137 | 0.76558 | 0.24005 | 2.8193 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-05-21 | 2 | 24.922 | 7.8487 | 32.7707 | 1.8681 | 0.76558 | 0.24362 | 2.8773 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.103 | 1.0674
2010-05-21 | 3 | 23.772 | 7.4814 | 31.2534 | 1.6991 | 0.76558 | 0.23234 | 2.6971 | 8.63% | 9.182% | 6.205% | 1.0944 | 1.1011 | 1.0662
2010-05-21 | 4 | 22.84 | 7.0576 | 29.8976 | 1.5549 | 0.76558 | 0.22226 | 2.5428 | 8.505% | 9.049% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-05-21 | 5 | 22.366 | 6.928 | 29.294 | 1.4928 | 0.76558 | 0.21778 | 2.4761 | 8.453% | 8.994% | 6.077% | 1.0923 | 1.0988 | 1.0647
2010-05-21 | 6 | 21.892 | 6.7125 | 28.6045 | 1.4233 | 0.76558 | 0.21265 | 2.4015 | 8.396% | 8.933% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-05-21 | 7 | 21.748 | 6.7112 | 28.4592 | 1.4089 | 0.76558 | 0.21157 | 2.386 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-05-21 | 8 | 21.504 | 6.666 | 28.17 | 1.3804 | 0.76558 | 0.20942 | 2.3554 | 8.361% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-05-21 | 9 | 21.388 | 6.7798 | 28.1678 | 1.3802 | 0.76558 | 0.2094 | 2.3552 | 8.361% | 8.896% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-05-21 | 10 | 21.992 | 6.9652 | 28.9572 | 1.4586 | 0.76558 | 0.21527 | 2.4395 | 8.424% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-05-21 | 11 | 22.494 | 7.2099 | 29.7039 | 1.5348 | 0.76558 | 0.22082 | 2.5212 | 8.488% | 9.031% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-05-21 | 12 | 23.284 | 7.4531 | 30.7371 | 1.6435 | 0.76558 | 0.2285 | 2.6375 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-05-21 | 13 | 25.496 | 8.3707 | 33.8667 | 1.9952 | 0.76558 | 0.25177 | 3.0125 | 8.895% | 9.465% | 6.396% | 1.0976 | 1.1045 | 1.0683
2010-05-21 | 14 | 28.814 | 10.0037 | 38.8177 | 2.6212 | 0.76558 | 0.28858 | 3.6753 | 9.468% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.073
2010-05-21 | 15 | 33.104 | 12.1919 | 45.2959 | 3.569 | 0.76558 | 0.33673 | 4.6714 | 10.31% | 10.97% | 7.415% | 1.115 | 1.1233 | 1.0801
2010-05-21 | 16 | 35.444 | 13.4326 | 48.8766 | 4.1556 | 0.76558 | 0.36335 | 5.2846 | 10.81% | 11.5% | 7.774% | 1.1212 | 1.13 | 1.0843
2010-05-21 | 17 | 36.866 | 14.5513 | 51.4173 | 4.5989 | 0.76558 | 0.38224 | 5.7467 | 11.18% | 11.89% | 8.036% | 1.1258 | 1.135 | 1.0874
2010-05-21 | 18 | 36.836 | 14.5581 | 51.3941 | 4.5947 | 0.76558 | 0.38207 | 5.7424 | 11.17% | 11.89% | 8.034% | 1.1258 | 1.1349 | 1.0874
2010-05-21 | 19 | 36.994 | 14.0198 | 51.0138 | 4.527 | 0.76558 | 0.37924 | 5.6718 | 11.12% | 11.83% | 7.994% | 1.1251 | 1.1342 | 1.0869
2010-05-21 | 20 | 36.764 | 13.2115 | 49.9755 | 4.3446 | 0.76558 | 0.37152 | 5.4817 | 10.97% | 11.67% | 7.887% | 1.1232 | 1.1321 | 1.0856
2010-05-21 | 21 | 38.13 | 13.014 | 51.144 | 4.5501 | 0.76558 | 0.38021 | 5.6959 | 11.14% | 11.85% | 8.008% | 1.1253 | 1.1344 | 1.087
2010-05-21 | 22 | 37.612 | 12.8605 | 50.4725 | 4.4314 | 0.76558 | 0.37522 | 5.5722 | 11.04% | 11.75% | 7.938% | 1.1241 | 1.1331 | 1.0862
2010-05-21 | 23 | 36.7062 | 12.7107 | 49.4169 | 4.248 | 0.76558 | 0.36737 | 5.381 | 10.89% | 11.59% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-05-21 | 24 | 35.6989 | 12.3862 | 48.085 | 4.0221 | 0.76558 | 0.35747 | 5.1452 | 10.7% | 11.38% | 7.693% | 1.1198 | 1.1285 | 1.0833
2010-05-21 | 25 | 34.1191 | 12.2081 | 46.3272 | 3.7334 | 0.76558 | 0.3444 | 4.8434 | 10.45% | 11.12% | 7.517% | 1.1168 | 1.1252 | 1.0813
2010-05-21 | 26 | 32.7144 | 11.659 | 44.3734 | 3.4252 | 0.76558 | 0.32988 | 4.5206 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-05-21 | 27 | 32.9729 | 12.0217 | 44.9946 | 3.5217 | 0.76558 | 0.3345 | 4.6218 | 10.27% | 10.93% | 7.385% | 1.1145 | 1.1227 | 1.0797
2010-05-21 | 28 | 33.2028 | 12.3586 | 45.5615 | 3.611 | 0.76558 | 0.33871 | 4.7153 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-05-21 | 29 | 32.4847 | 12.0805 | 44.5652 | 3.4548 | 0.76558 | 0.3313 | 4.5517 | 10.21% | 10.87% | 7.344% | 1.1138 | 1.1219 | 1.0793
2010-05-21 | 30 | 32.2688 | 11.6888 | 43.9576 | 3.3613 | 0.76558 | 0.32679 | 4.4536 | 10.13% | 10.78% | 7.285% | 1.1127 | 1.1208 | 1.0786
2010-05-21 | 31 | 33.9628 | 11.6563 | 45.6191 | 3.6202 | 0.76558 | 0.33914 | 4.7249 | 10.36% | 11.02% | 7.447% | 1.1155 | 1.1238 | 1.0805
2010-05-21 | 32 | 34.2787 | 11.7391 | 46.0178 | 3.6837 | 0.76558 | 0.3421 | 4.7914 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-05-21 | 33 | 34.2366 | 11.9678 | 46.2044 | 3.7137 | 0.76558 | 0.34349 | 4.8227 | 10.44% | 11.11% | 7.505% | 1.1165 | 1.1249 | 1.0811
2010-05-21 | 34 | 34.7525 | 12.4501 | 47.2027 | 3.8759 | 0.76558 | 0.35091 | 4.9923 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-05-21 | 35 | 35.5426 | 13.4488 | 48.9914 | 4.1752 | 0.76558 | 0.36421 | 5.305 | 10.83% | 11.52% | 7.786% | 1.1214 | 1.1302 | 1.0844
2010-05-21 | 36 | 38.3286 | 14.7474 | 53.076 | 4.9004 | 0.76558 | 0.39457 | 6.0605 | 11.42% | 12.15% | 8.21% | 1.1289 | 1.1383 | 1.0894
2010-05-21 | 37 | 39.0466 | 14.4555 | 53.5021 | 4.9794 | 0.76558 | 0.39774 | 6.1427 | 11.48% | 12.22% | 8.255% | 1.1297 | 1.1392 | 1.09
2010-05-21 | 38 | 38.8646 | 14.1969 | 53.0615 | 4.8977 | 0.76558 | 0.39447 | 6.0578 | 11.42% | 12.15% | 8.208% | 1.1289 | 1.1383 | 1.0894
2010-05-21 | 39 | 37.6326 | 13.71 | 51.3426 | 4.5855 | 0.76558 | 0.38169 | 5.7328 | 11.17% | 11.88% | 8.028% | 1.1257 | 1.1348 | 1.0873
2010-05-21 | 40 | 36.4547 | 13.0156 | 49.4703 | 4.2572 | 0.76558 | 0.36777 | 5.3905 | 10.9% | 11.59% | 7.835% | 1.1223 | 1.1311 | 1.085
2010-05-21 | 41 | 36.6707 | 12.7171 | 49.3878 | 4.243 | 0.76558 | 0.36715 | 5.3757 | 10.88% | 11.58% | 7.826% | 1.1221 | 1.131 | 1.0849
2010-05-21 | 42 | 36.4708 | 12.3139 | 48.7847 | 4.14 | 0.76558 | 0.36267 | 5.2683 | 10.8% | 11.49% | 7.764% | 1.1211 | 1.1298 | 1.0842
2010-05-21 | 43 | 34.6307 | 11.5415 | 46.1722 | 3.7085 | 0.76558 | 0.34325 | 4.8173 | 10.43% | 11.1% | 7.502% | 1.1165 | 1.1249 | 1.0811
2010-05-21 | 44 | 32.4907 | 10.7663 | 43.257 | 3.255 | 0.76558 | 0.32158 | 4.3421 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-05-21 | 45 | 29.3589 | 9.7548 | 39.1137 | 2.6613 | 0.76558 | 0.29078 | 3.7176 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2010-05-21 | 46 | 26.7168 | 8.7994 | 35.5162 | 2.1943 | 0.76558 | 0.26403 | 3.2239 | 9.077% | 9.658% | 6.526% | 1.0998 | 1.1069 | 1.0698
2010-05-21 | 47 | 26.1848 | 8.9911 | 35.1759 | 2.1524 | 0.76558 | 0.2615 | 3.1795 | 9.039% | 9.617% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-05-21 | 48 | 25.6108 | 9.4827 | 35.0935 | 2.1423 | 0.76558 | 0.26089 | 3.1688 | 9.03% | 9.608% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-05-22 | 1 | 23.5267 | 8.6223 | 32.149 | 1.7979 | 0.76558 | 0.239 | 2.8025 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-05-22 | 2 | 24.3167 | 8.2315 | 32.5482 | 1.8428 | 0.76558 | 0.24197 | 2.8504 | 8.757% | 9.318% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-05-22 | 3 | 23.5267 | 7.6774 | 31.2042 | 1.6938 | 0.76558 | 0.23198 | 2.6913 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-05-22 | 4 | 22.5507 | 7.4455 | 29.9962 | 1.5652 | 0.76558 | 0.223 | 2.5538 | 8.514% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-05-22 | 5 | 21.9767 | 7.1941 | 29.1708 | 1.4802 | 0.76558 | 0.21686 | 2.4627 | 8.442% | 8.983% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-05-22 | 6 | 21.2428 | 6.9544 | 28.1971 | 1.3831 | 0.76558 | 0.20962 | 2.3583 | 8.364% | 8.899% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-05-22 | 7 | 21.4008 | 6.9748 | 28.3756 | 1.4006 | 0.76558 | 0.21095 | 2.3772 | 8.377% | 8.914% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-05-22 | 8 | 21.3008 | 6.9994 | 28.3002 | 1.3932 | 0.76558 | 0.21039 | 2.3692 | 8.372% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-05-22 | 9 | 21.3008 | 6.8332 | 28.1339 | 1.3769 | 0.76558 | 0.20915 | 2.3516 | 8.359% | 8.894% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-05-22 | 10 | 21.5447 | 6.812 | 28.3568 | 1.3988 | 0.76558 | 0.21081 | 2.3752 | 8.376% | 8.912% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-05-22 | 11 | 21.9467 | 7.035 | 28.9817 | 1.4611 | 0.76558 | 0.21545 | 2.4421 | 8.426% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-05-22 | 12 | 22.4367 | 7.4856 | 29.9223 | 1.5575 | 0.76558 | 0.22245 | 2.5455 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-05-22 | 13 | 24.7347 | 8.497 | 33.2317 | 1.9211 | 0.76558 | 0.24705 | 2.9337 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2010-05-22 | 14 | 27.7507 | 10.1152 | 37.8659 | 2.4942 | 0.76558 | 0.2815 | 3.5413 | 9.352% | 9.951% | 6.724% | 1.1032 | 1.1105 | 1.0721
2010-05-22 | 15 | 31.3848 | 12.2591 | 43.6439 | 3.3135 | 0.76558 | 0.32445 | 4.4035 | 10.09% | 10.74% | 7.254% | 1.1122 | 1.1203 | 1.0782
2010-05-22 | 16 | 33.6248 | 13.3636 | 46.9884 | 3.8407 | 0.76558 | 0.34932 | 4.9556 | 10.55% | 11.22% | 7.583% | 1.1179 | 1.1264 | 1.0821
2010-05-22 | 17 | 35.2207 | 14.289 | 49.5097 | 4.264 | 0.76558 | 0.36806 | 5.3976 | 10.9% | 11.6% | 7.839% | 1.1224 | 1.1312 | 1.0851
2010-05-22 | 18 | 35.5227 | 14.2434 | 49.7662 | 4.3083 | 0.76558 | 0.36997 | 5.4438 | 10.94% | 11.64% | 7.865% | 1.1228 | 1.1317 | 1.0854
2010-05-22 | 19 | 35.2768 | 13.8123 | 49.0892 | 4.1919 | 0.76558 | 0.36493 | 5.3224 | 10.84% | 11.54% | 7.796% | 1.1216 | 1.1304 | 1.0845
2010-05-22 | 20 | 34.6889 | 13.3632 | 48.0521 | 4.0166 | 0.76558 | 0.35723 | 5.1394 | 10.7% | 11.38% | 7.69% | 1.1198 | 1.1284 | 1.0833
2010-05-22 | 21 | 35.3208 | 13.0658 | 48.3866 | 4.0727 | 0.76558 | 0.35971 | 5.198 | 10.74% | 11.43% | 7.724% | 1.1204 | 1.1291 | 1.0837
2010-05-22 | 22 | 34.6448 | 12.4999 | 47.1446 | 3.8663 | 0.76558 | 0.35048 | 4.9824 | 10.57% | 11.24% | 7.599% | 1.1182 | 1.1267 | 1.0822
2010-05-22 | 23 | 33.4829 | 11.8225 | 45.3054 | 3.5705 | 0.76558 | 0.33681 | 4.6729 | 10.31% | 10.97% | 7.416% | 1.115 | 1.1233 | 1.0801
2010-05-22 | 24 | 32.5628 | 11.6652 | 44.228 | 3.4027 | 0.76558 | 0.3288 | 4.4971 | 10.17% | 10.82% | 7.311% | 1.1132 | 1.1213 | 1.0789
2010-05-22 | 25 | 31.2124 | 11.4182 | 42.6307 | 3.1614 | 0.76558 | 0.31692 | 4.2439 | 9.955% | 10.59% | 7.158% | 1.1106 | 1.1185 | 1.0771
2010-05-22 | 26 | 30.5525 | 10.5377 | 41.0902 | 2.937 | 0.76558 | 0.30547 | 4.0081 | 9.754% | 10.38% | 7.013% | 1.1081 | 1.1158 | 1.0754
2010-05-22 | 27 | 30.3945 | 10.9634 | 41.3579 | 2.9754 | 0.76558 | 0.30746 | 4.0485 | 9.789% | 10.42% | 7.038% | 1.1085 | 1.1163 | 1.0757
2010-05-22 | 28 | 30.3225 | 11.069 | 41.3915 | 2.9803 | 0.76558 | 0.30771 | 4.0536 | 9.793% | 10.42% | 7.041% | 1.1086 | 1.1163 | 1.0757
2010-05-22 | 29 | 29.6466 | 10.6181 | 40.2647 | 2.8202 | 0.76558 | 0.29933 | 3.8851 | 9.649% | 10.27% | 6.938% | 1.1068 | 1.1144 | 1.0745
2010-05-22 | 30 | 29.9485 | 10.3048 | 40.2533 | 2.8186 | 0.76558 | 0.29925 | 3.8835 | 9.648% | 10.26% | 6.937% | 1.1068 | 1.1144 | 1.0745
2010-05-22 | 31 | 32.0165 | 10.32 | 42.3365 | 3.1179 | 0.76558 | 0.31473 | 4.1982 | 9.916% | 10.55% | 7.13% | 1.1101 | 1.118 | 1.0768
2010-05-22 | 32 | 32.9505 | 10.5939 | 43.5443 | 3.2984 | 0.76558 | 0.32371 | 4.3876 | 10.08% | 10.72% | 7.245% | 1.1121 | 1.1201 | 1.0781
2010-05-22 | 33 | 33.3525 | 11.0169 | 44.3694 | 3.4245 | 0.76558 | 0.32985 | 4.52 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-05-22 | 34 | 33.5544 | 11.1511 | 44.7055 | 3.4766 | 0.76558 | 0.33235 | 4.5745 | 10.23% | 10.89% | 7.357% | 1.114 | 1.1222 | 1.0794
2010-05-22 | 35 | 34.6604 | 11.8966 | 46.557 | 3.7705 | 0.76558 | 0.34611 | 4.8822 | 10.49% | 11.16% | 7.54% | 1.1172 | 1.1256 | 1.0815
2010-05-22 | 36 | 36.7864 | 13.1315 | 49.918 | 4.3346 | 0.76558 | 0.3711 | 5.4713 | 10.96% | 11.66% | 7.881% | 1.1231 | 1.132 | 1.0855
2010-05-22 | 37 | 37.3305 | 13.2808 | 50.6113 | 4.4558 | 0.76558 | 0.37625 | 5.5977 | 11.06% | 11.77% | 7.952% | 1.1244 | 1.1334 | 1.0864
2010-05-22 | 38 | 36.3685 | 12.9241 | 49.2926 | 4.2267 | 0.76558 | 0.36645 | 5.3587 | 10.87% | 11.57% | 7.816% | 1.122 | 1.1308 | 1.0848
2010-05-22 | 39 | 35.5645 | 12.5351 | 48.0996 | 4.0245 | 0.76558 | 0.35758 | 5.1477 | 10.7% | 11.39% | 7.695% | 1.1198 | 1.1285 | 1.0834
2010-05-22 | 40 | 34.6025 | 12.2129 | 46.8154 | 3.8125 | 0.76558 | 0.34803 | 4.9261 | 10.52% | 11.2% | 7.566% | 1.1176 | 1.1261 | 1.0818
2010-05-22 | 41 | 34.7164 | 11.7468 | 46.4632 | 3.7554 | 0.76558 | 0.34541 | 4.8664 | 10.47% | 11.14% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-05-22 | 42 | 34.4946 | 11.3924 | 45.887 | 3.6628 | 0.76558 | 0.34113 | 4.7695 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-05-22 | 43 | 32.9646 | 10.8637 | 43.8283 | 3.3415 | 0.76558 | 0.32582 | 4.4329 | 10.11% | 10.76% | 7.272% | 1.1125 | 1.1206 | 1.0784
2010-05-22 | 44 | 31.3986 | 10.3373 | 41.7359 | 3.0301 | 0.76558 | 0.31027 | 4.1059 | 9.838% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-05-22 | 45 | 29.0785 | 9.6576 | 38.7361 | 2.6102 | 0.76558 | 0.28797 | 3.6637 | 9.458% | 10.06% | 6.8% | 1.1045 | 1.1119 | 1.073
2010-05-22 | 46 | 26.9746 | 8.7406 | 35.7151 | 2.2189 | 0.76558 | 0.26551 | 3.25 | 9.1% | 9.682% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-05-22 | 47 | 27.0246 | 8.9167 | 35.9412 | 2.2471 | 0.76558 | 0.26719 | 3.2799 | 9.126% | 9.71% | 6.561% | 1.1004 | 1.1075 | 1.0702
2010-05-22 | 48 | 26.3646 | 9.2873 | 35.6518 | 2.2111 | 0.76558 | 0.26504 | 3.2417 | 9.093% | 9.674% | 6.538% | 1.1 | 1.1071 | 1.0699
2010-05-23 | 1 | 24.9485 | 8.4506 | 33.3992 | 1.9405 | 0.76558 | 0.24829 | 2.9543 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-05-23 | 2 | 25.6245 | 8.0291 | 33.6537 | 1.9702 | 0.76558 | 0.25019 | 2.9859 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-05-23 | 3 | 24.3605 | 7.5545 | 31.9151 | 1.7718 | 0.76558 | 0.23726 | 2.7747 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-05-23 | 4 | 23.2826 | 7.3119 | 30.5944 | 1.6282 | 0.76558 | 0.22744 | 2.6213 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-05-23 | 5 | 22.7086 | 7.1425 | 29.8511 | 1.5501 | 0.76558 | 0.22192 | 2.5376 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2010-05-23 | 6 | 22.3066 | 6.7616 | 29.0682 | 1.4698 | 0.76558 | 0.2161 | 2.4515 | 8.434% | 8.973% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-05-23 | 7 | 22.3066 | 6.6236 | 28.9302 | 1.4559 | 0.76558 | 0.21507 | 2.4366 | 8.422% | 8.961% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-05-23 | 8 | 21.9766 | 6.5769 | 28.5535 | 1.4182 | 0.76558 | 0.21227 | 2.3961 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2010-05-23 | 9 | 22.1345 | 6.829 | 28.9635 | 1.4593 | 0.76558 | 0.21532 | 2.4402 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-05-23 | 10 | 22.4365 | 6.8155 | 29.252 | 1.4885 | 0.76558 | 0.21746 | 2.4715 | 8.449% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-05-23 | 11 | 22.7526 | 7.0543 | 29.8068 | 1.5455 | 0.76558 | 0.22159 | 2.5327 | 8.497% | 9.041% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-05-23 | 12 | 22.6506 | 7.0683 | 29.7189 | 1.5364 | 0.76558 | 0.22093 | 2.5229 | 8.489% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-05-23 | 13 | 23.7426 | 7.4927 | 31.2353 | 1.6972 | 0.76558 | 0.23221 | 2.695 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-05-23 | 14 | 25.3526 | 7.9224 | 33.275 | 1.9261 | 0.76558 | 0.24737 | 2.939 | 8.832% | 9.398% | 6.351% | 1.0969 | 1.1037 | 1.0678
2010-05-23 | 15 | 26.2706 | 8.4669 | 34.7375 | 2.0991 | 0.76558 | 0.25824 | 3.1229 | 8.99% | 9.565% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-05-23 | 16 | 26.4006 | 9.306 | 35.7066 | 2.2178 | 0.76558 | 0.26545 | 3.2489 | 9.099% | 9.681% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-05-23 | 17 | 28.5685 | 10.8912 | 39.4597 | 2.7086 | 0.76558 | 0.29335 | 3.7675 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-05-23 | 18 | 30.7666 | 11.964 | 42.7305 | 3.1762 | 0.76558 | 0.31766 | 4.2595 | 9.968% | 10.61% | 7.167% | 1.1107 | 1.1186 | 1.0772
2010-05-23 | 19 | 33.0226 | 12.5926 | 45.6152 | 3.6195 | 0.76558 | 0.33911 | 4.7242 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0805
2010-05-23 | 20 | 34.5445 | 12.912 | 47.4565 | 3.9177 | 0.76558 | 0.3528 | 5.036 | 10.61% | 11.29% | 7.63% | 1.1187 | 1.1273 | 1.0826
2010-05-23 | 21 | 37.0305 | 13.2753 | 50.3058 | 4.4022 | 0.76558 | 0.37398 | 5.5418 | 11.02% | 11.72% | 7.921% | 1.1238 | 1.1328 | 1.086
2010-05-23 | 22 | 36.7865 | 13.2768 | 50.0633 | 4.3599 | 0.76558 | 0.37218 | 5.4976 | 10.98% | 11.68% | 7.896% | 1.1234 | 1.1323 | 1.0857
2010-05-23 | 23 | 36.1385 | 12.9548 | 49.0933 | 4.1926 | 0.76558 | 0.36497 | 5.3231 | 10.84% | 11.54% | 7.796% | 1.1216 | 1.1304 | 1.0846
2010-05-23 | 24 | 35.3786 | 12.588 | 47.9666 | 4.0023 | 0.76558 | 0.35659 | 5.1245 | 10.68% | 11.37% | 7.681% | 1.1196 | 1.1283 | 1.0832
2010-05-23 | 25 | 34.0125 | 12.3656 | 46.3781 | 3.7416 | 0.76558 | 0.34478 | 4.852 | 10.46% | 11.13% | 7.522% | 1.1168 | 1.1253 | 1.0813
2010-05-23 | 26 | 32.2904 | 11.9241 | 44.2145 | 3.4007 | 0.76558 | 0.3287 | 4.4949 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-05-23 | 27 | 32.4484 | 12.1345 | 44.5829 | 3.4576 | 0.76558 | 0.33143 | 4.5546 | 10.22% | 10.87% | 7.345% | 1.1138 | 1.122 | 1.0793
2010-05-23 | 28 | 32.9225 | 12.105 | 45.0275 | 3.5269 | 0.76558 | 0.33474 | 4.6272 | 10.28% | 10.93% | 7.389% | 1.1145 | 1.1228 | 1.0798
2010-05-23 | 29 | 32.0885 | 11.828 | 43.9165 | 3.355 | 0.76558 | 0.32648 | 4.447 | 10.13% | 10.77% | 7.281% | 1.1127 | 1.1208 | 1.0785
2010-05-23 | 30 | 31.6145 | 11.3837 | 42.9982 | 3.2161 | 0.76558 | 0.31965 | 4.3014 | 10% | 10.64% | 7.193% | 1.1112 | 1.1191 | 1.0775
2010-05-23 | 31 | 32.7484 | 11.4668 | 44.2152 | 3.4008 | 0.76558 | 0.3287 | 4.4951 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-05-23 | 32 | 32.6625 | 11.4174 | 44.0799 | 3.38 | 0.76558 | 0.3277 | 4.4733 | 10.15% | 10.8% | 7.296% | 1.1129 | 1.121 | 1.0787
2010-05-23 | 33 | 32.3466 | 11.6272 | 43.9738 | 3.3637 | 0.76558 | 0.32691 | 4.4562 | 10.13% | 10.78% | 7.286% | 1.1128 | 1.1209 | 1.0786
2010-05-23 | 34 | 32.6766 | 11.8174 | 44.4939 | 3.4438 | 0.76558 | 0.33077 | 4.5401 | 10.2% | 10.86% | 7.337% | 1.1136 | 1.1218 | 1.0792
2010-05-23 | 35 | 32.9786 | 12.2881 | 45.2666 | 3.5644 | 0.76558 | 0.33652 | 4.6665 | 10.31% | 10.97% | 7.412% | 1.1149 | 1.1232 | 1.0801
2010-05-23 | 36 | 34.3865 | 13.2773 | 47.6638 | 3.952 | 0.76558 | 0.35434 | 5.0719 | 10.64% | 11.32% | 7.651% | 1.1191 | 1.1277 | 1.0828
2010-05-23 | 37 | 35.0765 | 13.0453 | 48.1218 | 4.0283 | 0.76558 | 0.35774 | 5.1516 | 10.71% | 11.39% | 7.697% | 1.1199 | 1.1285 | 1.0834
2010-05-23 | 38 | 34.7026 | 12.5597 | 47.2624 | 3.8857 | 0.76558 | 0.35135 | 5.0026 | 10.58% | 11.26% | 7.61% | 1.1184 | 1.1269 | 1.0824
2010-05-23 | 39 | 33.6407 | 12.0196 | 45.6603 | 3.6267 | 0.76558 | 0.33944 | 4.7317 | 10.36% | 11.03% | 7.451% | 1.1156 | 1.1239 | 1.0805
2010-05-23 | 40 | 32.1608 | 11.4332 | 43.594 | 3.3059 | 0.76558 | 0.32408 | 4.3956 | 10.08% | 10.73% | 7.25% | 1.1121 | 1.1202 | 1.0782
2010-05-23 | 41 | 31.8868 | 11.3115 | 43.1983 | 3.2461 | 0.76558 | 0.32114 | 4.3329 | 10.03% | 10.67% | 7.212% | 1.1115 | 1.1195 | 1.0777
2010-05-23 | 42 | 31.2549 | 10.761 | 42.0159 | 3.0709 | 0.76558 | 0.31235 | 4.1488 | 9.874% | 10.51% | 7.1% | 1.1096 | 1.1174 | 1.0764
2010-05-23 | 43 | 29.8189 | 10.2843 | 40.1032 | 2.7977 | 0.76558 | 0.29813 | 3.8614 | 9.629% | 10.24% | 6.923% | 1.1065 | 1.1141 | 1.0744
2010-05-23 | 44 | 28.297 | 9.7192 | 38.0162 | 2.514 | 0.76558 | 0.28262 | 3.5622 | 9.37% | 9.97% | 6.737% | 1.1034 | 1.1107 | 1.0722
2010-05-23 | 45 | 25.7829 | 8.7159 | 34.4989 | 2.0704 | 0.76558 | 0.25647 | 3.0924 | 8.964% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-05-23 | 46 | 24.1749 | 8.0903 | 32.2652 | 1.8109 | 0.76558 | 0.23986 | 2.8164 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-05-23 | 47 | 24.6772 | 8.4473 | 33.1245 | 1.9087 | 0.76558 | 0.24625 | 2.9205 | 8.817% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-05-23 | 48 | 24.4912 | 9.1355 | 33.6267 | 1.967 | 0.76558 | 0.24998 | 2.9826 | 8.87% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-05-24 | 1 | 22.9672 | 8.2132 | 31.1804 | 1.6912 | 0.76558 | 0.2318 | 2.6886 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-05-24 | 2 | 23.2552 | 7.728 | 30.9831 | 1.6699 | 0.76558 | 0.23033 | 2.6658 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-05-24 | 3 | 22.2632 | 7.2911 | 29.5543 | 1.5194 | 0.76558 | 0.21971 | 2.5047 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-05-24 | 4 | 21.4172 | 6.8666 | 28.2838 | 1.3916 | 0.76558 | 0.21027 | 2.3674 | 8.37% | 8.906% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-05-24 | 5 | 20.6692 | 6.672 | 27.3413 | 1.3004 | 0.76558 | 0.20326 | 2.2692 | 8.3% | 8.831% | 5.967% | 1.0905 | 1.0969 | 1.0635
2010-05-24 | 6 | 19.8652 | 6.4178 | 26.283 | 1.2017 | 0.76558 | 0.19539 | 2.1626 | 8.228% | 8.755% | 5.916% | 1.0897 | 1.0959 | 1.0629
2010-05-24 | 7 | 19.6352 | 6.192 | 25.8272 | 1.1604 | 0.76558 | 0.192 | 2.1179 | 8.2% | 8.725% | 5.896% | 1.0893 | 1.0956 | 1.0627
2010-05-24 | 8 | 19.7072 | 6.1589 | 25.8661 | 1.1638 | 0.76558 | 0.19229 | 2.1217 | 8.203% | 8.728% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-05-24 | 9 | 19.9953 | 6.2107 | 26.206 | 1.1946 | 0.76558 | 0.19482 | 2.155 | 8.223% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-05-24 | 10 | 19.9794 | 6.1718 | 26.1512 | 1.1896 | 0.76558 | 0.19441 | 2.1496 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-05-24 | 11 | 20.1375 | 6.3276 | 26.4651 | 1.2184 | 0.76558 | 0.19674 | 2.1807 | 8.24% | 8.767% | 5.924% | 1.0898 | 1.0961 | 1.063
2010-05-24 | 12 | 20.2255 | 6.4129 | 26.6385 | 1.2344 | 0.76558 | 0.19803 | 2.198 | 8.251% | 8.779% | 5.933% | 1.0899 | 1.0962 | 1.0631
2010-05-24 | 13 | 21.0296 | 6.7203 | 27.7499 | 1.3395 | 0.76558 | 0.2063 | 2.3114 | 8.329% | 8.863% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-05-24 | 14 | 22.0056 | 6.9021 | 28.9078 | 1.4537 | 0.76558 | 0.2149 | 2.4341 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-05-24 | 15 | 22.5658 | 7.1581 | 29.7239 | 1.5369 | 0.76558 | 0.22097 | 2.5235 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-05-24 | 16 | 22.51 | 7.711 | 30.221 | 1.5887 | 0.76558 | 0.22467 | 2.579 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-05-24 | 17 | 24.52 | 8.8276 | 33.3476 | 1.9345 | 0.76558 | 0.24791 | 2.948 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2010-05-24 | 18 | 26.8178 | 9.957 | 36.7749 | 2.3525 | 0.76558 | 0.27339 | 3.3915 | 9.222% | 9.813% | 6.631% | 1.1016 | 1.1088 | 1.071
2010-05-24 | 19 | 28.4838 | 10.7567 | 39.2406 | 2.6786 | 0.76558 | 0.29172 | 3.7359 | 9.52% | 10.13% | 6.845% | 1.1052 | 1.1127 | 1.0735
2010-05-24 | 20 | 29.2459 | 11.283 | 40.5289 | 2.8574 | 0.76558 | 0.3013 | 3.9242 | 9.683% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-05-24 | 21 | 31.3863 | 11.8184 | 43.2047 | 3.2471 | 0.76558 | 0.32119 | 4.3339 | 10.03% | 10.67% | 7.212% | 1.1115 | 1.1195 | 1.0777
2010-05-24 | 22 | 30.9702 | 11.8311 | 42.8014 | 3.1868 | 0.76558 | 0.31819 | 4.2705 | 9.978% | 10.62% | 7.174% | 1.1108 | 1.1188 | 1.0773
2010-05-24 | 23 | 30.4963 | 11.8059 | 42.3022 | 3.1129 | 0.76558 | 0.31448 | 4.1929 | 9.912% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-05-24 | 24 | 29.8783 | 11.7525 | 41.6307 | 3.0148 | 0.76558 | 0.30949 | 4.0899 | 9.824% | 10.45% | 7.064% | 1.1089 | 1.1167 | 1.076
2010-05-24 | 25 | 29.1602 | 11.3982 | 40.5584 | 2.8615 | 0.76558 | 0.30152 | 3.9286 | 9.686% | 10.31% | 6.964% | 1.1073 | 1.1149 | 1.0749
2010-05-24 | 26 | 28.6003 | 10.7536 | 39.3539 | 2.6941 | 0.76558 | 0.29256 | 3.7522 | 9.535% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-05-24 | 27 | 28.8143 | 11.3167 | 40.131 | 2.8015 | 0.76558 | 0.29834 | 3.8654 | 9.632% | 10.25% | 6.925% | 1.1066 | 1.1142 | 1.0744
2010-05-24 | 28 | 28.7001 | 11.407 | 40.1072 | 2.7982 | 0.76558 | 0.29816 | 3.8619 | 9.629% | 10.25% | 6.923% | 1.1066 | 1.1141 | 1.0744
2010-05-24 | 29 | 27.9822 | 10.7794 | 38.7616 | 2.6136 | 0.76558 | 0.28816 | 3.6673 | 9.461% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2010-05-24 | 30 | 27.1783 | 10.2372 | 37.4154 | 2.4352 | 0.76558 | 0.27815 | 3.4789 | 9.298% | 9.893% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-05-24 | 31 | 28.7003 | 10.3256 | 39.0259 | 2.6494 | 0.76558 | 0.29012 | 3.7051 | 9.494% | 10.1% | 6.826% | 1.1049 | 1.1124 | 1.0733
2010-05-24 | 32 | 28.7144 | 10.1459 | 38.8603 | 2.6269 | 0.76558 | 0.28889 | 3.6814 | 9.473% | 10.08% | 6.811% | 1.1046 | 1.1121 | 1.0731
2010-05-24 | 33 | 28.6564 | 10.4474 | 39.1038 | 2.6599 | 0.76558 | 0.2907 | 3.7162 | 9.503% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-05-24 | 34 | 29.2324 | 10.4895 | 39.7218 | 2.7447 | 0.76558 | 0.2953 | 3.8056 | 9.581% | 10.19% | 6.888% | 1.106 | 1.1135 | 1.074
2010-05-24 | 35 | 29.7624 | 11.7342 | 41.4966 | 2.9954 | 0.76558 | 0.30849 | 4.0695 | 9.807% | 10.43% | 7.051% | 1.1087 | 1.1165 | 1.0759
2010-05-24 | 36 | 32.4343 | 13.0505 | 45.4848 | 3.5989 | 0.76558 | 0.33814 | 4.7026 | 10.34% | 11% | 7.434% | 1.1153 | 1.1236 | 1.0803
2010-05-24 | 37 | 33.6423 | 13.1062 | 46.7485 | 3.8016 | 0.76558 | 0.34753 | 4.9148 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.1259 | 1.0818
2010-05-24 | 38 | 33.9003 | 12.6223 | 46.5225 | 3.765 | 0.76558 | 0.34585 | 4.8764 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-05-24 | 39 | 33.1383 | 12.1459 | 45.2842 | 3.5672 | 0.76558 | 0.33665 | 4.6694 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-05-24 | 40 | 32.1622 | 11.7487 | 43.9109 | 3.3541 | 0.76558 | 0.32644 | 4.4461 | 10.13% | 10.77% | 7.28% | 1.1127 | 1.1207 | 1.0785
2010-05-24 | 41 | 32.3781 | 11.528 | 43.9061 | 3.3534 | 0.76558 | 0.3264 | 4.4454 | 10.12% | 10.77% | 7.28% | 1.1127 | 1.1207 | 1.0785
2010-05-24 | 42 | 31.96 | 10.9816 | 42.9415 | 3.2077 | 0.76558 | 0.31923 | 4.2925 | 9.996% | 10.64% | 7.187% | 1.1111 | 1.119 | 1.0774
2010-05-24 | 43 | 30.1661 | 10.2936 | 40.4597 | 2.8476 | 0.76558 | 0.30078 | 3.914 | 9.674% | 10.29% | 6.955% | 1.1071 | 1.1147 | 1.0748
2010-05-24 | 44 | 28.2401 | 9.6523 | 37.8924 | 2.4977 | 0.76558 | 0.2817 | 3.545 | 9.355% | 9.954% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-05-24 | 45 | 25.756 | 8.7163 | 34.4724 | 2.0672 | 0.76558 | 0.25627 | 3.089 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-05-24 | 46 | 23.6161 | 7.6861 | 31.3022 | 1.7045 | 0.76558 | 0.2327 | 2.7027 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-05-24 | 47 | 23.6441 | 8.0903 | 31.7344 | 1.7518 | 0.76558 | 0.23592 | 2.7533 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-05-24 | 48 | 22.8101 | 8.7468 | 31.557 | 1.7323 | 0.76558 | 0.2346 | 2.7325 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-05-25 | 1 | 21.1021 | 8.0143 | 29.1163 | 1.4747 | 0.76558 | 0.21645 | 2.4567 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-05-25 | 2 | 21.934 | 7.6581 | 29.5921 | 1.5233 | 0.76558 | 0.21999 | 2.5089 | 8.478% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-05-25 | 3 | 21.3741 | 7.22 | 28.5941 | 1.4223 | 0.76558 | 0.21257 | 2.4004 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-05-25 | 4 | 20.542 | 6.9247 | 27.4668 | 1.3124 | 0.76558 | 0.20419 | 2.2821 | 8.309% | 8.84% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-05-25 | 5 | 19.348 | 6.7651 | 26.1131 | 1.1862 | 0.76558 | 0.19413 | 2.1459 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-05-25 | 6 | 19.032 | 6.4758 | 25.5077 | 1.1318 | 0.76558 | 0.18963 | 2.087 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-05-25 | 7 | 19.234 | 6.47 | 25.704 | 1.1493 | 0.76558 | 0.19109 | 2.106 | 8.193% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-05-25 | 8 | 19.162 | 6.4244 | 25.5864 | 1.1388 | 0.76558 | 0.19021 | 2.0946 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-05-25 | 9 | 19.162 | 6.3624 | 25.5244 | 1.1333 | 0.76558 | 0.18975 | 2.0886 | 8.183% | 8.707% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-05-25 | 10 | 19.1339 | 6.4242 | 25.5582 | 1.1363 | 0.76558 | 0.19 | 2.0919 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-05-25 | 11 | 19.6499 | 6.6559 | 26.3057 | 1.2037 | 0.76558 | 0.19556 | 2.1649 | 8.23% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-05-25 | 12 | 20.6699 | 7.0221 | 27.692 | 1.334 | 0.76558 | 0.20587 | 2.3054 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-05-25 | 13 | 22.5959 | 7.9272 | 30.523 | 1.6207 | 0.76558 | 0.22691 | 2.6131 | 8.561% | 9.109% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-05-25 | 14 | 25.2519 | 9.3194 | 34.5713 | 2.0791 | 0.76558 | 0.25701 | 3.1016 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-05-25 | 15 | 28.7278 | 11.3222 | 40.05 | 2.7902 | 0.76558 | 0.29774 | 3.8535 | 9.622% | 10.24% | 6.918% | 1.1065 | 1.1141 | 1.0743
2010-05-25 | 16 | 31.3437 | 12.8369 | 44.1806 | 3.3955 | 0.76558 | 0.32844 | 4.4895 | 10.16% | 10.81% | 7.306% | 1.1131 | 1.1212 | 1.0788
2010-05-25 | 17 | 32.8938 | 13.6549 | 46.5487 | 3.7692 | 0.76558 | 0.34605 | 4.8808 | 10.49% | 11.16% | 7.539% | 1.1171 | 1.1256 | 1.0815
2010-05-25 | 18 | 33.3397 | 13.6632 | 47.0029 | 3.8431 | 0.76558 | 0.34943 | 4.9581 | 10.55% | 11.22% | 7.584% | 1.1179 | 1.1264 | 1.0821
2010-05-25 | 19 | 33.8638 | 13.3892 | 47.253 | 3.8841 | 0.76558 | 0.35128 | 5.001 | 10.58% | 11.26% | 7.609% | 1.1184 | 1.1269 | 1.0824
2010-05-25 | 20 | 33.5198 | 13.2282 | 46.748 | 3.8016 | 0.76558 | 0.34753 | 4.9147 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.1259 | 1.0818
2010-05-25 | 21 | 33.8777 | 13.0003 | 46.878 | 3.8227 | 0.76558 | 0.3485 | 4.9368 | 10.53% | 11.21% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-05-25 | 22 | 32.4417 | 12.4891 | 44.9308 | 3.5117 | 0.76558 | 0.33402 | 4.6113 | 10.26% | 10.92% | 7.379% | 1.1144 | 1.1226 | 1.0797
2010-05-25 | 23 | 31.2717 | 12.1322 | 43.4039 | 3.2771 | 0.76558 | 0.32267 | 4.3654 | 10.06% | 10.7% | 7.231% | 1.1118 | 1.1198 | 1.078
2010-05-25 | 24 | 30.3157 | 11.7752 | 42.0909 | 3.0818 | 0.76558 | 0.31291 | 4.1603 | 9.884% | 10.52% | 7.107% | 1.1097 | 1.1175 | 1.0765
2010-05-25 | 25 | 28.7576 | 11.4893 | 40.247 | 2.8177 | 0.76558 | 0.2992 | 3.8825 | 9.647% | 10.26% | 6.936% | 1.1068 | 1.1144 | 1.0745
2010-05-25 | 26 | 27.4636 | 10.8146 | 38.2783 | 2.5488 | 0.76558 | 0.28457 | 3.599 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-05-25 | 27 | 27.4136 | 11.1962 | 38.6098 | 2.5932 | 0.76558 | 0.28703 | 3.6458 | 9.443% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-05-25 | 28 | 27.3716 | 11.2222 | 38.5938 | 2.591 | 0.76558 | 0.28691 | 3.6435 | 9.441% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-05-25 | 29 | 27.3715 | 10.8779 | 38.2494 | 2.545 | 0.76558 | 0.28435 | 3.5949 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-05-25 | 30 | 26.7955 | 10.3048 | 37.1003 | 2.3944 | 0.76558 | 0.27581 | 3.4357 | 9.261% | 9.853% | 6.658% | 1.1021 | 1.1093 | 1.0713
2010-05-25 | 31 | 28.0534 | 10.2564 | 38.3099 | 2.553 | 0.76558 | 0.2848 | 3.6034 | 9.406% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2010-05-25 | 32 | 28.136 | 10.468 | 38.604 | 2.5924 | 0.76558 | 0.28699 | 3.6449 | 9.442% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-05-25 | 33 | 28.8971 | 10.9179 | 39.815 | 2.7576 | 0.76558 | 0.29599 | 3.8192 | 9.592% | 10.21% | 6.897% | 1.1061 | 1.1137 | 1.0741
2010-05-25 | 34 | 30.2446 | 11.5711 | 41.8157 | 3.0417 | 0.76558 | 0.31086 | 4.1181 | 9.848% | 10.48% | 7.081% | 1.1092 | 1.1171 | 1.0762
2010-05-25 | 35 | 31.5803 | 12.6933 | 44.2736 | 3.4098 | 0.76558 | 0.32914 | 4.5045 | 10.17% | 10.83% | 7.315% | 1.1133 | 1.1214 | 1.0789
2010-05-25 | 36 | 34.4995 | 14.2183 | 48.7178 | 4.1287 | 0.76558 | 0.36217 | 5.2564 | 10.79% | 11.48% | 7.758% | 1.1209 | 1.1297 | 1.0841
2010-05-25 | 37 | 35.7197 | 14.1333 | 49.853 | 4.3233 | 0.76558 | 0.37061 | 5.4595 | 10.95% | 11.65% | 7.874% | 1.123 | 1.1319 | 1.0855
2010-05-25 | 38 | 36.1515 | 13.6849 | 49.8363 | 4.3204 | 0.76558 | 0.37049 | 5.4565 | 10.95% | 11.65% | 7.872% | 1.1229 | 1.1319 | 1.0854
2010-05-25 | 39 | 35.8785 | 13.1812 | 49.0597 | 4.1868 | 0.76558 | 0.36472 | 5.3171 | 10.84% | 11.53% | 7.793% | 1.1216 | 1.1303 | 1.0845
2010-05-25 | 40 | 35.1182 | 12.6401 | 47.7583 | 3.9676 | 0.76558 | 0.35504 | 5.0883 | 10.65% | 11.34% | 7.66% | 1.1192 | 1.1279 | 1.083
2010-05-25 | 41 | 35.0471 | 12.2384 | 47.2855 | 3.8895 | 0.76558 | 0.35153 | 5.0066 | 10.59% | 11.27% | 7.613% | 1.1184 | 1.127 | 1.0824
2010-05-25 | 42 | 34.7875 | 11.832 | 46.6194 | 3.7807 | 0.76558 | 0.34657 | 4.8928 | 10.5% | 11.17% | 7.546% | 1.1173 | 1.1257 | 1.0816
2010-05-25 | 43 | 33.3943 | 11.0823 | 44.4765 | 3.4411 | 0.76558 | 0.33064 | 4.5373 | 10.2% | 10.85% | 7.335% | 1.1136 | 1.1218 | 1.0792
2010-05-25 | 44 | 31.6994 | 10.2564 | 41.9558 | 3.0621 | 0.76558 | 0.3119 | 4.1396 | 9.867% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-05-25 | 45 | 28.5979 | 9.1596 | 37.7575 | 2.4799 | 0.76558 | 0.28069 | 3.5262 | 9.339% | 9.937% | 6.715% | 1.103 | 1.1103 | 1.072
2010-05-25 | 46 | 26.0563 | 8.1424 | 34.1987 | 2.0345 | 0.76558 | 0.25424 | 3.0543 | 8.931% | 9.503% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-05-25 | 47 | 25.4667 | 8.4438 | 33.9105 | 2.0003 | 0.76558 | 0.25209 | 3.018 | 8.9% | 9.47% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-05-25 | 48 | 24.5908 | 8.8413 | 33.4321 | 1.9443 | 0.76558 | 0.24854 | 2.9584 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-05-26 | 1 | 23.1273 | 8.0156 | 31.143 | 1.6872 | 0.76558 | 0.23152 | 2.6843 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-05-26 | 2 | 24.1621 | 7.706 | 31.868 | 1.7666 | 0.76558 | 0.23691 | 2.7691 | 8.689% | 9.245% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-05-26 | 3 | 23.0966 | 7.2668 | 30.3634 | 1.6037 | 0.76558 | 0.22573 | 2.5951 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-05-26 | 4 | 22.1788 | 6.9455 | 29.1243 | 1.4755 | 0.76558 | 0.21651 | 2.4576 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-05-26 | 5 | 21.4736 | 6.8596 | 28.3332 | 1.3965 | 0.76558 | 0.21063 | 2.3727 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-05-26 | 6 | 21.0995 | 6.5137 | 27.6132 | 1.3264 | 0.76558 | 0.20528 | 2.2972 | 8.319% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2010-05-26 | 7 | 21.4017 | 6.5379 | 27.9396 | 1.3579 | 0.76558 | 0.20771 | 2.3312 | 8.344% | 8.878% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-05-26 | 8 | 21.4294 | 6.5468 | 27.9761 | 1.3615 | 0.76558 | 0.20798 | 2.335 | 8.347% | 8.881% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-05-26 | 9 | 21.1992 | 6.7065 | 27.9057 | 1.3546 | 0.76558 | 0.20745 | 2.3277 | 8.341% | 8.875% | 5.997% | 1.091 | 1.0974 | 1.0638
2010-05-26 | 10 | 21.4729 | 6.8248 | 28.2977 | 1.393 | 0.76558 | 0.21037 | 2.3689 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-05-26 | 11 | 22.4338 | 7.1158 | 29.5495 | 1.5189 | 0.76558 | 0.21967 | 2.5042 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-05-26 | 12 | 23.3692 | 7.5549 | 30.9241 | 1.6635 | 0.76558 | 0.22989 | 2.659 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-05-26 | 13 | 25.1492 | 8.4547 | 33.6039 | 1.9643 | 0.76558 | 0.24982 | 2.9797 | 8.867% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2010-05-26 | 14 | 28.0969 | 10.0082 | 38.1051 | 2.5258 | 0.76558 | 0.28328 | 3.5747 | 9.381% | 9.981% | 6.745% | 1.1035 | 1.1109 | 1.0723
2010-05-26 | 15 | 31.8909 | 12.1853 | 44.0762 | 3.3794 | 0.76558 | 0.32767 | 4.4727 | 10.15% | 10.8% | 7.296% | 1.1129 | 1.121 | 1.0787
2010-05-26 | 16 | 34.2875 | 13.3893 | 47.6768 | 3.9541 | 0.76558 | 0.35444 | 5.0741 | 10.64% | 11.32% | 7.652% | 1.1191 | 1.1277 | 1.0829
2010-05-26 | 17 | 35.8655 | 14.1026 | 49.968 | 4.3433 | 0.76558 | 0.37147 | 5.4803 | 10.97% | 11.67% | 7.886% | 1.1232 | 1.1321 | 1.0856
2010-05-26 | 18 | 36.6412 | 14.2412 | 50.8824 | 4.5037 | 0.76558 | 0.37827 | 5.6475 | 11.1% | 11.81% | 7.98% | 1.1248 | 1.1339 | 1.0867
2010-05-26 | 19 | 36.4248 | 14.0949 | 50.5197 | 4.4397 | 0.76558 | 0.37557 | 5.5809 | 11.05% | 11.75% | 7.943% | 1.1242 | 1.1332 | 1.0863
2010-05-26 | 20 | 35.7918 | 13.6156 | 49.4074 | 4.2464 | 0.76558 | 0.3673 | 5.3793 | 10.89% | 11.58% | 7.828% | 1.1222 | 1.131 | 1.0849
2010-05-26 | 21 | 36.5818 | 13.3899 | 49.9716 | 4.3439 | 0.76558 | 0.3715 | 5.481 | 10.97% | 11.67% | 7.886% | 1.1232 | 1.1321 | 1.0856
2010-05-26 | 22 | 35.6228 | 13.0332 | 48.656 | 4.1182 | 0.76558 | 0.36171 | 5.2455 | 10.78% | 11.47% | 7.751% | 1.1208 | 1.1296 | 1.084
2010-05-26 | 23 | 33.439 | 12.4668 | 45.9058 | 3.6658 | 0.76558 | 0.34127 | 4.7727 | 10.4% | 11.06% | 7.475% | 1.116 | 1.1244 | 1.0808
2010-05-26 | 24 | 32.0607 | 12.1626 | 44.2233 | 3.402 | 0.76558 | 0.32876 | 4.4964 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-05-26 | 25 | 30.1044 | 11.6223 | 41.7267 | 3.0287 | 0.76558 | 0.3102 | 4.1045 | 9.837% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-05-26 | 26 | 28.942 | 10.5254 | 39.4674 | 2.7096 | 0.76558 | 0.29341 | 3.7686 | 9.549% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-05-26 | 27 | 29.1436 | 10.6837 | 39.8273 | 2.7593 | 0.76558 | 0.29608 | 3.8209 | 9.594% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-05-26 | 28 | 29.3741 | 10.9601 | 40.3342 | 2.83 | 0.76558 | 0.29985 | 3.8954 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-05-26 | 29 | 28.2818 | 10.3226 | 38.6044 | 2.5924 | 0.76558 | 0.28699 | 3.645 | 9.442% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-05-26 | 30 | 27.966 | 9.9496 | 37.9155 | 2.5007 | 0.76558 | 0.28187 | 3.5482 | 9.358% | 9.957% | 6.729% | 1.1032 | 1.1106 | 1.0721
2010-05-26 | 31 | 30.1499 | 9.954 | 40.104 | 2.7978 | 0.76558 | 0.29814 | 3.8615 | 9.629% | 10.24% | 6.923% | 1.1065 | 1.1141 | 1.0744
2010-05-26 | 32 | 30.5373 | 9.9535 | 40.4907 | 2.852 | 0.76558 | 0.30101 | 3.9186 | 9.678% | 10.3% | 6.958% | 1.1071 | 1.1148 | 1.0748
2010-05-26 | 33 | 31.0968 | 10.4373 | 41.5341 | 3.0009 | 0.76558 | 0.30877 | 4.0752 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-05-26 | 34 | 32.0587 | 11.1497 | 43.2084 | 3.2477 | 0.76558 | 0.32122 | 4.3345 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-05-26 | 35 | 33.1362 | 12.5732 | 45.7094 | 3.6345 | 0.76558 | 0.33981 | 4.7399 | 10.37% | 11.03% | 7.456% | 1.1157 | 1.124 | 1.0806
2010-05-26 | 36 | 36.0921 | 14.288 | 50.3801 | 4.4152 | 0.76558 | 0.37453 | 5.5553 | 11.03% | 11.73% | 7.928% | 1.1239 | 1.1329 | 1.0861
2010-05-26 | 37 | 37.7155 | 14.5164 | 52.2319 | 4.7458 | 0.76558 | 0.3883 | 5.8997 | 11.3% | 12.02% | 8.121% | 1.1273 | 1.1366 | 1.0884
2010-05-26 | 38 | 38.1457 | 14.2178 | 52.3635 | 4.7697 | 0.76558 | 0.38928 | 5.9246 | 11.31% | 12.04% | 8.135% | 1.1276 | 1.1369 | 1.0886
2010-05-26 | 39 | 37.2118 | 13.8248 | 51.0365 | 4.531 | 0.76558 | 0.37941 | 5.676 | 11.12% | 11.83% | 7.996% | 1.1251 | 1.1342 | 1.0869
2010-05-26 | 40 | 36.7388 | 13.4603 | 50.1992 | 4.3836 | 0.76558 | 0.37319 | 5.5223 | 11% | 11.7% | 7.91% | 1.1236 | 1.1326 | 1.0859
2010-05-26 | 41 | 37.0849 | 13.0562 | 50.1411 | 4.3734 | 0.76558 | 0.37275 | 5.5118 | 10.99% | 11.7% | 7.904% | 1.1235 | 1.1325 | 1.0858
2010-05-26 | 42 | 36.9282 | 12.4976 | 49.4257 | 4.2495 | 0.76558 | 0.36744 | 5.3825 | 10.89% | 11.59% | 7.83% | 1.1222 | 1.1311 | 1.085
2010-05-26 | 43 | 35.3618 | 11.9412 | 47.303 | 3.8923 | 0.76558 | 0.35166 | 5.0096 | 10.59% | 11.27% | 7.615% | 1.1184 | 1.127 | 1.0824
2010-05-26 | 44 | 33.4219 | 11.2479 | 44.6698 | 3.4711 | 0.76558 | 0.33208 | 4.5687 | 10.23% | 10.88% | 7.354% | 1.1139 | 1.1221 | 1.0794
2010-05-26 | 45 | 29.9038 | 10.0167 | 39.9204 | 2.7722 | 0.76558 | 0.29677 | 3.8346 | 9.605% | 10.22% | 6.906% | 1.1063 | 1.1138 | 1.0742
2010-05-26 | 46 | 27.3906 | 8.9294 | 36.32 | 2.2947 | 0.76558 | 0.27001 | 3.3303 | 9.169% | 9.756% | 6.593% | 1.1009 | 1.1081 | 1.0706
2010-05-26 | 47 | 27.0309 | 9.039 | 36.0699 | 2.2632 | 0.76558 | 0.26815 | 3.2969 | 9.14% | 9.725% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-05-26 | 48 | 26.0425 | 9.4938 | 35.5363 | 2.1967 | 0.76558 | 0.26418 | 3.2265 | 9.079% | 9.661% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-05-27 | 1 | 24.5173 | 8.4796 | 32.997 | 1.894 | 0.76558 | 0.2453 | 2.9049 | 8.804% | 9.367% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-05-27 | 2 | 25.5245 | 8.2541 | 33.7787 | 1.9848 | 0.76558 | 0.25111 | 3.0015 | 8.886% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2010-05-27 | 3 | 24.6613 | 7.8563 | 32.5177 | 1.8394 | 0.76558 | 0.24174 | 2.8467 | 8.754% | 9.315% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-05-27 | 4 | 23.4842 | 7.594 | 31.0782 | 1.6801 | 0.76558 | 0.23104 | 2.6768 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-05-27 | 5 | 23.0083 | 7.4032 | 30.4116 | 1.6088 | 0.76558 | 0.22608 | 2.6005 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-05-27 | 6 | 22.923 | 7.2901 | 30.2132 | 1.5879 | 0.76558 | 0.22461 | 2.5781 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-05-27 | 7 | 22.7924 | 7.1393 | 29.9317 | 1.5585 | 0.76558 | 0.22252 | 2.5466 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-05-27 | 8 | 22.5922 | 7.041 | 29.6332 | 1.5275 | 0.76558 | 0.2203 | 2.5134 | 8.482% | 9.025% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-05-27 | 9 | 22.6348 | 7.1854 | 29.8202 | 1.5469 | 0.76558 | 0.22169 | 2.5341 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-05-27 | 10 | 22.7788 | 7.1975 | 29.9763 | 1.5631 | 0.76558 | 0.22285 | 2.5515 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-05-27 | 11 | 23.627 | 7.5153 | 31.1423 | 1.6871 | 0.76558 | 0.23152 | 2.6842 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-05-27 | 12 | 24.4449 | 7.8597 | 32.3046 | 1.8154 | 0.76558 | 0.24016 | 2.8211 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-05-27 | 13 | 26.1545 | 8.9443 | 35.0988 | 2.143 | 0.76558 | 0.26093 | 3.1695 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-05-27 | 14 | 29.7321 | 10.4829 | 40.2149 | 2.8133 | 0.76558 | 0.29896 | 3.8778 | 9.643% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-05-27 | 15 | 33.8573 | 12.8644 | 46.7217 | 3.7973 | 0.76558 | 0.34734 | 4.9102 | 10.51% | 11.18% | 7.556% | 1.1174 | 1.1259 | 1.0817
2010-05-27 | 16 | 35.8801 | 14.0965 | 49.9767 | 4.3448 | 0.76558 | 0.37153 | 5.4819 | 10.97% | 11.67% | 7.887% | 1.1232 | 1.1321 | 1.0856
2010-05-27 | 17 | 37.3446 | 15.1469 | 52.4916 | 4.7931 | 0.76558 | 0.39023 | 5.9489 | 11.33% | 12.06% | 8.148% | 1.1278 | 1.1371 | 1.0887
2010-05-27 | 18 | 37.7466 | 15.4458 | 53.1924 | 4.9219 | 0.76558 | 0.39544 | 6.0829 | 11.44% | 12.17% | 8.222% | 1.1291 | 1.1385 | 1.0896
2010-05-27 | 19 | 37.9481 | 15.1746 | 53.1227 | 4.909 | 0.76558 | 0.39492 | 6.0695 | 11.43% | 12.16% | 8.215% | 1.129 | 1.1384 | 1.0895
2010-05-27 | 20 | 36.9276 | 14.7237 | 51.6513 | 4.6408 | 0.76558 | 0.38398 | 5.7904 | 11.21% | 11.93% | 8.06% | 1.1263 | 1.1354 | 1.0877
2010-05-27 | 21 | 37.2445 | 14.6716 | 51.9161 | 4.6886 | 0.76558 | 0.38595 | 5.8401 | 11.25% | 11.97% | 8.088% | 1.1267 | 1.136 | 1.088
2010-05-27 | 22 | 36.4557 | 14.4018 | 50.8575 | 4.4993 | 0.76558 | 0.37808 | 5.6429 | 11.1% | 11.81% | 7.978% | 1.1248 | 1.1339 | 1.0867
2010-05-27 | 23 | 34.6599 | 13.9573 | 48.6172 | 4.1116 | 0.76558 | 0.36143 | 5.2386 | 10.78% | 11.46% | 7.747% | 1.1208 | 1.1295 | 1.084
2010-05-27 | 24 | 33.3099 | 13.5983 | 46.9083 | 3.8277 | 0.76558 | 0.34872 | 4.942 | 10.54% | 11.21% | 7.575% | 1.1178 | 1.1262 | 1.082
2010-05-27 | 25 | 31.053 | 13.3374 | 44.3904 | 3.4278 | 0.76558 | 0.33 | 4.5234 | 10.19% | 10.84% | 7.327% | 1.1135 | 1.1216 | 1.0791
2010-05-27 | 26 | 29.3596 | 12.7293 | 42.0889 | 3.0816 | 0.76558 | 0.31289 | 4.16 | 9.884% | 10.52% | 7.107% | 1.1097 | 1.1175 | 1.0765
2010-05-27 | 27 | 29.6751 | 13.0782 | 42.7533 | 3.1796 | 0.76558 | 0.31783 | 4.263 | 9.971% | 10.61% | 7.169% | 1.1108 | 1.1187 | 1.0772
2010-05-27 | 28 | 29.5316 | 13.241 | 42.7727 | 3.1825 | 0.76558 | 0.31798 | 4.266 | 9.974% | 10.61% | 7.171% | 1.1108 | 1.1187 | 1.0773
2010-05-27 | 29 | 29.0713 | 12.7357 | 41.807 | 3.0404 | 0.76558 | 0.3108 | 4.1168 | 9.847% | 10.48% | 7.08% | 1.1092 | 1.117 | 1.0762
2010-05-27 | 30 | 28.4396 | 12.2566 | 40.6962 | 2.881 | 0.76558 | 0.30254 | 3.9491 | 9.704% | 10.32% | 6.977% | 1.1075 | 1.1151 | 1.075
2010-05-27 | 31 | 30.1493 | 12.3616 | 42.5109 | 3.1437 | 0.76558 | 0.31603 | 4.2253 | 9.939% | 10.58% | 7.146% | 1.1104 | 1.1183 | 1.077
2010-05-27 | 32 | 31.1401 | 12.352 | 43.4922 | 3.2905 | 0.76558 | 0.32333 | 4.3794 | 10.07% | 10.71% | 7.24% | 1.112 | 1.12 | 1.078
2010-05-27 | 33 | 32.0336 | 12.6239 | 44.6576 | 3.4692 | 0.76558 | 0.33199 | 4.5667 | 10.23% | 10.88% | 7.353% | 1.1139 | 1.1221 | 1.0794
2010-05-27 | 34 | 32.7905 | 12.917 | 45.7075 | 3.6342 | 0.76558 | 0.33979 | 4.7396 | 10.37% | 11.03% | 7.456% | 1.1157 | 1.124 | 1.0806
2010-05-27 | 35 | 33.6963 | 14.0639 | 47.7602 | 3.968 | 0.76558 | 0.35506 | 5.0886 | 10.65% | 11.34% | 7.661% | 1.1193 | 1.1279 | 1.083
2010-05-27 | 36 | 37.0684 | 15.397 | 52.4654 | 4.7883 | 0.76558 | 0.39003 | 5.9439 | 11.33% | 12.05% | 8.146% | 1.1278 | 1.1371 | 1.0887
2010-05-27 | 37 | 38.5921 | 15.133 | 53.7251 | 5.021 | 0.76558 | 0.3994 | 6.186 | 11.51% | 12.25% | 8.279% | 1.1301 | 1.1396 | 1.0903
2010-05-27 | 38 | 38.8792 | 14.8767 | 53.7559 | 5.0267 | 0.76558 | 0.39963 | 6.1919 | 11.52% | 12.26% | 8.282% | 1.1302 | 1.1397 | 1.0903
2010-05-27 | 39 | 38.2764 | 14.4497 | 52.7261 | 4.836 | 0.76558 | 0.39197 | 5.9935 | 11.37% | 12.09% | 8.173% | 1.1283 | 1.1376 | 1.089
2010-05-27 | 40 | 37.3413 | 13.8791 | 51.2204 | 4.5637 | 0.76558 | 0.38078 | 5.7101 | 11.15% | 11.86% | 8.015% | 1.1255 | 1.1346 | 1.0871
2010-05-27 | 41 | 38.045 | 13.3209 | 51.3659 | 4.5897 | 0.76558 | 0.38186 | 5.7371 | 11.17% | 11.88% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-05-27 | 42 | 37.8305 | 12.8973 | 50.7278 | 4.4764 | 0.76558 | 0.37712 | 5.6191 | 11.08% | 11.79% | 7.964% | 1.1246 | 1.1336 | 1.0865
2010-05-27 | 43 | 35.805 | 12.193 | 47.998 | 4.0076 | 0.76558 | 0.35682 | 5.13 | 10.69% | 11.37% | 7.685% | 1.1197 | 1.1283 | 1.0832
2010-05-27 | 44 | 33.9253 | 11.3826 | 45.3079 | 3.5709 | 0.76558 | 0.33682 | 4.6733 | 10.31% | 10.97% | 7.416% | 1.115 | 1.1233 | 1.0801
2010-05-27 | 45 | 30.361 | 10.1535 | 40.5145 | 2.8553 | 0.76558 | 0.30119 | 3.9221 | 9.681% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-05-27 | 46 | 27.7798 | 8.9544 | 36.7343 | 2.3473 | 0.76558 | 0.27309 | 3.386 | 9.218% | 9.808% | 6.627% | 1.1015 | 1.1087 | 1.071
2010-05-27 | 47 | 27.478 | 9.168 | 36.646 | 2.3361 | 0.76558 | 0.27243 | 3.3741 | 9.207% | 9.797% | 6.62% | 1.1014 | 1.1086 | 1.0709
2010-05-27 | 48 | 26.372 | 9.6032 | 35.9752 | 2.2513 | 0.76558 | 0.26744 | 3.2844 | 9.13% | 9.714% | 6.564% | 1.1005 | 1.1076 | 1.0703
2010-05-28 | 1 | 24.7059 | 8.6602 | 33.366 | 1.9366 | 0.76558 | 0.24805 | 2.9502 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-05-28 | 2 | 25.5826 | 8.4147 | 33.9972 | 2.0106 | 0.76558 | 0.25274 | 3.0289 | 8.909% | 9.479% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-05-28 | 3 | 25.0785 | 8.0502 | 33.1287 | 1.9092 | 0.76558 | 0.24628 | 2.921 | 8.817% | 9.382% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-05-28 | 4 | 24.2874 | 7.8158 | 32.1032 | 1.7928 | 0.76558 | 0.23866 | 2.797 | 8.713% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-05-28 | 5 | 23.5831 | 7.6598 | 31.2428 | 1.698 | 0.76558 | 0.23226 | 2.6958 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-05-28 | 6 | 23.0949 | 7.3839 | 30.4788 | 1.616 | 0.76558 | 0.22658 | 2.6081 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-05-28 | 7 | 23.2834 | 7.2034 | 30.4868 | 1.6168 | 0.76558 | 0.22664 | 2.609 | 8.558% | 9.106% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-05-28 | 8 | 23.3379 | 7.1605 | 30.4984 | 1.618 | 0.76558 | 0.22673 | 2.6103 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-05-28 | 9 | 23.3549 | 7.3437 | 30.6986 | 1.6393 | 0.76558 | 0.22822 | 2.6331 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-05-28 | 10 | 23.1811 | 7.5281 | 30.7092 | 1.6405 | 0.76558 | 0.2283 | 2.6344 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-05-28 | 11 | 23.6482 | 7.7215 | 31.3698 | 1.7118 | 0.76558 | 0.23321 | 2.7106 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2010-05-28 | 12 | 24.8318 | 8.1872 | 33.0189 | 1.8965 | 0.76558 | 0.24547 | 2.9076 | 8.806% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2010-05-28 | 13 | 26.9689 | 9.181 | 36.1499 | 2.2733 | 0.76558 | 0.26874 | 3.3076 | 9.15% | 9.735% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-05-28 | 14 | 30.2781 | 10.916 | 41.1942 | 2.9519 | 0.76558 | 0.30624 | 4.0238 | 9.768% | 10.39% | 7.023% | 1.1083 | 1.116 | 1.0755
2010-05-28 | 15 | 34.0201 | 13.1659 | 47.186 | 3.8731 | 0.76558 | 0.35079 | 4.9895 | 10.57% | 11.25% | 7.603% | 1.1182 | 1.1268 | 1.0823
2010-05-28 | 16 | 36.368 | 14.1685 | 50.5365 | 4.4427 | 0.76558 | 0.37569 | 5.584 | 11.05% | 11.76% | 7.944% | 1.1242 | 1.1332 | 1.0863
2010-05-28 | 17 | 38.1125 | 14.9871 | 53.0996 | 4.9048 | 0.76558 | 0.39475 | 6.0651 | 11.42% | 12.15% | 8.212% | 1.1289 | 1.1383 | 1.0895
2010-05-28 | 18 | 38.6304 | 15.3036 | 53.9339 | 5.0601 | 0.76558 | 0.40095 | 6.2266 | 11.54% | 12.28% | 8.301% | 1.1305 | 1.14 | 1.0905
2010-05-28 | 19 | 38.8386 | 15.3359 | 54.1745 | 5.1053 | 0.76558 | 0.40274 | 6.2737 | 11.58% | 12.32% | 8.326% | 1.131 | 1.1405 | 1.0908
2010-05-28 | 20 | 38.014 | 14.959 | 52.973 | 4.8814 | 0.76558 | 0.39381 | 6.0408 | 11.4% | 12.13% | 8.199% | 1.1287 | 1.1381 | 1.0893
2010-05-28 | 21 | 38.5246 | 14.7198 | 53.2445 | 4.9316 | 0.76558 | 0.39583 | 6.093 | 11.44% | 12.18% | 8.228% | 1.1292 | 1.1386 | 1.0897
2010-05-28 | 22 | 37.5182 | 14.2762 | 51.7944 | 4.6666 | 0.76558 | 0.38505 | 5.8172 | 11.23% | 11.95% | 8.075% | 1.1265 | 1.1357 | 1.0878
2010-05-28 | 23 | 35.293 | 13.5667 | 48.8597 | 4.1528 | 0.76558 | 0.36323 | 5.2816 | 10.81% | 11.5% | 7.772% | 1.1212 | 1.13 | 1.0843
2010-05-28 | 24 | 33.5106 | 13.4197 | 46.9303 | 3.8313 | 0.76558 | 0.34889 | 4.9457 | 10.54% | 11.21% | 7.577% | 1.1178 | 1.1263 | 1.082
2010-05-28 | 25 | 31.8857 | 12.9374 | 44.8231 | 3.4949 | 0.76558 | 0.33322 | 4.5937 | 10.25% | 10.9% | 7.369% | 1.1142 | 1.1224 | 1.0795
2010-05-28 | 26 | 30.6226 | 12.1763 | 42.7989 | 3.1864 | 0.76558 | 0.31817 | 4.2701 | 9.977% | 10.62% | 7.174% | 1.1108 | 1.1188 | 1.0773
2010-05-28 | 27 | 31.3264 | 12.5614 | 43.8878 | 3.3506 | 0.76558 | 0.32627 | 4.4424 | 10.12% | 10.77% | 7.278% | 1.1126 | 1.1207 | 1.0785
2010-05-28 | 28 | 31.7853 | 12.841 | 44.6263 | 3.4643 | 0.76558 | 0.33176 | 4.5616 | 10.22% | 10.88% | 7.35% | 1.1139 | 1.122 | 1.0793
2010-05-28 | 29 | 31.0391 | 12.4458 | 43.4849 | 3.2894 | 0.76558 | 0.32327 | 4.3782 | 10.07% | 10.71% | 7.239% | 1.112 | 1.12 | 1.078
2010-05-28 | 30 | 31.0381 | 12.1273 | 43.1654 | 3.2412 | 0.76558 | 0.3209 | 4.3277 | 10.03% | 10.67% | 7.209% | 1.1114 | 1.1194 | 1.0777
2010-05-28 | 31 | 32.4333 | 12.3957 | 44.829 | 3.4959 | 0.76558 | 0.33326 | 4.5947 | 10.25% | 10.91% | 7.369% | 1.1142 | 1.1224 | 1.0796
2010-05-28 | 32 | 32.6197 | 12.5154 | 45.1351 | 3.5438 | 0.76558 | 0.33554 | 4.6449 | 10.29% | 10.95% | 7.399% | 1.1147 | 1.123 | 1.0799
2010-05-28 | 33 | 32.3627 | 12.8831 | 45.2459 | 3.5612 | 0.76558 | 0.33636 | 4.6631 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-05-28 | 34 | 32.9357 | 13.2856 | 46.2213 | 3.7164 | 0.76558 | 0.34361 | 4.8256 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.125 | 1.0812
2010-05-28 | 35 | 33.5379 | 14.1293 | 47.6672 | 3.9525 | 0.76558 | 0.35436 | 5.0725 | 10.64% | 11.32% | 7.651% | 1.1191 | 1.1277 | 1.0829
2010-05-28 | 36 | 36.1187 | 15.1064 | 51.2251 | 4.5646 | 0.76558 | 0.38081 | 5.711 | 11.15% | 11.86% | 8.016% | 1.1255 | 1.1346 | 1.0871
2010-05-28 | 37 | 37.2822 | 15.0566 | 52.3389 | 4.7652 | 0.76558 | 0.38909 | 5.9199 | 11.31% | 12.03% | 8.132% | 1.1275 | 1.1368 | 1.0885
2010-05-28 | 38 | 37.4381 | 14.4883 | 51.9265 | 4.6904 | 0.76558 | 0.38603 | 5.842 | 11.25% | 11.97% | 8.089% | 1.1268 | 1.136 | 1.088
2010-05-28 | 39 | 36.4338 | 13.9704 | 50.4042 | 4.4194 | 0.76558 | 0.37471 | 5.5597 | 11.03% | 11.74% | 7.931% | 1.124 | 1.133 | 1.0861
2010-05-28 | 40 | 36.0486 | 13.42 | 49.4686 | 4.2569 | 0.76558 | 0.36776 | 5.3902 | 10.9% | 11.59% | 7.834% | 1.1223 | 1.1311 | 1.085
2010-05-28 | 41 | 36.5235 | 13.2049 | 49.7284 | 4.3017 | 0.76558 | 0.36969 | 5.437 | 10.93% | 11.63% | 7.861% | 1.1228 | 1.1316 | 1.0853
2010-05-28 | 42 | 36.2647 | 12.7643 | 49.029 | 4.1816 | 0.76558 | 0.36449 | 5.3116 | 10.83% | 11.53% | 7.789% | 1.1215 | 1.1303 | 1.0845
2010-05-28 | 43 | 34.1837 | 12.2047 | 46.3884 | 3.7433 | 0.76558 | 0.34486 | 4.8537 | 10.46% | 11.13% | 7.523% | 1.1169 | 1.1253 | 1.0814
2010-05-28 | 44 | 32.4039 | 11.5624 | 43.9663 | 3.3626 | 0.76558 | 0.32685 | 4.455 | 10.13% | 10.78% | 7.285% | 1.1128 | 1.1208 | 1.0786
2010-05-28 | 45 | 29.3419 | 10.4925 | 39.8344 | 2.7603 | 0.76558 | 0.29613 | 3.822 | 9.595% | 10.21% | 6.899% | 1.1061 | 1.1137 | 1.0741
2010-05-28 | 46 | 26.5421 | 9.324 | 35.8662 | 2.2377 | 0.76558 | 0.26663 | 3.2699 | 9.117% | 9.701% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-05-28 | 47 | 26.3262 | 9.5698 | 35.896 | 2.2414 | 0.76558 | 0.26686 | 3.2739 | 9.12% | 9.704% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-05-28 | 48 | 25.308 | 10.0543 | 35.3623 | 2.1753 | 0.76558 | 0.26289 | 3.2037 | 9.06% | 9.64% | 6.514% | 1.0996 | 1.1067 | 1.0697
2010-05-29 | 1 | 23.5569 | 9.1571 | 32.714 | 1.8617 | 0.76558 | 0.2432 | 2.8704 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-05-29 | 2 | 24.8931 | 9.0061 | 33.8992 | 1.999 | 0.76558 | 0.25201 | 3.0166 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-05-29 | 3 | 23.8576 | 8.5192 | 32.3769 | 1.8235 | 0.76558 | 0.24069 | 2.8298 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2010-05-29 | 4 | 22.7062 | 8.1399 | 30.8461 | 1.6551 | 0.76558 | 0.22931 | 2.65 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-05-29 | 5 | 21.7881 | 7.7062 | 29.4943 | 1.5133 | 0.76558 | 0.21926 | 2.4981 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-05-29 | 6 | 21.5868 | 7.5004 | 29.0872 | 1.4718 | 0.76558 | 0.21624 | 2.4536 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-05-29 | 7 | 21.8029 | 7.3219 | 29.1248 | 1.4756 | 0.76558 | 0.21652 | 2.4577 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-05-29 | 8 | 21.7584 | 7.3278 | 29.0862 | 1.4717 | 0.76558 | 0.21623 | 2.4535 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-05-29 | 9 | 21.6442 | 7.3767 | 29.0209 | 1.4651 | 0.76558 | 0.21574 | 2.4464 | 8.43% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-05-29 | 10 | 21.7309 | 7.5161 | 29.247 | 1.488 | 0.76558 | 0.21743 | 2.471 | 8.449% | 8.989% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-05-29 | 11 | 22.4922 | 7.7943 | 30.2864 | 1.5956 | 0.76558 | 0.22515 | 2.5864 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-05-29 | 12 | 23.225 | 8.4167 | 31.6417 | 1.7416 | 0.76558 | 0.23523 | 2.7424 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-05-29 | 13 | 24.7787 | 9.4046 | 34.1833 | 2.0326 | 0.76558 | 0.25412 | 3.0523 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2010-05-29 | 14 | 27.8519 | 10.7458 | 38.5977 | 2.5915 | 0.76558 | 0.28694 | 3.6441 | 9.441% | 10.05% | 6.788% | 1.1043 | 1.1117 | 1.0728
2010-05-29 | 15 | 31.7294 | 12.9053 | 44.6347 | 3.4656 | 0.76558 | 0.33182 | 4.563 | 10.22% | 10.88% | 7.35% | 1.1139 | 1.122 | 1.0793
2010-05-29 | 16 | 34.1694 | 14.2225 | 48.3919 | 4.0736 | 0.76558 | 0.35975 | 5.1989 | 10.74% | 11.43% | 7.725% | 1.1204 | 1.1291 | 1.0837
2010-05-29 | 17 | 35.3896 | 15.3493 | 50.7389 | 4.4783 | 0.76558 | 0.3772 | 5.6211 | 11.08% | 11.79% | 7.965% | 1.1246 | 1.1336 | 1.0865
2010-05-29 | 18 | 35.6918 | 15.7052 | 51.397 | 4.5953 | 0.76558 | 0.38209 | 5.7429 | 11.17% | 11.89% | 8.034% | 1.1258 | 1.1349 | 1.0874
2010-05-29 | 19 | 35.6623 | 15.5009 | 51.1632 | 4.5535 | 0.76558 | 0.38035 | 5.6995 | 11.14% | 11.85% | 8.01% | 1.1254 | 1.1345 | 1.0871
2010-05-29 | 20 | 34.8738 | 15.0339 | 49.9078 | 4.3328 | 0.76558 | 0.37102 | 5.4694 | 10.96% | 11.66% | 7.88% | 1.1231 | 1.132 | 1.0855
2010-05-29 | 21 | 35.5345 | 14.5013 | 50.0358 | 4.3551 | 0.76558 | 0.37197 | 5.4926 | 10.98% | 11.68% | 7.893% | 1.1233 | 1.1322 | 1.0857
2010-05-29 | 22 | 34.9754 | 13.9238 | 48.8992 | 4.1595 | 0.76558 | 0.36352 | 5.2886 | 10.82% | 11.51% | 7.776% | 1.1213 | 1.13 | 1.0843
2010-05-29 | 23 | 33.437 | 13.0693 | 46.5063 | 3.7623 | 0.76558 | 0.34573 | 4.8737 | 10.48% | 11.15% | 7.535% | 1.1171 | 1.1255 | 1.0815
2010-05-29 | 24 | 31.7275 | 12.2954 | 44.0228 | 3.3712 | 0.76558 | 0.32727 | 4.4641 | 10.14% | 10.79% | 7.291% | 1.1128 | 1.1209 | 1.0786
2010-05-29 | 25 | 29.5306 | 11.89 | 41.4206 | 2.9845 | 0.76558 | 0.30793 | 4.058 | 9.797% | 10.42% | 7.044% | 1.1086 | 1.1164 | 1.0758
2010-05-29 | 26 | 27.3873 | 10.9648 | 38.3521 | 2.5587 | 0.76558 | 0.28511 | 3.6093 | 9.411% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-05-29 | 27 | 27.8475 | 11.249 | 39.0965 | 2.659 | 0.76558 | 0.29065 | 3.7152 | 9.503% | 10.11% | 6.832% | 1.105 | 1.1125 | 1.0733
2010-05-29 | 28 | 28.5103 | 11.314 | 39.8243 | 2.7589 | 0.76558 | 0.29606 | 3.8205 | 9.593% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-05-29 | 29 | 27.9488 | 10.6511 | 38.5999 | 2.5918 | 0.76558 | 0.28696 | 3.6444 | 9.441% | 10.05% | 6.788% | 1.1043 | 1.1117 | 1.0728
2010-05-29 | 30 | 27.9183 | 10.272 | 38.1903 | 2.5371 | 0.76558 | 0.28391 | 3.5866 | 9.391% | 9.992% | 6.752% | 1.1036 | 1.111 | 1.0724
2010-05-29 | 31 | 29.0838 | 10.2682 | 39.352 | 2.6938 | 0.76558 | 0.29255 | 3.7519 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-05-29 | 32 | 29.2865 | 10.4106 | 39.6971 | 2.7413 | 0.76558 | 0.29511 | 3.802 | 9.577% | 10.19% | 6.886% | 1.1059 | 1.1135 | 1.074
2010-05-29 | 33 | 29.485 | 10.6905 | 40.1754 | 2.8077 | 0.76558 | 0.29867 | 3.872 | 9.638% | 10.25% | 6.929% | 1.1067 | 1.1143 | 1.0745
2010-05-29 | 34 | 30.0307 | 10.9286 | 40.9593 | 2.9184 | 0.76558 | 0.3045 | 3.9884 | 9.738% | 10.36% | 7.001% | 1.1079 | 1.1156 | 1.0753
2010-05-29 | 35 | 31.0652 | 11.9851 | 43.0503 | 3.2239 | 0.76558 | 0.32004 | 4.3096 | 10.01% | 10.65% | 7.198% | 1.1112 | 1.1192 | 1.0776
2010-05-29 | 36 | 33.4495 | 13.1726 | 46.6221 | 3.7811 | 0.76558 | 0.34659 | 4.8933 | 10.5% | 11.17% | 7.546% | 1.1173 | 1.1257 | 1.0816
2010-05-29 | 37 | 34.1668 | 13.305 | 47.4718 | 3.9202 | 0.76558 | 0.35291 | 5.0387 | 10.61% | 11.29% | 7.631% | 1.1187 | 1.1273 | 1.0826
2010-05-29 | 38 | 34.8135 | 13.0276 | 47.8411 | 3.9814 | 0.76558 | 0.35566 | 5.1026 | 10.67% | 11.35% | 7.669% | 1.1194 | 1.128 | 1.0831
2010-05-29 | 39 | 34.3968 | 12.618 | 47.0149 | 3.8451 | 0.76558 | 0.34951 | 4.9602 | 10.55% | 11.23% | 7.586% | 1.1179 | 1.1264 | 1.0821
2010-05-29 | 40 | 33.5776 | 12.292 | 45.8696 | 3.66 | 0.76558 | 0.341 | 4.7666 | 10.39% | 11.06% | 7.472% | 1.116 | 1.1243 | 1.0807
2010-05-29 | 41 | 33.8674 | 12.1091 | 45.9765 | 3.6771 | 0.76558 | 0.34179 | 4.7845 | 10.41% | 11.07% | 7.482% | 1.1162 | 1.1245 | 1.0809
2010-05-29 | 42 | 33.2229 | 11.6415 | 44.8644 | 3.5014 | 0.76558 | 0.33353 | 4.6005 | 10.25% | 10.91% | 7.373% | 1.1143 | 1.1225 | 1.0796
2010-05-29 | 43 | 31.9582 | 11.1877 | 43.1459 | 3.2383 | 0.76558 | 0.32075 | 4.3246 | 10.02% | 10.66% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-05-29 | 44 | 30.5631 | 10.7552 | 41.3182 | 2.9697 | 0.76558 | 0.30716 | 4.0425 | 9.784% | 10.41% | 7.035% | 1.1084 | 1.1162 | 1.0757
2010-05-29 | 45 | 27.9343 | 9.8266 | 37.7608 | 2.4804 | 0.76558 | 0.28072 | 3.5267 | 9.34% | 9.937% | 6.715% | 1.103 | 1.1103 | 1.072
2010-05-29 | 46 | 25.5348 | 8.8233 | 34.3581 | 2.0535 | 0.76558 | 0.25542 | 3.0745 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-05-29 | 47 | 25.8503 | 9.1024 | 34.9528 | 2.1252 | 0.76558 | 0.25984 | 3.1506 | 9.014% | 9.591% | 6.481% | 1.0991 | 1.1061 | 1.0693
2010-05-29 | 48 | 25.4767 | 9.5503 | 35.027 | 2.1342 | 0.76558 | 0.26039 | 3.1602 | 9.022% | 9.6% | 6.487% | 1.0992 | 1.1062 | 1.0694
2010-05-30 | 1 | 23.9986 | 8.6428 | 32.6414 | 1.8534 | 0.76558 | 0.24266 | 2.8617 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-05-30 | 2 | 24.7618 | 8.3191 | 33.0809 | 1.9037 | 0.76558 | 0.24593 | 2.9152 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-05-30 | 3 | 23.4831 | 7.7392 | 31.2222 | 1.6958 | 0.76558 | 0.23211 | 2.6934 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-05-30 | 4 | 22.2626 | 7.3697 | 29.6323 | 1.5274 | 0.76558 | 0.22029 | 2.5133 | 8.482% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-05-30 | 5 | 21.6301 | 7.1212 | 28.7513 | 1.438 | 0.76558 | 0.21374 | 2.4173 | 8.408% | 8.946% | 6.045% | 1.0918 | 1.0982 | 1.0643
2010-05-30 | 6 | 21.2556 | 7.0531 | 28.3087 | 1.394 | 0.76558 | 0.21045 | 2.3701 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-05-30 | 7 | 20.8251 | 6.8989 | 27.724 | 1.337 | 0.76558 | 0.2061 | 2.3087 | 8.328% | 8.861% | 5.988% | 1.0908 | 1.0972 | 1.0637
2010-05-30 | 8 | 20.71 | 6.7339 | 27.4439 | 1.3102 | 0.76558 | 0.20402 | 2.2798 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-05-30 | 9 | 20.8551 | 6.7985 | 27.6536 | 1.3303 | 0.76558 | 0.20558 | 2.3014 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-05-30 | 10 | 21.5865 | 6.8734 | 28.4599 | 1.409 | 0.76558 | 0.21157 | 2.3861 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-05-30 | 11 | 21.9746 | 7.0336 | 29.0081 | 1.4638 | 0.76558 | 0.21565 | 2.445 | 8.429% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-05-30 | 12 | 22.3771 | 7.2747 | 29.6517 | 1.5294 | 0.76558 | 0.22043 | 2.5155 | 8.483% | 9.026% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-05-30 | 13 | 23.5413 | 7.775 | 31.3162 | 1.706 | 0.76558 | 0.23281 | 2.7044 | 8.636% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-05-30 | 14 | 25.121 | 8.3959 | 33.5169 | 1.9542 | 0.76558 | 0.24917 | 2.9689 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-05-30 | 15 | 26.0228 | 9.0206 | 35.0434 | 2.1362 | 0.76558 | 0.26052 | 3.1623 | 9.024% | 9.602% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-05-30 | 16 | 26.6851 | 9.6702 | 36.3553 | 2.2992 | 0.76558 | 0.27027 | 3.335 | 9.173% | 9.76% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-05-30 | 17 | 29.1838 | 11.0904 | 40.2742 | 2.8216 | 0.76558 | 0.2994 | 3.8865 | 9.65% | 10.27% | 6.938% | 1.1068 | 1.1144 | 1.0746
2010-05-30 | 18 | 31.9258 | 12.6315 | 44.5574 | 3.4536 | 0.76558 | 0.33125 | 4.5504 | 10.21% | 10.87% | 7.343% | 1.1137 | 1.1219 | 1.0792
2010-05-30 | 19 | 33.821 | 13.5634 | 47.3844 | 3.9058 | 0.76558 | 0.35226 | 5.0236 | 10.6% | 11.28% | 7.623% | 1.1186 | 1.1271 | 1.0825
2010-05-30 | 20 | 34.4109 | 13.9286 | 48.3395 | 4.0648 | 0.76558 | 0.35936 | 5.1897 | 10.74% | 11.42% | 7.719% | 1.1203 | 1.129 | 1.0836
2010-05-30 | 21 | 36.3939 | 14.2625 | 50.6564 | 4.4638 | 0.76558 | 0.37659 | 5.6059 | 11.07% | 11.77% | 7.957% | 1.1244 | 1.1335 | 1.0864
2010-05-30 | 22 | 36.2082 | 14.0919 | 50.3001 | 4.4012 | 0.76558 | 0.37394 | 5.5407 | 11.02% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-05-30 | 23 | 34.5404 | 13.4646 | 48.005 | 4.0087 | 0.76558 | 0.35687 | 5.1312 | 10.69% | 11.37% | 7.685% | 1.1197 | 1.1283 | 1.0833
2010-05-30 | 24 | 33.117 | 13.2018 | 46.3188 | 3.7321 | 0.76558 | 0.34434 | 4.842 | 10.45% | 11.12% | 7.516% | 1.1167 | 1.1251 | 1.0813
2010-05-30 | 25 | 31.8961 | 12.4672 | 44.3632 | 3.4236 | 0.76558 | 0.3298 | 4.519 | 10.19% | 10.84% | 7.324% | 1.1134 | 1.1216 | 1.079
2010-05-30 | 26 | 30.905 | 11.7054 | 42.6104 | 3.1584 | 0.76558 | 0.31677 | 4.2407 | 9.952% | 10.59% | 7.156% | 1.1105 | 1.1184 | 1.0771
2010-05-30 | 27 | 31.3659 | 11.9666 | 43.3324 | 3.2663 | 0.76558 | 0.32214 | 4.3541 | 10.05% | 10.69% | 7.225% | 1.1117 | 1.1197 | 1.0779
2010-05-30 | 28 | 31.4817 | 12.0076 | 43.4893 | 3.29 | 0.76558 | 0.3233 | 4.3789 | 10.07% | 10.71% | 7.24% | 1.112 | 1.12 | 1.078
2010-05-30 | 29 | 30.7633 | 11.4006 | 42.1639 | 3.0925 | 0.76558 | 0.31345 | 4.1716 | 9.894% | 10.53% | 7.114% | 1.1098 | 1.1177 | 1.0766
2010-05-30 | 30 | 29.4702 | 10.9101 | 40.3803 | 2.8364 | 0.76558 | 0.30019 | 3.9022 | 9.664% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-05-30 | 31 | 31.1384 | 10.8918 | 42.0302 | 3.073 | 0.76558 | 0.31246 | 4.151 | 9.876% | 10.51% | 7.101% | 1.1096 | 1.1174 | 1.0764
2010-05-30 | 32 | 31.4408 | 10.6984 | 42.1392 | 3.0889 | 0.76558 | 0.31327 | 4.1678 | 9.89% | 10.52% | 7.111% | 1.1098 | 1.1176 | 1.0766
2010-05-30 | 33 | 30.7641 | 10.8491 | 41.6132 | 3.0123 | 0.76558 | 0.30936 | 4.0872 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-05-30 | 34 | 32.243 | 11.506 | 43.749 | 3.3294 | 0.76558 | 0.32524 | 4.4202 | 10.1% | 10.75% | 7.265% | 1.1124 | 1.1205 | 1.0783
2010-05-30 | 35 | 32.931 | 12.5428 | 45.4738 | 3.5971 | 0.76558 | 0.33806 | 4.7008 | 10.34% | 11% | 7.433% | 1.1153 | 1.1236 | 1.0803
2010-05-30 | 36 | 35.3708 | 13.5367 | 48.9075 | 4.1609 | 0.76558 | 0.36358 | 5.29 | 10.82% | 11.51% | 7.777% | 1.1213 | 1.1301 | 1.0843
2010-05-30 | 37 | 36.0616 | 13.5079 | 49.5695 | 4.2743 | 0.76558 | 0.36851 | 5.4084 | 10.91% | 11.61% | 7.845% | 1.1225 | 1.1313 | 1.0851
2010-05-30 | 38 | 35.6873 | 13.1278 | 48.8152 | 4.1452 | 0.76558 | 0.3629 | 5.2737 | 10.8% | 11.49% | 7.768% | 1.1211 | 1.1299 | 1.0842
2010-05-30 | 39 | 34.2521 | 12.5391 | 46.7912 | 3.8086 | 0.76558 | 0.34785 | 4.922 | 10.52% | 11.19% | 7.563% | 1.1176 | 1.126 | 1.0818
2010-05-30 | 40 | 32.9585 | 12.1562 | 45.1147 | 3.5405 | 0.76558 | 0.33539 | 4.6415 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-05-30 | 41 | 33.5198 | 11.7521 | 45.2719 | 3.5653 | 0.76558 | 0.33656 | 4.6674 | 10.31% | 10.97% | 7.413% | 1.1149 | 1.1232 | 1.0801
2010-05-30 | 42 | 33.0331 | 11.3137 | 44.3468 | 3.421 | 0.76558 | 0.32968 | 4.5163 | 10.18% | 10.84% | 7.322% | 1.1134 | 1.1215 | 1.079
2010-05-30 | 43 | 31.6096 | 10.8654 | 42.475 | 3.1384 | 0.76558 | 0.31576 | 4.2197 | 9.935% | 10.57% | 7.143% | 1.1103 | 1.1182 | 1.0769
2010-05-30 | 44 | 29.9889 | 10.3727 | 40.3616 | 2.8338 | 0.76558 | 0.30005 | 3.8994 | 9.661% | 10.28% | 6.946% | 1.1069 | 1.1146 | 1.0747
2010-05-30 | 45 | 27.7767 | 9.6605 | 37.4372 | 2.438 | 0.76558 | 0.27831 | 3.4819 | 9.301% | 9.896% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-05-30 | 46 | 25.9083 | 9.0135 | 34.9218 | 2.1214 | 0.76558 | 0.25961 | 3.1466 | 9.01% | 9.587% | 6.479% | 1.099 | 1.106 | 1.0693
2010-05-30 | 47 | 26.1968 | 9.3482 | 35.545 | 2.1978 | 0.76558 | 0.26425 | 3.2276 | 9.08% | 9.662% | 6.529% | 1.0999 | 1.1069 | 1.0698
2010-05-30 | 48 | 25.5792 | 9.9947 | 35.5739 | 2.2014 | 0.76558 | 0.26446 | 3.2314 | 9.084% | 9.665% | 6.531% | 1.0999 | 1.107 | 1.0699
2010-05-31 | 1 | 23.8538 | 9.0632 | 32.9171 | 1.8848 | 0.76558 | 0.24471 | 2.8951 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2010-05-31 | 2 | 24.9764 | 8.5559 | 33.5323 | 1.956 | 0.76558 | 0.24928 | 2.9708 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-05-31 | 3 | 24.3159 | 8.1602 | 32.4761 | 1.8347 | 0.76558 | 0.24143 | 2.8417 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2010-05-31 | 4 | 23.4946 | 7.6313 | 31.1259 | 1.6853 | 0.76558 | 0.23139 | 2.6823 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.1009 | 1.0661
2010-05-31 | 5 | 23.2935 | 7.4281 | 30.7216 | 1.6418 | 0.76558 | 0.22839 | 2.6358 | 8.58% | 9.129% | 6.169% | 1.0938 | 1.1005 | 1.0657
2010-05-31 | 6 | 24.3707 | 7.385 | 31.7557 | 1.7542 | 0.76558 | 0.23608 | 2.7558 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0665
2010-05-31 | 7 | 24.7454 | 7.2123 | 31.9577 | 1.7766 | 0.76558 | 0.23758 | 2.7797 | 8.698% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-05-31 | 8 | 24.7761 | 7.0772 | 31.8533 | 1.765 | 0.76558 | 0.2368 | 2.7674 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-05-31 | 9 | 24.5155 | 6.9578 | 31.4733 | 1.7231 | 0.76558 | 0.23398 | 2.7227 | 8.651% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-05-31 | 10 | 24.4873 | 7.1276 | 31.6149 | 1.7387 | 0.76558 | 0.23503 | 2.7393 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-05-31 | 11 | 24.4931 | 7.1804 | 31.6735 | 1.7451 | 0.76558 | 0.23546 | 2.7462 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-05-31 | 12 | 24.984 | 7.3426 | 32.3266 | 1.8178 | 0.76558 | 0.24032 | 2.8237 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2010-05-31 | 13 | 25.3847 | 7.6263 | 33.011 | 1.8956 | 0.76558 | 0.24541 | 2.9066 | 8.805% | 9.368% | 6.331% | 1.0966 | 1.1034 | 1.0676
2010-05-31 | 14 | 26.3969 | 8.0776 | 34.4745 | 2.0674 | 0.76558 | 0.25629 | 3.0893 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-05-31 | 15 | 26.8358 | 8.406 | 35.2419 | 2.1605 | 0.76558 | 0.26199 | 3.1881 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-05-31 | 16 | 26.8993 | 8.8395 | 35.7388 | 2.2218 | 0.76558 | 0.26569 | 3.2531 | 9.102% | 9.685% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-05-31 | 17 | 29.0068 | 10.0042 | 39.011 | 2.6473 | 0.76558 | 0.29001 | 3.7029 | 9.492% | 10.1% | 6.825% | 1.1049 | 1.1123 | 1.0732
2010-05-31 | 18 | 31.3689 | 11.2822 | 42.6511 | 3.1644 | 0.76558 | 0.31707 | 4.2471 | 9.958% | 10.6% | 7.16% | 1.1106 | 1.1185 | 1.0771
2010-05-31 | 19 | 33.6364 | 12.2505 | 45.8869 | 3.6628 | 0.76558 | 0.34113 | 4.7695 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-05-31 | 20 | 35.4334 | 12.6983 | 48.1317 | 4.0299 | 0.76558 | 0.35782 | 5.1533 | 10.71% | 11.39% | 7.698% | 1.1199 | 1.1286 | 1.0834
2010-05-31 | 21 | 38.0618 | 12.7293 | 50.791 | 4.4875 | 0.76558 | 0.37759 | 5.6307 | 11.09% | 11.8% | 7.971% | 1.1247 | 1.1337 | 1.0866
2010-05-31 | 22 | 39.4631 | 12.994 | 52.4571 | 4.7868 | 0.76558 | 0.38997 | 5.9423 | 11.33% | 12.05% | 8.145% | 1.1278 | 1.137 | 1.0887
2010-05-31 | 23 | 38.3776 | 12.5978 | 50.9755 | 4.5202 | 0.76558 | 0.37896 | 5.6647 | 11.11% | 11.82% | 7.99% | 1.125 | 1.1341 | 1.0868
2010-05-31 | 24 | 37.0699 | 12.334 | 49.4039 | 4.2458 | 0.76558 | 0.36727 | 5.3786 | 10.89% | 11.58% | 7.828% | 1.1222 | 1.131 | 1.0849
2010-05-31 | 25 | 35.5613 | 11.6403 | 47.2016 | 3.8757 | 0.76558 | 0.3509 | 4.9922 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-05-31 | 26 | 34.571 | 11.0305 | 45.6016 | 3.6174 | 0.76558 | 0.33901 | 4.722 | 10.35% | 11.02% | 7.445% | 1.1155 | 1.1238 | 1.0804
2010-05-31 | 27 | 34.5415 | 11.4285 | 45.97 | 3.6761 | 0.76558 | 0.34175 | 4.7834 | 10.41% | 11.07% | 7.482% | 1.1161 | 1.1245 | 1.0809
2010-05-31 | 28 | 34.7714 | 11.4793 | 46.2507 | 3.7211 | 0.76558 | 0.34383 | 4.8305 | 10.44% | 11.11% | 7.509% | 1.1166 | 1.125 | 1.0812
2010-05-31 | 29 | 34.7579 | 10.9706 | 45.7285 | 3.6375 | 0.76558 | 0.33995 | 4.7431 | 10.37% | 11.04% | 7.458% | 1.1157 | 1.1241 | 1.0806
2010-05-31 | 30 | 34.1269 | 10.6093 | 44.7362 | 3.4814 | 0.76558 | 0.33257 | 4.5795 | 10.24% | 10.89% | 7.36% | 1.114 | 1.1222 | 1.0795
2010-05-31 | 31 | 35.6078 | 10.6045 | 46.2123 | 3.7149 | 0.76558 | 0.34355 | 4.824 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.1249 | 1.0811
2010-05-31 | 32 | 36.1406 | 10.5868 | 46.7273 | 3.7982 | 0.76558 | 0.34738 | 4.9111 | 10.51% | 11.18% | 7.557% | 1.1174 | 1.1259 | 1.0817
2010-05-31 | 33 | 36.4558 | 10.912 | 47.3678 | 3.903 | 0.76558 | 0.35214 | 5.0207 | 10.6% | 11.28% | 7.621% | 1.1186 | 1.1271 | 1.0825
2010-05-31 | 34 | 37.0145 | 11.2257 | 48.2403 | 4.0481 | 0.76558 | 0.35862 | 5.1723 | 10.72% | 11.41% | 7.709% | 1.1201 | 1.1288 | 1.0835
2010-05-31 | 35 | 38.0333 | 12.2493 | 50.2826 | 4.3981 | 0.76558 | 0.37381 | 5.5375 | 11.01% | 11.72% | 7.918% | 1.1238 | 1.1327 | 1.086
2010-05-31 | 36 | 40.0005 | 13.7473 | 53.7478 | 5.0252 | 0.76558 | 0.39957 | 6.1904 | 11.52% | 12.25% | 8.281% | 1.1302 | 1.1397 | 1.0903
2010-05-31 | 37 | 40.9901 | 13.9503 | 54.9404 | 5.2507 | 0.76558 | 0.40843 | 6.4247 | 11.69% | 12.44% | 8.408% | 1.1324 | 1.1421 | 1.0918
2010-05-31 | 38 | 41.2642 | 13.4218 | 54.686 | 5.2022 | 0.76558 | 0.40654 | 6.3743 | 11.66% | 12.4% | 8.381% | 1.1319 | 1.1416 | 1.0915
2010-05-31 | 39 | 40.4041 | 12.966 | 53.3702 | 4.9549 | 0.76558 | 0.39676 | 6.1172 | 11.46% | 12.2% | 8.241% | 1.1295 | 1.1389 | 1.0898
2010-05-31 | 40 | 39.3547 | 12.4507 | 51.8054 | 4.6686 | 0.76558 | 0.38513 | 5.8193 | 11.23% | 11.95% | 8.077% | 1.1265 | 1.1357 | 1.0879
2010-05-31 | 41 | 39.3849 | 12.4537 | 51.8386 | 4.6746 | 0.76558 | 0.38537 | 5.8255 | 11.24% | 11.96% | 8.08% | 1.1266 | 1.1358 | 1.0879
2010-05-31 | 42 | 38.3207 | 11.9482 | 50.269 | 4.3958 | 0.76558 | 0.37371 | 5.535 | 11.01% | 11.72% | 7.917% | 1.1237 | 1.1327 | 1.086
2010-05-31 | 43 | 37.7019 | 11.5254 | 49.2273 | 4.2155 | 0.76558 | 0.36596 | 5.347 | 10.86% | 11.56% | 7.81% | 1.1219 | 1.1307 | 1.0847
2010-05-31 | 44 | 35.6918 | 10.9588 | 46.6506 | 3.7857 | 0.76558 | 0.34681 | 4.8981 | 10.5% | 11.17% | 7.549% | 1.1173 | 1.1258 | 1.0817
2010-05-31 | 45 | 32.3735 | 9.9377 | 42.3112 | 3.1142 | 0.76558 | 0.31455 | 4.1943 | 9.913% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-05-31 | 46 | 30.0042 | 9.0651 | 39.0693 | 2.6553 | 0.76558 | 0.29045 | 3.7113 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-05-31 | 47 | 31.0536 | 9.4682 | 40.5219 | 2.8564 | 0.76558 | 0.30124 | 3.9232 | 9.682% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-05-31 | 48 | 30.7372 | 9.8455 | 40.5828 | 2.865 | 0.76558 | 0.3017 | 3.9322 | 9.689% | 10.31% | 6.967% | 1.1073 | 1.1149 | 1.0749
2010-06-01 | 1 | 28.7832 | 8.8574 | 37.6406 | 2.4646 | 0.76558 | 0.27983 | 3.51 | 9.325% | 9.922% | 6.705% | 1.1028 | 1.1101 | 1.0719
2010-06-01 | 2 | 28.9011 | 8.7281 | 37.6292 | 2.4631 | 0.76558 | 0.27974 | 3.5084 | 9.324% | 9.92% | 6.704% | 1.1028 | 1.1101 | 1.0719
2010-06-01 | 3 | 27.3779 | 8.3631 | 35.741 | 2.2221 | 0.76558 | 0.2657 | 3.2534 | 9.103% | 9.685% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-06-01 | 4 | 27.0316 | 8.0422 | 35.0738 | 2.1399 | 0.76558 | 0.26074 | 3.1663 | 9.027% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-06-01 | 5 | 26.2992 | 7.8362 | 34.1354 | 2.027 | 0.76558 | 0.25377 | 3.0463 | 8.924% | 9.495% | 6.416% | 1.098 | 1.1049 | 1.0686
2010-06-01 | 6 | 24.7925 | 7.6583 | 32.4508 | 1.8318 | 0.76558 | 0.24124 | 2.8387 | 8.748% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-06-01 | 7 | 23.7725 | 7.6367 | 31.4092 | 1.7161 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-06-01 | 8 | 23.4962 | 7.57 | 31.0661 | 1.6788 | 0.76558 | 0.23095 | 2.6754 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-06-01 | 9 | 23.3976 | 7.5189 | 30.9165 | 1.6627 | 0.76558 | 0.22984 | 2.6581 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-06-01 | 10 | 23.7853 | 7.5426 | 31.3279 | 1.7073 | 0.76558 | 0.2329 | 2.7057 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-06-01 | 11 | 23.9158 | 7.6319 | 31.5477 | 1.7313 | 0.76558 | 0.23453 | 2.7314 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-06-01 | 12 | 24.3896 | 7.8572 | 32.2469 | 1.8089 | 0.76558 | 0.23973 | 2.8142 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.0669
2010-06-01 | 13 | 25.4237 | 8.3288 | 33.7525 | 1.9817 | 0.76558 | 0.25092 | 2.9982 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-06-01 | 14 | 26.7732 | 8.9379 | 35.7112 | 2.2184 | 0.76558 | 0.26548 | 3.2495 | 9.099% | 9.682% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-06-01 | 15 | 27.1896 | 9.3451 | 36.5347 | 2.3219 | 0.76558 | 0.2716 | 3.3591 | 9.194% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2010-06-01 | 16 | 27.1599 | 9.8928 | 37.0527 | 2.3882 | 0.76558 | 0.27545 | 3.4293 | 9.255% | 9.847% | 6.654% | 1.102 | 1.1092 | 1.0713
2010-06-01 | 17 | 29.0721 | 11.2397 | 40.3119 | 2.8268 | 0.76558 | 0.29968 | 3.8921 | 9.655% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-06-01 | 18 | 32.3328 | 12.5463 | 44.8792 | 3.5037 | 0.76558 | 0.33364 | 4.6029 | 10.26% | 10.91% | 7.374% | 1.1143 | 1.1225 | 1.0796
2010-06-01 | 19 | 34.719 | 13.6564 | 48.3755 | 4.0708 | 0.76558 | 0.35963 | 5.1961 | 10.74% | 11.43% | 7.723% | 1.1203 | 1.129 | 1.0837
2010-06-01 | 20 | 35.7508 | 14.2906 | 50.0414 | 4.3561 | 0.76558 | 0.37201 | 5.4937 | 10.98% | 11.68% | 7.893% | 1.1233 | 1.1323 | 1.0857
2010-06-01 | 21 | 37.5179 | 14.9571 | 52.475 | 4.79 | 0.76558 | 0.39011 | 5.9457 | 11.33% | 12.06% | 8.147% | 1.1278 | 1.1371 | 1.0887
2010-06-01 | 22 | 36.5852 | 14.8104 | 51.3955 | 4.595 | 0.76558 | 0.38208 | 5.7427 | 11.17% | 11.89% | 8.034% | 1.1258 | 1.1349 | 1.0874
2010-06-01 | 23 | 35.5641 | 13.8831 | 49.4472 | 4.2532 | 0.76558 | 0.3676 | 5.3864 | 10.89% | 11.59% | 7.832% | 1.1222 | 1.1311 | 1.085
2010-06-01 | 24 | 34.3431 | 12.8706 | 47.2137 | 3.8777 | 0.76558 | 0.35099 | 4.9942 | 10.58% | 11.25% | 7.606% | 1.1183 | 1.1268 | 1.0823
2010-06-01 | 25 | 32.0575 | 12.0071 | 44.0646 | 3.3776 | 0.76558 | 0.32758 | 4.4708 | 10.15% | 10.8% | 7.295% | 1.1129 | 1.121 | 1.0787
2010-06-01 | 26 | 30.449 | 11.0726 | 41.5216 | 2.999 | 0.76558 | 0.30868 | 4.0733 | 9.81% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-06-01 | 27 | 30.2476 | 10.8253 | 41.0729 | 2.9346 | 0.76558 | 0.30534 | 4.0055 | 9.752% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-06-01 | 28 | 29.6441 | 10.9405 | 40.5846 | 2.8652 | 0.76558 | 0.30171 | 3.9325 | 9.69% | 10.31% | 6.967% | 1.1073 | 1.1149 | 1.0749
2010-06-01 | 29 | 28.624 | 10.336 | 38.96 | 2.6404 | 0.76558 | 0.28963 | 3.6956 | 9.486% | 10.09% | 6.82% | 1.1048 | 1.1123 | 1.0732
2010-06-01 | 30 | 28.096 | 9.9587 | 38.0547 | 2.5191 | 0.76558 | 0.2829 | 3.5676 | 9.375% | 9.975% | 6.741% | 1.1034 | 1.1108 | 1.0723
2010-06-01 | 31 | 29.7474 | 9.8595 | 39.6069 | 2.7288 | 0.76558 | 0.29444 | 3.7889 | 9.566% | 10.18% | 6.878% | 1.1058 | 1.1133 | 1.0739
2010-06-01 | 32 | 29.7776 | 9.7354 | 39.5131 | 2.7159 | 0.76558 | 0.29374 | 3.7752 | 9.554% | 10.17% | 6.87% | 1.1056 | 1.1132 | 1.0738
2010-06-01 | 33 | 30.4504 | 10.2156 | 40.6661 | 2.8767 | 0.76558 | 0.30232 | 3.9446 | 9.7% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-06-01 | 34 | 32.2456 | 11.0041 | 43.2497 | 3.2539 | 0.76558 | 0.32152 | 4.341 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-06-01 | 35 | 33.8813 | 12.6413 | 46.5226 | 3.765 | 0.76558 | 0.34585 | 4.8764 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-06-01 | 36 | 37.2981 | 13.8879 | 51.186 | 4.5576 | 0.76558 | 0.38052 | 5.7037 | 11.14% | 11.86% | 8.012% | 1.1254 | 1.1345 | 1.0871
2010-06-01 | 37 | 38.3169 | 13.7801 | 52.097 | 4.7213 | 0.76558 | 0.3873 | 5.8741 | 11.28% | 12% | 8.107% | 1.1271 | 1.1363 | 1.0882
2010-06-01 | 38 | 38.2457 | 13.5823 | 51.8281 | 4.6727 | 0.76558 | 0.3853 | 5.8235 | 11.24% | 11.96% | 8.079% | 1.1266 | 1.1358 | 1.0879
2010-06-01 | 39 | 37.6998 | 13.2535 | 50.9532 | 4.5163 | 0.76558 | 0.37879 | 5.6606 | 11.11% | 11.82% | 7.988% | 1.125 | 1.134 | 1.0868
2010-06-01 | 40 | 36.8962 | 12.9536 | 49.8498 | 4.3228 | 0.76558 | 0.37059 | 5.4589 | 10.95% | 11.65% | 7.874% | 1.123 | 1.1319 | 1.0855
2010-06-01 | 41 | 37.9182 | 12.6323 | 50.5504 | 4.4451 | 0.76558 | 0.3758 | 5.5865 | 11.05% | 11.76% | 7.946% | 1.1242 | 1.1333 | 1.0863
2010-06-01 | 42 | 38.1484 | 12.2781 | 50.4264 | 4.4234 | 0.76558 | 0.37488 | 5.5638 | 11.03% | 11.74% | 7.933% | 1.124 | 1.133 | 1.0862
2010-06-01 | 43 | 36.5398 | 11.7017 | 48.2415 | 4.0483 | 0.76558 | 0.35863 | 5.1725 | 10.72% | 11.41% | 7.709% | 1.1201 | 1.1288 | 1.0835
2010-06-01 | 44 | 35.0017 | 10.9373 | 45.9389 | 3.6711 | 0.76558 | 0.34152 | 4.7782 | 10.4% | 11.07% | 7.478% | 1.1161 | 1.1244 | 1.0808
2010-06-01 | 45 | 33.0787 | 9.86 | 42.9387 | 3.2072 | 0.76558 | 0.31921 | 4.292 | 9.996% | 10.64% | 7.187% | 1.1111 | 1.119 | 1.0774
2010-06-01 | 46 | 30.7233 | 8.8158 | 39.5391 | 2.7195 | 0.76558 | 0.29394 | 3.779 | 9.558% | 10.17% | 6.872% | 1.1057 | 1.1132 | 1.0738
2010-06-01 | 47 | 30.594 | 9.1823 | 39.7763 | 2.7522 | 0.76558 | 0.2957 | 3.8135 | 9.587% | 10.2% | 6.893% | 1.106 | 1.1136 | 1.074
2010-06-01 | 48 | 29.975 | 9.7093 | 39.6843 | 2.7395 | 0.76558 | 0.29502 | 3.8001 | 9.576% | 10.19% | 6.885% | 1.1059 | 1.1134 | 1.0739
2010-06-02 | 1 | 28.4527 | 8.9854 | 37.438 | 2.4382 | 0.76558 | 0.27832 | 3.482 | 9.301% | 9.896% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-06-02 | 2 | 29.7176 | 8.7426 | 38.4602 | 2.5731 | 0.76558 | 0.28592 | 3.6246 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1115 | 1.0727
2010-06-02 | 3 | 29.1282 | 8.3531 | 37.4812 | 2.4438 | 0.76558 | 0.27864 | 3.488 | 9.306% | 9.902% | 6.691% | 1.1026 | 1.1099 | 1.0717
2010-06-02 | 4 | 27.9784 | 8.1826 | 36.161 | 2.2747 | 0.76558 | 0.26882 | 3.3091 | 9.151% | 9.737% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-06-02 | 5 | 26.9583 | 7.9849 | 34.9432 | 2.124 | 0.76558 | 0.25977 | 3.1494 | 9.013% | 9.59% | 6.48% | 1.0991 | 1.1061 | 1.0693
2010-06-02 | 6 | 26.7859 | 7.7108 | 34.4967 | 2.0701 | 0.76558 | 0.25645 | 3.0921 | 8.964% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-06-02 | 7 | 26.8719 | 7.5397 | 34.4116 | 2.0599 | 0.76558 | 0.25582 | 3.0813 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-06-02 | 8 | 26.5697 | 7.5784 | 34.1481 | 2.0285 | 0.76558 | 0.25386 | 3.0479 | 8.926% | 9.497% | 6.417% | 1.098 | 1.1049 | 1.0686
2010-06-02 | 9 | 26.8865 | 7.7415 | 34.628 | 2.0859 | 0.76558 | 0.25743 | 3.1089 | 8.978% | 9.553% | 6.455% | 1.0986 | 1.1056 | 1.069
2010-06-02 | 10 | 26.7008 | 7.8541 | 34.555 | 2.0771 | 0.76558 | 0.25689 | 3.0996 | 8.97% | 9.544% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-06-02 | 11 | 27.116 | 8.2615 | 35.3775 | 2.1771 | 0.76558 | 0.263 | 3.2057 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-06-02 | 12 | 28.1812 | 8.6342 | 36.8154 | 2.3577 | 0.76558 | 0.27369 | 3.397 | 9.227% | 9.818% | 6.634% | 1.1017 | 1.1089 | 1.0711
2010-06-02 | 13 | 29.9473 | 9.8228 | 39.7701 | 2.7514 | 0.76558 | 0.29566 | 3.8126 | 9.587% | 10.2% | 6.893% | 1.106 | 1.1136 | 1.074
2010-06-02 | 14 | 32.7791 | 11.531 | 44.3101 | 3.4154 | 0.76558 | 0.32941 | 4.5104 | 10.18% | 10.83% | 7.319% | 1.1133 | 1.1215 | 1.079
2010-06-02 | 15 | 36.3708 | 13.499 | 49.8698 | 4.3262 | 0.76558 | 0.37074 | 5.4625 | 10.95% | 11.65% | 7.876% | 1.123 | 1.1319 | 1.0855
2010-06-02 | 16 | 38.4917 | 14.8865 | 53.3782 | 4.9564 | 0.76558 | 0.39682 | 6.1188 | 11.46% | 12.2% | 8.242% | 1.1295 | 1.1389 | 1.0898
2010-06-02 | 17 | 40.5033 | 16.147 | 56.6503 | 5.5826 | 0.76558 | 0.42114 | 6.7693 | 11.95% | 12.71% | 8.592% | 1.1357 | 1.1457 | 1.094
2010-06-02 | 18 | 41.6661 | 16.3538 | 58.0199 | 5.8558 | 0.76558 | 0.43133 | 7.0527 | 12.16% | 12.93% | 8.74% | 1.1384 | 1.1485 | 1.0958
2010-06-02 | 19 | 42.0246 | 16.2509 | 58.2755 | 5.9075 | 0.76558 | 0.43323 | 7.1063 | 12.19% | 12.97% | 8.768% | 1.1389 | 1.1491 | 1.0961
2010-06-02 | 20 | 40.9321 | 15.5074 | 56.4395 | 5.5412 | 0.76558 | 0.41958 | 6.7263 | 11.92% | 12.68% | 8.569% | 1.1353 | 1.1452 | 1.0937
2010-06-02 | 21 | 42.4421 | 14.9966 | 57.4387 | 5.7391 | 0.76558 | 0.42701 | 6.9317 | 12.07% | 12.84% | 8.677% | 1.1372 | 1.1473 | 1.095
2010-06-02 | 22 | 41.4511 | 14.3184 | 55.7695 | 5.4104 | 0.76558 | 0.4146 | 6.5906 | 11.82% | 12.57% | 8.497% | 1.134 | 1.1438 | 1.0929
2010-06-02 | 23 | 38.6211 | 13.6853 | 52.3064 | 4.7593 | 0.76558 | 0.38885 | 5.9138 | 11.31% | 12.03% | 8.129% | 1.1275 | 1.1367 | 1.0885
2010-06-02 | 24 | 35.9929 | 13.0879 | 49.0808 | 4.1904 | 0.76558 | 0.36487 | 5.3209 | 10.84% | 11.53% | 7.795% | 1.1216 | 1.1304 | 1.0845
2010-06-02 | 25 | 33.5902 | 12.4834 | 46.0736 | 3.6927 | 0.76558 | 0.34252 | 4.8008 | 10.42% | 11.09% | 7.492% | 1.1163 | 1.1247 | 1.081
2010-06-02 | 26 | 31.9251 | 11.5651 | 43.4902 | 3.2902 | 0.76558 | 0.32331 | 4.3791 | 10.07% | 10.71% | 7.24% | 1.112 | 1.12 | 1.078
2010-06-02 | 27 | 32.2421 | 11.874 | 44.1161 | 3.3855 | 0.76558 | 0.32796 | 4.4791 | 10.15% | 10.8% | 7.3% | 1.113 | 1.1211 | 1.0787
2010-06-02 | 28 | 32.0287 | 11.922 | 43.9507 | 3.3602 | 0.76558 | 0.32674 | 4.4525 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-06-02 | 29 | 31.3091 | 11.4422 | 42.7512 | 3.1793 | 0.76558 | 0.31782 | 4.2627 | 9.971% | 10.61% | 7.169% | 1.1108 | 1.1187 | 1.0772
2010-06-02 | 30 | 30.5916 | 11.1628 | 41.7544 | 3.0328 | 0.76558 | 0.31041 | 4.1088 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-06-02 | 31 | 32.361 | 11.0088 | 43.3698 | 3.272 | 0.76558 | 0.32242 | 4.36 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-06-02 | 32 | 32.7489 | 11.0108 | 43.7598 | 3.3311 | 0.76558 | 0.32532 | 4.422 | 10.11% | 10.75% | 7.266% | 1.1124 | 1.1205 | 1.0783
2010-06-02 | 33 | 33.9546 | 11.3715 | 45.3261 | 3.5738 | 0.76558 | 0.33696 | 4.6763 | 10.32% | 10.98% | 7.418% | 1.115 | 1.1233 | 1.0801
2010-06-02 | 34 | 35.2317 | 11.9836 | 47.2153 | 3.8779 | 0.76558 | 0.351 | 4.9945 | 10.58% | 11.26% | 7.606% | 1.1183 | 1.1268 | 1.0823
2010-06-02 | 35 | 36.839 | 13.4859 | 50.3248 | 4.4055 | 0.76558 | 0.37412 | 5.5452 | 11.02% | 11.72% | 7.923% | 1.1238 | 1.1328 | 1.086
2010-06-02 | 36 | 40.4564 | 15.0264 | 55.4828 | 5.3549 | 0.76558 | 0.41247 | 6.5329 | 11.77% | 12.53% | 8.466% | 1.1335 | 1.1432 | 1.0925
2010-06-02 | 37 | 41.7042 | 15.0858 | 56.79 | 5.6102 | 0.76558 | 0.42218 | 6.798 | 11.97% | 12.74% | 8.607% | 1.136 | 1.146 | 1.0942
2010-06-02 | 38 | 42.0523 | 14.7045 | 56.7568 | 5.6036 | 0.76558 | 0.42194 | 6.7912 | 11.97% | 12.73% | 8.603% | 1.1359 | 1.1459 | 1.0941
2010-06-02 | 39 | 41.4352 | 14.2369 | 55.6721 | 5.3915 | 0.76558 | 0.41387 | 6.571 | 11.8% | 12.56% | 8.486% | 1.1338 | 1.1436 | 1.0927
2010-06-02 | 40 | 40.7895 | 13.8925 | 54.682 | 5.2014 | 0.76558 | 0.40651 | 6.3735 | 11.66% | 12.4% | 8.38% | 1.1319 | 1.1416 | 1.0915
2010-06-02 | 41 | 41.5081 | 13.7038 | 55.2118 | 5.3027 | 0.76558 | 0.41045 | 6.4788 | 11.73% | 12.49% | 8.437% | 1.1329 | 1.1427 | 1.0921
2010-06-02 | 42 | 41.5093 | 13.3392 | 54.8485 | 5.2332 | 0.76558 | 0.40775 | 6.4065 | 11.68% | 12.43% | 8.398% | 1.1323 | 1.1419 | 1.0917
2010-06-02 | 43 | 39.641 | 12.6449 | 52.2859 | 4.7556 | 0.76558 | 0.3887 | 5.9099 | 11.3% | 12.03% | 8.127% | 1.1274 | 1.1367 | 1.0885
2010-06-02 | 44 | 37.6867 | 11.9145 | 49.6012 | 4.2798 | 0.76558 | 0.36874 | 5.4141 | 10.92% | 11.61% | 7.848% | 1.1225 | 1.1314 | 1.0852
2010-06-02 | 45 | 34.7577 | 10.9042 | 45.6619 | 3.627 | 0.76558 | 0.33946 | 4.732 | 10.36% | 11.03% | 7.451% | 1.1156 | 1.1239 | 1.0805
2010-06-02 | 46 | 31.6701 | 9.672 | 41.3421 | 2.9732 | 0.76558 | 0.30734 | 4.0461 | 9.787% | 10.41% | 7.037% | 1.1085 | 1.1162 | 1.0757
2010-06-02 | 47 | 31.8718 | 9.8936 | 41.7654 | 3.0344 | 0.76558 | 0.31049 | 4.1104 | 9.842% | 10.47% | 7.076% | 1.1092 | 1.117 | 1.0762
2010-06-02 | 48 | 31.2248 | 10.409 | 41.6338 | 3.0153 | 0.76558 | 0.30951 | 4.0904 | 9.825% | 10.45% | 7.064% | 1.109 | 1.1167 | 1.076
2010-06-03 | 1 | 29.689 | 9.6316 | 39.3206 | 2.6895 | 0.76558 | 0.29231 | 3.7474 | 9.53% | 10.14% | 6.852% | 1.1053 | 1.1128 | 1.0736
2010-06-03 | 2 | 31.3427 | 9.5851 | 40.9278 | 2.9139 | 0.76558 | 0.30426 | 3.9837 | 9.734% | 10.36% | 6.998% | 1.1078 | 1.1155 | 1.0753
2010-06-03 | 3 | 30.7823 | 9.114 | 39.8963 | 2.7688 | 0.76558 | 0.29659 | 3.831 | 9.602% | 10.22% | 6.904% | 1.1062 | 1.1138 | 1.0742
2010-06-03 | 4 | 29.748 | 8.7455 | 38.4934 | 2.5776 | 0.76558 | 0.28616 | 3.6293 | 9.428% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-06-03 | 5 | 28.8136 | 8.5095 | 37.3232 | 2.4232 | 0.76558 | 0.27746 | 3.4663 | 9.287% | 9.882% | 6.677% | 1.1024 | 1.1097 | 1.0716
2010-06-03 | 6 | 28.1956 | 8.3289 | 36.5246 | 2.3206 | 0.76558 | 0.27153 | 3.3577 | 9.193% | 9.781% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-06-03 | 7 | 28.1813 | 8.3067 | 36.488 | 2.316 | 0.76558 | 0.27126 | 3.3528 | 9.189% | 9.777% | 6.607% | 1.1012 | 1.1084 | 1.0707
2010-06-03 | 8 | 28.0954 | 8.2113 | 36.3067 | 2.293 | 0.76558 | 0.26991 | 3.3285 | 9.168% | 9.754% | 6.592% | 1.1009 | 1.1081 | 1.0706
2010-06-03 | 9 | 28.1683 | 8.2189 | 36.3872 | 2.3032 | 0.76558 | 0.27051 | 3.3393 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-06-03 | 10 | 28.0517 | 8.4761 | 36.5278 | 2.321 | 0.76558 | 0.27155 | 3.3582 | 9.193% | 9.782% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-06-03 | 11 | 28.5396 | 8.7033 | 37.2429 | 2.4128 | 0.76558 | 0.27687 | 3.4553 | 9.278% | 9.871% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-06-03 | 12 | 29.7175 | 9.046 | 38.7635 | 2.6139 | 0.76558 | 0.28817 | 3.6676 | 9.461% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2010-06-03 | 13 | 31.599 | 10.1859 | 41.7849 | 3.0372 | 0.76558 | 0.31063 | 4.1134 | 9.844% | 10.47% | 7.078% | 1.1092 | 1.117 | 1.0762
2010-06-03 | 14 | 35.1041 | 11.8806 | 46.9847 | 3.8401 | 0.76558 | 0.34929 | 4.955 | 10.55% | 11.22% | 7.583% | 1.1179 | 1.1264 | 1.082
2010-06-03 | 15 | 39.0377 | 14.3249 | 53.3626 | 4.9535 | 0.76558 | 0.3967 | 6.1157 | 11.46% | 12.19% | 8.24% | 1.1294 | 1.1389 | 1.0898
2010-06-03 | 16 | 40.6449 | 15.6647 | 56.3096 | 5.5157 | 0.76558 | 0.41861 | 6.6999 | 11.9% | 12.66% | 8.555% | 1.1351 | 1.1449 | 1.0936
2010-06-03 | 17 | 42.554 | 16.306 | 58.86 | 6.0266 | 0.76558 | 0.43757 | 7.2298 | 12.28% | 13.07% | 8.831% | 1.14 | 1.1503 | 1.0969
2010-06-03 | 18 | 42.9554 | 16.3776 | 59.333 | 6.1239 | 0.76558 | 0.44109 | 7.3306 | 12.35% | 13.15% | 8.883% | 1.141 | 1.1514 | 1.0975
2010-06-03 | 19 | 43.3706 | 16.2932 | 59.6638 | 6.1924 | 0.76558 | 0.44355 | 7.4015 | 12.41% | 13.2% | 8.919% | 1.1416 | 1.1521 | 1.0979
2010-06-03 | 20 | 42.8115 | 16.3798 | 59.1913 | 6.0947 | 0.76558 | 0.44004 | 7.3003 | 12.33% | 13.12% | 8.868% | 1.1407 | 1.151 | 1.0973
2010-06-03 | 21 | 43.6041 | 16.3645 | 59.9687 | 6.2558 | 0.76558 | 0.44581 | 7.4672 | 12.45% | 13.25% | 8.953% | 1.1422 | 1.1527 | 1.0983
2010-06-03 | 22 | 43.1468 | 16.3238 | 59.4706 | 6.1523 | 0.76558 | 0.44211 | 7.36 | 12.38% | 13.17% | 8.898% | 1.1412 | 1.1516 | 1.0977
2010-06-03 | 23 | 41.6956 | 15.9313 | 57.6269 | 5.7768 | 0.76558 | 0.42841 | 6.9707 | 12.1% | 12.87% | 8.697% | 1.1376 | 1.1477 | 1.0953
2010-06-03 | 24 | 40.0271 | 15.3098 | 55.337 | 5.3268 | 0.76558 | 0.41138 | 6.5038 | 11.75% | 12.51% | 8.45% | 1.1332 | 1.1429 | 1.0923
2010-06-03 | 25 | 37.1827 | 14.6517 | 51.8344 | 4.6738 | 0.76558 | 0.38534 | 5.8247 | 11.24% | 11.96% | 8.08% | 1.1266 | 1.1358 | 1.0879
2010-06-03 | 26 | 34.6245 | 13.9272 | 48.5517 | 4.1006 | 0.76558 | 0.36094 | 5.2271 | 10.77% | 11.46% | 7.741% | 1.1206 | 1.1294 | 1.0839
2010-06-03 | 27 | 34.669 | 14.2167 | 48.8857 | 4.1572 | 0.76558 | 0.36342 | 5.2862 | 10.81% | 11.51% | 7.775% | 1.1212 | 1.13 | 1.0843
2010-06-03 | 28 | 34.2673 | 14.1578 | 48.4251 | 4.0792 | 0.76558 | 0.36 | 5.2048 | 10.75% | 11.44% | 7.728% | 1.1204 | 1.1291 | 1.0838
2010-06-03 | 29 | 33.5786 | 13.3118 | 46.8905 | 3.8248 | 0.76558 | 0.34859 | 4.9389 | 10.53% | 11.21% | 7.573% | 1.1177 | 1.1262 | 1.0819
2010-06-03 | 30 | 33.1497 | 12.8254 | 45.9751 | 3.6769 | 0.76558 | 0.34178 | 4.7843 | 10.41% | 11.07% | 7.482% | 1.1161 | 1.1245 | 1.0809
2010-06-03 | 31 | 34.271 | 12.999 | 47.27 | 3.8869 | 0.76558 | 0.35141 | 5.0039 | 10.59% | 11.26% | 7.611% | 1.1184 | 1.1269 | 1.0824
2010-06-03 | 32 | 34.3567 | 12.7273 | 47.0841 | 3.8564 | 0.76558 | 0.35003 | 4.972 | 10.56% | 11.24% | 7.593% | 1.1181 | 1.1266 | 1.0822
2010-06-03 | 33 | 34.5146 | 12.9608 | 47.4753 | 3.9208 | 0.76558 | 0.35294 | 5.0393 | 10.61% | 11.29% | 7.632% | 1.1187 | 1.1273 | 1.0826
2010-06-03 | 34 | 35.2037 | 13.3593 | 48.563 | 4.1025 | 0.76558 | 0.36102 | 5.2291 | 10.77% | 11.46% | 7.742% | 1.1207 | 1.1294 | 1.0839
2010-06-03 | 35 | 36.9092 | 14.7998 | 51.7089 | 4.6512 | 0.76558 | 0.38441 | 5.8012 | 11.22% | 11.94% | 8.066% | 1.1264 | 1.1356 | 1.0877
2010-06-03 | 36 | 40.0693 | 16.042 | 56.1113 | 5.4769 | 0.76558 | 0.41714 | 6.6596 | 11.87% | 12.63% | 8.534% | 1.1347 | 1.1445 | 1.0933
2010-06-03 | 37 | 41.6904 | 15.8695 | 57.5599 | 5.7633 | 0.76558 | 0.42791 | 6.9568 | 12.09% | 12.86% | 8.69% | 1.1375 | 1.1476 | 1.0952
2010-06-03 | 38 | 42.2809 | 15.7261 | 58.007 | 5.8532 | 0.76558 | 0.43123 | 7.05 | 12.15% | 12.93% | 8.739% | 1.1384 | 1.1485 | 1.0958
2010-06-03 | 39 | 41.6495 | 15.3935 | 57.043 | 5.6603 | 0.76558 | 0.42406 | 6.8499 | 12.01% | 12.78% | 8.634% | 1.1365 | 1.1465 | 1.0945
2010-06-03 | 40 | 40.7181 | 14.7516 | 55.4696 | 5.3524 | 0.76558 | 0.41237 | 6.5303 | 11.77% | 12.53% | 8.465% | 1.1334 | 1.1432 | 1.0925
2010-06-03 | 41 | 41.4944 | 14.5773 | 56.0717 | 5.4692 | 0.76558 | 0.41684 | 6.6516 | 11.86% | 12.62% | 8.529% | 1.1346 | 1.1445 | 1.0932
2010-06-03 | 42 | 41.6545 | 14.1519 | 55.8064 | 5.4176 | 0.76558 | 0.41487 | 6.598 | 11.82% | 12.58% | 8.501% | 1.1341 | 1.1439 | 1.0929
2010-06-03 | 43 | 39.9287 | 13.4187 | 53.3474 | 4.9506 | 0.76558 | 0.39659 | 6.1128 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1388 | 1.0898
2010-06-03 | 44 | 37.6595 | 12.6118 | 50.2713 | 4.3962 | 0.76558 | 0.37372 | 5.5355 | 11.01% | 11.72% | 7.917% | 1.1237 | 1.1327 | 1.086
2010-06-03 | 45 | 33.9687 | 11.1779 | 45.1466 | 3.5456 | 0.76558 | 0.33563 | 4.6468 | 10.29% | 10.95% | 7.4% | 1.1147 | 1.123 | 1.0799
2010-06-03 | 46 | 30.7365 | 10.0615 | 40.798 | 2.8954 | 0.76558 | 0.3033 | 3.9643 | 9.717% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-06-03 | 47 | 30.1621 | 10.3767 | 40.5388 | 2.8587 | 0.76558 | 0.30137 | 3.9257 | 9.684% | 10.3% | 6.963% | 1.1072 | 1.1149 | 1.0748
2010-06-03 | 48 | 29.3153 | 10.894 | 40.2094 | 2.8125 | 0.76558 | 0.29892 | 3.877 | 9.642% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-06-04 | 1 | 27.4046 | 9.9691 | 37.3736 | 2.4298 | 0.76558 | 0.27784 | 3.4732 | 9.293% | 9.888% | 6.682% | 1.1025 | 1.1097 | 1.0716
2010-06-04 | 2 | 29.0866 | 9.7617 | 38.8483 | 2.6253 | 0.76558 | 0.2888 | 3.6797 | 9.472% | 10.08% | 6.81% | 1.1046 | 1.1121 | 1.0731
2010-06-04 | 3 | 28.8564 | 9.3847 | 38.2411 | 2.5439 | 0.76558 | 0.28429 | 3.5937 | 9.398% | 9.999% | 6.757% | 1.1037 | 1.1111 | 1.0725
2010-06-04 | 4 | 28.2537 | 9.0148 | 37.2684 | 2.4161 | 0.76558 | 0.27706 | 3.4587 | 9.281% | 9.875% | 6.673% | 1.1023 | 1.1096 | 1.0715
2010-06-04 | 5 | 27.3607 | 8.7826 | 36.1433 | 2.2724 | 0.76558 | 0.26869 | 3.3067 | 9.149% | 9.734% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-06-04 | 6 | 27.0893 | 8.5736 | 35.6629 | 2.2124 | 0.76558 | 0.26512 | 3.2431 | 9.094% | 9.676% | 6.538% | 1.1 | 1.1071 | 1.07
2010-06-04 | 7 | 27.5197 | 8.4601 | 35.9798 | 2.2519 | 0.76558 | 0.26748 | 3.285 | 9.13% | 9.714% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-06-04 | 8 | 27.5771 | 8.3832 | 35.9603 | 2.2495 | 0.76558 | 0.26733 | 3.2824 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2010-06-04 | 9 | 27.6925 | 8.4967 | 36.1891 | 2.2782 | 0.76558 | 0.26903 | 3.3128 | 9.154% | 9.74% | 6.582% | 1.1008 | 1.1079 | 1.0705
2010-06-04 | 10 | 27.6618 | 8.5463 | 36.208 | 2.2806 | 0.76558 | 0.26917 | 3.3153 | 9.156% | 9.742% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-06-04 | 11 | 28.1378 | 8.7735 | 36.9114 | 2.37 | 0.76558 | 0.2744 | 3.41 | 9.238% | 9.83% | 6.642% | 1.1018 | 1.109 | 1.0712
2010-06-04 | 12 | 29.862 | 9.0737 | 38.9358 | 2.6371 | 0.76558 | 0.28945 | 3.6922 | 9.483% | 10.09% | 6.818% | 1.1048 | 1.1122 | 1.0732
2010-06-04 | 13 | 32.2035 | 10.1717 | 42.3753 | 3.1236 | 0.76558 | 0.31502 | 4.2042 | 9.921% | 10.56% | 7.134% | 1.1101 | 1.118 | 1.0768
2010-06-04 | 14 | 35.4486 | 11.7891 | 47.2378 | 3.8816 | 0.76558 | 0.35117 | 4.9984 | 10.58% | 11.26% | 7.608% | 1.1183 | 1.1269 | 1.0823
2010-06-04 | 15 | 39.4109 | 14.0274 | 53.4383 | 4.9675 | 0.76558 | 0.39727 | 6.1304 | 11.47% | 12.21% | 8.248% | 1.1296 | 1.139 | 1.0899
2010-06-04 | 16 | 40.9292 | 15.2873 | 56.2165 | 5.4975 | 0.76558 | 0.41792 | 6.681 | 11.88% | 12.64% | 8.545% | 1.1349 | 1.1448 | 1.0934
2010-06-04 | 17 | 40.917 | 16.2961 | 57.213 | 5.6941 | 0.76558 | 0.42533 | 6.885 | 12.03% | 12.8% | 8.652% | 1.1368 | 1.1468 | 1.0947
2010-06-04 | 18 | 41.3029 | 16.2768 | 57.5797 | 5.7673 | 0.76558 | 0.42805 | 6.9609 | 12.09% | 12.86% | 8.692% | 1.1375 | 1.1476 | 1.0952
2010-06-04 | 19 | 42.5966 | 16.1994 | 58.796 | 6.0135 | 0.76558 | 0.4371 | 7.2162 | 12.27% | 13.06% | 8.825% | 1.1399 | 1.1502 | 1.0968
2010-06-04 | 20 | 41.1744 | 15.7658 | 56.9402 | 5.6399 | 0.76558 | 0.4233 | 6.8288 | 11.99% | 12.76% | 8.623% | 1.1363 | 1.1463 | 1.0944
2010-06-04 | 21 | 41.1875 | 15.3626 | 56.5502 | 5.5629 | 0.76558 | 0.4204 | 6.7489 | 11.93% | 12.7% | 8.581% | 1.1355 | 1.1455 | 1.0939
2010-06-04 | 22 | 40.1809 | 15.0246 | 55.2055 | 5.3015 | 0.76558 | 0.4104 | 6.4775 | 11.73% | 12.48% | 8.436% | 1.1329 | 1.1427 | 1.0921
2010-06-04 | 23 | 38.4638 | 14.6677 | 53.1315 | 4.9106 | 0.76558 | 0.39499 | 6.0712 | 11.43% | 12.16% | 8.216% | 1.129 | 1.1384 | 1.0895
2010-06-04 | 24 | 37.0551 | 14.3579 | 51.413 | 4.5981 | 0.76558 | 0.38221 | 5.7459 | 11.18% | 11.89% | 8.036% | 1.1258 | 1.135 | 1.0874
2010-06-04 | 25 | 34.9283 | 14.0619 | 48.9902 | 4.175 | 0.76558 | 0.3642 | 5.3047 | 10.83% | 11.52% | 7.785% | 1.1214 | 1.1302 | 1.0844
2010-06-04 | 26 | 32.4004 | 13.4131 | 45.8135 | 3.6511 | 0.76558 | 0.34058 | 4.7572 | 10.38% | 11.05% | 7.466% | 1.1159 | 1.1242 | 1.0807
2010-06-04 | 27 | 32.9338 | 13.7317 | 46.6655 | 3.7881 | 0.76558 | 0.34692 | 4.9006 | 10.5% | 11.17% | 7.551% | 1.1173 | 1.1258 | 1.0817
2010-06-04 | 28 | 33.8674 | 13.8466 | 47.714 | 3.9603 | 0.76558 | 0.35471 | 5.0806 | 10.65% | 11.33% | 7.656% | 1.1192 | 1.1278 | 1.0829
2010-06-04 | 29 | 33.2487 | 13.3568 | 46.6056 | 3.7784 | 0.76558 | 0.34647 | 4.8905 | 10.49% | 11.16% | 7.545% | 1.1172 | 1.1257 | 1.0816
2010-06-04 | 30 | 32.5733 | 12.6153 | 45.1885 | 3.5521 | 0.76558 | 0.33594 | 4.6537 | 10.3% | 10.96% | 7.404% | 1.1148 | 1.1231 | 1.08
2010-06-04 | 31 | 34.0529 | 12.4626 | 46.5155 | 3.7638 | 0.76558 | 0.3458 | 4.8752 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-06-04 | 32 | 34.4279 | 12.2782 | 46.7061 | 3.7947 | 0.76558 | 0.34722 | 4.9075 | 10.51% | 11.18% | 7.555% | 1.1174 | 1.1259 | 1.0817
2010-06-04 | 33 | 35.1591 | 12.9205 | 48.0796 | 4.0212 | 0.76558 | 0.35743 | 5.1442 | 10.7% | 11.38% | 7.693% | 1.1198 | 1.1285 | 1.0833
2010-06-04 | 34 | 35.6456 | 13.2711 | 48.9167 | 4.1625 | 0.76558 | 0.36365 | 5.2917 | 10.82% | 11.51% | 7.778% | 1.1213 | 1.1301 | 1.0843
2010-06-04 | 35 | 36.722 | 14.3039 | 51.0259 | 4.5291 | 0.76558 | 0.37933 | 5.6741 | 11.12% | 11.83% | 7.995% | 1.1251 | 1.1342 | 1.0869
2010-06-04 | 36 | 38.8466 | 15.5901 | 54.4367 | 5.1549 | 0.76558 | 0.40469 | 6.3251 | 11.62% | 12.36% | 8.354% | 1.1315 | 1.1411 | 1.0912
2010-06-04 | 37 | 39.8511 | 15.6052 | 55.4563 | 5.3498 | 0.76558 | 0.41227 | 6.5276 | 11.77% | 12.52% | 8.463% | 1.1334 | 1.1432 | 1.0925
2010-06-04 | 38 | 40.2537 | 15.1831 | 55.4368 | 5.346 | 0.76558 | 0.41212 | 6.5237 | 11.77% | 12.52% | 8.461% | 1.1334 | 1.1431 | 1.0924
2010-06-04 | 39 | 39.6644 | 14.6047 | 54.2691 | 5.1232 | 0.76558 | 0.40344 | 6.2922 | 11.59% | 12.34% | 8.336% | 1.1312 | 1.1407 | 1.0909
2010-06-04 | 40 | 38.3607 | 13.9228 | 52.2835 | 4.7551 | 0.76558 | 0.38868 | 5.9094 | 11.3% | 12.03% | 8.127% | 1.1274 | 1.1367 | 1.0885
2010-06-04 | 41 | 38.5197 | 13.5829 | 52.1027 | 4.7223 | 0.76558 | 0.38734 | 5.8752 | 11.28% | 12% | 8.108% | 1.1271 | 1.1363 | 1.0882
2010-06-04 | 42 | 38.6205 | 13.2694 | 51.8899 | 4.6838 | 0.76558 | 0.38576 | 5.8351 | 11.25% | 11.96% | 8.085% | 1.1267 | 1.1359 | 1.088
2010-06-04 | 43 | 36.9683 | 12.4739 | 49.4422 | 4.2524 | 0.76558 | 0.36756 | 5.3855 | 10.89% | 11.59% | 7.832% | 1.1222 | 1.1311 | 1.085
2010-06-04 | 44 | 34.9719 | 11.8368 | 46.8087 | 3.8114 | 0.76558 | 0.34798 | 4.925 | 10.52% | 11.19% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-06-04 | 45 | 31.309 | 10.5583 | 41.8673 | 3.0492 | 0.76558 | 0.31125 | 4.126 | 9.855% | 10.49% | 7.086% | 1.1093 | 1.1171 | 1.0763
2010-06-04 | 46 | 27.8632 | 9.489 | 37.3523 | 2.427 | 0.76558 | 0.27768 | 3.4703 | 9.291% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-06-04 | 47 | 27.8197 | 9.8392 | 37.6588 | 2.467 | 0.76558 | 0.27996 | 3.5125 | 9.327% | 9.924% | 6.706% | 1.1029 | 1.1102 | 1.0719
2010-06-04 | 48 | 26.9302 | 10.41 | 37.3403 | 2.4254 | 0.76558 | 0.27759 | 3.4686 | 9.289% | 9.884% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-06-05 | 1 | 25.5082 | 9.5189 | 35.0271 | 2.1342 | 0.76558 | 0.2604 | 3.1602 | 9.022% | 9.6% | 6.487% | 1.0992 | 1.1062 | 1.0694
2010-06-05 | 2 | 26.4267 | 9.4296 | 35.8562 | 2.2365 | 0.76558 | 0.26656 | 3.2686 | 9.116% | 9.699% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-06-05 | 3 | 25.3363 | 9.0897 | 34.426 | 2.0616 | 0.76558 | 0.25593 | 3.0831 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-06-05 | 4 | 24.4435 | 8.7425 | 33.1861 | 1.9158 | 0.76558 | 0.24671 | 2.9281 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-06-05 | 5 | 23.783 | 8.5123 | 32.2953 | 1.8143 | 0.76558 | 0.24009 | 2.82 | 8.732% | 9.291% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-06-05 | 6 | 23.2226 | 8.4729 | 31.6956 | 1.7476 | 0.76558 | 0.23563 | 2.7488 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1017 | 1.0665
2010-06-05 | 7 | 23.1507 | 8.3554 | 31.5061 | 1.7267 | 0.76558 | 0.23422 | 2.7265 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2010-06-05 | 8 | 23.1072 | 8.244 | 31.3512 | 1.7098 | 0.76558 | 0.23307 | 2.7084 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-06-05 | 9 | 23.3229 | 8.2623 | 31.5852 | 1.7354 | 0.76558 | 0.23481 | 2.7358 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-06-05 | 10 | 23.3823 | 8.4737 | 31.856 | 1.7653 | 0.76558 | 0.23682 | 2.7677 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-06-05 | 11 | 23.4544 | 8.6538 | 32.1083 | 1.7934 | 0.76558 | 0.2387 | 2.7976 | 8.713% | 9.271% | 6.265% | 1.0954 | 1.1022 | 1.0668
2010-06-05 | 12 | 24.0273 | 9.0555 | 33.0828 | 1.9039 | 0.76558 | 0.24594 | 2.9154 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-06-05 | 13 | 26.067 | 10.0558 | 36.1228 | 2.2698 | 0.76558 | 0.26854 | 3.304 | 9.146% | 9.732% | 6.576% | 1.1007 | 1.1078 | 1.0704
2010-06-05 | 14 | 29.5019 | 11.696 | 41.1979 | 2.9525 | 0.76558 | 0.30627 | 4.0243 | 9.768% | 10.39% | 7.023% | 1.1083 | 1.116 | 1.0755
2010-06-05 | 15 | 33.278 | 13.5769 | 46.8549 | 3.819 | 0.76558 | 0.34832 | 4.9329 | 10.53% | 11.2% | 7.57% | 1.1177 | 1.1261 | 1.0819
2010-06-05 | 16 | 34.4679 | 14.8659 | 49.3338 | 4.2337 | 0.76558 | 0.36675 | 5.3661 | 10.88% | 11.57% | 7.821% | 1.122 | 1.1309 | 1.0848
2010-06-05 | 17 | 35.9621 | 15.7333 | 51.6953 | 4.6488 | 0.76558 | 0.38431 | 5.7987 | 11.22% | 11.93% | 8.065% | 1.1263 | 1.1355 | 1.0877
2010-06-05 | 18 | 36.4501 | 15.8582 | 52.3083 | 4.7597 | 0.76558 | 0.38887 | 5.9141 | 11.31% | 12.03% | 8.129% | 1.1275 | 1.1367 | 1.0885
2010-06-05 | 19 | 36.4777 | 15.6752 | 52.1528 | 4.7314 | 0.76558 | 0.38771 | 5.8847 | 11.28% | 12.01% | 8.113% | 1.1272 | 1.1364 | 1.0883
2010-06-05 | 20 | 35.5442 | 15.0099 | 50.5541 | 4.4458 | 0.76558 | 0.37583 | 5.5872 | 11.05% | 11.76% | 7.946% | 1.1243 | 1.1333 | 1.0863
2010-06-05 | 21 | 36.3491 | 14.6318 | 50.9809 | 4.5212 | 0.76558 | 0.379 | 5.6657 | 11.11% | 11.82% | 7.991% | 1.125 | 1.1341 | 1.0868
2010-06-05 | 22 | 35.632 | 14.2062 | 49.8382 | 4.3208 | 0.76558 | 0.3705 | 5.4568 | 10.95% | 11.65% | 7.872% | 1.123 | 1.1319 | 1.0855
2010-06-05 | 23 | 33.7809 | 13.6205 | 47.4014 | 3.9086 | 0.76558 | 0.35239 | 5.0265 | 10.6% | 11.28% | 7.624% | 1.1186 | 1.1272 | 1.0825
2010-06-05 | 24 | 32.2282 | 13.238 | 45.4661 | 3.5959 | 0.76558 | 0.338 | 4.6995 | 10.34% | 11% | 7.432% | 1.1153 | 1.1236 | 1.0803
2010-06-05 | 25 | 30.5037 | 12.8089 | 43.3126 | 3.2633 | 0.76558 | 0.32199 | 4.3509 | 10.05% | 10.69% | 7.223% | 1.1117 | 1.1197 | 1.0778
2010-06-05 | 26 | 29.239 | 11.6423 | 40.8813 | 2.9073 | 0.76558 | 0.30392 | 3.9768 | 9.728% | 10.35% | 6.994% | 1.1078 | 1.1155 | 1.0752
2010-06-05 | 27 | 29.8572 | 11.953 | 41.8102 | 3.0409 | 0.76558 | 0.31082 | 4.1173 | 9.848% | 10.48% | 7.08% | 1.1092 | 1.117 | 1.0762
2010-06-05 | 28 | 30.3598 | 12.1545 | 42.5143 | 3.1442 | 0.76558 | 0.31606 | 4.2258 | 9.94% | 10.58% | 7.147% | 1.1104 | 1.1183 | 1.077
2010-06-05 | 29 | 29.5991 | 11.6266 | 41.2256 | 2.9564 | 0.76558 | 0.30648 | 4.0285 | 9.772% | 10.4% | 7.026% | 1.1083 | 1.116 | 1.0756
2010-06-05 | 30 | 29.3118 | 11.2126 | 40.5244 | 2.8567 | 0.76558 | 0.30126 | 3.9236 | 9.682% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-06-05 | 31 | 31.3234 | 11.2152 | 42.5386 | 3.1478 | 0.76558 | 0.31624 | 4.2296 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-06-05 | 32 | 31.6242 | 11.1846 | 42.8088 | 3.1879 | 0.76558 | 0.31825 | 4.2717 | 9.979% | 10.62% | 7.175% | 1.1108 | 1.1188 | 1.0773
2010-06-05 | 33 | 31.8548 | 11.4522 | 43.307 | 3.2625 | 0.76558 | 0.32195 | 4.35 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-06-05 | 34 | 32.4304 | 12.1073 | 44.5377 | 3.4506 | 0.76558 | 0.3311 | 4.5472 | 10.21% | 10.86% | 7.341% | 1.1137 | 1.1219 | 1.0792
2010-06-05 | 35 | 33.4775 | 12.7919 | 46.2695 | 3.7241 | 0.76558 | 0.34397 | 4.8337 | 10.45% | 11.12% | 7.511% | 1.1167 | 1.1251 | 1.0812
2010-06-05 | 36 | 37.5849 | 14.0522 | 51.6371 | 4.6383 | 0.76558 | 0.38388 | 5.7878 | 11.21% | 11.93% | 8.059% | 1.1262 | 1.1354 | 1.0877
2010-06-05 | 37 | 39.7544 | 13.9948 | 53.7492 | 5.0255 | 0.76558 | 0.39958 | 6.1907 | 11.52% | 12.25% | 8.281% | 1.1302 | 1.1397 | 1.0903
2010-06-05 | 38 | 40.8425 | 14.13 | 54.9725 | 5.2568 | 0.76558 | 0.40867 | 6.4311 | 11.7% | 12.45% | 8.411% | 1.1325 | 1.1422 | 1.0918
2010-06-05 | 39 | 40.3854 | 13.4935 | 53.879 | 5.0498 | 0.76558 | 0.40054 | 6.2159 | 11.54% | 12.28% | 8.295% | 1.1304 | 1.1399 | 1.0905
2010-06-05 | 40 | 40.0406 | 12.9298 | 52.9704 | 4.8809 | 0.76558 | 0.39379 | 6.0403 | 11.4% | 12.13% | 8.199% | 1.1287 | 1.1381 | 1.0893
2010-06-05 | 41 | 40.5293 | 12.7703 | 53.2996 | 4.9418 | 0.76558 | 0.39624 | 6.1036 | 11.45% | 12.18% | 8.234% | 1.1293 | 1.1387 | 1.0897
2010-06-05 | 42 | 40.6161 | 12.3218 | 52.9379 | 4.8749 | 0.76558 | 0.39355 | 6.034 | 11.4% | 12.13% | 8.195% | 1.1286 | 1.138 | 1.0893
2010-06-05 | 43 | 38.8937 | 11.9453 | 50.839 | 4.496 | 0.76558 | 0.37794 | 5.6395 | 11.09% | 11.8% | 7.976% | 1.1248 | 1.1338 | 1.0867
2010-06-05 | 44 | 36.8683 | 11.1934 | 48.0617 | 4.0182 | 0.76558 | 0.3573 | 5.1411 | 10.7% | 11.38% | 7.691% | 1.1198 | 1.1284 | 1.0833
2010-06-05 | 45 | 34.2964 | 10.223 | 44.5194 | 3.4477 | 0.76558 | 0.33096 | 4.5443 | 10.21% | 10.86% | 7.339% | 1.1137 | 1.1218 | 1.0792
2010-06-05 | 46 | 31.655 | 9.4274 | 41.0824 | 2.9359 | 0.76558 | 0.30541 | 4.0069 | 9.753% | 10.38% | 7.013% | 1.1081 | 1.1158 | 1.0754
2010-06-05 | 47 | 31.7688 | 9.7051 | 41.4739 | 2.9922 | 0.76558 | 0.30832 | 4.0661 | 9.804% | 10.43% | 7.049% | 1.1087 | 1.1165 | 1.0758
2010-06-05 | 48 | 31.2097 | 10.335 | 41.5447 | 3.0024 | 0.76558 | 0.30885 | 4.0768 | 9.813% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-06-06 | 1 | 29.7305 | 9.515 | 39.2455 | 2.6793 | 0.76558 | 0.29176 | 3.7366 | 9.521% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-06-06 | 2 | 30.9083 | 9.4507 | 40.359 | 2.8335 | 0.76558 | 0.30003 | 3.8991 | 9.661% | 10.28% | 6.946% | 1.1069 | 1.1146 | 1.0746
2010-06-06 | 3 | 29.9039 | 8.8824 | 38.7863 | 2.6169 | 0.76558 | 0.28834 | 3.6708 | 9.464% | 10.07% | 6.805% | 1.1045 | 1.112 | 1.073
2010-06-06 | 4 | 28.7271 | 8.4573 | 37.1844 | 2.4052 | 0.76558 | 0.27643 | 3.4472 | 9.271% | 9.864% | 6.666% | 1.1022 | 1.1094 | 1.0714
2010-06-06 | 5 | 27.9191 | 8.0221 | 35.9412 | 2.2471 | 0.76558 | 0.26719 | 3.2799 | 9.126% | 9.71% | 6.561% | 1.1004 | 1.1075 | 1.0702
2010-06-06 | 6 | 27.5156 | 7.9035 | 35.419 | 2.1823 | 0.76558 | 0.26331 | 3.2112 | 9.066% | 9.646% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-06-06 | 7 | 27.5326 | 7.7766 | 35.3092 | 2.1688 | 0.76558 | 0.26249 | 3.1968 | 9.054% | 9.633% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-06-06 | 8 | 27.4728 | 7.7006 | 35.1734 | 2.1521 | 0.76558 | 0.26148 | 3.1792 | 9.039% | 9.617% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-06-06 | 9 | 27.0271 | 7.6064 | 34.6335 | 2.0865 | 0.76558 | 0.25747 | 3.1096 | 8.979% | 9.553% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-06-06 | 10 | 27.0996 | 7.5983 | 34.6979 | 2.0943 | 0.76558 | 0.25795 | 3.1178 | 8.986% | 9.561% | 6.461% | 1.0987 | 1.1057 | 1.0691
2010-06-06 | 11 | 27.4298 | 7.727 | 35.1568 | 2.1501 | 0.76558 | 0.26136 | 3.177 | 9.037% | 9.615% | 6.497% | 1.0993 | 1.1064 | 1.0695
2010-06-06 | 12 | 27.9027 | 7.8737 | 35.7764 | 2.2265 | 0.76558 | 0.26597 | 3.2581 | 9.107% | 9.69% | 6.548% | 1.1002 | 1.1073 | 1.0701
2010-06-06 | 13 | 28.9225 | 8.1396 | 37.0621 | 2.3894 | 0.76558 | 0.27552 | 3.4305 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-06-06 | 14 | 30.1998 | 8.7036 | 38.9034 | 2.6328 | 0.76558 | 0.28921 | 3.6875 | 9.479% | 10.09% | 6.815% | 1.1047 | 1.1122 | 1.0731
2010-06-06 | 15 | 31.3229 | 9.0667 | 40.3896 | 2.8377 | 0.76558 | 0.30026 | 3.9036 | 9.665% | 10.28% | 6.949% | 1.107 | 1.1146 | 1.0747
2010-06-06 | 16 | 31.7512 | 9.7154 | 41.4666 | 2.9911 | 0.76558 | 0.30827 | 4.0649 | 9.803% | 10.43% | 7.048% | 1.1087 | 1.1164 | 1.0758
2010-06-06 | 17 | 33.5039 | 11.2802 | 44.7842 | 3.4889 | 0.76558 | 0.33293 | 4.5874 | 10.24% | 10.9% | 7.365% | 1.1141 | 1.1223 | 1.0795
2010-06-06 | 18 | 34.5237 | 12.3276 | 46.8514 | 3.8184 | 0.76558 | 0.3483 | 4.9323 | 10.53% | 11.2% | 7.569% | 1.1177 | 1.1261 | 1.0819
2010-06-06 | 19 | 36.0898 | 13.1565 | 49.2463 | 4.2187 | 0.76558 | 0.3661 | 5.3504 | 10.86% | 11.56% | 7.812% | 1.1219 | 1.1307 | 1.0847
2010-06-06 | 20 | 37.1674 | 13.4784 | 50.6458 | 4.4619 | 0.76558 | 0.37651 | 5.604 | 11.07% | 11.77% | 7.956% | 1.1244 | 1.1334 | 1.0864
2010-06-06 | 21 | 39.4372 | 13.9524 | 53.3896 | 4.9585 | 0.76558 | 0.3969 | 6.1209 | 11.46% | 12.2% | 8.243% | 1.1295 | 1.1389 | 1.0898
2010-06-06 | 22 | 39.4218 | 13.7846 | 53.2064 | 4.9245 | 0.76558 | 0.39554 | 6.0856 | 11.44% | 12.17% | 8.224% | 1.1291 | 1.1386 | 1.0896
2010-06-06 | 23 | 38.4014 | 13.425 | 51.8265 | 4.6724 | 0.76558 | 0.38528 | 5.8232 | 11.24% | 11.96% | 8.079% | 1.1266 | 1.1358 | 1.0879
2010-06-06 | 24 | 36.5489 | 13.1803 | 49.7292 | 4.3019 | 0.76558 | 0.36969 | 5.4371 | 10.93% | 11.63% | 7.861% | 1.1228 | 1.1316 | 1.0853
2010-06-06 | 25 | 34.695 | 12.7878 | 47.4828 | 3.922 | 0.76558 | 0.35299 | 5.0406 | 10.62% | 11.29% | 7.633% | 1.1188 | 1.1273 | 1.0826
2010-06-06 | 26 | 33.1872 | 11.8879 | 45.0751 | 3.5343 | 0.76558 | 0.33509 | 4.635 | 10.28% | 10.94% | 7.393% | 1.1146 | 1.1229 | 1.0798
2010-06-06 | 27 | 33.7038 | 12.0833 | 45.7871 | 3.6469 | 0.76558 | 0.34039 | 4.7528 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0807
2010-06-06 | 28 | 33.8498 | 12.1618 | 46.0116 | 3.6827 | 0.76558 | 0.34206 | 4.7904 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-06-06 | 29 | 32.8699 | 11.8153 | 44.6852 | 3.4735 | 0.76558 | 0.33219 | 4.5712 | 10.23% | 10.88% | 7.355% | 1.114 | 1.1221 | 1.0794
2010-06-06 | 30 | 32.9569 | 11.2569 | 44.2138 | 3.4006 | 0.76558 | 0.32869 | 4.4948 | 10.17% | 10.82% | 7.309% | 1.1132 | 1.1213 | 1.0789
2010-06-06 | 31 | 34.5678 | 11.3294 | 45.8972 | 3.6644 | 0.76558 | 0.34121 | 4.7712 | 10.4% | 11.06% | 7.474% | 1.116 | 1.1244 | 1.0808
2010-06-06 | 32 | 35.013 | 11.2466 | 46.2596 | 3.7225 | 0.76558 | 0.3439 | 4.832 | 10.45% | 11.11% | 7.51% | 1.1166 | 1.125 | 1.0812
2010-06-06 | 33 | 35.9894 | 11.4068 | 47.3962 | 3.9077 | 0.76558 | 0.35235 | 5.0256 | 10.6% | 11.28% | 7.624% | 1.1186 | 1.1272 | 1.0825
2010-06-06 | 34 | 37.799 | 11.7276 | 49.5266 | 4.2669 | 0.76558 | 0.36819 | 5.4007 | 10.9% | 11.6% | 7.84% | 1.1224 | 1.1313 | 1.0851
2010-06-06 | 35 | 39.45 | 12.7426 | 52.1926 | 4.7386 | 0.76558 | 0.38801 | 5.8922 | 11.29% | 12.01% | 8.117% | 1.1273 | 1.1365 | 1.0883
2010-06-06 | 36 | 41.5745 | 13.8768 | 55.4513 | 5.3488 | 0.76558 | 0.41223 | 6.5266 | 11.77% | 12.52% | 8.463% | 1.1334 | 1.1432 | 1.0925
2010-06-06 | 37 | 41.703 | 13.858 | 55.561 | 5.37 | 0.76558 | 0.41305 | 6.5486 | 11.79% | 12.54% | 8.474% | 1.1336 | 1.1434 | 1.0926
2010-06-06 | 38 | 41.3729 | 13.4338 | 54.8067 | 5.2252 | 0.76558 | 0.40744 | 6.3982 | 11.67% | 12.42% | 8.394% | 1.1322 | 1.1418 | 1.0916
2010-06-06 | 39 | 40.7878 | 12.9322 | 53.7201 | 5.02 | 0.76558 | 0.39936 | 6.185 | 11.51% | 12.25% | 8.278% | 1.1301 | 1.1396 | 1.0903
2010-06-06 | 40 | 39.8395 | 12.3825 | 52.222 | 4.744 | 0.76558 | 0.38822 | 5.8978 | 11.29% | 12.02% | 8.12% | 1.1273 | 1.1366 | 1.0884
2010-06-06 | 41 | 40.2693 | 12.1235 | 52.3928 | 4.7751 | 0.76558 | 0.38949 | 5.9301 | 11.32% | 12.04% | 8.138% | 1.1276 | 1.1369 | 1.0886
2010-06-06 | 42 | 39.7241 | 11.7153 | 51.4394 | 4.6028 | 0.76558 | 0.38241 | 5.7508 | 11.18% | 11.9% | 8.038% | 1.1259 | 1.135 | 1.0874
2010-06-06 | 43 | 37.9279 | 11.0626 | 48.9905 | 4.175 | 0.76558 | 0.3642 | 5.3048 | 10.83% | 11.52% | 7.785% | 1.1214 | 1.1302 | 1.0844
2010-06-06 | 44 | 36.3339 | 10.5456 | 46.8795 | 3.823 | 0.76558 | 0.34851 | 4.9371 | 10.53% | 11.21% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-06-06 | 45 | 33.2726 | 9.7884 | 43.0611 | 3.2256 | 0.76558 | 0.32012 | 4.3113 | 10.01% | 10.65% | 7.199% | 1.1113 | 1.1192 | 1.0776
2010-06-06 | 46 | 30.1588 | 9.1419 | 39.3007 | 2.6868 | 0.76558 | 0.29217 | 3.7445 | 9.528% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0735
2010-06-06 | 47 | 30.7612 | 9.7165 | 40.4777 | 2.8501 | 0.76558 | 0.30092 | 3.9166 | 9.676% | 10.3% | 6.957% | 1.1071 | 1.1148 | 1.0748
2010-06-06 | 48 | 30.4456 | 10.2993 | 40.7449 | 2.8879 | 0.76558 | 0.3029 | 3.9564 | 9.71% | 10.33% | 6.982% | 1.1075 | 1.1152 | 1.0751
2010-06-07 | 1 | 29.4822 | 9.4755 | 38.9577 | 2.6401 | 0.76558 | 0.28962 | 3.6953 | 9.485% | 10.09% | 6.82% | 1.1048 | 1.1123 | 1.0732
2010-06-07 | 2 | 30.7909 | 9.1351 | 39.926 | 2.773 | 0.76558 | 0.29681 | 3.8354 | 9.606% | 10.22% | 6.907% | 1.1063 | 1.1138 | 1.0742
2010-06-07 | 3 | 30.1565 | 8.6657 | 38.8222 | 2.6218 | 0.76558 | 0.28861 | 3.676 | 9.469% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-06-07 | 4 | 29.4092 | 8.2933 | 37.7026 | 2.4727 | 0.76558 | 0.28029 | 3.5186 | 9.333% | 9.93% | 6.71% | 1.1029 | 1.1102 | 1.0719
2010-06-07 | 5 | 28.9346 | 8.0734 | 37.0079 | 2.3825 | 0.76558 | 0.27512 | 3.4232 | 9.25% | 9.842% | 6.651% | 1.1019 | 1.1092 | 1.0712
2010-06-07 | 6 | 28.4047 | 7.8315 | 36.2362 | 2.2841 | 0.76558 | 0.26938 | 3.3191 | 9.16% | 9.746% | 6.586% | 1.1008 | 1.108 | 1.0705
2010-06-07 | 7 | 28.1756 | 7.6807 | 35.8563 | 2.2365 | 0.76558 | 0.26656 | 3.2686 | 9.116% | 9.699% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-06-07 | 8 | 28.0324 | 7.6252 | 35.6576 | 2.2118 | 0.76558 | 0.26508 | 3.2424 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.07
2010-06-07 | 9 | 28.1035 | 7.5705 | 35.6739 | 2.2138 | 0.76558 | 0.2652 | 3.2446 | 9.095% | 9.677% | 6.539% | 1.1001 | 1.1071 | 1.07
2010-06-07 | 10 | 28.3897 | 7.5986 | 35.9884 | 2.253 | 0.76558 | 0.26754 | 3.2861 | 9.131% | 9.715% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-06-07 | 11 | 28.8507 | 7.729 | 36.5797 | 2.3276 | 0.76558 | 0.27194 | 3.3652 | 9.2% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-06-07 | 12 | 28.9529 | 7.7905 | 36.7434 | 2.3485 | 0.76558 | 0.27315 | 3.3872 | 9.219% | 9.809% | 6.628% | 1.1015 | 1.1088 | 1.071
2010-06-07 | 13 | 30.1148 | 8.1736 | 38.2884 | 2.5502 | 0.76558 | 0.28464 | 3.6004 | 9.403% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-06-07 | 14 | 31.5074 | 8.5473 | 40.0547 | 2.7909 | 0.76558 | 0.29777 | 3.8542 | 9.622% | 10.24% | 6.919% | 1.1065 | 1.1141 | 1.0743
2010-06-07 | 15 | 32.3421 | 8.5903 | 40.9324 | 2.9145 | 0.76558 | 0.3043 | 3.9844 | 9.734% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2010-06-07 | 16 | 32.0937 | 8.8401 | 40.9338 | 2.9147 | 0.76558 | 0.30431 | 3.9846 | 9.734% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2010-06-07 | 17 | 32.7118 | 10.0527 | 42.7645 | 3.1813 | 0.76558 | 0.31792 | 4.2648 | 9.973% | 10.61% | 7.17% | 1.1108 | 1.1187 | 1.0772
2010-06-07 | 18 | 34.522 | 11.3178 | 45.8398 | 3.6553 | 0.76558 | 0.34078 | 4.7616 | 10.39% | 11.05% | 7.469% | 1.1159 | 1.1243 | 1.0807
2010-06-07 | 19 | 37.2816 | 12.0572 | 49.3388 | 4.2346 | 0.76558 | 0.36679 | 5.367 | 10.88% | 11.57% | 7.821% | 1.1221 | 1.1309 | 1.0848
2010-06-07 | 20 | 38.3301 | 12.5143 | 50.8444 | 4.497 | 0.76558 | 0.37798 | 5.6405 | 11.09% | 11.8% | 7.976% | 1.1248 | 1.1338 | 1.0867
2010-06-07 | 21 | 40.6598 | 12.7976 | 53.4574 | 4.9711 | 0.76558 | 0.39741 | 6.1341 | 11.47% | 12.21% | 8.25% | 1.1296 | 1.1391 | 1.0899
2010-06-07 | 22 | 40.3452 | 12.6542 | 52.9994 | 4.8863 | 0.76558 | 0.394 | 6.0458 | 11.41% | 12.14% | 8.202% | 1.1288 | 1.1381 | 1.0893
2010-06-07 | 23 | 38.995 | 12.0428 | 51.0379 | 4.5313 | 0.76558 | 0.37942 | 5.6763 | 11.12% | 11.83% | 7.996% | 1.1251 | 1.1342 | 1.0869
2010-06-07 | 24 | 37.2712 | 11.6292 | 48.9004 | 4.1597 | 0.76558 | 0.36353 | 5.2888 | 10.82% | 11.51% | 7.776% | 1.1213 | 1.13 | 1.0843
2010-06-07 | 25 | 34.9125 | 10.9865 | 45.899 | 3.6647 | 0.76558 | 0.34122 | 4.7715 | 10.4% | 11.06% | 7.475% | 1.116 | 1.1244 | 1.0808
2010-06-07 | 26 | 32.4578 | 10.1231 | 42.5809 | 3.154 | 0.76558 | 0.31655 | 4.2361 | 9.948% | 10.59% | 7.153% | 1.1105 | 1.1184 | 1.077
2010-06-07 | 27 | 32.76 | 10.2851 | 43.0451 | 3.2232 | 0.76558 | 0.32 | 4.3087 | 10.01% | 10.65% | 7.197% | 1.1112 | 1.1192 | 1.0776
2010-06-07 | 28 | 32.9185 | 10.4931 | 43.4116 | 3.2783 | 0.76558 | 0.32273 | 4.3666 | 10.06% | 10.7% | 7.232% | 1.1118 | 1.1198 | 1.078
2010-06-07 | 29 | 32.4871 | 10.0218 | 42.5089 | 3.1434 | 0.76558 | 0.31602 | 4.225 | 9.939% | 10.58% | 7.146% | 1.1104 | 1.1183 | 1.077
2010-06-07 | 30 | 32.545 | 9.7265 | 42.2715 | 3.1083 | 0.76558 | 0.31425 | 4.1882 | 9.908% | 10.54% | 7.124% | 1.11 | 1.1178 | 1.0767
2010-06-07 | 31 | 34.4864 | 9.8407 | 44.3271 | 3.418 | 0.76558 | 0.32953 | 4.5131 | 10.18% | 10.83% | 7.32% | 1.1134 | 1.1215 | 1.079
2010-06-07 | 32 | 35.2051 | 9.9125 | 45.1176 | 3.541 | 0.76558 | 0.33541 | 4.642 | 10.29% | 10.95% | 7.398% | 1.1147 | 1.1229 | 1.0799
2010-06-07 | 33 | 35.8792 | 10.5111 | 46.3902 | 3.7436 | 0.76558 | 0.34487 | 4.854 | 10.46% | 11.13% | 7.523% | 1.1169 | 1.1253 | 1.0814
2010-06-07 | 34 | 37.7896 | 11.1065 | 48.8961 | 4.1589 | 0.76558 | 0.3635 | 5.288 | 10.81% | 11.51% | 7.776% | 1.1213 | 1.13 | 1.0843
2010-06-07 | 35 | 40.0421 | 12.7756 | 52.8177 | 4.8528 | 0.76558 | 0.39265 | 6.011 | 11.38% | 12.11% | 8.183% | 1.1284 | 1.1378 | 1.0891
2010-06-07 | 36 | 42.6833 | 14.1979 | 56.8812 | 5.6282 | 0.76558 | 0.42286 | 6.8167 | 11.98% | 12.75% | 8.617% | 1.1362 | 1.1461 | 1.0943
2010-06-07 | 37 | 43.4861 | 14.1342 | 57.6203 | 5.7755 | 0.76558 | 0.42836 | 6.9694 | 12.1% | 12.87% | 8.697% | 1.1376 | 1.1477 | 1.0952
2010-06-07 | 38 | 43.2704 | 13.8619 | 57.1322 | 5.678 | 0.76558 | 0.42473 | 6.8683 | 12.02% | 12.79% | 8.644% | 1.1366 | 1.1467 | 1.0946
2010-06-07 | 39 | 42.9691 | 13.5276 | 56.4967 | 5.5524 | 0.76558 | 0.42 | 6.738 | 11.93% | 12.69% | 8.575% | 1.1354 | 1.1453 | 1.0938
2010-06-07 | 40 | 41.9071 | 13.2478 | 55.1549 | 5.2918 | 0.76558 | 0.41003 | 6.4674 | 11.73% | 12.48% | 8.431% | 1.1328 | 1.1425 | 1.0921
2010-06-07 | 41 | 42.1545 | 13.1295 | 55.284 | 5.3166 | 0.76558 | 0.41099 | 6.4932 | 11.75% | 12.5% | 8.445% | 1.1331 | 1.1428 | 1.0922
2010-06-07 | 42 | 41.5939 | 12.5415 | 54.1354 | 5.098 | 0.76558 | 0.40245 | 6.266 | 11.57% | 12.32% | 8.322% | 1.1309 | 1.1405 | 1.0908
2010-06-07 | 43 | 39.1241 | 11.7384 | 50.8625 | 4.5002 | 0.76558 | 0.37812 | 5.6439 | 11.1% | 11.81% | 7.978% | 1.1248 | 1.1339 | 1.0867
2010-06-07 | 44 | 36.9388 | 11.1158 | 48.0547 | 4.017 | 0.76558 | 0.35724 | 5.1399 | 10.7% | 11.38% | 7.69% | 1.1198 | 1.1284 | 1.0833
2010-06-07 | 45 | 33.3192 | 10.0321 | 43.3513 | 3.2692 | 0.76558 | 0.32228 | 4.357 | 10.05% | 10.69% | 7.226% | 1.1117 | 1.1197 | 1.0779
2010-06-07 | 46 | 30.6049 | 8.8863 | 39.4912 | 2.7129 | 0.76558 | 0.29358 | 3.7721 | 9.552% | 10.16% | 6.868% | 1.1056 | 1.1131 | 1.0737
2010-06-07 | 47 | 30.3767 | 9.3621 | 39.7388 | 2.747 | 0.76558 | 0.29542 | 3.808 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-06-07 | 48 | 29.4839 | 9.9946 | 39.4785 | 2.7112 | 0.76558 | 0.29349 | 3.7702 | 9.55% | 10.16% | 6.867% | 1.1056 | 1.1131 | 1.0737
2010-06-08 | 1 | 27.2862 | 9.246 | 36.5322 | 2.3216 | 0.76558 | 0.27158 | 3.3588 | 9.194% | 9.782% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-06-08 | 2 | 28.307 | 9.2005 | 37.5075 | 2.4472 | 0.76558 | 0.27884 | 3.4916 | 9.309% | 9.905% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-06-08 | 3 | 27.7458 | 8.8435 | 36.5893 | 2.3289 | 0.76558 | 0.27201 | 3.3664 | 9.201% | 9.789% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-06-08 | 4 | 26.683 | 8.6749 | 35.3579 | 2.1747 | 0.76558 | 0.26285 | 3.2032 | 9.059% | 9.639% | 6.514% | 1.0996 | 1.1067 | 1.0697
2010-06-08 | 5 | 26.0786 | 8.4528 | 34.5314 | 2.0743 | 0.76558 | 0.25671 | 3.0965 | 8.967% | 9.541% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-06-08 | 6 | 25.4325 | 8.2653 | 33.6978 | 1.9753 | 0.76558 | 0.25051 | 2.9914 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-06-08 | 7 | 25.1435 | 8.3377 | 33.4813 | 1.95 | 0.76558 | 0.2489 | 2.9645 | 8.854% | 9.421% | 6.366% | 1.0971 | 1.104 | 1.068
2010-06-08 | 8 | 25.2011 | 8.2546 | 33.4557 | 1.947 | 0.76558 | 0.24871 | 2.9613 | 8.851% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2010-06-08 | 9 | 25.1878 | 8.3287 | 33.5165 | 1.9541 | 0.76558 | 0.24917 | 2.9689 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-06-08 | 10 | 25.1578 | 8.6683 | 33.8261 | 1.9904 | 0.76558 | 0.25147 | 3.0074 | 8.891% | 9.46% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-06-08 | 11 | 25.5461 | 8.7941 | 34.3402 | 2.0514 | 0.76558 | 0.25529 | 3.0722 | 8.946% | 9.519% | 6.432% | 1.0983 | 1.1052 | 1.0687
2010-06-08 | 12 | 26.6694 | 9.1211 | 35.7906 | 2.2283 | 0.76558 | 0.26607 | 3.2599 | 9.108% | 9.691% | 6.549% | 1.1002 | 1.1073 | 1.0701
2010-06-08 | 13 | 28.924 | 10.3219 | 39.2459 | 2.6793 | 0.76558 | 0.29176 | 3.7367 | 9.521% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-06-08 | 14 | 32.1701 | 12.083 | 44.2531 | 3.4066 | 0.76558 | 0.32898 | 4.5012 | 10.17% | 10.82% | 7.313% | 1.1132 | 1.1214 | 1.0789
2010-06-08 | 15 | 36.1191 | 14.2233 | 50.3424 | 4.4086 | 0.76558 | 0.37425 | 5.5485 | 11.02% | 11.73% | 7.924% | 1.1239 | 1.1328 | 1.0861
2010-06-08 | 16 | 37.7869 | 15.4655 | 53.2524 | 4.933 | 0.76558 | 0.39588 | 6.0945 | 11.44% | 12.18% | 8.229% | 1.1292 | 1.1387 | 1.0897
2010-06-08 | 17 | 39.6828 | 16.3142 | 55.997 | 5.4546 | 0.76558 | 0.41629 | 6.6365 | 11.85% | 12.61% | 8.521% | 1.1344 | 1.1443 | 1.0931
2010-06-08 | 18 | 40.7448 | 16.3402 | 57.085 | 5.6686 | 0.76558 | 0.42438 | 6.8586 | 12.01% | 12.78% | 8.639% | 1.1366 | 1.1466 | 1.0946
2010-06-08 | 19 | 40.7718 | 16.3748 | 57.1466 | 5.6809 | 0.76558 | 0.42483 | 6.8713 | 12.02% | 12.79% | 8.645% | 1.1367 | 1.1467 | 1.0946
2010-06-08 | 20 | 39.8408 | 16.2862 | 56.127 | 5.48 | 0.76558 | 0.41725 | 6.6628 | 11.87% | 12.63% | 8.535% | 1.1347 | 1.1446 | 1.0933
2010-06-08 | 21 | 41.636 | 16.037 | 57.673 | 5.786 | 0.76558 | 0.42875 | 6.9803 | 12.1% | 12.88% | 8.702% | 1.1377 | 1.1478 | 1.0953
2010-06-08 | 22 | 41.0909 | 15.1177 | 56.2087 | 5.4959 | 0.76558 | 0.41786 | 6.6794 | 11.88% | 12.64% | 8.544% | 1.1349 | 1.1447 | 1.0934
2010-06-08 | 23 | 39.51 | 14.1451 | 53.6551 | 5.0079 | 0.76558 | 0.39888 | 6.1724 | 11.5% | 12.24% | 8.271% | 1.13 | 1.1395 | 1.0902
2010-06-08 | 24 | 37.4844 | 13.6474 | 51.1318 | 4.548 | 0.76558 | 0.38012 | 5.6937 | 11.14% | 11.85% | 8.006% | 1.1253 | 1.1344 | 1.087
2010-06-08 | 25 | 35.0847 | 12.8944 | 47.9791 | 4.0044 | 0.76558 | 0.35668 | 5.1267 | 10.69% | 11.37% | 7.683% | 1.1196 | 1.1283 | 1.0832
2010-06-08 | 26 | 33.1462 | 12.0582 | 45.2044 | 3.5546 | 0.76558 | 0.33606 | 4.6563 | 10.3% | 10.96% | 7.406% | 1.1148 | 1.1231 | 1.08
2010-06-08 | 27 | 33.3189 | 12.2043 | 45.5232 | 3.605 | 0.76558 | 0.33843 | 4.709 | 10.34% | 11.01% | 7.437% | 1.1154 | 1.1237 | 1.0803
2010-06-08 | 28 | 33.2612 | 12.4195 | 45.6807 | 3.6299 | 0.76558 | 0.3396 | 4.7351 | 10.37% | 11.03% | 7.453% | 1.1156 | 1.124 | 1.0805
2010-06-08 | 29 | 32.3723 | 11.8474 | 44.2197 | 3.4015 | 0.76558 | 0.32873 | 4.4958 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-06-08 | 30 | 32.2569 | 11.4126 | 43.6696 | 3.3174 | 0.76558 | 0.32464 | 4.4076 | 10.09% | 10.74% | 7.257% | 1.1123 | 1.1203 | 1.0782
2010-06-08 | 31 | 34.3109 | 11.6143 | 45.9253 | 3.6689 | 0.76558 | 0.34141 | 4.7759 | 10.4% | 11.06% | 7.477% | 1.1161 | 1.1244 | 1.0808
2010-06-08 | 32 | 35.001 | 11.5488 | 46.5498 | 3.7694 | 0.76558 | 0.34606 | 4.881 | 10.49% | 11.16% | 7.539% | 1.1171 | 1.1256 | 1.0815
2010-06-08 | 33 | 35.1723 | 12.4319 | 47.6042 | 3.9421 | 0.76558 | 0.3539 | 5.0616 | 10.63% | 11.31% | 7.645% | 1.119 | 1.1276 | 1.0828
2010-06-08 | 34 | 36.4335 | 13.285 | 49.7185 | 4.3 | 0.76558 | 0.36961 | 5.4352 | 10.93% | 11.63% | 7.86% | 1.1227 | 1.1316 | 1.0853
2010-06-08 | 35 | 37.4538 | 14.6286 | 52.0824 | 4.7186 | 0.76558 | 0.38719 | 5.8714 | 11.27% | 11.99% | 8.105% | 1.1271 | 1.1363 | 1.0882
2010-06-08 | 36 | 40.0241 | 15.7513 | 55.7754 | 5.4115 | 0.76558 | 0.41464 | 6.5918 | 11.82% | 12.57% | 8.497% | 1.134 | 1.1438 | 1.0929
2010-06-08 | 37 | 40.9777 | 15.5912 | 56.5689 | 5.5666 | 0.76558 | 0.42054 | 6.7527 | 11.94% | 12.7% | 8.583% | 1.1356 | 1.1455 | 1.0939
2010-06-08 | 38 | 40.79 | 15.2633 | 56.0533 | 5.4656 | 0.76558 | 0.41671 | 6.6479 | 11.86% | 12.62% | 8.527% | 1.1346 | 1.1444 | 1.0932
2010-06-08 | 39 | 40.3465 | 14.8001 | 55.1466 | 5.2902 | 0.76558 | 0.40997 | 6.4657 | 11.72% | 12.48% | 8.43% | 1.1328 | 1.1425 | 1.0921
2010-06-08 | 40 | 39.1184 | 14.2322 | 53.3506 | 4.9512 | 0.76558 | 0.39661 | 6.1134 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1389 | 1.0898
2010-06-08 | 41 | 39.3908 | 13.8272 | 53.218 | 4.9266 | 0.76558 | 0.39563 | 6.0879 | 11.44% | 12.17% | 8.225% | 1.1292 | 1.1386 | 1.0896
2010-06-08 | 42 | 39.4637 | 13.3846 | 52.8483 | 4.8584 | 0.76558 | 0.39288 | 6.0169 | 11.39% | 12.11% | 8.186% | 1.1285 | 1.1378 | 1.0892
2010-06-08 | 43 | 37.3167 | 12.9668 | 50.2834 | 4.3983 | 0.76558 | 0.37381 | 5.5377 | 11.01% | 11.72% | 7.918% | 1.1238 | 1.1327 | 1.086
2010-06-08 | 44 | 35.521 | 12.0161 | 47.5371 | 3.931 | 0.76558 | 0.3534 | 5.0499 | 10.62% | 11.3% | 7.638% | 1.1189 | 1.1274 | 1.0827
2010-06-08 | 45 | 31.8088 | 10.9056 | 42.7144 | 3.1738 | 0.76558 | 0.31754 | 4.2569 | 9.966% | 10.6% | 7.166% | 1.1107 | 1.1186 | 1.0772
2010-06-08 | 46 | 28.2395 | 9.8144 | 38.0539 | 2.519 | 0.76558 | 0.2829 | 3.5675 | 9.375% | 9.975% | 6.741% | 1.1034 | 1.1108 | 1.0723
2010-06-08 | 47 | 27.7726 | 10.0946 | 37.8672 | 2.4944 | 0.76558 | 0.28151 | 3.5415 | 9.352% | 9.951% | 6.724% | 1.1032 | 1.1105 | 1.0721
2010-06-08 | 48 | 27.364 | 10.6125 | 37.9765 | 2.5088 | 0.76558 | 0.28232 | 3.5567 | 9.366% | 9.965% | 6.734% | 1.1033 | 1.1107 | 1.0722
2010-06-09 | 1 | 25.6677 | 9.6474 | 35.3151 | 2.1695 | 0.76558 | 0.26254 | 3.1976 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-06-09 | 2 | 26.7259 | 9.5355 | 36.2614 | 2.2873 | 0.76558 | 0.26957 | 3.3225 | 9.163% | 9.749% | 6.588% | 1.1009 | 1.108 | 1.0705
2010-06-09 | 3 | 25.5475 | 9.1882 | 34.7357 | 2.0989 | 0.76558 | 0.25823 | 3.1227 | 8.99% | 9.565% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-06-09 | 4 | 24.4691 | 8.9079 | 33.377 | 1.9379 | 0.76558 | 0.24813 | 2.9516 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-06-09 | 5 | 23.9809 | 8.6328 | 32.6137 | 1.8503 | 0.76558 | 0.24245 | 2.8583 | 8.764% | 9.325% | 6.301% | 1.0961 | 1.1028 | 1.0673
2010-06-09 | 6 | 23.547 | 8.4129 | 31.96 | 1.7768 | 0.76558 | 0.23759 | 2.78 | 8.698% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-06-09 | 7 | 22.7733 | 8.2233 | 30.9967 | 1.6713 | 0.76558 | 0.23043 | 2.6673 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2010-06-09 | 8 | 22.4285 | 8.2477 | 30.6762 | 1.637 | 0.76558 | 0.22805 | 2.6306 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-06-09 | 9 | 22.7439 | 8.1797 | 30.9236 | 1.6635 | 0.76558 | 0.22989 | 2.6589 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-06-09 | 10 | 22.9744 | 8.3317 | 31.3061 | 1.7049 | 0.76558 | 0.23273 | 2.7032 | 8.635% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-06-09 | 11 | 23.0888 | 8.5168 | 31.6056 | 1.7377 | 0.76558 | 0.23496 | 2.7382 | 8.664% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-06-09 | 12 | 23.8786 | 9.0897 | 32.9684 | 1.8907 | 0.76558 | 0.24509 | 2.9014 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2010-06-09 | 13 | 25.9069 | 10.0685 | 35.9754 | 2.2514 | 0.76558 | 0.26745 | 3.2844 | 9.13% | 9.714% | 6.564% | 1.1005 | 1.1076 | 1.0703
2010-06-09 | 14 | 29.3677 | 11.7535 | 41.1212 | 2.9415 | 0.76558 | 0.3057 | 4.0128 | 9.758% | 10.38% | 7.016% | 1.1081 | 1.1159 | 1.0755
2010-06-09 | 15 | 33.0318 | 13.9156 | 46.9474 | 3.834 | 0.76558 | 0.34901 | 4.9486 | 10.54% | 11.22% | 7.579% | 1.1178 | 1.1263 | 1.082
2010-06-09 | 16 | 34.8704 | 15.0917 | 49.9621 | 4.3423 | 0.76558 | 0.37142 | 5.4793 | 10.97% | 11.67% | 7.885% | 1.1232 | 1.1321 | 1.0856
2010-06-09 | 17 | 36.1906 | 16.1142 | 52.3048 | 4.759 | 0.76558 | 0.38884 | 5.9134 | 11.31% | 12.03% | 8.129% | 1.1275 | 1.1367 | 1.0885
2010-06-09 | 18 | 36.6357 | 16.1777 | 52.8134 | 4.852 | 0.76558 | 0.39262 | 6.0102 | 11.38% | 12.11% | 8.182% | 1.1284 | 1.1378 | 1.0891
2010-06-09 | 19 | 36.7225 | 16.1305 | 52.853 | 4.8593 | 0.76558 | 0.39292 | 6.0178 | 11.39% | 12.11% | 8.186% | 1.1285 | 1.1378 | 1.0892
2010-06-09 | 20 | 35.4446 | 15.5041 | 50.9488 | 4.5155 | 0.76558 | 0.37876 | 5.6598 | 11.11% | 11.82% | 7.987% | 1.125 | 1.134 | 1.0868
2010-06-09 | 21 | 36.4815 | 14.6823 | 51.1637 | 4.5536 | 0.76558 | 0.38036 | 5.6996 | 11.14% | 11.85% | 8.01% | 1.1254 | 1.1345 | 1.0871
2010-06-09 | 22 | 35.4486 | 13.8347 | 49.2832 | 4.2251 | 0.76558 | 0.36638 | 5.357 | 10.87% | 11.57% | 7.815% | 1.122 | 1.1308 | 1.0848
2010-06-09 | 23 | 33.7361 | 13.1782 | 46.9142 | 3.8286 | 0.76558 | 0.34877 | 4.943 | 10.54% | 11.21% | 7.576% | 1.1178 | 1.1263 | 1.082
2010-06-09 | 24 | 32.6596 | 13.0645 | 45.7242 | 3.6369 | 0.76558 | 0.33992 | 4.7424 | 10.37% | 11.04% | 7.457% | 1.1157 | 1.124 | 1.0806
2010-06-09 | 25 | 30.5762 | 12.4986 | 43.0748 | 3.2276 | 0.76558 | 0.32022 | 4.3134 | 10.01% | 10.65% | 7.2% | 1.1113 | 1.1193 | 1.0776
2010-06-09 | 26 | 29.2976 | 11.4579 | 40.7555 | 2.8894 | 0.76558 | 0.30298 | 3.958 | 9.711% | 10.33% | 6.983% | 1.1076 | 1.1152 | 1.0751
2010-06-09 | 27 | 30.0422 | 11.687 | 41.7293 | 3.0291 | 0.76558 | 0.31022 | 4.1049 | 9.837% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-06-09 | 28 | 30.4614 | 11.908 | 42.3694 | 3.1228 | 0.76558 | 0.31498 | 4.2033 | 9.921% | 10.56% | 7.133% | 1.1101 | 1.118 | 1.0768
2010-06-09 | 29 | 29.4286 | 11.2324 | 40.6609 | 2.876 | 0.76558 | 0.30228 | 3.9439 | 9.699% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-06-09 | 30 | 28.7389 | 10.9828 | 39.7216 | 2.7447 | 0.76558 | 0.2953 | 3.8055 | 9.581% | 10.19% | 6.888% | 1.106 | 1.1135 | 1.074
2010-06-09 | 31 | 31.0082 | 11.1067 | 42.1149 | 3.0854 | 0.76558 | 0.31309 | 4.164 | 9.887% | 10.52% | 7.109% | 1.1097 | 1.1176 | 1.0765
2010-06-09 | 32 | 31.4958 | 11.0894 | 42.5853 | 3.1547 | 0.76558 | 0.31658 | 4.2368 | 9.949% | 10.59% | 7.153% | 1.1105 | 1.1184 | 1.077
2010-06-09 | 33 | 31.7548 | 11.2236 | 42.9785 | 3.2132 | 0.76558 | 0.31951 | 4.2983 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-06-09 | 34 | 32.6288 | 11.8352 | 44.464 | 3.4392 | 0.76558 | 0.33055 | 4.5353 | 10.2% | 10.85% | 7.334% | 1.1136 | 1.1217 | 1.0791
2010-06-09 | 35 | 33.5618 | 13.2841 | 46.8459 | 3.8175 | 0.76558 | 0.34826 | 4.9313 | 10.53% | 11.2% | 7.569% | 1.1177 | 1.1261 | 1.0819
2010-06-09 | 36 | 36.2317 | 14.6876 | 50.9193 | 4.5102 | 0.76558 | 0.37854 | 5.6544 | 11.1% | 11.82% | 7.984% | 1.1249 | 1.134 | 1.0868
2010-06-09 | 37 | 37.4939 | 14.7276 | 52.2215 | 4.7439 | 0.76558 | 0.38822 | 5.8977 | 11.29% | 12.02% | 8.12% | 1.1273 | 1.1366 | 1.0884
2010-06-09 | 38 | 37.8827 | 14.3414 | 52.2241 | 4.7443 | 0.76558 | 0.38824 | 5.8982 | 11.29% | 12.02% | 8.12% | 1.1273 | 1.1366 | 1.0884
2010-06-09 | 39 | 37.1651 | 13.9145 | 51.0796 | 4.5387 | 0.76558 | 0.37973 | 5.684 | 11.13% | 11.84% | 8.001% | 1.1252 | 1.1343 | 1.087
2010-06-09 | 40 | 36.1179 | 13.2931 | 49.4109 | 4.247 | 0.76558 | 0.36733 | 5.3799 | 10.89% | 11.58% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-06-09 | 41 | 36.4918 | 13.0064 | 49.4982 | 4.262 | 0.76558 | 0.36798 | 5.3956 | 10.9% | 11.6% | 7.837% | 1.1223 | 1.1312 | 1.085
2010-06-09 | 42 | 36.0628 | 12.5379 | 48.6008 | 4.1089 | 0.76558 | 0.3613 | 5.2357 | 10.77% | 11.46% | 7.746% | 1.1207 | 1.1295 | 1.084
2010-06-09 | 43 | 34.2523 | 11.8376 | 46.0899 | 3.6953 | 0.76558 | 0.34264 | 4.8035 | 10.42% | 11.09% | 7.493% | 1.1163 | 1.1247 | 1.081
2010-06-09 | 44 | 32.4428 | 11.1931 | 43.6358 | 3.3122 | 0.76558 | 0.32439 | 4.4022 | 10.09% | 10.73% | 7.254% | 1.1122 | 1.1202 | 1.0782
2010-06-09 | 45 | 29.1509 | 10.0675 | 39.2183 | 2.6755 | 0.76558 | 0.29155 | 3.7327 | 9.518% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-06-09 | 46 | 26.2956 | 8.9714 | 35.267 | 2.1636 | 0.76558 | 0.26218 | 3.1913 | 9.049% | 9.628% | 6.506% | 1.0995 | 1.1065 | 1.0696
2010-06-09 | 47 | 25.8632 | 9.2963 | 35.1595 | 2.1504 | 0.76558 | 0.26138 | 3.1774 | 9.037% | 9.615% | 6.498% | 1.0993 | 1.1064 | 1.0695
2010-06-09 | 48 | 25.1172 | 9.8623 | 34.9794 | 2.1284 | 0.76558 | 0.26004 | 3.1541 | 9.017% | 9.594% | 6.483% | 1.0991 | 1.1061 | 1.0693
2010-06-10 | 1 | 23.7232 | 9.0095 | 32.7327 | 1.8638 | 0.76558 | 0.24334 | 2.8727 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-06-10 | 2 | 24.9175 | 8.7463 | 33.6637 | 1.9713 | 0.76558 | 0.25026 | 2.9872 | 8.874% | 9.441% | 6.38% | 1.0974 | 1.1043 | 1.0681
2010-06-10 | 3 | 23.8103 | 8.4152 | 32.2255 | 1.8065 | 0.76558 | 0.23957 | 2.8116 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-06-10 | 4 | 22.5586 | 8.1199 | 30.6785 | 1.6372 | 0.76558 | 0.22807 | 2.6309 | 8.576% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-06-10 | 5 | 21.8125 | 7.8545 | 29.667 | 1.531 | 0.76558 | 0.22055 | 2.5171 | 8.485% | 9.028% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-06-10 | 6 | 21.5683 | 7.6149 | 29.1832 | 1.4815 | 0.76558 | 0.21695 | 2.464 | 8.443% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-06-10 | 7 | 21.3829 | 7.5516 | 28.9345 | 1.4564 | 0.76558 | 0.2151 | 2.437 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-06-10 | 8 | 20.8073 | 7.4525 | 28.2598 | 1.3892 | 0.76558 | 0.21009 | 2.3649 | 8.368% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-06-10 | 9 | 20.8652 | 7.5611 | 28.4262 | 1.4056 | 0.76558 | 0.21132 | 2.3825 | 8.381% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-06-10 | 10 | 21.2809 | 7.6717 | 28.9526 | 1.4582 | 0.76558 | 0.21524 | 2.439 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-06-10 | 11 | 22.1303 | 7.9127 | 30.0431 | 1.5701 | 0.76558 | 0.22334 | 2.559 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-06-10 | 12 | 22.7769 | 8.318 | 31.0949 | 1.682 | 0.76558 | 0.23116 | 2.6787 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-06-10 | 13 | 24.5447 | 9.3129 | 33.8576 | 1.9941 | 0.76558 | 0.2517 | 3.0114 | 8.894% | 9.463% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-06-10 | 14 | 28.1075 | 11.0839 | 39.1914 | 2.6719 | 0.76558 | 0.29135 | 3.7288 | 9.514% | 10.12% | 6.841% | 1.1051 | 1.1126 | 1.0734
2010-06-10 | 15 | 32.1866 | 13.262 | 45.4487 | 3.5932 | 0.76558 | 0.33787 | 4.6966 | 10.33% | 11% | 7.43% | 1.1152 | 1.1235 | 1.0803
2010-06-10 | 16 | 33.5637 | 14.3196 | 47.8833 | 3.9884 | 0.76558 | 0.35597 | 5.11 | 10.67% | 11.35% | 7.673% | 1.1195 | 1.1281 | 1.0831
2010-06-10 | 17 | 34.7683 | 15.208 | 49.9763 | 4.3447 | 0.76558 | 0.37153 | 5.4818 | 10.97% | 11.67% | 7.887% | 1.1232 | 1.1321 | 1.0856
2010-06-10 | 18 | 34.8975 | 15.2384 | 50.1359 | 4.3725 | 0.76558 | 0.37272 | 5.5108 | 10.99% | 11.7% | 7.903% | 1.1235 | 1.1324 | 1.0858
2010-06-10 | 19 | 34.91 | 14.9569 | 49.8669 | 4.3257 | 0.76558 | 0.37072 | 5.462 | 10.95% | 11.65% | 7.875% | 1.123 | 1.1319 | 1.0855
2010-06-10 | 20 | 34.4359 | 14.46 | 48.896 | 4.1589 | 0.76558 | 0.3635 | 5.288 | 10.81% | 11.51% | 7.776% | 1.1213 | 1.13 | 1.0843
2010-06-10 | 21 | 35.9756 | 14.356 | 50.3316 | 4.4067 | 0.76558 | 0.37417 | 5.5465 | 11.02% | 11.73% | 7.923% | 1.1238 | 1.1328 | 1.0861
2010-06-10 | 22 | 35.1867 | 14.1603 | 49.347 | 4.236 | 0.76558 | 0.36685 | 5.3684 | 10.88% | 11.58% | 7.822% | 1.1221 | 1.1309 | 1.0849
2010-06-10 | 23 | 33.9653 | 13.857 | 47.8223 | 3.9783 | 0.76558 | 0.35552 | 5.0994 | 10.66% | 11.35% | 7.667% | 1.1194 | 1.128 | 1.083
2010-06-10 | 24 | 32.658 | 13.5632 | 46.2212 | 3.7164 | 0.76558 | 0.34361 | 4.8255 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.125 | 1.0812
2010-06-10 | 25 | 31.1644 | 13.0266 | 44.191 | 3.3971 | 0.76558 | 0.32852 | 4.4912 | 10.16% | 10.81% | 7.307% | 1.1131 | 1.1212 | 1.0788
2010-06-10 | 26 | 29.8124 | 12.3425 | 42.1549 | 3.0912 | 0.76558 | 0.31338 | 4.1702 | 9.893% | 10.53% | 7.113% | 1.1098 | 1.1176 | 1.0766
2010-06-10 | 27 | 29.7989 | 12.3964 | 42.1953 | 3.0972 | 0.76558 | 0.31369 | 4.1764 | 9.898% | 10.53% | 7.117% | 1.1099 | 1.1177 | 1.0766
2010-06-10 | 28 | 29.8856 | 12.2987 | 42.1842 | 3.0955 | 0.76558 | 0.3136 | 4.1747 | 9.896% | 10.53% | 7.115% | 1.1098 | 1.1177 | 1.0766
2010-06-10 | 29 | 29.6847 | 12.0336 | 41.7183 | 3.0275 | 0.76558 | 0.31014 | 4.1032 | 9.836% | 10.47% | 7.072% | 1.1091 | 1.1169 | 1.0761
2010-06-10 | 30 | 30.0127 | 11.9966 | 42.0093 | 3.0699 | 0.76558 | 0.3123 | 4.1478 | 9.874% | 10.51% | 7.099% | 1.1096 | 1.1174 | 1.0764
2010-06-10 | 31 | 31.7249 | 12.1084 | 43.8333 | 3.3423 | 0.76558 | 0.32586 | 4.4337 | 10.11% | 10.76% | 7.273% | 1.1125 | 1.1206 | 1.0784
2010-06-10 | 32 | 32.0053 | 12.1287 | 44.134 | 3.3883 | 0.76558 | 0.3281 | 4.482 | 10.16% | 10.81% | 7.302% | 1.113 | 1.1211 | 1.0788
2010-06-10 | 33 | 31.6009 | 12.3294 | 43.9303 | 3.3571 | 0.76558 | 0.32658 | 4.4493 | 10.13% | 10.78% | 7.282% | 1.1127 | 1.1208 | 1.0785
2010-06-10 | 34 | 32.0526 | 12.8173 | 44.8699 | 3.5022 | 0.76558 | 0.33357 | 4.6014 | 10.25% | 10.91% | 7.373% | 1.1143 | 1.1225 | 1.0796
2010-06-10 | 35 | 33.1867 | 13.7717 | 46.9583 | 3.8358 | 0.76558 | 0.34909 | 4.9505 | 10.54% | 11.22% | 7.58% | 1.1178 | 1.1263 | 1.082
2010-06-10 | 36 | 35.6726 | 14.8473 | 50.52 | 4.4398 | 0.76558 | 0.37557 | 5.5809 | 11.05% | 11.75% | 7.943% | 1.1242 | 1.1332 | 1.0863
2010-06-10 | 37 | 36.7704 | 14.7982 | 51.5686 | 4.626 | 0.76558 | 0.38337 | 5.7749 | 11.2% | 11.92% | 8.052% | 1.1261 | 1.1353 | 1.0876
2010-06-10 | 38 | 36.9632 | 14.3343 | 51.2975 | 4.5775 | 0.76558 | 0.38135 | 5.7244 | 11.16% | 11.87% | 8.024% | 1.1256 | 1.1347 | 1.0872
2010-06-10 | 39 | 36.2107 | 13.7686 | 49.9794 | 4.3453 | 0.76558 | 0.37155 | 5.4824 | 10.97% | 11.67% | 7.887% | 1.1232 | 1.1321 | 1.0856
2010-06-10 | 40 | 35.1542 | 13.1635 | 48.3177 | 4.0611 | 0.76558 | 0.3592 | 5.1859 | 10.73% | 11.42% | 7.717% | 1.1202 | 1.1289 | 1.0836
2010-06-10 | 41 | 35.3138 | 12.7022 | 48.016 | 4.0106 | 0.76558 | 0.35696 | 5.1331 | 10.69% | 11.37% | 7.686% | 1.1197 | 1.1283 | 1.0833
2010-06-10 | 42 | 35.0705 | 12.3709 | 47.4414 | 3.9152 | 0.76558 | 0.35269 | 5.0334 | 10.61% | 11.29% | 7.628% | 1.1187 | 1.1273 | 1.0826
2010-06-10 | 43 | 33.3822 | 11.7397 | 45.1219 | 3.5417 | 0.76558 | 0.33544 | 4.6427 | 10.29% | 10.95% | 7.398% | 1.1147 | 1.1229 | 1.0799
2010-06-10 | 44 | 31.3434 | 10.9845 | 42.3279 | 3.1166 | 0.76558 | 0.31467 | 4.1969 | 9.915% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-06-10 | 45 | 28.3555 | 9.9682 | 38.3237 | 2.5549 | 0.76558 | 0.2849 | 3.6054 | 9.408% | 10.01% | 6.764% | 1.1038 | 1.1112 | 1.0725
2010-06-10 | 46 | 25.6056 | 8.9703 | 34.5759 | 2.0796 | 0.76558 | 0.25704 | 3.1022 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-06-10 | 47 | 25.4597 | 9.2987 | 34.7584 | 2.1016 | 0.76558 | 0.2584 | 3.1256 | 8.992% | 9.568% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-06-10 | 48 | 24.6287 | 9.7046 | 34.3332 | 2.0505 | 0.76558 | 0.25524 | 3.0713 | 8.946% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2010-06-11 | 1 | 23.3144 | 8.8661 | 32.1804 | 1.8014 | 0.76558 | 0.23923 | 2.8062 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-06-11 | 2 | 24.6586 | 8.6152 | 33.2739 | 1.9259 | 0.76558 | 0.24736 | 2.9389 | 8.832% | 9.398% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-06-11 | 3 | 23.8103 | 8.1619 | 31.9722 | 1.7782 | 0.76558 | 0.23769 | 2.7815 | 8.7% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-06-11 | 4 | 22.531 | 7.7882 | 30.3192 | 1.5991 | 0.76558 | 0.2254 | 2.5901 | 8.543% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-06-11 | 5 | 21.5956 | 7.6392 | 29.2348 | 1.4867 | 0.76558 | 0.21733 | 2.4697 | 8.448% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-06-11 | 6 | 21.6386 | 7.4922 | 29.1308 | 1.4762 | 0.76558 | 0.21656 | 2.4583 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0986 | 1.0646
2010-06-11 | 7 | 21.4505 | 7.3612 | 28.8118 | 1.444 | 0.76558 | 0.21419 | 2.4238 | 8.413% | 8.951% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-06-11 | 8 | 21.0637 | 7.2736 | 28.3373 | 1.3969 | 0.76558 | 0.21066 | 2.3731 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-06-11 | 9 | 21.1781 | 7.4771 | 28.6553 | 1.4284 | 0.76558 | 0.21303 | 2.407 | 8.4% | 8.937% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-06-11 | 10 | 21.4798 | 7.6229 | 29.1027 | 1.4733 | 0.76558 | 0.21635 | 2.4553 | 8.437% | 8.976% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-06-11 | 11 | 22.2125 | 7.7774 | 29.9899 | 1.5645 | 0.76558 | 0.22295 | 2.5531 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-06-11 | 12 | 23.1038 | 8.2619 | 31.3657 | 1.7114 | 0.76558 | 0.23318 | 2.7101 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-06-11 | 13 | 24.6706 | 9.4201 | 34.0907 | 2.0217 | 0.76558 | 0.25343 | 3.0407 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1049 | 1.0685
2010-06-11 | 14 | 27.5454 | 11.0349 | 38.5802 | 2.5892 | 0.76558 | 0.28681 | 3.6416 | 9.439% | 10.04% | 6.787% | 1.1042 | 1.1116 | 1.0728
2010-06-11 | 15 | 31.5539 | 13.1229 | 44.6768 | 3.4722 | 0.76558 | 0.33213 | 4.5699 | 10.23% | 10.88% | 7.354% | 1.1139 | 1.1221 | 1.0794
2010-06-11 | 16 | 33.2906 | 14.4107 | 47.7013 | 3.9582 | 0.76558 | 0.35462 | 5.0784 | 10.65% | 11.33% | 7.655% | 1.1191 | 1.1277 | 1.0829
2010-06-11 | 17 | 34.6697 | 15.2211 | 49.8908 | 4.3299 | 0.76558 | 0.37089 | 5.4663 | 10.96% | 11.66% | 7.878% | 1.123 | 1.132 | 1.0855
2010-06-11 | 18 | 34.9988 | 15.3862 | 50.385 | 4.4161 | 0.76558 | 0.37457 | 5.5562 | 11.03% | 11.73% | 7.929% | 1.1239 | 1.1329 | 1.0861
2010-06-11 | 19 | 34.855 | 15.1798 | 50.0348 | 4.3549 | 0.76558 | 0.37196 | 5.4925 | 10.98% | 11.68% | 7.893% | 1.1233 | 1.1322 | 1.0857
2010-06-11 | 20 | 33.8067 | 14.7086 | 48.5153 | 4.0944 | 0.76558 | 0.36067 | 5.2207 | 10.76% | 11.45% | 7.737% | 1.1206 | 1.1293 | 1.0839
2010-06-11 | 21 | 34.9842 | 14.3985 | 49.3827 | 4.2421 | 0.76558 | 0.36712 | 5.3748 | 10.88% | 11.58% | 7.826% | 1.1221 | 1.131 | 1.0849
2010-06-11 | 22 | 33.8811 | 14.058 | 47.9392 | 3.9977 | 0.76558 | 0.35639 | 5.1197 | 10.68% | 11.36% | 7.679% | 1.1196 | 1.1282 | 1.0832
2010-06-11 | 23 | 32.13 | 13.036 | 45.1661 | 3.5486 | 0.76558 | 0.33577 | 4.65 | 10.3% | 10.95% | 7.402% | 1.1148 | 1.123 | 1.0799
2010-06-11 | 24 | 30.4908 | 12.5833 | 43.0741 | 3.2275 | 0.76558 | 0.32022 | 4.3133 | 10.01% | 10.65% | 7.2% | 1.1113 | 1.1193 | 1.0776
2010-06-11 | 25 | 29.0243 | 11.7528 | 40.777 | 2.8925 | 0.76558 | 0.30314 | 3.9612 | 9.714% | 10.34% | 6.985% | 1.1076 | 1.1153 | 1.0751
2010-06-11 | 26 | 27.4609 | 11.1729 | 38.6338 | 2.5964 | 0.76558 | 0.28721 | 3.6492 | 9.446% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-06-11 | 27 | 28.049 | 11.5853 | 39.6343 | 2.7326 | 0.76558 | 0.29465 | 3.7928 | 9.57% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-06-11 | 28 | 28.1351 | 11.6134 | 39.7485 | 2.7484 | 0.76558 | 0.2955 | 3.8094 | 9.584% | 10.2% | 6.891% | 1.106 | 1.1136 | 1.074
2010-06-11 | 29 | 27.2603 | 10.8764 | 38.1367 | 2.53 | 0.76558 | 0.28351 | 3.5791 | 9.385% | 9.986% | 6.748% | 1.1036 | 1.1109 | 1.0724
2010-06-11 | 30 | 27.1007 | 10.4122 | 37.5129 | 2.4479 | 0.76558 | 0.27888 | 3.4924 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.1099 | 1.0717
2010-06-11 | 31 | 29.0569 | 10.5445 | 39.6014 | 2.7281 | 0.76558 | 0.2944 | 3.7881 | 9.565% | 10.18% | 6.878% | 1.1058 | 1.1133 | 1.0739
2010-06-11 | 32 | 29.6313 | 10.601 | 40.2323 | 2.8157 | 0.76558 | 0.29909 | 3.8804 | 9.645% | 10.26% | 6.935% | 1.1067 | 1.1144 | 1.0745
2010-06-11 | 33 | 29.6152 | 11.1675 | 40.7827 | 2.8933 | 0.76558 | 0.30318 | 3.962 | 9.715% | 10.34% | 6.985% | 1.1076 | 1.1153 | 1.0751
2010-06-11 | 34 | 30.463 | 11.6391 | 42.1022 | 3.0835 | 0.76558 | 0.31299 | 4.1621 | 9.886% | 10.52% | 7.108% | 1.1097 | 1.1175 | 1.0765
2010-06-11 | 35 | 32.0262 | 12.8477 | 44.874 | 3.5029 | 0.76558 | 0.3336 | 4.602 | 10.26% | 10.91% | 7.374% | 1.1143 | 1.1225 | 1.0796
2010-06-11 | 36 | 34.4811 | 14.0803 | 48.5614 | 4.1022 | 0.76558 | 0.36101 | 5.2288 | 10.77% | 11.46% | 7.742% | 1.1207 | 1.1294 | 1.0839
2010-06-11 | 37 | 35.7445 | 13.9362 | 49.6807 | 4.2935 | 0.76558 | 0.36933 | 5.4284 | 10.93% | 11.63% | 7.856% | 1.1227 | 1.1316 | 1.0853
2010-06-11 | 38 | 35.8572 | 13.6517 | 49.5089 | 4.2639 | 0.76558 | 0.36806 | 5.3975 | 10.9% | 11.6% | 7.839% | 1.1224 | 1.1312 | 1.0851
2010-06-11 | 39 | 34.6222 | 13.2643 | 47.8864 | 3.989 | 0.76558 | 0.35599 | 5.1105 | 10.67% | 11.36% | 7.673% | 1.1195 | 1.1281 | 1.0831
2010-06-11 | 40 | 33.8491 | 12.6677 | 46.5168 | 3.764 | 0.76558 | 0.34581 | 4.8754 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-06-11 | 41 | 34.1808 | 12.2657 | 46.4465 | 3.7527 | 0.76558 | 0.34529 | 4.8635 | 10.47% | 11.14% | 7.529% | 1.117 | 1.1254 | 1.0814
2010-06-11 | 42 | 34.0955 | 11.8283 | 45.9238 | 3.6687 | 0.76558 | 0.3414 | 4.7757 | 10.4% | 11.06% | 7.477% | 1.1161 | 1.1244 | 1.0808
2010-06-11 | 43 | 32.1992 | 11.3004 | 43.4996 | 3.2916 | 0.76558 | 0.32338 | 4.3805 | 10.07% | 10.71% | 7.241% | 1.112 | 1.12 | 1.0781
2010-06-11 | 44 | 30.3313 | 10.69 | 41.0213 | 2.9272 | 0.76558 | 0.30496 | 3.9977 | 9.746% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0754
2010-06-11 | 45 | 27.2855 | 9.4325 | 36.7179 | 2.3453 | 0.76558 | 0.27297 | 3.3838 | 9.216% | 9.805% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-06-11 | 46 | 24.5851 | 8.4682 | 33.0533 | 1.9005 | 0.76558 | 0.24572 | 2.9118 | 8.809% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-06-11 | 47 | 24.5443 | 9.0096 | 33.5539 | 1.9585 | 0.76558 | 0.24944 | 2.9735 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-06-11 | 48 | 23.5958 | 9.5239 | 33.1196 | 1.9081 | 0.76558 | 0.24622 | 2.9199 | 8.816% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-06-12 | 1 | 22.287 | 8.7605 | 31.0475 | 1.6768 | 0.76558 | 0.23081 | 2.6732 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-06-12 | 2 | 23.7831 | 8.4852 | 32.2683 | 1.8113 | 0.76558 | 0.23989 | 2.8167 | 8.729% | 9.288% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-06-12 | 3 | 22.5616 | 8.1203 | 30.6818 | 1.6376 | 0.76558 | 0.22809 | 2.6312 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-06-12 | 4 | 21.3838 | 7.7613 | 29.1452 | 1.4776 | 0.76558 | 0.21667 | 2.4599 | 8.44% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-06-12 | 5 | 20.6631 | 7.4249 | 28.088 | 1.3724 | 0.76558 | 0.20881 | 2.3468 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-06-12 | 6 | 20.3333 | 7.2075 | 27.5408 | 1.3194 | 0.76558 | 0.20474 | 2.2898 | 8.314% | 8.846% | 5.978% | 1.0907 | 1.097 | 1.0636
2010-06-12 | 7 | 20.2049 | 7.1192 | 27.3241 | 1.2988 | 0.76558 | 0.20313 | 2.2675 | 8.298% | 8.829% | 5.967% | 1.0905 | 1.0968 | 1.0635
2010-06-12 | 8 | 20.0603 | 6.9768 | 27.0372 | 1.2716 | 0.76558 | 0.201 | 2.2382 | 8.278% | 8.808% | 5.952% | 1.0903 | 1.0966 | 1.0633
2010-06-12 | 9 | 19.6292 | 6.9472 | 26.5764 | 1.2286 | 0.76558 | 0.19757 | 2.1918 | 8.247% | 8.775% | 5.93% | 1.0899 | 1.0962 | 1.063
2010-06-12 | 10 | 19.8308 | 7.0158 | 26.8466 | 1.2538 | 0.76558 | 0.19958 | 2.2189 | 8.265% | 8.794% | 5.943% | 1.0901 | 1.0964 | 1.0632
2010-06-12 | 11 | 20.2337 | 7.2289 | 27.4626 | 1.312 | 0.76558 | 0.20416 | 2.2817 | 8.308% | 8.84% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-06-12 | 12 | 21.312 | 7.6536 | 28.9656 | 1.4595 | 0.76558 | 0.21533 | 2.4404 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-06-12 | 13 | 23.1064 | 8.562 | 31.6684 | 1.7446 | 0.76558 | 0.23543 | 2.7456 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-06-12 | 14 | 25.9085 | 10.1021 | 36.0106 | 2.2558 | 0.76558 | 0.26771 | 3.2891 | 9.134% | 9.718% | 6.567% | 1.1005 | 1.1076 | 1.0703
2010-06-12 | 15 | 29.9451 | 12.1803 | 42.1254 | 3.0869 | 0.76558 | 0.31317 | 4.1656 | 9.889% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-06-12 | 16 | 31.9964 | 13.6431 | 45.6395 | 3.6234 | 0.76558 | 0.33929 | 4.7283 | 10.36% | 11.02% | 7.449% | 1.1156 | 1.1239 | 1.0805
2010-06-12 | 17 | 33.5634 | 14.5804 | 48.1438 | 4.032 | 0.76558 | 0.35791 | 5.1554 | 10.71% | 11.39% | 7.699% | 1.1199 | 1.1286 | 1.0834
2010-06-12 | 18 | 34.095 | 14.6014 | 48.6964 | 4.125 | 0.76558 | 0.36201 | 5.2526 | 10.79% | 11.48% | 7.755% | 1.1209 | 1.1296 | 1.0841
2010-06-12 | 19 | 34.2816 | 14.2042 | 48.4858 | 4.0894 | 0.76558 | 0.36045 | 5.2155 | 10.76% | 11.45% | 7.734% | 1.1205 | 1.1292 | 1.0838
2010-06-12 | 20 | 33.1476 | 13.9012 | 47.0488 | 3.8506 | 0.76558 | 0.34977 | 4.966 | 10.55% | 11.23% | 7.589% | 1.118 | 1.1265 | 1.0821
2010-06-12 | 21 | 34.5979 | 13.7507 | 48.3486 | 4.0663 | 0.76558 | 0.35943 | 5.1913 | 10.74% | 11.42% | 7.72% | 1.1203 | 1.129 | 1.0837
2010-06-12 | 22 | 34.183 | 13.1996 | 47.3826 | 3.9055 | 0.76558 | 0.35225 | 5.0233 | 10.6% | 11.28% | 7.623% | 1.1186 | 1.1271 | 1.0825
2010-06-12 | 23 | 32.5327 | 12.2312 | 44.7639 | 3.4857 | 0.76558 | 0.33278 | 4.5841 | 10.24% | 10.9% | 7.363% | 1.1141 | 1.1223 | 1.0795
2010-06-12 | 24 | 30.9371 | 11.9229 | 42.86 | 3.1955 | 0.76558 | 0.31863 | 4.2797 | 9.985% | 10.62% | 7.179% | 1.1109 | 1.1189 | 1.0773
2010-06-12 | 25 | 28.9103 | 11.4732 | 40.3835 | 2.8369 | 0.76558 | 0.30022 | 3.9027 | 9.664% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-06-12 | 26 | 28.3067 | 10.7985 | 39.1052 | 2.6601 | 0.76558 | 0.29071 | 3.7164 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-06-12 | 27 | 28.8666 | 11.434 | 40.3006 | 2.8253 | 0.76558 | 0.2996 | 3.8904 | 9.654% | 10.27% | 6.941% | 1.1069 | 1.1145 | 1.0746
2010-06-12 | 28 | 28.5932 | 11.7817 | 40.3749 | 2.8357 | 0.76558 | 0.30015 | 3.9014 | 9.663% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-06-12 | 29 | 27.46 | 11.3405 | 38.8005 | 2.6188 | 0.76558 | 0.28845 | 3.6729 | 9.466% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-06-12 | 30 | 27.2729 | 10.9922 | 38.2651 | 2.5471 | 0.76558 | 0.28447 | 3.5971 | 9.401% | 10% | 6.759% | 1.1038 | 1.1111 | 1.0725
2010-06-12 | 31 | 29.3142 | 10.8052 | 40.1194 | 2.7999 | 0.76558 | 0.29825 | 3.8637 | 9.631% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-06-12 | 32 | 29.3857 | 10.5875 | 39.9732 | 2.7795 | 0.76558 | 0.29717 | 3.8423 | 9.612% | 10.23% | 6.911% | 1.1063 | 1.1139 | 1.0742
2010-06-12 | 33 | 29.184 | 10.6977 | 39.8817 | 2.7668 | 0.76558 | 0.29649 | 3.8289 | 9.601% | 10.22% | 6.903% | 1.1062 | 1.1138 | 1.0741
2010-06-12 | 34 | 30.1464 | 11.1267 | 41.273 | 2.9632 | 0.76558 | 0.30683 | 4.0356 | 9.778% | 10.4% | 7.03% | 1.1084 | 1.1161 | 1.0756
2010-06-12 | 35 | 31.3251 | 12.2601 | 43.5851 | 3.3045 | 0.76558 | 0.32402 | 4.3941 | 10.08% | 10.73% | 7.249% | 1.1121 | 1.1202 | 1.0782
2010-06-12 | 36 | 33.1341 | 13.0046 | 46.1387 | 3.7031 | 0.76558 | 0.343 | 4.8117 | 10.43% | 11.1% | 7.498% | 1.1164 | 1.1248 | 1.0811
2010-06-12 | 37 | 33.7496 | 12.8501 | 46.5997 | 3.7775 | 0.76558 | 0.34643 | 4.8895 | 10.49% | 11.16% | 7.544% | 1.1172 | 1.1257 | 1.0816
2010-06-12 | 38 | 33.4324 | 12.6296 | 46.062 | 3.6908 | 0.76558 | 0.34243 | 4.7988 | 10.42% | 11.08% | 7.491% | 1.1163 | 1.1247 | 1.081
2010-06-12 | 39 | 33.0754 | 12.1444 | 45.2198 | 3.5571 | 0.76558 | 0.33617 | 4.6588 | 10.3% | 10.96% | 7.408% | 1.1149 | 1.1231 | 1.08
2010-06-12 | 40 | 32.4851 | 11.6771 | 44.1621 | 3.3926 | 0.76558 | 0.32831 | 4.4865 | 10.16% | 10.81% | 7.304% | 1.1131 | 1.1212 | 1.0788
2010-06-12 | 41 | 32.8869 | 11.2766 | 44.1635 | 3.3928 | 0.76558 | 0.32832 | 4.4867 | 10.16% | 10.81% | 7.305% | 1.1131 | 1.1212 | 1.0788
2010-06-12 | 42 | 32.5567 | 11.0746 | 43.6313 | 3.3116 | 0.76558 | 0.32436 | 4.4015 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2010-06-12 | 43 | 30.8033 | 10.5094 | 41.3127 | 2.9689 | 0.76558 | 0.30712 | 4.0416 | 9.783% | 10.41% | 7.034% | 1.1084 | 1.1162 | 1.0757
2010-06-12 | 44 | 29.2377 | 9.9271 | 39.1648 | 2.6683 | 0.76558 | 0.29116 | 3.725 | 9.511% | 10.12% | 6.838% | 1.1051 | 1.1126 | 1.0734
2010-06-12 | 45 | 26.6521 | 9.0649 | 35.717 | 2.2191 | 0.76558 | 0.26552 | 3.2502 | 9.1% | 9.682% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-06-12 | 46 | 24.7139 | 8.3808 | 33.0946 | 1.9052 | 0.76558 | 0.24603 | 2.9168 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2010-06-12 | 47 | 25.0302 | 8.656 | 33.6862 | 1.974 | 0.76558 | 0.25043 | 2.99 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-06-12 | 48 | 24.2825 | 9.1455 | 33.4279 | 1.9438 | 0.76558 | 0.24851 | 2.9579 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-06-13 | 1 | 23.0774 | 8.2987 | 31.376 | 1.7125 | 0.76558 | 0.23325 | 2.7113 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2010-06-13 | 2 | 24.371 | 8.0145 | 32.3855 | 1.8245 | 0.76558 | 0.24076 | 2.8308 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-06-13 | 3 | 23.4797 | 7.5149 | 30.9945 | 1.6711 | 0.76558 | 0.23042 | 2.6671 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2010-06-13 | 4 | 22.0002 | 7.1849 | 29.1852 | 1.4817 | 0.76558 | 0.21697 | 2.4642 | 8.443% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-06-13 | 5 | 21.1801 | 6.9018 | 28.0819 | 1.3718 | 0.76558 | 0.20876 | 2.3461 | 8.355% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-06-13 | 6 | 20.9502 | 6.803 | 27.7532 | 1.3399 | 0.76558 | 0.20632 | 2.3118 | 8.33% | 8.863% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-06-13 | 7 | 21.0674 | 6.6749 | 27.7424 | 1.3388 | 0.76558 | 0.20624 | 2.3106 | 8.329% | 8.862% | 5.988% | 1.0909 | 1.0972 | 1.0637
2010-06-13 | 8 | 20.8645 | 6.6328 | 27.4974 | 1.3153 | 0.76558 | 0.20442 | 2.2853 | 8.311% | 8.843% | 5.976% | 1.0906 | 1.097 | 1.0636
2010-06-13 | 9 | 20.6207 | 6.7257 | 27.3464 | 1.3009 | 0.76558 | 0.2033 | 2.2697 | 8.3% | 8.831% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-06-13 | 10 | 20.8509 | 6.7829 | 27.6338 | 1.3284 | 0.76558 | 0.20543 | 2.2994 | 8.321% | 8.853% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-06-13 | 11 | 21.5672 | 6.8928 | 28.46 | 1.409 | 0.76558 | 0.21158 | 2.3861 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-06-13 | 12 | 22.0705 | 6.9985 | 29.069 | 1.4699 | 0.76558 | 0.2161 | 2.4516 | 8.434% | 8.973% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-06-13 | 13 | 23.3075 | 7.5015 | 30.809 | 1.6512 | 0.76558 | 0.22904 | 2.6458 | 8.588% | 9.137% | 6.175% | 1.0939 | 1.1006 | 1.0658
2010-06-13 | 14 | 24.5263 | 7.8707 | 32.3971 | 1.8258 | 0.76558 | 0.24084 | 2.8322 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-06-13 | 15 | 25.4758 | 8.433 | 33.9088 | 2.0001 | 0.76558 | 0.25208 | 3.0178 | 8.9% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-06-13 | 16 | 25.8924 | 9.0917 | 34.9841 | 2.129 | 0.76558 | 0.26008 | 3.1547 | 9.017% | 9.595% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-06-13 | 17 | 28.1035 | 10.4577 | 38.5611 | 2.5866 | 0.76558 | 0.28667 | 3.6389 | 9.437% | 10.04% | 6.785% | 1.1042 | 1.1116 | 1.0728
2010-06-13 | 18 | 30.7336 | 11.6713 | 42.4049 | 3.128 | 0.76558 | 0.31524 | 4.2088 | 9.925% | 10.56% | 7.136% | 1.1102 | 1.1181 | 1.0768
2010-06-13 | 19 | 32.5856 | 12.6122 | 45.1978 | 3.5536 | 0.76558 | 0.33601 | 4.6552 | 10.3% | 10.96% | 7.405% | 1.1148 | 1.1231 | 1.08
2010-06-13 | 20 | 33.6341 | 13.1177 | 46.7519 | 3.8022 | 0.76558 | 0.34756 | 4.9153 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.126 | 1.0818
2010-06-13 | 21 | 35.8205 | 13.3074 | 49.1279 | 4.1985 | 0.76558 | 0.36522 | 5.3293 | 10.85% | 11.54% | 7.8% | 1.1217 | 1.1305 | 1.0846
2010-06-13 | 22 | 36.1919 | 13.2086 | 49.4005 | 4.2452 | 0.76558 | 0.36725 | 5.378 | 10.89% | 11.58% | 7.827% | 1.1222 | 1.131 | 1.0849
2010-06-13 | 23 | 34.9583 | 12.6578 | 47.6161 | 3.944 | 0.76558 | 0.35398 | 5.0636 | 10.63% | 11.31% | 7.646% | 1.119 | 1.1276 | 1.0828
2010-06-13 | 24 | 33.7483 | 12.3082 | 46.0565 | 3.6899 | 0.76558 | 0.34239 | 4.7979 | 10.42% | 11.08% | 7.49% | 1.1163 | 1.1247 | 1.081
2010-06-13 | 25 | 31.4347 | 11.8517 | 43.2864 | 3.2594 | 0.76558 | 0.3218 | 4.3468 | 10.04% | 10.68% | 7.22% | 1.1116 | 1.1196 | 1.0778
2010-06-13 | 26 | 29.868 | 11.1315 | 40.9995 | 2.9241 | 0.76558 | 0.3048 | 3.9945 | 9.743% | 10.37% | 7.005% | 1.1079 | 1.1157 | 1.0753
2010-06-13 | 27 | 30.5587 | 11.2751 | 41.8338 | 3.0443 | 0.76558 | 0.311 | 4.1209 | 9.851% | 10.48% | 7.083% | 1.1093 | 1.1171 | 1.0762
2010-06-13 | 28 | 30.6025 | 11.2587 | 41.8612 | 3.0483 | 0.76558 | 0.3112 | 4.1251 | 9.854% | 10.48% | 7.085% | 1.1093 | 1.1171 | 1.0763
2010-06-13 | 29 | 30.3433 | 10.8097 | 41.153 | 2.946 | 0.76558 | 0.30594 | 4.0176 | 9.762% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-06-13 | 30 | 29.9139 | 10.4703 | 40.3842 | 2.837 | 0.76558 | 0.30022 | 3.9028 | 9.664% | 10.28% | 6.949% | 1.107 | 1.1146 | 1.0747
2010-06-13 | 31 | 32.0416 | 10.7423 | 42.7838 | 3.1842 | 0.76558 | 0.31806 | 4.2678 | 9.975% | 10.61% | 7.172% | 1.1108 | 1.1187 | 1.0773
2010-06-13 | 32 | 32.7462 | 10.6075 | 43.3538 | 3.2696 | 0.76558 | 0.3223 | 4.3574 | 10.05% | 10.69% | 7.227% | 1.1117 | 1.1197 | 1.0779
2010-06-13 | 33 | 32.9747 | 10.933 | 43.9076 | 3.3536 | 0.76558 | 0.32641 | 4.4456 | 10.12% | 10.77% | 7.28% | 1.1127 | 1.1207 | 1.0785
2010-06-13 | 34 | 33.6627 | 11.1829 | 44.8456 | 3.4984 | 0.76558 | 0.33339 | 4.5974 | 10.25% | 10.91% | 7.371% | 1.1142 | 1.1224 | 1.0796
2010-06-13 | 35 | 34.209 | 11.9993 | 46.2083 | 3.7143 | 0.76558 | 0.34352 | 4.8234 | 10.44% | 11.11% | 7.505% | 1.1165 | 1.1249 | 1.0811
2010-06-13 | 36 | 35.6418 | 12.745 | 48.3868 | 4.0728 | 0.76558 | 0.35971 | 5.198 | 10.74% | 11.43% | 7.724% | 1.1204 | 1.1291 | 1.0837
2010-06-13 | 37 | 36.0303 | 12.6306 | 48.6608 | 4.119 | 0.76558 | 0.36175 | 5.2463 | 10.78% | 11.47% | 7.752% | 1.1208 | 1.1296 | 1.084
2010-06-13 | 38 | 35.4711 | 12.1459 | 47.617 | 3.9442 | 0.76558 | 0.35399 | 5.0638 | 10.63% | 11.31% | 7.646% | 1.119 | 1.1276 | 1.0828
2010-06-13 | 39 | 34.1347 | 11.5902 | 45.725 | 3.637 | 0.76558 | 0.33993 | 4.7425 | 10.37% | 11.04% | 7.457% | 1.1157 | 1.124 | 1.0806
2010-06-13 | 40 | 32.4979 | 10.8084 | 43.3063 | 3.2624 | 0.76558 | 0.32194 | 4.3499 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-06-13 | 41 | 33.0429 | 10.439 | 43.4819 | 3.2889 | 0.76558 | 0.32325 | 4.3777 | 10.07% | 10.71% | 7.239% | 1.112 | 1.12 | 1.078
2010-06-13 | 42 | 32.9159 | 10.0477 | 42.9637 | 3.211 | 0.76558 | 0.3194 | 4.296 | 9.999% | 10.64% | 7.189% | 1.1111 | 1.1191 | 1.0775
2010-06-13 | 43 | 31.4505 | 9.5887 | 41.0392 | 2.9298 | 0.76558 | 0.30509 | 4.0004 | 9.748% | 10.37% | 7.009% | 1.108 | 1.1157 | 1.0754
2010-06-13 | 44 | 30.1001 | 9.2234 | 39.3235 | 2.6899 | 0.76558 | 0.29234 | 3.7478 | 9.531% | 10.14% | 6.853% | 1.1053 | 1.1129 | 1.0736
2010-06-13 | 45 | 27.6298 | 8.7203 | 36.3502 | 2.2985 | 0.76558 | 0.27023 | 3.3343 | 9.173% | 9.76% | 6.595% | 1.101 | 1.1082 | 1.0706
2010-06-13 | 46 | 25.5038 | 8.15 | 33.6538 | 1.9702 | 0.76558 | 0.25019 | 2.9859 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-06-13 | 47 | 25.8911 | 8.7246 | 34.6156 | 2.0844 | 0.76558 | 0.25734 | 3.1073 | 8.977% | 9.551% | 6.454% | 1.0986 | 1.1056 | 1.069
2010-06-13 | 48 | 25.5769 | 9.3532 | 34.9301 | 2.1224 | 0.76558 | 0.25967 | 3.1477 | 9.011% | 9.588% | 6.479% | 1.099 | 1.106 | 1.0693
2010-06-14 | 1 | 24.0223 | 8.4922 | 32.5145 | 1.839 | 0.76558 | 0.24172 | 2.8463 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-06-14 | 2 | 25.5902 | 8.1722 | 33.7624 | 1.9829 | 0.76558 | 0.25099 | 2.9995 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-06-14 | 3 | 24.8998 | 7.7422 | 32.642 | 1.8535 | 0.76558 | 0.24266 | 2.8617 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-06-14 | 4 | 23.6786 | 7.4581 | 31.1367 | 1.6865 | 0.76558 | 0.23147 | 2.6835 | 8.619% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-06-14 | 5 | 22.7426 | 7.2028 | 29.9454 | 1.5599 | 0.76558 | 0.22262 | 2.5481 | 8.509% | 9.054% | 6.118% | 1.093 | 1.0995 | 1.0652
2010-06-14 | 6 | 22.1693 | 6.9862 | 29.1555 | 1.4787 | 0.76558 | 0.21675 | 2.461 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-06-14 | 7 | 22.0246 | 6.9411 | 28.9657 | 1.4595 | 0.76558 | 0.21533 | 2.4404 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-06-14 | 8 | 22.1249 | 6.8619 | 28.9868 | 1.4616 | 0.76558 | 0.21549 | 2.4427 | 8.427% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-06-14 | 9 | 21.8237 | 6.8635 | 28.6872 | 1.4316 | 0.76558 | 0.21326 | 2.4104 | 8.402% | 8.94% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-06-14 | 10 | 21.9537 | 6.8683 | 28.8219 | 1.445 | 0.76558 | 0.21427 | 2.4249 | 8.413% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-06-14 | 11 | 22.355 | 6.9746 | 29.3296 | 1.4964 | 0.76558 | 0.21804 | 2.48 | 8.456% | 8.997% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-06-14 | 12 | 22.988 | 7.1775 | 30.1654 | 1.5829 | 0.76558 | 0.22425 | 2.5727 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-06-14 | 13 | 24.0072 | 7.3402 | 31.3474 | 1.7094 | 0.76558 | 0.23304 | 2.708 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-06-14 | 14 | 24.9988 | 7.6346 | 32.6334 | 1.8525 | 0.76558 | 0.2426 | 2.8607 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-06-14 | 15 | 25.3736 | 7.7968 | 33.1705 | 1.914 | 0.76558 | 0.24659 | 2.9262 | 8.822% | 9.386% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-06-14 | 16 | 24.9718 | 7.9884 | 32.9602 | 1.8898 | 0.76558 | 0.24503 | 2.9004 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-06-14 | 17 | 27.0267 | 9.0807 | 36.1075 | 2.2679 | 0.76558 | 0.26843 | 3.3019 | 9.145% | 9.73% | 6.575% | 1.1007 | 1.1078 | 1.0704
2010-06-14 | 18 | 29.512 | 10.4037 | 39.9157 | 2.7715 | 0.76558 | 0.29674 | 3.8339 | 9.605% | 10.22% | 6.906% | 1.1063 | 1.1138 | 1.0742
2010-06-14 | 19 | 32.0655 | 11.3757 | 43.4412 | 3.2828 | 0.76558 | 0.32295 | 4.3713 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-06-14 | 20 | 33.2449 | 11.7911 | 45.0359 | 3.5282 | 0.76558 | 0.3348 | 4.6286 | 10.28% | 10.94% | 7.39% | 1.1145 | 1.1228 | 1.0798
2010-06-14 | 21 | 36.6514 | 12.3549 | 49.0063 | 4.1777 | 0.76558 | 0.36432 | 5.3076 | 10.83% | 11.52% | 7.787% | 1.1215 | 1.1302 | 1.0844
2010-06-14 | 22 | 37.1128 | 12.4203 | 49.533 | 4.268 | 0.76558 | 0.36823 | 5.4018 | 10.91% | 11.6% | 7.841% | 1.1224 | 1.1313 | 1.0851
2010-06-14 | 23 | 35.9031 | 12.2819 | 48.185 | 4.0389 | 0.76558 | 0.35821 | 5.1627 | 10.71% | 11.4% | 7.704% | 1.12 | 1.1287 | 1.0835
2010-06-14 | 24 | 34.9239 | 11.8216 | 46.7455 | 3.8011 | 0.76558 | 0.34751 | 4.9142 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.1259 | 1.0818
2010-06-14 | 25 | 32.7558 | 11.0965 | 43.8523 | 3.3452 | 0.76558 | 0.326 | 4.4368 | 10.12% | 10.77% | 7.274% | 1.1126 | 1.1206 | 1.0785
2010-06-14 | 26 | 31.3031 | 10.6786 | 41.9817 | 3.0659 | 0.76558 | 0.3121 | 4.1436 | 9.87% | 10.5% | 7.096% | 1.1095 | 1.1173 | 1.0764
2010-06-14 | 27 | 31.375 | 11.1037 | 42.4787 | 3.1389 | 0.76558 | 0.31579 | 4.2203 | 9.935% | 10.57% | 7.143% | 1.1103 | 1.1182 | 1.0769
2010-06-14 | 28 | 31.0755 | 11.1006 | 42.1761 | 3.0943 | 0.76558 | 0.31354 | 4.1735 | 9.895% | 10.53% | 7.115% | 1.1098 | 1.1177 | 1.0766
2010-06-14 | 29 | 29.6105 | 10.5801 | 40.1905 | 2.8098 | 0.76558 | 0.29878 | 3.8742 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-06-14 | 30 | 29.0071 | 9.8881 | 38.8953 | 2.6316 | 0.76558 | 0.28915 | 3.6864 | 9.478% | 10.08% | 6.814% | 1.1047 | 1.1122 | 1.0731
2010-06-14 | 31 | 30.9627 | 9.8923 | 40.855 | 2.9035 | 0.76558 | 0.30372 | 3.9728 | 9.724% | 10.35% | 6.992% | 1.1077 | 1.1154 | 1.0752
2010-06-14 | 32 | 31.5371 | 9.7946 | 41.3317 | 2.9717 | 0.76558 | 0.30726 | 4.0445 | 9.786% | 10.41% | 7.036% | 1.1085 | 1.1162 | 1.0757
2010-06-14 | 33 | 31.6095 | 10.2544 | 41.8638 | 3.0487 | 0.76558 | 0.31122 | 4.1255 | 9.855% | 10.49% | 7.085% | 1.1093 | 1.1171 | 1.0763
2010-06-14 | 34 | 32.5859 | 10.7827 | 43.3686 | 3.2718 | 0.76558 | 0.32241 | 4.3598 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-06-14 | 35 | 34.0803 | 12.1963 | 46.2765 | 3.7253 | 0.76558 | 0.34403 | 4.8349 | 10.45% | 11.12% | 7.512% | 1.1167 | 1.1251 | 1.0812
2010-06-14 | 36 | 37.4675 | 13.6346 | 51.1021 | 4.5427 | 0.76558 | 0.3799 | 5.6882 | 11.13% | 11.84% | 8.003% | 1.1253 | 1.1343 | 1.087
2010-06-14 | 37 | 39.4624 | 13.6491 | 53.1115 | 4.907 | 0.76558 | 0.39484 | 6.0674 | 11.42% | 12.15% | 8.214% | 1.129 | 1.1384 | 1.0895
2010-06-14 | 38 | 39.9939 | 13.2777 | 53.2716 | 4.9366 | 0.76558 | 0.39603 | 6.0982 | 11.45% | 12.18% | 8.231% | 1.1293 | 1.1387 | 1.0897
2010-06-14 | 39 | 39.8071 | 12.9514 | 52.7585 | 4.8419 | 0.76558 | 0.39221 | 5.9997 | 11.37% | 12.1% | 8.177% | 1.1283 | 1.1377 | 1.089
2010-06-14 | 40 | 39.1471 | 12.4635 | 51.6106 | 4.6335 | 0.76558 | 0.38368 | 5.7828 | 11.2% | 11.92% | 8.056% | 1.1262 | 1.1354 | 1.0876
2010-06-14 | 41 | 39.6355 | 12.374 | 52.0095 | 4.7054 | 0.76558 | 0.38664 | 5.8577 | 11.26% | 11.98% | 8.098% | 1.1269 | 1.1362 | 1.0881
2010-06-14 | 42 | 39.3341 | 11.853 | 51.187 | 4.5578 | 0.76558 | 0.38053 | 5.7039 | 11.14% | 11.86% | 8.012% | 1.1254 | 1.1345 | 1.0871
2010-06-14 | 43 | 36.9071 | 11.1355 | 48.0426 | 4.015 | 0.76558 | 0.35715 | 5.1378 | 10.69% | 11.38% | 7.689% | 1.1197 | 1.1284 | 1.0833
2010-06-14 | 44 | 35.2988 | 10.4609 | 45.7598 | 3.6425 | 0.76558 | 0.34018 | 4.7483 | 10.38% | 11.04% | 7.461% | 1.1158 | 1.1241 | 1.0806
2010-06-14 | 45 | 32.4404 | 9.4743 | 41.9147 | 3.0561 | 0.76558 | 0.3116 | 4.1333 | 9.861% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-06-14 | 46 | 29.3363 | 8.2832 | 37.6195 | 2.4618 | 0.76558 | 0.27967 | 3.5071 | 9.323% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-06-14 | 47 | 29.0497 | 8.7314 | 37.781 | 2.483 | 0.76558 | 0.28087 | 3.5295 | 9.342% | 9.94% | 6.717% | 1.103 | 1.1104 | 1.072
2010-06-14 | 48 | 28.6912 | 9.2944 | 37.9856 | 2.51 | 0.76558 | 0.28239 | 3.558 | 9.367% | 9.966% | 6.735% | 1.1033 | 1.1107 | 1.0722
2010-06-15 | 1 | 27.5706 | 8.6346 | 36.2053 | 2.2802 | 0.76558 | 0.26915 | 3.315 | 9.156% | 9.742% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-06-15 | 2 | 29.1252 | 8.3493 | 37.4745 | 2.4429 | 0.76558 | 0.27859 | 3.4871 | 9.305% | 9.901% | 6.69% | 1.1026 | 1.1099 | 1.0717
2010-06-15 | 3 | 27.9454 | 8.0633 | 36.0087 | 2.2555 | 0.76558 | 0.26769 | 3.2888 | 9.133% | 9.718% | 6.567% | 1.1005 | 1.1076 | 1.0703
2010-06-15 | 4 | 27.0231 | 7.7413 | 34.7644 | 2.1023 | 0.76558 | 0.25844 | 3.1264 | 8.993% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-06-15 | 5 | 26.6928 | 7.4373 | 34.1301 | 2.0263 | 0.76558 | 0.25373 | 3.0456 | 8.924% | 9.495% | 6.416% | 1.098 | 1.1049 | 1.0686
2010-06-15 | 6 | 26.2179 | 7.2243 | 33.4422 | 1.9455 | 0.76558 | 0.24861 | 2.9597 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.104 | 1.068
2010-06-15 | 7 | 25.6138 | 7.1499 | 32.7637 | 1.8673 | 0.76558 | 0.24357 | 2.8765 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-06-15 | 8 | 25.2964 | 7.1061 | 32.4025 | 1.8264 | 0.76558 | 0.24088 | 2.8328 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-06-15 | 9 | 24.9676 | 7.2024 | 32.17 | 1.8003 | 0.76558 | 0.23916 | 2.805 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-06-15 | 10 | 25.6138 | 7.3805 | 32.9943 | 1.8937 | 0.76558 | 0.24528 | 2.9046 | 8.803% | 9.367% | 6.33% | 1.0965 | 1.1033 | 1.0676
2010-06-15 | 11 | 26.2594 | 7.5265 | 33.7859 | 1.9857 | 0.76558 | 0.25117 | 3.0024 | 8.887% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2010-06-15 | 12 | 26.9088 | 7.9745 | 34.8832 | 2.1167 | 0.76558 | 0.25933 | 3.1416 | 9.006% | 9.583% | 6.475% | 1.099 | 1.106 | 1.0692
2010-06-15 | 13 | 29.1939 | 8.9681 | 38.162 | 2.5334 | 0.76558 | 0.2837 | 3.5826 | 9.388% | 9.989% | 6.75% | 1.1036 | 1.111 | 1.0724
2010-06-15 | 14 | 32.6712 | 10.5487 | 43.2199 | 3.2494 | 0.76558 | 0.3213 | 4.3363 | 10.03% | 10.68% | 7.214% | 1.1115 | 1.1195 | 1.0777
2010-06-15 | 15 | 36.7508 | 12.7451 | 49.4958 | 4.2616 | 0.76558 | 0.36796 | 5.3951 | 10.9% | 11.6% | 7.837% | 1.1223 | 1.1312 | 1.085
2010-06-15 | 16 | 38.4011 | 13.9229 | 52.324 | 4.7625 | 0.76558 | 0.38898 | 5.9171 | 11.31% | 12.03% | 8.131% | 1.1275 | 1.1368 | 1.0885
2010-06-15 | 17 | 39.323 | 14.8472 | 54.1702 | 5.1045 | 0.76558 | 0.40271 | 6.2728 | 11.58% | 12.32% | 8.326% | 1.131 | 1.1405 | 1.0908
2010-06-15 | 18 | 38.7618 | 14.6009 | 53.3627 | 4.9535 | 0.76558 | 0.3967 | 6.1158 | 11.46% | 12.19% | 8.24% | 1.1294 | 1.1389 | 1.0898
2010-06-15 | 19 | 39.1355 | 14.0471 | 53.1826 | 4.9201 | 0.76558 | 0.39537 | 6.081 | 11.43% | 12.17% | 8.221% | 1.1291 | 1.1385 | 1.0896
2010-06-15 | 20 | 38.6307 | 13.3942 | 52.0249 | 4.7082 | 0.76558 | 0.38676 | 5.8606 | 11.26% | 11.99% | 8.099% | 1.127 | 1.1362 | 1.0881
2010-06-15 | 21 | 39.8375 | 13.3032 | 53.1408 | 4.9124 | 0.76558 | 0.39506 | 6.073 | 11.43% | 12.16% | 8.217% | 1.129 | 1.1384 | 1.0895
2010-06-15 | 22 | 39.4068 | 13.2398 | 52.6466 | 4.8214 | 0.76558 | 0.39138 | 5.9784 | 11.36% | 12.08% | 8.165% | 1.1281 | 1.1374 | 1.0889
2010-06-15 | 23 | 37.5243 | 12.7716 | 50.2959 | 4.4005 | 0.76558 | 0.37391 | 5.54 | 11.01% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-06-15 | 24 | 36.6334 | 12.7375 | 49.3709 | 4.2401 | 0.76558 | 0.36703 | 5.3727 | 10.88% | 11.58% | 7.824% | 1.1221 | 1.131 | 1.0849
2010-06-15 | 25 | 34.8944 | 12.3484 | 47.2428 | 3.8825 | 0.76558 | 0.35121 | 4.9992 | 10.58% | 11.26% | 7.608% | 1.1183 | 1.1269 | 1.0824
2010-06-15 | 26 | 33.673 | 11.7656 | 45.4386 | 3.5916 | 0.76558 | 0.3378 | 4.6949 | 10.33% | 10.99% | 7.429% | 1.1152 | 1.1235 | 1.0803
2010-06-15 | 27 | 34.277 | 12.1005 | 46.3776 | 3.7415 | 0.76558 | 0.34478 | 4.8519 | 10.46% | 11.13% | 7.522% | 1.1168 | 1.1253 | 1.0813
2010-06-15 | 28 | 34.4628 | 12.2852 | 46.748 | 3.8016 | 0.76558 | 0.34753 | 4.9147 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.1259 | 1.0818
2010-06-15 | 29 | 34.2925 | 11.9834 | 46.2759 | 3.7252 | 0.76558 | 0.34402 | 4.8348 | 10.45% | 11.12% | 7.512% | 1.1167 | 1.1251 | 1.0812
2010-06-15 | 30 | 34.364 | 11.6812 | 46.0452 | 3.6881 | 0.76558 | 0.34231 | 4.796 | 10.42% | 11.08% | 7.489% | 1.1163 | 1.1246 | 1.081
2010-06-15 | 31 | 36.0303 | 11.7341 | 47.7645 | 3.9687 | 0.76558 | 0.35509 | 5.0893 | 10.66% | 11.34% | 7.661% | 1.1193 | 1.1279 | 1.083
2010-06-15 | 32 | 36.6075 | 11.9385 | 48.5461 | 4.0996 | 0.76558 | 0.3609 | 5.2261 | 10.77% | 11.45% | 7.74% | 1.1206 | 1.1294 | 1.0839
2010-06-15 | 33 | 36.9656 | 12.3172 | 49.2827 | 4.225 | 0.76558 | 0.36637 | 5.3569 | 10.87% | 11.57% | 7.815% | 1.122 | 1.1308 | 1.0848
2010-06-15 | 34 | 38.9177 | 12.9062 | 51.8239 | 4.6719 | 0.76558 | 0.38527 | 5.8228 | 11.24% | 11.95% | 8.078% | 1.1266 | 1.1358 | 1.0879
2010-06-15 | 35 | 39.8381 | 14.1472 | 53.9853 | 5.0697 | 0.76558 | 0.40133 | 6.2366 | 11.55% | 12.29% | 8.306% | 1.1306 | 1.1401 | 1.0906
2010-06-15 | 36 | 41.3309 | 15.5561 | 56.8869 | 5.6294 | 0.76558 | 0.4229 | 6.8179 | 11.98% | 12.75% | 8.617% | 1.1362 | 1.1462 | 1.0943
2010-06-15 | 37 | 41.173 | 15.0807 | 56.2537 | 5.5047 | 0.76558 | 0.4182 | 6.6885 | 11.89% | 12.65% | 8.549% | 1.1349 | 1.1448 | 1.0935
2010-06-15 | 38 | 42.6496 | 14.4933 | 57.143 | 5.6802 | 0.76558 | 0.42481 | 6.8705 | 12.02% | 12.79% | 8.645% | 1.1367 | 1.1467 | 1.0946
2010-06-15 | 39 | 42.3776 | 13.9099 | 56.2875 | 5.5114 | 0.76558 | 0.41845 | 6.6954 | 11.89% | 12.66% | 8.552% | 1.135 | 1.1449 | 1.0935
2010-06-15 | 40 | 41.5442 | 13.2282 | 54.7724 | 5.2187 | 0.76558 | 0.40718 | 6.3914 | 11.67% | 12.42% | 8.39% | 1.1321 | 1.1418 | 1.0916
2010-06-15 | 41 | 42.4758 | 13.042 | 55.5178 | 5.3617 | 0.76558 | 0.41273 | 6.54 | 11.78% | 12.53% | 8.47% | 1.1335 | 1.1433 | 1.0925
2010-06-15 | 42 | 41.9051 | 12.5746 | 54.4797 | 5.163 | 0.76558 | 0.40501 | 6.3336 | 11.63% | 12.37% | 8.359% | 1.1315 | 1.1412 | 1.0912
2010-06-15 | 43 | 39.8517 | 11.8209 | 51.6726 | 4.6447 | 0.76558 | 0.38414 | 5.7944 | 11.21% | 11.93% | 8.063% | 1.1263 | 1.1355 | 1.0877
2010-06-15 | 44 | 38.4303 | 10.8956 | 49.3259 | 4.2324 | 0.76558 | 0.36669 | 5.3647 | 10.88% | 11.57% | 7.82% | 1.122 | 1.1309 | 1.0848
2010-06-15 | 45 | 34.6073 | 9.8685 | 44.4759 | 3.441 | 0.76558 | 0.33064 | 4.5372 | 10.2% | 10.85% | 7.335% | 1.1136 | 1.1218 | 1.0792
2010-06-15 | 46 | 30.6989 | 8.8292 | 39.5281 | 2.718 | 0.76558 | 0.29386 | 3.7774 | 9.556% | 10.17% | 6.871% | 1.1057 | 1.1132 | 1.0738
2010-06-15 | 47 | 30.7272 | 9.1218 | 39.8491 | 2.7623 | 0.76558 | 0.29624 | 3.8241 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-06-15 | 48 | 30.0686 | 9.6118 | 39.6804 | 2.739 | 0.76558 | 0.29499 | 3.7995 | 9.575% | 10.19% | 6.885% | 1.1059 | 1.1134 | 1.0739
2010-06-16 | 1 | 28.4453 | 8.9114 | 37.3567 | 2.4276 | 0.76558 | 0.27771 | 3.4709 | 9.291% | 9.886% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-06-16 | 2 | 30.0705 | 8.7234 | 38.7938 | 2.6179 | 0.76558 | 0.2884 | 3.6719 | 9.465% | 10.07% | 6.805% | 1.1045 | 1.112 | 1.073
2010-06-16 | 3 | 29.2079 | 8.336 | 37.5439 | 2.452 | 0.76558 | 0.27911 | 3.4966 | 9.313% | 9.91% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-06-16 | 4 | 28.2444 | 7.9923 | 36.2367 | 2.2842 | 0.76558 | 0.26939 | 3.3192 | 9.16% | 9.746% | 6.586% | 1.1008 | 1.108 | 1.0705
2010-06-16 | 5 | 27.5402 | 7.7798 | 35.32 | 2.1701 | 0.76558 | 0.26257 | 3.1982 | 9.055% | 9.635% | 6.511% | 1.0996 | 1.1066 | 1.0696
2010-06-16 | 6 | 26.7181 | 7.5982 | 34.3163 | 2.0485 | 0.76558 | 0.25511 | 3.0692 | 8.944% | 9.516% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-06-16 | 7 | 25.7555 | 7.6158 | 33.3713 | 1.9372 | 0.76558 | 0.24809 | 2.9509 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-06-16 | 8 | 26.8187 | 7.5915 | 34.4101 | 2.0597 | 0.76558 | 0.25581 | 3.0811 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-06-16 | 9 | 26.8612 | 7.5467 | 34.4079 | 2.0595 | 0.76558 | 0.25579 | 3.0808 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-06-16 | 10 | 26.9599 | 7.6468 | 34.6067 | 2.0833 | 0.76558 | 0.25727 | 3.1062 | 8.976% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-06-16 | 11 | 27.6218 | 8.068 | 35.6898 | 2.2158 | 0.76558 | 0.26532 | 3.2467 | 9.097% | 9.679% | 6.541% | 1.1001 | 1.1072 | 1.07
2010-06-16 | 12 | 28.4262 | 8.6196 | 37.0458 | 2.3873 | 0.76558 | 0.2754 | 3.4283 | 9.254% | 9.847% | 6.654% | 1.102 | 1.1092 | 1.0713
2010-06-16 | 13 | 30.3667 | 9.7594 | 40.1261 | 2.8008 | 0.76558 | 0.2983 | 3.8647 | 9.631% | 10.25% | 6.925% | 1.1066 | 1.1142 | 1.0744
2010-06-16 | 14 | 33.499 | 11.2996 | 44.7987 | 3.4911 | 0.76558 | 0.33304 | 4.5897 | 10.25% | 10.9% | 7.366% | 1.1141 | 1.1223 | 1.0795
2010-06-16 | 15 | 37.3619 | 13.4794 | 50.8413 | 4.4964 | 0.76558 | 0.37796 | 5.64 | 11.09% | 11.8% | 7.976% | 1.1248 | 1.1338 | 1.0867
2010-06-16 | 16 | 39.097 | 14.6408 | 53.7378 | 5.0234 | 0.76558 | 0.39949 | 6.1884 | 11.52% | 12.25% | 8.28% | 1.1301 | 1.1396 | 1.0903
2010-06-16 | 17 | 41.3363 | 15.7289 | 57.0652 | 5.6647 | 0.76558 | 0.42423 | 6.8545 | 12.01% | 12.78% | 8.636% | 1.1365 | 1.1465 | 1.0945
2010-06-16 | 18 | 41.7811 | 16.0416 | 57.8226 | 5.8161 | 0.76558 | 0.42986 | 7.0115 | 12.13% | 12.9% | 8.719% | 1.138 | 1.1481 | 1.0955
2010-06-16 | 19 | 41.5505 | 15.8961 | 57.4467 | 5.7407 | 0.76558 | 0.42707 | 6.9333 | 12.07% | 12.84% | 8.678% | 1.1373 | 1.1473 | 1.095
2010-06-16 | 20 | 41.1204 | 15.0242 | 56.1446 | 5.4834 | 0.76558 | 0.41739 | 6.6664 | 11.87% | 12.63% | 8.537% | 1.1347 | 1.1446 | 1.0933
2010-06-16 | 21 | 42.9168 | 14.5515 | 57.4683 | 5.745 | 0.76558 | 0.42723 | 6.9378 | 12.07% | 12.85% | 8.68% | 1.1373 | 1.1474 | 1.0951
2010-06-16 | 22 | 41.9978 | 13.8506 | 55.8484 | 5.4257 | 0.76558 | 0.41518 | 6.6065 | 11.83% | 12.59% | 8.505% | 1.1342 | 1.144 | 1.093
2010-06-16 | 23 | 40.3463 | 13.0123 | 53.3586 | 4.9527 | 0.76558 | 0.39667 | 6.115 | 11.46% | 12.19% | 8.24% | 1.1294 | 1.1389 | 1.0898
2010-06-16 | 24 | 39.2837 | 12.5423 | 51.8259 | 4.6723 | 0.76558 | 0.38528 | 5.8231 | 11.24% | 11.96% | 8.079% | 1.1266 | 1.1358 | 1.0879
2010-06-16 | 25 | 37.1432 | 11.9296 | 49.0728 | 4.1891 | 0.76558 | 0.36481 | 5.3194 | 10.84% | 11.53% | 7.794% | 1.1216 | 1.1304 | 1.0845
2010-06-16 | 26 | 35.5915 | 11.151 | 46.7425 | 3.8006 | 0.76558 | 0.34749 | 4.9137 | 10.51% | 11.19% | 7.558% | 1.1175 | 1.1259 | 1.0818
2010-06-16 | 27 | 35.7941 | 11.3006 | 47.0947 | 3.8582 | 0.76558 | 0.35011 | 4.9738 | 10.56% | 11.24% | 7.594% | 1.1181 | 1.1266 | 1.0822
2010-06-16 | 28 | 36.0263 | 11.608 | 47.6343 | 3.9471 | 0.76558 | 0.35412 | 5.0668 | 10.64% | 11.32% | 7.648% | 1.119 | 1.1276 | 1.0828
2010-06-16 | 29 | 36.3149 | 11.1778 | 47.4926 | 3.9236 | 0.76558 | 0.35307 | 5.0423 | 10.62% | 11.3% | 7.634% | 1.1188 | 1.1274 | 1.0826
2010-06-16 | 30 | 35.8414 | 11.0982 | 46.9396 | 3.8328 | 0.76558 | 0.34895 | 4.9473 | 10.54% | 11.21% | 7.578% | 1.1178 | 1.1263 | 1.082
2010-06-16 | 31 | 37.8527 | 11.269 | 49.1217 | 4.1974 | 0.76558 | 0.36518 | 5.3282 | 10.85% | 11.54% | 7.799% | 1.1217 | 1.1305 | 1.0846
2010-06-16 | 32 | 38.2993 | 11.4431 | 49.7424 | 4.3042 | 0.76558 | 0.36979 | 5.4395 | 10.94% | 11.64% | 7.863% | 1.1228 | 1.1317 | 1.0853
2010-06-16 | 33 | 38.9302 | 11.9847 | 50.9148 | 4.5094 | 0.76558 | 0.37851 | 5.6535 | 11.1% | 11.81% | 7.984% | 1.1249 | 1.134 | 1.0868
2010-06-16 | 34 | 41.0542 | 12.7144 | 53.7686 | 5.0291 | 0.76558 | 0.39972 | 6.1944 | 11.52% | 12.26% | 8.283% | 1.1302 | 1.1397 | 1.0903
2010-06-16 | 35 | 42.5173 | 14.0471 | 56.5644 | 5.5657 | 0.76558 | 0.42051 | 6.7518 | 11.94% | 12.7% | 8.582% | 1.1355 | 1.1455 | 1.0939
2010-06-16 | 36 | 44.678 | 15.0766 | 59.7546 | 6.2112 | 0.76558 | 0.44422 | 7.421 | 12.42% | 13.21% | 8.929% | 1.1418 | 1.1523 | 1.098
2010-06-16 | 37 | 44.6672 | 14.6671 | 59.3343 | 6.1242 | 0.76558 | 0.4411 | 7.3308 | 12.36% | 13.15% | 8.883% | 1.141 | 1.1514 | 1.0975
2010-06-16 | 38 | 45.5295 | 14.6372 | 60.1667 | 6.2972 | 0.76558 | 0.44729 | 7.5101 | 12.48% | 13.28% | 8.975% | 1.1426 | 1.1531 | 1.0986
2010-06-16 | 39 | 44.5882 | 14.2063 | 58.7945 | 6.0132 | 0.76558 | 0.43709 | 7.2159 | 12.27% | 13.06% | 8.824% | 1.1399 | 1.1502 | 1.0968
2010-06-16 | 40 | 43.7243 | 13.2861 | 57.0104 | 5.6538 | 0.76558 | 0.42382 | 6.8432 | 12% | 12.77% | 8.631% | 1.1364 | 1.1464 | 1.0945
2010-06-16 | 41 | 44.3983 | 13.1184 | 57.5166 | 5.7547 | 0.76558 | 0.42759 | 6.9479 | 12.08% | 12.85% | 8.685% | 1.1374 | 1.1475 | 1.0951
2010-06-16 | 42 | 44.2408 | 12.6929 | 56.9338 | 5.6386 | 0.76558 | 0.42325 | 6.8275 | 11.99% | 12.76% | 8.622% | 1.1363 | 1.1463 | 1.0944
2010-06-16 | 43 | 42.0168 | 11.9942 | 54.011 | 5.0746 | 0.76558 | 0.40152 | 6.2417 | 11.56% | 12.3% | 8.309% | 1.1307 | 1.1402 | 1.0906
2010-06-16 | 44 | 40.2924 | 11.4919 | 51.7843 | 4.6648 | 0.76558 | 0.38497 | 5.8153 | 11.23% | 11.95% | 8.074% | 1.1265 | 1.1357 | 1.0878
2010-06-16 | 45 | 36.2458 | 10.3336 | 46.5794 | 3.7742 | 0.76558 | 0.34628 | 4.886 | 10.49% | 11.16% | 7.542% | 1.1172 | 1.1256 | 1.0816
2010-06-16 | 46 | 33.0273 | 9.215 | 42.2423 | 3.1041 | 0.76558 | 0.31403 | 4.1837 | 9.904% | 10.54% | 7.121% | 1.1099 | 1.1178 | 1.0767
2010-06-16 | 47 | 32.5744 | 9.4133 | 41.9877 | 3.0668 | 0.76558 | 0.31214 | 4.1445 | 9.871% | 10.5% | 7.097% | 1.1095 | 1.1173 | 1.0764
2010-06-16 | 48 | 31.7066 | 10.0072 | 41.7138 | 3.0269 | 0.76558 | 0.31011 | 4.1026 | 9.835% | 10.46% | 7.071% | 1.1091 | 1.1169 | 1.0761
2010-06-17 | 1 | 30.1978 | 9.238 | 39.4358 | 2.7053 | 0.76558 | 0.29317 | 3.7641 | 9.545% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-06-17 | 2 | 31.719 | 9.1481 | 40.8671 | 2.9052 | 0.76558 | 0.30381 | 3.9746 | 9.726% | 10.35% | 6.993% | 1.1077 | 1.1154 | 1.0752
2010-06-17 | 3 | 31.1289 | 8.7689 | 39.8978 | 2.7691 | 0.76558 | 0.29661 | 3.8312 | 9.603% | 10.22% | 6.904% | 1.1062 | 1.1138 | 1.0742
2010-06-17 | 4 | 30.2936 | 8.4498 | 38.7434 | 2.6111 | 0.76558 | 0.28802 | 3.6647 | 9.459% | 10.06% | 6.801% | 1.1045 | 1.1119 | 1.073
2010-06-17 | 5 | 29.3853 | 8.1513 | 37.5365 | 2.451 | 0.76558 | 0.27905 | 3.4956 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-06-17 | 6 | 28.7969 | 8.0202 | 36.8171 | 2.3579 | 0.76558 | 0.2737 | 3.3972 | 9.227% | 9.818% | 6.634% | 1.1017 | 1.1089 | 1.0711
2010-06-17 | 7 | 29.0412 | 8.0209 | 37.0621 | 2.3894 | 0.76558 | 0.27552 | 3.4305 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-06-17 | 8 | 29.0685 | 7.9885 | 37.057 | 2.3888 | 0.76558 | 0.27549 | 3.4298 | 9.256% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-06-17 | 9 | 28.9398 | 8.1508 | 37.0907 | 2.3931 | 0.76558 | 0.27574 | 3.4344 | 9.26% | 9.852% | 6.658% | 1.102 | 1.1093 | 1.0713
2010-06-17 | 10 | 29.067 | 8.2967 | 37.3637 | 2.4285 | 0.76558 | 0.27777 | 3.4718 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-06-17 | 11 | 29.8295 | 8.7114 | 38.5408 | 2.5839 | 0.76558 | 0.28652 | 3.636 | 9.434% | 10.04% | 6.783% | 1.1042 | 1.1116 | 1.0728
2010-06-17 | 12 | 30.865 | 9.1459 | 40.0108 | 2.7848 | 0.76558 | 0.29745 | 3.8478 | 9.617% | 10.23% | 6.915% | 1.1064 | 1.114 | 1.0743
2010-06-17 | 13 | 33.0753 | 10.1809 | 43.2563 | 3.2549 | 0.76558 | 0.32157 | 4.342 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-06-17 | 14 | 36.3103 | 11.9624 | 48.2727 | 4.0536 | 0.76558 | 0.35887 | 5.178 | 10.73% | 11.41% | 7.712% | 1.1202 | 1.1288 | 1.0836
2010-06-17 | 15 | 40.8184 | 14.3717 | 55.1901 | 5.2986 | 0.76558 | 0.41029 | 6.4744 | 11.73% | 12.48% | 8.435% | 1.1329 | 1.1426 | 1.0921
2010-06-17 | 16 | 42.9564 | 15.4326 | 58.389 | 5.9306 | 0.76558 | 0.43407 | 7.1302 | 12.21% | 12.99% | 8.78% | 1.1391 | 1.1493 | 1.0963
2010-06-17 | 17 | 44.2477 | 16.2027 | 60.4503 | 6.3567 | 0.76558 | 0.4494 | 7.5717 | 12.53% | 13.33% | 9.006% | 1.1432 | 1.1538 | 1.099
2010-06-17 | 18 | 44.0761 | 16.3 | 60.3761 | 6.3411 | 0.76558 | 0.44884 | 7.5555 | 12.51% | 13.32% | 8.998% | 1.143 | 1.1536 | 1.0989
2010-06-17 | 19 | 44.4059 | 16.3031 | 60.709 | 6.4112 | 0.76558 | 0.45132 | 7.6281 | 12.57% | 13.37% | 9.034% | 1.1437 | 1.1543 | 1.0993
2010-06-17 | 20 | 43.3288 | 16.0111 | 59.3399 | 6.1253 | 0.76558 | 0.44114 | 7.332 | 12.36% | 13.15% | 8.884% | 1.141 | 1.1514 | 1.0975
2010-06-17 | 21 | 44.7506 | 15.9243 | 60.6749 | 6.404 | 0.76558 | 0.45106 | 7.6207 | 12.56% | 13.36% | 9.031% | 1.1436 | 1.1543 | 1.0993
2010-06-17 | 22 | 44.1358 | 15.5445 | 59.6803 | 6.1958 | 0.76558 | 0.44367 | 7.405 | 12.41% | 13.2% | 8.921% | 1.1417 | 1.1521 | 1.098
2010-06-17 | 23 | 42.0424 | 14.669 | 56.7114 | 5.5947 | 0.76558 | 0.4216 | 6.7819 | 11.96% | 12.72% | 8.598% | 1.1358 | 1.1458 | 1.0941
2010-06-17 | 24 | 40.3473 | 14.0299 | 54.3772 | 5.1436 | 0.76558 | 0.40425 | 6.3134 | 11.61% | 12.35% | 8.348% | 1.1314 | 1.1409 | 1.0911
2010-06-17 | 25 | 38.1335 | 13.4691 | 51.6026 | 4.6321 | 0.76558 | 0.38362 | 5.7813 | 11.2% | 11.92% | 8.055% | 1.1262 | 1.1353 | 1.0876
2010-06-17 | 26 | 36.5699 | 12.4354 | 49.0053 | 4.1775 | 0.76558 | 0.36431 | 5.3074 | 10.83% | 11.52% | 7.787% | 1.1215 | 1.1302 | 1.0844
2010-06-17 | 27 | 36.8628 | 12.911 | 49.7738 | 4.3096 | 0.76558 | 0.37002 | 5.4452 | 10.94% | 11.64% | 7.866% | 1.1228 | 1.1317 | 1.0854
2010-06-17 | 28 | 36.4917 | 13.0208 | 49.5125 | 4.2645 | 0.76558 | 0.36808 | 5.3981 | 10.9% | 11.6% | 7.839% | 1.1224 | 1.1312 | 1.0851
2010-06-17 | 29 | 36.0204 | 12.6242 | 48.6446 | 4.1163 | 0.76558 | 0.36163 | 5.2435 | 10.78% | 11.47% | 7.75% | 1.1208 | 1.1295 | 1.084
2010-06-17 | 30 | 35.4359 | 12.2915 | 47.7274 | 3.9625 | 0.76558 | 0.35481 | 5.0829 | 10.65% | 11.33% | 7.657% | 1.1192 | 1.1278 | 1.0829
2010-06-17 | 31 | 37.6631 | 12.568 | 50.2311 | 4.3892 | 0.76558 | 0.37342 | 5.5282 | 11.01% | 11.71% | 7.913% | 1.1237 | 1.1326 | 1.0859
2010-06-17 | 32 | 38.713 | 12.835 | 51.548 | 4.6223 | 0.76558 | 0.38321 | 5.7711 | 11.2% | 11.91% | 8.05% | 1.1261 | 1.1352 | 1.0875
2010-06-17 | 33 | 39.4448 | 12.8841 | 52.3289 | 4.7634 | 0.76558 | 0.38902 | 5.918 | 11.31% | 12.03% | 8.131% | 1.1275 | 1.1368 | 1.0885
2010-06-17 | 34 | 40.4066 | 13.0552 | 53.4617 | 4.9719 | 0.76558 | 0.39744 | 6.1349 | 11.48% | 12.21% | 8.251% | 1.1296 | 1.1391 | 1.0899
2010-06-17 | 35 | 41.2528 | 14.3322 | 55.585 | 5.3747 | 0.76558 | 0.41323 | 6.5535 | 11.79% | 12.54% | 8.477% | 1.1337 | 1.1434 | 1.0926
2010-06-17 | 36 | 43.6083 | 15.1702 | 58.7785 | 6.01 | 0.76558 | 0.43697 | 7.2125 | 12.27% | 13.06% | 8.823% | 1.1399 | 1.1502 | 1.0968
2010-06-17 | 37 | 43.3319 | 14.4624 | 57.7942 | 5.8104 | 0.76558 | 0.42965 | 7.0056 | 12.12% | 12.9% | 8.715% | 1.1379 | 1.1481 | 1.0955
2010-06-17 | 38 | 45.8844 | 14.998 | 60.8824 | 6.4479 | 0.76558 | 0.45261 | 7.6661 | 12.59% | 13.4% | 9.053% | 1.1441 | 1.1547 | 1.0995
2010-06-17 | 39 | 45.1787 | 14.863 | 60.0417 | 6.2711 | 0.76558 | 0.44636 | 7.483 | 12.46% | 13.26% | 8.961% | 1.1424 | 1.1529 | 1.0984
2010-06-17 | 40 | 45.0608 | 14.1163 | 59.1771 | 6.0917 | 0.76558 | 0.43993 | 7.2972 | 12.33% | 13.12% | 8.866% | 1.1407 | 1.151 | 1.0973
2010-06-17 | 41 | 45.4633 | 13.9039 | 59.3671 | 6.1309 | 0.76558 | 0.44134 | 7.3379 | 12.36% | 13.15% | 8.887% | 1.141 | 1.1514 | 1.0975
2010-06-17 | 42 | 45.5222 | 13.5371 | 59.0593 | 6.0675 | 0.76558 | 0.43905 | 7.2722 | 12.31% | 13.1% | 8.853% | 1.1404 | 1.1508 | 1.0971
2010-06-17 | 43 | 43.1631 | 12.8866 | 56.0497 | 5.4649 | 0.76558 | 0.41668 | 6.6471 | 11.86% | 12.62% | 8.527% | 1.1346 | 1.1444 | 1.0932
2010-06-17 | 44 | 40.8654 | 12.0328 | 52.8982 | 4.8676 | 0.76558 | 0.39325 | 6.0264 | 11.39% | 12.12% | 8.191% | 1.1286 | 1.1379 | 1.0892
2010-06-17 | 45 | 37.0421 | 10.7705 | 47.8126 | 3.9767 | 0.76558 | 0.35544 | 5.0977 | 10.66% | 11.34% | 7.666% | 1.1193 | 1.128 | 1.083
2010-06-17 | 46 | 33.3356 | 9.6392 | 42.9748 | 3.2126 | 0.76558 | 0.31948 | 4.2977 | 10% | 10.64% | 7.19% | 1.1111 | 1.1191 | 1.0775
2010-06-17 | 47 | 33.0187 | 10.0651 | 43.0839 | 3.229 | 0.76558 | 0.32029 | 4.3148 | 10.01% | 10.66% | 7.201% | 1.1113 | 1.1193 | 1.0776
2010-06-17 | 48 | 32.0289 | 10.5747 | 42.6036 | 3.1574 | 0.76558 | 0.31672 | 4.2397 | 9.951% | 10.59% | 7.155% | 1.1105 | 1.1184 | 1.0771
2010-06-18 | 1 | 30.3492 | 9.8661 | 40.2153 | 2.8133 | 0.76558 | 0.29897 | 3.8778 | 9.643% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-06-18 | 2 | 32.3312 | 9.7147 | 42.046 | 3.0753 | 0.76558 | 0.31257 | 4.1534 | 9.878% | 10.51% | 7.102% | 1.1096 | 1.1174 | 1.0765
2010-06-18 | 3 | 31.8823 | 9.3728 | 41.2551 | 2.9607 | 0.76558 | 0.3067 | 4.0329 | 9.776% | 10.4% | 7.029% | 1.1083 | 1.1161 | 1.0756
2010-06-18 | 4 | 30.8036 | 9.0225 | 39.826 | 2.7591 | 0.76558 | 0.29607 | 3.8208 | 9.594% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-06-18 | 5 | 29.6237 | 8.779 | 38.4027 | 2.5654 | 0.76558 | 0.28549 | 3.6165 | 9.417% | 10.02% | 6.771% | 1.104 | 1.1114 | 1.0726
2010-06-18 | 6 | 28.748 | 8.6306 | 37.3786 | 2.4304 | 0.76558 | 0.27788 | 3.4739 | 9.294% | 9.889% | 6.682% | 1.1025 | 1.1097 | 1.0716
2010-06-18 | 7 | 28.9912 | 8.5272 | 37.5184 | 2.4486 | 0.76558 | 0.27892 | 3.4931 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.11 | 1.0717
2010-06-18 | 8 | 28.5164 | 8.6191 | 37.1355 | 2.3989 | 0.76558 | 0.27607 | 3.4406 | 9.265% | 9.858% | 6.661% | 1.1021 | 1.1094 | 1.0714
2010-06-18 | 9 | 28.3578 | 8.6334 | 36.9912 | 2.3803 | 0.76558 | 0.275 | 3.4209 | 9.248% | 9.84% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-06-18 | 10 | 28.1559 | 8.5542 | 36.7101 | 2.3443 | 0.76558 | 0.27291 | 3.3827 | 9.215% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.071
2010-06-18 | 11 | 28.8887 | 8.9209 | 37.8095 | 2.4868 | 0.76558 | 0.28108 | 3.5334 | 9.345% | 9.943% | 6.719% | 1.1031 | 1.1104 | 1.072
2010-06-18 | 12 | 30.0953 | 9.2786 | 39.3739 | 2.6968 | 0.76558 | 0.29271 | 3.7551 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-06-18 | 13 | 32.7129 | 10.5231 | 43.236 | 3.2518 | 0.76558 | 0.32142 | 4.3388 | 10.04% | 10.68% | 7.215% | 1.1115 | 1.1195 | 1.0778
2010-06-18 | 14 | 36.4043 | 12.2194 | 48.6237 | 4.1127 | 0.76558 | 0.36147 | 5.2398 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-06-18 | 15 | 40.641 | 14.5202 | 55.1612 | 5.293 | 0.76558 | 0.41008 | 6.4687 | 11.73% | 12.48% | 8.432% | 1.1328 | 1.1426 | 1.0921
2010-06-18 | 16 | 42.3036 | 15.66 | 57.9636 | 5.8445 | 0.76558 | 0.43091 | 7.041 | 12.15% | 12.92% | 8.734% | 1.1383 | 1.1484 | 1.0957
2010-06-18 | 17 | 43.8114 | 16.36 | 60.1714 | 6.2982 | 0.76558 | 0.44732 | 7.5111 | 12.48% | 13.28% | 8.975% | 1.1426 | 1.1532 | 1.0986
2010-06-18 | 18 | 43.9244 | 16.3002 | 60.2246 | 6.3093 | 0.76558 | 0.44772 | 7.5226 | 12.49% | 13.29% | 8.981% | 1.1427 | 1.1533 | 1.0987
2010-06-18 | 19 | 44.3888 | 16.298 | 60.6868 | 6.4065 | 0.76558 | 0.45115 | 7.6233 | 12.56% | 13.37% | 9.032% | 1.1437 | 1.1543 | 1.0993
2010-06-18 | 20 | 43.6238 | 15.9337 | 59.5575 | 6.1703 | 0.76558 | 0.44276 | 7.3787 | 12.39% | 13.18% | 8.908% | 1.1414 | 1.1518 | 1.0978
2010-06-18 | 21 | 44.8335 | 15.3046 | 60.1381 | 6.2912 | 0.76558 | 0.44707 | 7.5039 | 12.48% | 13.28% | 8.971% | 1.1426 | 1.1531 | 1.0986
2010-06-18 | 22 | 44.0567 | 14.6388 | 58.6956 | 5.993 | 0.76558 | 0.43635 | 7.1949 | 12.26% | 13.04% | 8.814% | 1.1397 | 1.15 | 1.0967
2010-06-18 | 23 | 42.3607 | 13.8098 | 56.1705 | 5.4885 | 0.76558 | 0.41758 | 6.6716 | 11.88% | 12.64% | 8.54% | 1.1348 | 1.1447 | 1.0934
2010-06-18 | 24 | 40.4784 | 13.0725 | 53.5509 | 4.9885 | 0.76558 | 0.3981 | 6.1522 | 11.49% | 12.22% | 8.26% | 1.1298 | 1.1393 | 1.09
2010-06-18 | 25 | 37.7942 | 12.2369 | 50.0311 | 4.3543 | 0.76558 | 0.37194 | 5.4918 | 10.98% | 11.68% | 7.892% | 1.1233 | 1.1322 | 1.0857
2010-06-18 | 26 | 36.0721 | 11.2498 | 47.3219 | 3.8955 | 0.76558 | 0.3518 | 5.0128 | 10.59% | 11.27% | 7.616% | 1.1185 | 1.127 | 1.0824
2010-06-18 | 27 | 35.5187 | 11.6306 | 47.1493 | 3.8671 | 0.76558 | 0.35051 | 4.9832 | 10.57% | 11.25% | 7.599% | 1.1182 | 1.1267 | 1.0822
2010-06-18 | 28 | 36.311 | 11.7651 | 48.0761 | 4.0206 | 0.76558 | 0.3574 | 5.1436 | 10.7% | 11.38% | 7.692% | 1.1198 | 1.1285 | 1.0833
2010-06-18 | 29 | 35.9104 | 11.5043 | 47.4147 | 3.9107 | 0.76558 | 0.35249 | 5.0288 | 10.61% | 11.28% | 7.626% | 1.1186 | 1.1272 | 1.0826
2010-06-18 | 30 | 35.4343 | 11.08 | 46.5144 | 3.7636 | 0.76558 | 0.34579 | 4.875 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-06-18 | 31 | 37.6034 | 11.1257 | 48.7291 | 4.1306 | 0.76558 | 0.36226 | 5.2584 | 10.79% | 11.48% | 7.759% | 1.121 | 1.1297 | 1.0841
2010-06-18 | 32 | 38.7446 | 11.1769 | 49.9215 | 4.3352 | 0.76558 | 0.37112 | 5.4719 | 10.96% | 11.66% | 7.881% | 1.1231 | 1.132 | 1.0856
2010-06-18 | 33 | 39.6197 | 11.7005 | 51.3202 | 4.5815 | 0.76558 | 0.38152 | 5.7286 | 11.16% | 11.88% | 8.026% | 1.1257 | 1.1348 | 1.0873
2010-06-18 | 34 | 40.9803 | 12.1521 | 53.1324 | 4.9108 | 0.76558 | 0.39499 | 6.0714 | 11.43% | 12.16% | 8.216% | 1.129 | 1.1384 | 1.0895
2010-06-18 | 35 | 41.6913 | 13.676 | 55.3673 | 5.3326 | 0.76558 | 0.41161 | 6.5098 | 11.76% | 12.51% | 8.454% | 1.1332 | 1.143 | 1.0923
2010-06-18 | 36 | 44.2277 | 15.1298 | 59.3576 | 6.129 | 0.76558 | 0.44127 | 7.3358 | 12.36% | 13.15% | 8.886% | 1.141 | 1.1514 | 1.0975
2010-06-18 | 37 | 45.6865 | 15.4113 | 61.0979 | 6.4936 | 0.76558 | 0.45421 | 7.7134 | 12.62% | 13.43% | 9.077% | 1.1445 | 1.1552 | 1.0998
2010-06-18 | 38 | 43.485 | 15.3164 | 58.8014 | 6.0146 | 0.76558 | 0.43714 | 7.2174 | 12.27% | 13.06% | 8.825% | 1.1399 | 1.1502 | 1.0968
2010-06-18 | 39 | 42.6037 | 15.0171 | 57.6208 | 5.7755 | 0.76558 | 0.42836 | 6.9695 | 12.1% | 12.87% | 8.697% | 1.1376 | 1.1477 | 1.0952
2010-06-18 | 40 | 41.7661 | 14.5079 | 56.274 | 5.5087 | 0.76558 | 0.41835 | 6.6926 | 11.89% | 12.65% | 8.551% | 1.135 | 1.1449 | 1.0935
2010-06-18 | 41 | 43.7018 | 14.1289 | 57.8307 | 5.8177 | 0.76558 | 0.42992 | 7.0132 | 12.13% | 12.9% | 8.719% | 1.138 | 1.1481 | 1.0955
2010-06-18 | 42 | 44.9765 | 13.7644 | 58.7409 | 6.0023 | 0.76558 | 0.43669 | 7.2045 | 12.26% | 13.05% | 8.818% | 1.1398 | 1.1501 | 1.0967
2010-06-18 | 43 | 43.1496 | 13.0688 | 56.2184 | 5.4978 | 0.76558 | 0.41793 | 6.6814 | 11.88% | 12.65% | 8.545% | 1.1349 | 1.1448 | 1.0934
2010-06-18 | 44 | 41.7963 | 12.2747 | 54.0711 | 5.0859 | 0.76558 | 0.40197 | 6.2534 | 11.57% | 12.31% | 8.315% | 1.1308 | 1.1403 | 1.0907
2010-06-18 | 45 | 37.5692 | 11.2311 | 48.8003 | 4.1427 | 0.76558 | 0.36279 | 5.271 | 10.8% | 11.49% | 7.766% | 1.1211 | 1.1298 | 1.0842
2010-06-18 | 46 | 34.3209 | 9.7893 | 44.1102 | 3.3846 | 0.76558 | 0.32792 | 4.4781 | 10.15% | 10.8% | 7.299% | 1.113 | 1.1211 | 1.0787
2010-06-18 | 47 | 34.2734 | 10.2294 | 44.5028 | 3.4452 | 0.76558 | 0.33084 | 4.5416 | 10.21% | 10.86% | 7.338% | 1.1136 | 1.1218 | 1.0792
2010-06-18 | 48 | 32.4479 | 10.7362 | 43.1841 | 3.244 | 0.76558 | 0.32104 | 4.3306 | 10.03% | 10.67% | 7.21% | 1.1115 | 1.1194 | 1.0777
2010-06-19 | 1 | 30.3444 | 9.9868 | 40.3312 | 2.8295 | 0.76558 | 0.29983 | 3.8949 | 9.657% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-06-19 | 2 | 30.6584 | 9.9297 | 40.5882 | 2.8657 | 0.76558 | 0.30174 | 3.933 | 9.69% | 10.31% | 6.967% | 1.1073 | 1.115 | 1.0749
2010-06-19 | 3 | 29.5064 | 9.5573 | 39.0637 | 2.6545 | 0.76558 | 0.2904 | 3.7105 | 9.499% | 10.11% | 6.829% | 1.105 | 1.1124 | 1.0733
2010-06-19 | 4 | 29.1316 | 9.1559 | 38.2876 | 2.5501 | 0.76558 | 0.28463 | 3.6003 | 9.403% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-06-19 | 5 | 28.9563 | 8.8475 | 37.8038 | 2.486 | 0.76558 | 0.28104 | 3.5326 | 9.345% | 9.943% | 6.719% | 1.1031 | 1.1104 | 1.072
2010-06-19 | 6 | 28.7268 | 8.6396 | 37.3664 | 2.4288 | 0.76558 | 0.27779 | 3.4722 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-06-19 | 7 | 29.4263 | 8.5487 | 37.975 | 2.5086 | 0.76558 | 0.28231 | 3.5565 | 9.365% | 9.965% | 6.734% | 1.1033 | 1.1107 | 1.0722
2010-06-19 | 8 | 29.7393 | 8.5403 | 38.2795 | 2.549 | 0.76558 | 0.28457 | 3.5991 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-06-19 | 9 | 29.7683 | 8.5112 | 38.2795 | 2.549 | 0.76558 | 0.28457 | 3.5991 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-06-19 | 10 | 29.9632 | 8.6431 | 38.6063 | 2.5927 | 0.76558 | 0.287 | 3.6453 | 9.442% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-06-19 | 11 | 30.4794 | 9.0184 | 39.4978 | 2.7138 | 0.76558 | 0.29363 | 3.773 | 9.552% | 10.16% | 6.868% | 1.1056 | 1.1131 | 1.0737
2010-06-19 | 12 | 31.8554 | 9.4023 | 41.2578 | 2.9611 | 0.76558 | 0.30672 | 4.0333 | 9.776% | 10.4% | 7.029% | 1.1084 | 1.1161 | 1.0756
2010-06-19 | 13 | 34.3077 | 10.4663 | 44.7741 | 3.4873 | 0.76558 | 0.33286 | 4.5857 | 10.24% | 10.9% | 7.364% | 1.1141 | 1.1223 | 1.0795
2010-06-19 | 14 | 37.9678 | 12.2528 | 50.2206 | 4.3873 | 0.76558 | 0.37335 | 5.5262 | 11% | 11.71% | 7.912% | 1.1236 | 1.1326 | 1.0859
2010-06-19 | 15 | 42.0731 | 14.7444 | 56.8175 | 5.6156 | 0.76558 | 0.42239 | 6.8036 | 11.97% | 12.74% | 8.61% | 1.136 | 1.146 | 1.0942
2010-06-19 | 16 | 43.6628 | 16.0291 | 59.6919 | 6.1982 | 0.76558 | 0.44376 | 7.4075 | 12.41% | 13.2% | 8.923% | 1.1417 | 1.1521 | 1.098
2010-06-19 | 17 | 44.8274 | 16.3521 | 61.1795 | 6.511 | 0.76558 | 0.45482 | 7.7314 | 12.64% | 13.45% | 9.086% | 1.1447 | 1.1553 | 1.0999
2010-06-19 | 18 | 44.5252 | 16.3458 | 60.871 | 6.4455 | 0.76558 | 0.45252 | 7.6636 | 12.59% | 13.4% | 9.052% | 1.144 | 1.1547 | 1.0995
2010-06-19 | 19 | 45.476 | 16.2962 | 61.7722 | 6.6377 | 0.76558 | 0.45922 | 7.8625 | 12.73% | 13.54% | 9.152% | 1.1458 | 1.1566 | 1.1007
2010-06-19 | 20 | 45.0081 | 16.3285 | 61.3366 | 6.5445 | 0.76558 | 0.45598 | 7.766 | 12.66% | 13.47% | 9.103% | 1.145 | 1.1557 | 1.1002
2010-06-19 | 21 | 46.6302 | 16.247 | 62.8771 | 6.8773 | 0.76558 | 0.46744 | 8.1104 | 12.9% | 13.72% | 9.274% | 1.1481 | 1.1591 | 1.1022
2010-06-19 | 22 | 45.482 | 15.775 | 61.257 | 6.5275 | 0.76558 | 0.45539 | 7.7485 | 12.65% | 13.46% | 9.095% | 1.1448 | 1.1555 | 1.1
2010-06-19 | 23 | 43.8659 | 14.674 | 58.5399 | 5.9613 | 0.76558 | 0.43519 | 7.162 | 12.23% | 13.02% | 8.797% | 1.1394 | 1.1497 | 1.0965
2010-06-19 | 24 | 42.3594 | 14.1386 | 56.498 | 5.5526 | 0.76558 | 0.42001 | 6.7382 | 11.93% | 12.69% | 8.575% | 1.1354 | 1.1453 | 1.0938
2010-06-19 | 25 | 39.3236 | 13.0926 | 52.4162 | 4.7793 | 0.76558 | 0.38967 | 5.9346 | 11.32% | 12.05% | 8.141% | 1.1277 | 1.137 | 1.0886
2010-06-19 | 26 | 36.3988 | 12.1136 | 48.5124 | 4.0939 | 0.76558 | 0.36065 | 5.2201 | 10.76% | 11.45% | 7.737% | 1.1206 | 1.1293 | 1.0839
2010-06-19 | 27 | 35.8438 | 12.6971 | 48.5409 | 4.0987 | 0.76558 | 0.36086 | 5.2252 | 10.76% | 11.45% | 7.74% | 1.1206 | 1.1293 | 1.0839
2010-06-19 | 28 | 35.9922 | 12.9396 | 48.9317 | 4.165 | 0.76558 | 0.36376 | 5.2944 | 10.82% | 11.51% | 7.779% | 1.1213 | 1.1301 | 1.0844
2010-06-19 | 29 | 36.2039 | 12.4515 | 48.6554 | 4.1181 | 0.76558 | 0.36171 | 5.2454 | 10.78% | 11.47% | 7.751% | 1.1208 | 1.1296 | 1.084
2010-06-19 | 30 | 36.1871 | 11.9241 | 48.1111 | 4.0265 | 0.76558 | 0.35766 | 5.1497 | 10.7% | 11.39% | 7.696% | 1.1199 | 1.1285 | 1.0834
2010-06-19 | 31 | 38.4071 | 11.7297 | 50.1367 | 4.3727 | 0.76558 | 0.37272 | 5.511 | 10.99% | 11.7% | 7.903% | 1.1235 | 1.1324 | 1.0858
2010-06-19 | 32 | 38.7134 | 11.5824 | 50.2959 | 4.4005 | 0.76558 | 0.37391 | 5.54 | 11.01% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-06-19 | 33 | 39.4925 | 11.9318 | 51.4243 | 4.6001 | 0.76558 | 0.38229 | 5.748 | 11.18% | 11.89% | 8.037% | 1.1258 | 1.135 | 1.0874
2010-06-19 | 34 | 40.3388 | 12.4645 | 52.8033 | 4.8502 | 0.76558 | 0.39255 | 6.0083 | 11.38% | 12.11% | 8.181% | 1.1284 | 1.1377 | 1.0891
2010-06-19 | 35 | 41.5813 | 13.43 | 55.0112 | 5.2643 | 0.76558 | 0.40896 | 6.4388 | 11.7% | 12.45% | 8.416% | 1.1326 | 1.1423 | 1.0919
2010-06-19 | 36 | 43.4557 | 14.4481 | 57.9038 | 5.8324 | 0.76558 | 0.43046 | 7.0285 | 12.14% | 12.92% | 8.727% | 1.1382 | 1.1483 | 1.0956
2010-06-19 | 37 | 44.3766 | 14.2774 | 58.654 | 5.9845 | 0.76558 | 0.43604 | 7.1861 | 12.25% | 13.04% | 8.809% | 1.1396 | 1.1499 | 1.0966
2010-06-19 | 38 | 43.783 | 14.0699 | 57.8529 | 5.8222 | 0.76558 | 0.43009 | 7.0178 | 12.13% | 12.91% | 8.722% | 1.1381 | 1.1482 | 1.0956
2010-06-19 | 39 | 41.9584 | 13.8063 | 55.7647 | 5.4095 | 0.76558 | 0.41456 | 6.5896 | 11.82% | 12.57% | 8.496% | 1.134 | 1.1438 | 1.0929
2010-06-19 | 40 | 41.235 | 13.3077 | 54.5427 | 5.175 | 0.76558 | 0.40548 | 6.346 | 11.63% | 12.38% | 8.366% | 1.1317 | 1.1413 | 1.0913
2010-06-19 | 41 | 42.2293 | 13.099 | 55.3283 | 5.3251 | 0.76558 | 0.41132 | 6.502 | 11.75% | 12.5% | 8.449% | 1.1332 | 1.1429 | 1.0923
2010-06-19 | 42 | 41.5859 | 12.7449 | 54.3307 | 5.1348 | 0.76558 | 0.4039 | 6.3043 | 11.6% | 12.35% | 8.343% | 1.1313 | 1.1409 | 1.091
2010-06-19 | 43 | 40.0721 | 12.3077 | 52.3798 | 4.7727 | 0.76558 | 0.3894 | 5.9277 | 11.32% | 12.04% | 8.137% | 1.1276 | 1.1369 | 1.0886
2010-06-19 | 44 | 39.0522 | 11.6832 | 50.7354 | 4.4777 | 0.76558 | 0.37717 | 5.6205 | 11.08% | 11.79% | 7.965% | 1.1246 | 1.1336 | 1.0865
2010-06-19 | 45 | 36.5349 | 10.756 | 47.2909 | 3.8904 | 0.76558 | 0.35157 | 5.0075 | 10.59% | 11.27% | 7.613% | 1.1184 | 1.127 | 1.0824
2010-06-19 | 46 | 32.1785 | 9.8515 | 42.03 | 3.0729 | 0.76558 | 0.31246 | 4.151 | 9.876% | 10.51% | 7.101% | 1.1096 | 1.1174 | 1.0764
2010-06-19 | 47 | 33.3843 | 10.2422 | 43.6265 | 3.3108 | 0.76558 | 0.32432 | 4.4007 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2010-06-19 | 48 | 33.826 | 10.8792 | 44.7052 | 3.4766 | 0.76558 | 0.33234 | 4.5745 | 10.23% | 10.89% | 7.357% | 1.114 | 1.1222 | 1.0794
2010-06-20 | 1 | 32.575 | 10.1358 | 42.7107 | 3.1733 | 0.76558 | 0.31752 | 4.2564 | 9.966% | 10.6% | 7.165% | 1.1107 | 1.1186 | 1.0772
2010-06-20 | 2 | 34.2666 | 9.9589 | 44.2255 | 3.4024 | 0.76558 | 0.32878 | 4.4967 | 10.17% | 10.82% | 7.311% | 1.1132 | 1.1213 | 1.0789
2010-06-20 | 3 | 33.4159 | 9.3777 | 42.7936 | 3.1856 | 0.76558 | 0.31813 | 4.2693 | 9.977% | 10.62% | 7.173% | 1.1108 | 1.1188 | 1.0773
2010-06-20 | 4 | 32.1376 | 9.1301 | 41.2677 | 2.9625 | 0.76558 | 0.30679 | 4.0348 | 9.777% | 10.4% | 7.03% | 1.1084 | 1.1161 | 1.0756
2010-06-20 | 5 | 31.4849 | 8.8237 | 40.3086 | 2.8264 | 0.76558 | 0.29966 | 3.8916 | 9.655% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-06-20 | 6 | 31.0917 | 8.6211 | 39.7128 | 2.7434 | 0.76558 | 0.29523 | 3.8042 | 9.579% | 10.19% | 6.888% | 1.1059 | 1.1135 | 1.074
2010-06-20 | 7 | 30.8462 | 8.5175 | 39.3637 | 2.6954 | 0.76558 | 0.29263 | 3.7536 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-06-20 | 8 | 30.6828 | 8.4528 | 39.1356 | 2.6643 | 0.76558 | 0.29094 | 3.7208 | 9.507% | 10.12% | 6.836% | 1.1051 | 1.1125 | 1.0734
2010-06-20 | 9 | 30.9097 | 8.5148 | 39.4245 | 2.7038 | 0.76558 | 0.29309 | 3.7624 | 9.543% | 10.15% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-06-20 | 10 | 30.9052 | 8.6042 | 39.5094 | 2.7154 | 0.76558 | 0.29372 | 3.7747 | 9.554% | 10.17% | 6.869% | 1.1056 | 1.1132 | 1.0738
2010-06-20 | 11 | 30.8478 | 8.7515 | 39.5993 | 2.7278 | 0.76558 | 0.29439 | 3.7877 | 9.565% | 10.18% | 6.877% | 1.1058 | 1.1133 | 1.0739
2010-06-20 | 12 | 31.6198 | 8.9097 | 40.5295 | 2.8574 | 0.76558 | 0.3013 | 3.9243 | 9.683% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-06-20 | 13 | 32.7086 | 9.4131 | 42.1217 | 3.0864 | 0.76558 | 0.31314 | 4.1651 | 9.888% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-06-20 | 14 | 34.6173 | 9.9779 | 44.5952 | 3.4595 | 0.76558 | 0.33153 | 4.5566 | 10.22% | 10.87% | 7.346% | 1.1138 | 1.122 | 1.0793
2010-06-20 | 15 | 36.1662 | 10.7469 | 46.9131 | 3.8285 | 0.76558 | 0.34876 | 4.9428 | 10.54% | 11.21% | 7.575% | 1.1178 | 1.1263 | 1.082
2010-06-20 | 16 | 35.8762 | 11.4104 | 47.2866 | 3.8897 | 0.76558 | 0.35153 | 5.0068 | 10.59% | 11.27% | 7.613% | 1.1184 | 1.127 | 1.0824
2010-06-20 | 17 | 37.7826 | 12.7157 | 50.4983 | 4.436 | 0.76558 | 0.37541 | 5.577 | 11.04% | 11.75% | 7.941% | 1.1241 | 1.1332 | 1.0863
2010-06-20 | 18 | 39.6199 | 14.1479 | 53.7679 | 5.029 | 0.76558 | 0.39972 | 6.1943 | 11.52% | 12.26% | 8.283% | 1.1302 | 1.1397 | 1.0903
2010-06-20 | 19 | 41.1656 | 15.0122 | 56.1778 | 5.4899 | 0.76558 | 0.41763 | 6.6731 | 11.88% | 12.64% | 8.541% | 1.1348 | 1.1447 | 1.0934
2010-06-20 | 20 | 40.4573 | 15.1653 | 55.6225 | 5.3819 | 0.76558 | 0.4135 | 6.561 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-06-20 | 21 | 43.6879 | 15.4139 | 59.1017 | 6.0762 | 0.76558 | 0.43937 | 7.2812 | 12.32% | 13.11% | 8.858% | 1.1405 | 1.1509 | 1.0972
2010-06-20 | 22 | 43.9326 | 14.9648 | 58.8974 | 6.0343 | 0.76558 | 0.43785 | 7.2377 | 12.29% | 13.08% | 8.836% | 1.1401 | 1.1504 | 1.0969
2010-06-20 | 23 | 42.8567 | 14.2613 | 57.1179 | 5.6752 | 0.76558 | 0.42462 | 6.8654 | 12.02% | 12.79% | 8.642% | 1.1366 | 1.1466 | 1.0946
2010-06-20 | 24 | 41.4216 | 13.6096 | 55.0312 | 5.2681 | 0.76558 | 0.40911 | 6.4428 | 11.71% | 12.46% | 8.418% | 1.1326 | 1.1423 | 1.0919
2010-06-20 | 25 | 38.8374 | 12.5313 | 51.3687 | 4.5902 | 0.76558 | 0.38188 | 5.7377 | 11.17% | 11.88% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-06-20 | 26 | 37.2018 | 11.5644 | 48.7662 | 4.1369 | 0.76558 | 0.36253 | 5.265 | 10.8% | 11.49% | 7.763% | 1.121 | 1.1298 | 1.0842
2010-06-20 | 27 | 37.4808 | 11.6219 | 49.1027 | 4.1942 | 0.76558 | 0.36504 | 5.3248 | 10.84% | 11.54% | 7.797% | 1.1216 | 1.1304 | 1.0846
2010-06-20 | 28 | 37.6037 | 11.5524 | 49.1561 | 4.2033 | 0.76558 | 0.36543 | 5.3343 | 10.85% | 11.55% | 7.802% | 1.1217 | 1.1305 | 1.0846
2010-06-20 | 29 | 36.7509 | 11.023 | 47.774 | 3.9702 | 0.76558 | 0.35516 | 5.091 | 10.66% | 11.34% | 7.662% | 1.1193 | 1.1279 | 1.083
2010-06-20 | 30 | 36.0909 | 10.5531 | 46.644 | 3.7847 | 0.76558 | 0.34676 | 4.897 | 10.5% | 11.17% | 7.549% | 1.1173 | 1.1258 | 1.0816
2010-06-20 | 31 | 38.6224 | 10.6404 | 49.2628 | 4.2216 | 0.76558 | 0.36623 | 5.3534 | 10.87% | 11.56% | 7.813% | 1.1219 | 1.1307 | 1.0848
2010-06-20 | 32 | 38.787 | 10.6298 | 49.4167 | 4.248 | 0.76558 | 0.36737 | 5.3809 | 10.89% | 11.59% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-06-20 | 33 | 38.7755 | 11.0613 | 49.8368 | 4.3205 | 0.76558 | 0.37049 | 5.4566 | 10.95% | 11.65% | 7.872% | 1.123 | 1.1319 | 1.0854
2010-06-20 | 34 | 39.9218 | 11.8632 | 51.785 | 4.6649 | 0.76558 | 0.38498 | 5.8155 | 11.23% | 11.95% | 8.074% | 1.1265 | 1.1357 | 1.0878
2010-06-20 | 35 | 42.317 | 13.1101 | 55.4271 | 5.3442 | 0.76558 | 0.41205 | 6.5218 | 11.77% | 12.52% | 8.46% | 1.1334 | 1.1431 | 1.0924
2010-06-20 | 36 | 45.5639 | 14.4094 | 59.9733 | 6.2568 | 0.76558 | 0.44585 | 7.4682 | 12.45% | 13.25% | 8.953% | 1.1422 | 1.1527 | 1.0983
2010-06-20 | 37 | 46.9525 | 14.4179 | 61.3704 | 6.5517 | 0.76558 | 0.45623 | 7.7735 | 12.67% | 13.48% | 9.107% | 1.145 | 1.1558 | 1.1002
2010-06-20 | 38 | 46.6157 | 13.9909 | 60.6066 | 6.3896 | 0.76558 | 0.45056 | 7.6057 | 12.55% | 13.35% | 9.023% | 1.1435 | 1.1541 | 1.0992
2010-06-20 | 39 | 44.8144 | 13.3191 | 58.1335 | 5.8788 | 0.76558 | 0.43217 | 7.0765 | 12.17% | 12.95% | 8.752% | 1.1386 | 1.1488 | 1.0959
2010-06-20 | 40 | 43.0706 | 12.6757 | 55.7463 | 5.4059 | 0.76558 | 0.41442 | 6.5859 | 11.81% | 12.57% | 8.494% | 1.134 | 1.1438 | 1.0928
2010-06-20 | 41 | 44.0404 | 12.599 | 56.6394 | 5.5805 | 0.76558 | 0.42106 | 6.7671 | 11.95% | 12.71% | 8.59% | 1.1357 | 1.1456 | 1.094
2010-06-20 | 42 | 43.9914 | 12.3074 | 56.2987 | 5.5136 | 0.76558 | 0.41853 | 6.6977 | 11.9% | 12.66% | 8.554% | 1.135 | 1.1449 | 1.0935
2010-06-20 | 43 | 40.9708 | 11.7808 | 52.7516 | 4.8407 | 0.76558 | 0.39216 | 5.9984 | 11.37% | 12.1% | 8.176% | 1.1283 | 1.1376 | 1.089
2010-06-20 | 44 | 39.8297 | 11.6129 | 51.4426 | 4.6034 | 0.76558 | 0.38243 | 5.7514 | 11.18% | 11.9% | 8.039% | 1.1259 | 1.135 | 1.0874
2010-06-20 | 45 | 36.6763 | 10.8851 | 47.5615 | 3.935 | 0.76558 | 0.35358 | 5.0542 | 10.63% | 11.31% | 7.641% | 1.1189 | 1.1275 | 1.0827
2010-06-20 | 46 | 33.4695 | 10.0965 | 43.5659 | 3.3016 | 0.76558 | 0.32387 | 4.3911 | 10.08% | 10.72% | 7.247% | 1.1121 | 1.1201 | 1.0781
2010-06-20 | 47 | 33.7803 | 10.5749 | 44.3552 | 3.4223 | 0.76558 | 0.32974 | 4.5177 | 10.19% | 10.84% | 7.323% | 1.1134 | 1.1215 | 1.079
2010-06-20 | 48 | 33.2583 | 11.3724 | 44.6307 | 3.465 | 0.76558 | 0.33179 | 4.5624 | 10.22% | 10.88% | 7.35% | 1.1139 | 1.122 | 1.0793
2010-06-21 | 1 | 31.2836 | 10.4695 | 41.7531 | 3.0326 | 0.76558 | 0.3104 | 4.1086 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2010-06-21 | 2 | 32.9134 | 10.3171 | 43.2305 | 3.251 | 0.76558 | 0.32138 | 4.3379 | 10.03% | 10.68% | 7.215% | 1.1115 | 1.1195 | 1.0778
2010-06-21 | 3 | 31.8882 | 9.8379 | 41.7261 | 3.0287 | 0.76558 | 0.3102 | 4.1044 | 9.837% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-06-21 | 4 | 30.7199 | 9.4653 | 40.1853 | 2.8091 | 0.76558 | 0.29874 | 3.8734 | 9.639% | 10.26% | 6.93% | 1.1067 | 1.1143 | 1.0745
2010-06-21 | 5 | 29.0036 | 9.1387 | 38.1423 | 2.5307 | 0.76558 | 0.28355 | 3.5799 | 9.386% | 9.986% | 6.748% | 1.1036 | 1.1109 | 1.0724
2010-06-21 | 6 | 28.4943 | 8.8991 | 37.3934 | 2.4323 | 0.76558 | 0.27799 | 3.4759 | 9.296% | 9.89% | 6.683% | 1.1025 | 1.1098 | 1.0716
2010-06-21 | 7 | 28.1469 | 8.9165 | 37.0634 | 2.3896 | 0.76558 | 0.27553 | 3.4307 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-06-21 | 8 | 28.3018 | 8.8145 | 37.1163 | 2.3964 | 0.76558 | 0.27593 | 3.4379 | 9.263% | 9.855% | 6.66% | 1.1021 | 1.1093 | 1.0713
2010-06-21 | 9 | 28.6716 | 8.9447 | 37.6163 | 2.4614 | 0.76558 | 0.27964 | 3.5067 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-06-21 | 10 | 29.4899 | 8.926 | 38.4159 | 2.5672 | 0.76558 | 0.28559 | 3.6184 | 9.419% | 10.02% | 6.772% | 1.104 | 1.1114 | 1.0726
2010-06-21 | 11 | 30.3058 | 8.9643 | 39.2701 | 2.6826 | 0.76558 | 0.29194 | 3.7401 | 9.524% | 10.13% | 6.848% | 1.1053 | 1.1128 | 1.0735
2010-06-21 | 12 | 31.2212 | 9.0952 | 40.3165 | 2.8275 | 0.76558 | 0.29972 | 3.8928 | 9.656% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-06-21 | 13 | 31.7827 | 9.454 | 41.2367 | 2.958 | 0.76558 | 0.30656 | 4.0302 | 9.773% | 10.4% | 7.027% | 1.1083 | 1.1161 | 1.0756
2010-06-21 | 14 | 32.8115 | 9.8671 | 42.6786 | 3.1685 | 0.76558 | 0.31728 | 4.2514 | 9.961% | 10.6% | 7.162% | 1.1106 | 1.1186 | 1.0771
2010-06-21 | 15 | 33.7439 | 10.1544 | 43.8983 | 3.3522 | 0.76558 | 0.32635 | 4.4441 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-06-21 | 16 | 32.9675 | 10.3091 | 43.2766 | 3.2579 | 0.76558 | 0.32172 | 4.3452 | 10.04% | 10.68% | 7.219% | 1.1116 | 1.1196 | 1.0778
2010-06-21 | 17 | 34.6625 | 11.8067 | 46.4692 | 3.7563 | 0.76558 | 0.34546 | 4.8674 | 10.47% | 11.14% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-06-21 | 18 | 36.2692 | 13.4903 | 49.7595 | 4.3071 | 0.76558 | 0.36992 | 5.4426 | 10.94% | 11.64% | 7.864% | 1.1228 | 1.1317 | 1.0854
2010-06-21 | 19 | 37.7662 | 14.1342 | 51.9004 | 4.6857 | 0.76558 | 0.38583 | 5.8371 | 11.25% | 11.97% | 8.086% | 1.1267 | 1.1359 | 1.088
2010-06-21 | 20 | 38.9583 | 14.5696 | 53.5278 | 4.9842 | 0.76558 | 0.39793 | 6.1477 | 11.49% | 12.22% | 8.258% | 1.1298 | 1.1392 | 1.09
2010-06-21 | 21 | 42.1807 | 14.9575 | 57.1382 | 5.6792 | 0.76558 | 0.42477 | 6.8696 | 12.02% | 12.79% | 8.644% | 1.1367 | 1.1467 | 1.0946
2010-06-21 | 22 | 42.3838 | 14.5413 | 56.9251 | 5.6369 | 0.76558 | 0.42319 | 6.8257 | 11.99% | 12.76% | 8.621% | 1.1362 | 1.1462 | 1.0943
2010-06-21 | 23 | 41.015 | 14.1477 | 55.1627 | 5.2933 | 0.76558 | 0.41009 | 6.469 | 11.73% | 12.48% | 8.432% | 1.1328 | 1.1426 | 1.0921
2010-06-21 | 24 | 39.5488 | 13.5592 | 53.108 | 4.9063 | 0.76558 | 0.39481 | 6.0667 | 11.42% | 12.15% | 8.213% | 1.129 | 1.1384 | 1.0895
2010-06-21 | 25 | 36.5994 | 12.7687 | 49.3681 | 4.2396 | 0.76558 | 0.36701 | 5.3722 | 10.88% | 11.58% | 7.824% | 1.1221 | 1.1309 | 1.0849
2010-06-21 | 26 | 34.8007 | 11.6807 | 46.4813 | 3.7583 | 0.76558 | 0.34555 | 4.8694 | 10.48% | 11.15% | 7.532% | 1.117 | 1.1254 | 1.0815
2010-06-21 | 27 | 34.8886 | 11.6647 | 46.5533 | 3.7699 | 0.76558 | 0.34608 | 4.8816 | 10.49% | 11.16% | 7.539% | 1.1171 | 1.1256 | 1.0815
2010-06-21 | 28 | 34.9747 | 11.831 | 46.8058 | 3.811 | 0.76558 | 0.34796 | 4.9245 | 10.52% | 11.19% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-06-21 | 29 | 34.5089 | 11.1404 | 45.6493 | 3.625 | 0.76558 | 0.33936 | 4.7299 | 10.36% | 11.02% | 7.45% | 1.1156 | 1.1239 | 1.0805
2010-06-21 | 30 | 33.9474 | 10.7765 | 44.7238 | 3.4795 | 0.76558 | 0.33248 | 4.5775 | 10.24% | 10.89% | 7.359% | 1.114 | 1.1222 | 1.0794
2010-06-21 | 31 | 36.0083 | 10.9482 | 46.9565 | 3.8355 | 0.76558 | 0.34908 | 4.9502 | 10.54% | 11.22% | 7.58% | 1.1178 | 1.1263 | 1.082
2010-06-21 | 32 | 37.2698 | 11.0472 | 48.317 | 4.061 | 0.76558 | 0.35919 | 5.1858 | 10.73% | 11.42% | 7.717% | 1.1202 | 1.1289 | 1.0836
2010-06-21 | 33 | 37.8609 | 11.5011 | 49.362 | 4.2386 | 0.76558 | 0.36696 | 5.3711 | 10.88% | 11.58% | 7.823% | 1.1221 | 1.1309 | 1.0849
2010-06-21 | 34 | 39.0049 | 12.1683 | 51.1731 | 4.5553 | 0.76558 | 0.38043 | 5.7013 | 11.14% | 11.85% | 8.011% | 1.1254 | 1.1345 | 1.0871
2010-06-21 | 35 | 39.7535 | 13.7283 | 53.4818 | 4.9756 | 0.76558 | 0.39759 | 6.1388 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.09
2010-06-21 | 36 | 42.3553 | 14.9908 | 57.3461 | 5.7206 | 0.76558 | 0.42632 | 6.9125 | 12.05% | 12.83% | 8.667% | 1.1371 | 1.1471 | 1.0949
2010-06-21 | 37 | 43.852 | 14.982 | 58.834 | 6.0213 | 0.76558 | 0.43738 | 7.2243 | 12.28% | 13.06% | 8.829% | 1.14 | 1.1503 | 1.0968
2010-06-21 | 38 | 43.6167 | 14.6435 | 58.2602 | 5.9044 | 0.76558 | 0.43311 | 7.1031 | 12.19% | 12.97% | 8.766% | 1.1388 | 1.1491 | 1.0961
2010-06-21 | 39 | 42.8357 | 14.3747 | 57.2104 | 5.6936 | 0.76558 | 0.42531 | 6.8845 | 12.03% | 12.8% | 8.652% | 1.1368 | 1.1468 | 1.0947
2010-06-21 | 40 | 41.3651 | 13.7367 | 55.1018 | 5.2816 | 0.76558 | 0.40963 | 6.4568 | 11.72% | 12.47% | 8.425% | 1.1327 | 1.1424 | 1.092
2010-06-21 | 41 | 42.3678 | 13.4571 | 55.8249 | 5.4211 | 0.76558 | 0.41501 | 6.6017 | 11.83% | 12.58% | 8.503% | 1.1341 | 1.1439 | 1.0929
2010-06-21 | 42 | 42.35 | 13.2419 | 55.5919 | 5.376 | 0.76558 | 0.41328 | 6.5548 | 11.79% | 12.55% | 8.478% | 1.1337 | 1.1435 | 1.0926
2010-06-21 | 43 | 40.0351 | 12.5699 | 52.6051 | 4.8138 | 0.76558 | 0.39107 | 5.9705 | 11.35% | 12.08% | 8.16% | 1.128 | 1.1373 | 1.0889
2010-06-21 | 44 | 38.1948 | 11.8809 | 50.0757 | 4.362 | 0.76558 | 0.37227 | 5.4999 | 10.98% | 11.69% | 7.897% | 1.1234 | 1.1323 | 1.0857
2010-06-21 | 45 | 34.0826 | 10.6679 | 44.7505 | 3.4836 | 0.76558 | 0.33268 | 4.5819 | 10.24% | 10.89% | 7.362% | 1.1141 | 1.1223 | 1.0795
2010-06-21 | 46 | 31.1833 | 9.5324 | 40.7157 | 2.8838 | 0.76558 | 0.30269 | 3.952 | 9.706% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2010-06-21 | 47 | 31.1216 | 9.8923 | 41.0139 | 2.9262 | 0.76558 | 0.3049 | 3.9966 | 9.745% | 10.37% | 7.006% | 1.108 | 1.1157 | 1.0753
2010-06-21 | 48 | 30.7328 | 10.5798 | 41.3125 | 2.9689 | 0.76558 | 0.30712 | 4.0416 | 9.783% | 10.41% | 7.034% | 1.1084 | 1.1162 | 1.0757
2010-06-22 | 1 | 29.2367 | 9.9869 | 39.2237 | 2.6763 | 0.76558 | 0.29159 | 3.7334 | 9.518% | 10.13% | 6.844% | 1.1052 | 1.1127 | 1.0735
2010-06-22 | 2 | 31.4827 | 9.8847 | 41.3674 | 2.9768 | 0.76558 | 0.30753 | 4.0499 | 9.79% | 10.42% | 7.039% | 1.1085 | 1.1163 | 1.0757
2010-06-22 | 3 | 30.5765 | 9.5002 | 40.0767 | 2.794 | 0.76558 | 0.29794 | 3.8575 | 9.625% | 10.24% | 6.921% | 1.1065 | 1.1141 | 1.0744
2010-06-22 | 4 | 29.3815 | 9.2115 | 38.5929 | 2.5909 | 0.76558 | 0.2869 | 3.6434 | 9.441% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-06-22 | 5 | 28.2749 | 8.9711 | 37.246 | 2.4132 | 0.76558 | 0.27689 | 3.4557 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-06-22 | 6 | 27.7266 | 8.7178 | 36.4444 | 2.3104 | 0.76558 | 0.27093 | 3.347 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-06-22 | 7 | 27.6678 | 8.6846 | 36.3524 | 2.2988 | 0.76558 | 0.27025 | 3.3346 | 9.173% | 9.76% | 6.595% | 1.101 | 1.1082 | 1.0706
2010-06-22 | 8 | 27.573 | 8.613 | 36.186 | 2.2778 | 0.76558 | 0.26901 | 3.3124 | 9.154% | 9.74% | 6.582% | 1.1008 | 1.1079 | 1.0705
2010-06-22 | 9 | 27.5792 | 8.8199 | 36.3991 | 2.3047 | 0.76558 | 0.2706 | 3.3409 | 9.178% | 9.766% | 6.599% | 1.1011 | 1.1082 | 1.0707
2010-06-22 | 10 | 27.513 | 8.8337 | 36.3466 | 2.2981 | 0.76558 | 0.27021 | 3.3339 | 9.172% | 9.759% | 6.595% | 1.101 | 1.1081 | 1.0706
2010-06-22 | 11 | 28.3485 | 8.9124 | 37.2609 | 2.4151 | 0.76558 | 0.277 | 3.4577 | 9.28% | 9.874% | 6.672% | 1.1023 | 1.1096 | 1.0715
2010-06-22 | 12 | 29.7284 | 9.379 | 39.1074 | 2.6604 | 0.76558 | 0.29073 | 3.7167 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-06-22 | 13 | 31.4929 | 10.4393 | 41.9322 | 3.0587 | 0.76558 | 0.31173 | 4.136 | 9.863% | 10.49% | 7.092% | 1.1094 | 1.1173 | 1.0763
2010-06-22 | 14 | 34.6675 | 12.0269 | 46.6943 | 3.7928 | 0.76558 | 0.34713 | 4.9055 | 10.51% | 11.18% | 7.554% | 1.1174 | 1.1258 | 1.0817
2010-06-22 | 15 | 38.4636 | 14.0836 | 52.5472 | 4.8032 | 0.76558 | 0.39064 | 5.9594 | 11.34% | 12.07% | 8.154% | 1.1279 | 1.1372 | 1.0888
2010-06-22 | 16 | 40.4085 | 14.997 | 55.4056 | 5.34 | 0.76558 | 0.41189 | 6.5175 | 11.76% | 12.52% | 8.458% | 1.1333 | 1.1431 | 1.0924
2010-06-22 | 17 | 42.6117 | 15.8838 | 58.4956 | 5.9522 | 0.76558 | 0.43486 | 7.1527 | 12.23% | 13.01% | 8.792% | 1.1393 | 1.1496 | 1.0964
2010-06-22 | 18 | 43.9875 | 16.3194 | 60.3069 | 6.3266 | 0.76558 | 0.44833 | 7.5405 | 12.5% | 13.3% | 8.99% | 1.1429 | 1.1535 | 1.0988
2010-06-22 | 19 | 44.4926 | 16.2933 | 60.7858 | 6.4275 | 0.76558 | 0.45189 | 7.6449 | 12.58% | 13.38% | 9.043% | 1.1439 | 1.1545 | 1.0994
2010-06-22 | 20 | 43.9693 | 16.1743 | 60.1436 | 6.2924 | 0.76558 | 0.44712 | 7.5051 | 12.48% | 13.28% | 8.972% | 1.1426 | 1.1531 | 1.0986
2010-06-22 | 21 | 46.1244 | 16.0975 | 62.2219 | 6.7347 | 0.76558 | 0.46257 | 7.9629 | 12.8% | 13.62% | 9.201% | 1.1468 | 1.1576 | 1.1013
2010-06-22 | 22 | 45.907 | 15.9534 | 61.8604 | 6.6567 | 0.76558 | 0.45988 | 7.8822 | 12.74% | 13.56% | 9.161% | 1.146 | 1.1568 | 1.1009
2010-06-22 | 23 | 44.101 | 15.4763 | 59.5773 | 6.1744 | 0.76558 | 0.4429 | 7.3829 | 12.39% | 13.19% | 8.91% | 1.1415 | 1.1519 | 1.0978
2010-06-22 | 24 | 42.7082 | 15.2277 | 57.9359 | 5.8389 | 0.76558 | 0.4307 | 7.0352 | 12.14% | 12.92% | 8.731% | 1.1382 | 1.1484 | 1.0957
2010-06-22 | 25 | 39.6577 | 14.8641 | 54.5218 | 5.171 | 0.76558 | 0.40532 | 6.3419 | 11.63% | 12.38% | 8.363% | 1.1316 | 1.1412 | 1.0913
2010-06-22 | 26 | 37.72 | 14.1723 | 51.8923 | 4.6843 | 0.76558 | 0.38577 | 5.8356 | 11.25% | 11.97% | 8.086% | 1.1267 | 1.1359 | 1.088
2010-06-22 | 27 | 37.5219 | 14.5743 | 52.0962 | 4.7211 | 0.76558 | 0.38729 | 5.874 | 11.28% | 12% | 8.107% | 1.1271 | 1.1363 | 1.0882
2010-06-22 | 28 | 37.9502 | 14.8651 | 52.8153 | 4.8524 | 0.76558 | 0.39264 | 6.0106 | 11.38% | 12.11% | 8.182% | 1.1284 | 1.1378 | 1.0891
2010-06-22 | 29 | 37.4789 | 14.4156 | 51.8945 | 4.6847 | 0.76558 | 0.38579 | 5.836 | 11.25% | 11.97% | 8.086% | 1.1267 | 1.1359 | 1.088
2010-06-22 | 30 | 36.843 | 13.8914 | 50.7344 | 4.4775 | 0.76558 | 0.37717 | 5.6203 | 11.08% | 11.79% | 7.965% | 1.1246 | 1.1336 | 1.0865
2010-06-22 | 31 | 39.1771 | 14.165 | 53.3421 | 4.9496 | 0.76558 | 0.39655 | 6.1118 | 11.46% | 12.19% | 8.238% | 1.1294 | 1.1388 | 1.0898
2010-06-22 | 32 | 40.1613 | 14.247 | 54.4083 | 5.1495 | 0.76558 | 0.40448 | 6.3196 | 11.62% | 12.36% | 8.351% | 1.1314 | 1.141 | 1.0911
2010-06-22 | 33 | 41.2819 | 14.571 | 55.8529 | 5.4266 | 0.76558 | 0.41522 | 6.6074 | 11.83% | 12.59% | 8.506% | 1.1342 | 1.144 | 1.093
2010-06-22 | 34 | 42.5367 | 14.9641 | 57.5008 | 5.7515 | 0.76558 | 0.42747 | 6.9446 | 12.08% | 12.85% | 8.684% | 1.1374 | 1.1475 | 1.0951
2010-06-22 | 35 | 43.0962 | 15.8208 | 58.9171 | 6.0383 | 0.76558 | 0.438 | 7.2419 | 12.29% | 13.08% | 8.838% | 1.1401 | 1.1505 | 1.0969
2010-06-22 | 36 | 45.5808 | 16.3541 | 61.9349 | 6.6728 | 0.76558 | 0.46043 | 7.8988 | 12.75% | 13.57% | 9.17% | 1.1462 | 1.157 | 1.101
2010-06-22 | 37 | 46.7593 | 16.3304 | 63.0897 | 6.9239 | 0.76558 | 0.46902 | 8.1585 | 12.93% | 13.76% | 9.298% | 1.1485 | 1.1595 | 1.1025
2010-06-22 | 38 | 46.7422 | 15.8885 | 62.6308 | 6.8235 | 0.76558 | 0.4656 | 8.0547 | 12.86% | 13.68% | 9.247% | 1.1476 | 1.1585 | 1.1019
2010-06-22 | 39 | 46.1355 | 15.1332 | 61.2688 | 6.53 | 0.76558 | 0.45548 | 7.7511 | 12.65% | 13.46% | 9.096% | 1.1448 | 1.1555 | 1.1001
2010-06-22 | 40 | 45.1201 | 14.3362 | 59.4562 | 6.1494 | 0.76558 | 0.442 | 7.3569 | 12.37% | 13.17% | 8.897% | 1.1412 | 1.1516 | 1.0977
2010-06-22 | 41 | 45.7977 | 14.2451 | 60.0428 | 6.2713 | 0.76558 | 0.44637 | 7.4832 | 12.46% | 13.26% | 8.961% | 1.1424 | 1.1529 | 1.0984
2010-06-22 | 42 | 45.5766 | 13.876 | 59.4525 | 6.1486 | 0.76558 | 0.44198 | 7.3561 | 12.37% | 13.17% | 8.896% | 1.1412 | 1.1516 | 1.0977
2010-06-22 | 43 | 43.5903 | 13.1358 | 56.7261 | 5.5976 | 0.76558 | 0.42171 | 6.7849 | 11.96% | 12.73% | 8.6% | 1.1359 | 1.1458 | 1.0941
2010-06-22 | 44 | 41.0103 | 12.1982 | 53.2085 | 4.9249 | 0.76558 | 0.39556 | 6.086 | 11.44% | 12.17% | 8.224% | 1.1292 | 1.1386 | 1.0896
2010-06-22 | 45 | 36.6521 | 11.0551 | 47.7072 | 3.9591 | 0.76558 | 0.35466 | 5.0794 | 10.65% | 11.33% | 7.655% | 1.1192 | 1.1278 | 1.0829
2010-06-22 | 46 | 32.6657 | 9.9091 | 42.5747 | 3.1531 | 0.76558 | 0.31651 | 4.2352 | 9.948% | 10.58% | 7.152% | 1.1105 | 1.1184 | 1.077
2010-06-22 | 47 | 32.2131 | 10.1828 | 42.3958 | 3.1267 | 0.76558 | 0.31518 | 4.2074 | 9.924% | 10.56% | 7.135% | 1.1102 | 1.1181 | 1.0768
2010-06-22 | 48 | 31.529 | 10.7762 | 42.3052 | 3.1133 | 0.76558 | 0.3145 | 4.1934 | 9.912% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-06-23 | 1 | 30.5177 | 10.1401 | 40.6578 | 2.8756 | 0.76558 | 0.30226 | 3.9434 | 9.699% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-06-23 | 2 | 33.0714 | 9.8665 | 42.9379 | 3.2071 | 0.76558 | 0.31921 | 4.2919 | 9.996% | 10.64% | 7.187% | 1.1111 | 1.119 | 1.0774
2010-06-23 | 3 | 33.0206 | 9.3813 | 42.402 | 3.1276 | 0.76558 | 0.31522 | 4.2084 | 9.925% | 10.56% | 7.136% | 1.1102 | 1.1181 | 1.0768
2010-06-23 | 4 | 32.5976 | 9.0144 | 41.612 | 3.0121 | 0.76558 | 0.30935 | 4.087 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-06-23 | 5 | 32.1631 | 8.8339 | 40.997 | 2.9237 | 0.76558 | 0.30478 | 3.9941 | 9.742% | 10.37% | 7.005% | 1.1079 | 1.1156 | 1.0753
2010-06-23 | 6 | 31.3131 | 8.6157 | 39.9289 | 2.7734 | 0.76558 | 0.29684 | 3.8358 | 9.607% | 10.22% | 6.907% | 1.1063 | 1.1139 | 1.0742
2010-06-23 | 7 | 31.1822 | 8.458 | 39.6402 | 2.7334 | 0.76558 | 0.29469 | 3.7937 | 9.57% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-06-23 | 8 | 30.9454 | 8.5195 | 39.4649 | 2.7093 | 0.76558 | 0.29339 | 3.7683 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-06-23 | 9 | 31.0012 | 8.6049 | 39.6061 | 2.7287 | 0.76558 | 0.29444 | 3.7887 | 9.566% | 10.18% | 6.878% | 1.1058 | 1.1133 | 1.0739
2010-06-23 | 10 | 31.2691 | 8.6185 | 39.8876 | 2.7676 | 0.76558 | 0.29653 | 3.8297 | 9.601% | 10.22% | 6.903% | 1.1062 | 1.1138 | 1.0742
2010-06-23 | 11 | 32.2729 | 8.945 | 41.2178 | 2.9553 | 0.76558 | 0.30642 | 4.0273 | 9.771% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2010-06-23 | 12 | 33.0014 | 9.4396 | 42.441 | 3.1333 | 0.76558 | 0.31551 | 4.2144 | 9.93% | 10.57% | 7.14% | 1.1102 | 1.1181 | 1.0769
2010-06-23 | 13 | 34.6397 | 10.5343 | 45.1739 | 3.5499 | 0.76558 | 0.33583 | 4.6513 | 10.3% | 10.96% | 7.403% | 1.1148 | 1.123 | 1.0799
2010-06-23 | 14 | 38.6577 | 12.1265 | 50.7842 | 4.4863 | 0.76558 | 0.37754 | 5.6295 | 11.09% | 11.79% | 7.97% | 1.1247 | 1.1337 | 1.0866
2010-06-23 | 15 | 43.1213 | 14.37 | 57.4913 | 5.7496 | 0.76558 | 0.4274 | 6.9426 | 12.08% | 12.85% | 8.683% | 1.1373 | 1.1474 | 1.0951
2010-06-23 | 16 | 44.1416 | 15.3273 | 59.4689 | 6.152 | 0.76558 | 0.4421 | 7.3597 | 12.38% | 13.17% | 8.898% | 1.1412 | 1.1516 | 1.0977
2010-06-23 | 17 | 44.6896 | 16.341 | 61.0307 | 6.4793 | 0.76558 | 0.45371 | 7.6986 | 12.61% | 13.42% | 9.07% | 1.1444 | 1.155 | 1.0997
2010-06-23 | 18 | 44.5199 | 16.3025 | 60.8224 | 6.4352 | 0.76558 | 0.45216 | 7.6529 | 12.58% | 13.39% | 9.047% | 1.1439 | 1.1546 | 1.0995
2010-06-23 | 19 | 44.7936 | 16.2214 | 61.015 | 6.476 | 0.76558 | 0.45359 | 7.6952 | 12.61% | 13.42% | 9.068% | 1.1443 | 1.155 | 1.0997
2010-06-23 | 20 | 44.2694 | 15.9811 | 60.2506 | 6.3148 | 0.76558 | 0.44791 | 7.5283 | 12.49% | 13.29% | 8.984% | 1.1428 | 1.1533 | 1.0987
2010-06-23 | 21 | 46.8315 | 15.8111 | 62.6426 | 6.8261 | 0.76558 | 0.46569 | 8.0574 | 12.86% | 13.69% | 9.248% | 1.1476 | 1.1586 | 1.1019
2010-06-23 | 22 | 46.8001 | 15.4177 | 62.2179 | 6.7339 | 0.76558 | 0.46254 | 7.962 | 12.8% | 13.62% | 9.201% | 1.1467 | 1.1576 | 1.1013
2010-06-23 | 23 | 45.4974 | 14.8319 | 60.3293 | 6.3313 | 0.76558 | 0.4485 | 7.5454 | 12.51% | 13.31% | 8.992% | 1.1429 | 1.1535 | 1.0988
2010-06-23 | 24 | 43.8436 | 14.625 | 58.4685 | 5.9467 | 0.76558 | 0.43466 | 7.147 | 12.22% | 13.01% | 8.789% | 1.1393 | 1.1495 | 1.0964
2010-06-23 | 25 | 41.4273 | 14.1963 | 55.6236 | 5.3821 | 0.76558 | 0.41351 | 6.5612 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-06-23 | 26 | 39.7866 | 13.5188 | 53.3054 | 4.9428 | 0.76558 | 0.39628 | 6.1047 | 11.45% | 12.19% | 8.234% | 1.1293 | 1.1388 | 1.0897
2010-06-23 | 27 | 39.9709 | 14.1228 | 54.0938 | 5.0901 | 0.76558 | 0.40214 | 6.2578 | 11.57% | 12.31% | 8.318% | 1.1308 | 1.1404 | 1.0907
2010-06-23 | 28 | 39.9184 | 14.6245 | 54.5429 | 5.175 | 0.76558 | 0.40548 | 6.3461 | 11.63% | 12.38% | 8.366% | 1.1317 | 1.1413 | 1.0913
2010-06-23 | 29 | 39.0196 | 14.3122 | 53.3318 | 4.9477 | 0.76558 | 0.39647 | 6.1098 | 11.46% | 12.19% | 8.237% | 1.1294 | 1.1388 | 1.0898
2010-06-23 | 30 | 38.8932 | 14.0137 | 52.9069 | 4.8692 | 0.76558 | 0.39332 | 6.0281 | 11.39% | 12.12% | 8.192% | 1.1286 | 1.138 | 1.0892
2010-06-23 | 31 | 41.515 | 14.2002 | 55.7152 | 5.3999 | 0.76558 | 0.41419 | 6.5796 | 11.81% | 12.57% | 8.491% | 1.1339 | 1.1437 | 1.0928
2010-06-23 | 32 | 42.2489 | 14.3236 | 56.5725 | 5.5673 | 0.76558 | 0.42057 | 6.7534 | 11.94% | 12.7% | 8.583% | 1.1356 | 1.1455 | 1.0939
2010-06-23 | 33 | 43.1752 | 14.6427 | 57.8179 | 5.8151 | 0.76558 | 0.42983 | 7.0105 | 12.13% | 12.9% | 8.718% | 1.138 | 1.1481 | 1.0955
2010-06-23 | 34 | 44.7136 | 14.9499 | 59.6635 | 6.1923 | 0.76558 | 0.44355 | 7.4014 | 12.41% | 13.2% | 8.919% | 1.1416 | 1.1521 | 1.0979
2010-06-23 | 35 | 46.3816 | 15.7732 | 62.1548 | 6.7202 | 0.76558 | 0.46207 | 7.9479 | 12.79% | 13.61% | 9.194% | 1.1466 | 1.1575 | 1.1012
2010-06-23 | 36 | 46.5947 | 16.0262 | 62.6209 | 6.8214 | 0.76558 | 0.46553 | 8.0525 | 12.86% | 13.68% | 9.246% | 1.1476 | 1.1585 | 1.1019
2010-06-23 | 37 | 43.1951 | 15.4854 | 58.6806 | 5.9899 | 0.76558 | 0.43624 | 7.1918 | 12.26% | 13.04% | 8.812% | 1.1397 | 1.15 | 1.0966
2010-06-23 | 38 | 46.3281 | 16.1345 | 62.4625 | 6.7869 | 0.76558 | 0.46435 | 8.0169 | 12.83% | 13.66% | 9.228% | 1.1472 | 1.1582 | 1.1017
2010-06-23 | 39 | 46.1416 | 15.6361 | 61.7777 | 6.6389 | 0.76558 | 0.45926 | 7.8638 | 12.73% | 13.54% | 9.152% | 1.1459 | 1.1567 | 1.1007
2010-06-23 | 40 | 47.4514 | 14.9836 | 62.4351 | 6.781 | 0.76558 | 0.46415 | 8.0107 | 12.83% | 13.65% | 9.225% | 1.1472 | 1.1581 | 1.1016
2010-06-23 | 41 | 47.4212 | 14.6755 | 62.0967 | 6.7077 | 0.76558 | 0.46163 | 7.9349 | 12.78% | 13.6% | 9.188% | 1.1465 | 1.1574 | 1.1012
2010-06-23 | 42 | 47.424 | 14.2798 | 61.7037 | 6.623 | 0.76558 | 0.45871 | 7.8473 | 12.72% | 13.53% | 9.144% | 1.1457 | 1.1565 | 1.1006
2010-06-23 | 43 | 47.1346 | 13.6547 | 60.7893 | 6.4282 | 0.76558 | 0.45191 | 7.6457 | 12.58% | 13.38% | 9.043% | 1.1439 | 1.1545 | 1.0994
2010-06-23 | 44 | 45.1744 | 12.8513 | 58.0257 | 5.857 | 0.76558 | 0.43137 | 7.0539 | 12.16% | 12.93% | 8.741% | 1.1384 | 1.1486 | 1.0958
2010-06-23 | 45 | 41.3706 | 11.3822 | 52.7528 | 4.8409 | 0.76558 | 0.39217 | 5.9986 | 11.37% | 12.1% | 8.176% | 1.1283 | 1.1376 | 1.089
2010-06-23 | 46 | 37.3578 | 10.2528 | 47.6106 | 3.9431 | 0.76558 | 0.35394 | 5.0627 | 10.63% | 11.31% | 7.645% | 1.119 | 1.1276 | 1.0828
2010-06-23 | 47 | 36.7809 | 10.5295 | 47.3104 | 3.8936 | 0.76558 | 0.35171 | 5.0109 | 10.59% | 11.27% | 7.615% | 1.1185 | 1.127 | 1.0824
2010-06-23 | 48 | 35.6124 | 11.1067 | 46.7191 | 3.7969 | 0.76558 | 0.34732 | 4.9097 | 10.51% | 11.18% | 7.556% | 1.1174 | 1.1259 | 1.0817
2010-06-24 | 1 | 32.827 | 10.3248 | 43.1518 | 3.2392 | 0.76558 | 0.3208 | 4.3255 | 10.02% | 10.67% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-06-24 | 2 | 34.443 | 10.1234 | 44.5664 | 3.455 | 0.76558 | 0.33131 | 4.5519 | 10.21% | 10.87% | 7.344% | 1.1138 | 1.1219 | 1.0793
2010-06-24 | 3 | 33.0086 | 9.7851 | 42.7938 | 3.1856 | 0.76558 | 0.31813 | 4.2693 | 9.977% | 10.62% | 7.173% | 1.1108 | 1.1188 | 1.0773
2010-06-24 | 4 | 31.2009 | 9.3433 | 40.5442 | 2.8595 | 0.76558 | 0.30141 | 3.9265 | 9.685% | 10.3% | 6.963% | 1.1072 | 1.1149 | 1.0748
2010-06-24 | 5 | 29.2774 | 8.9884 | 38.2658 | 2.5472 | 0.76558 | 0.28447 | 3.5972 | 9.401% | 10% | 6.759% | 1.1038 | 1.1111 | 1.0725
2010-06-24 | 6 | 28.355 | 8.681 | 37.036 | 2.3861 | 0.76558 | 0.27533 | 3.427 | 9.253% | 9.845% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-06-24 | 7 | 28.4592 | 8.6534 | 37.1126 | 2.3959 | 0.76558 | 0.2759 | 3.4374 | 9.262% | 9.855% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-06-24 | 8 | 28.3904 | 8.5676 | 36.9581 | 2.376 | 0.76558 | 0.27475 | 3.4164 | 9.244% | 9.836% | 6.646% | 1.1019 | 1.1091 | 1.0712
2010-06-24 | 9 | 27.9774 | 8.6642 | 36.6416 | 2.3355 | 0.76558 | 0.2724 | 3.3735 | 9.207% | 9.796% | 6.62% | 1.1014 | 1.1086 | 1.0709
2010-06-24 | 10 | 28.1185 | 8.7575 | 36.876 | 2.3655 | 0.76558 | 0.27414 | 3.4052 | 9.234% | 9.825% | 6.639% | 1.1017 | 1.109 | 1.0711
2010-06-24 | 11 | 28.9298 | 9.0331 | 37.9628 | 2.507 | 0.76558 | 0.28222 | 3.5548 | 9.364% | 9.963% | 6.733% | 1.1033 | 1.1107 | 1.0722
2010-06-24 | 12 | 29.9057 | 9.4023 | 39.308 | 2.6878 | 0.76558 | 0.29222 | 3.7456 | 9.529% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0736
2010-06-24 | 13 | 31.9273 | 10.4949 | 42.4222 | 3.1306 | 0.76558 | 0.31537 | 4.2115 | 9.928% | 10.56% | 7.138% | 1.1102 | 1.1181 | 1.0769
2010-06-24 | 14 | 35.2603 | 12.1493 | 47.4097 | 3.9099 | 0.76558 | 0.35245 | 5.028 | 10.61% | 11.28% | 7.625% | 1.1186 | 1.1272 | 1.0825
2010-06-24 | 15 | 39.7309 | 14.3852 | 54.116 | 5.0943 | 0.76558 | 0.40231 | 6.2622 | 11.57% | 12.31% | 8.32% | 1.1309 | 1.1404 | 1.0908
2010-06-24 | 16 | 41.2114 | 15.1873 | 56.3988 | 5.5332 | 0.76558 | 0.41928 | 6.718 | 11.91% | 12.67% | 8.564% | 1.1352 | 1.1451 | 1.0937
2010-06-24 | 17 | 42.4495 | 16.318 | 58.7675 | 6.0077 | 0.76558 | 0.43689 | 7.2102 | 12.27% | 13.05% | 8.821% | 1.1398 | 1.1501 | 1.0967
2010-06-24 | 18 | 43.2123 | 16.3186 | 59.5309 | 6.1648 | 0.76558 | 0.44256 | 7.3729 | 12.39% | 13.18% | 8.905% | 1.1414 | 1.1518 | 1.0978
2010-06-24 | 19 | 43.714 | 16.1656 | 59.8796 | 6.2372 | 0.76558 | 0.44515 | 7.448 | 12.44% | 13.23% | 8.943% | 1.1421 | 1.1525 | 1.0982
2010-06-24 | 20 | 42.9561 | 15.9362 | 58.8922 | 6.0332 | 0.76558 | 0.43781 | 7.2366 | 12.29% | 13.07% | 8.835% | 1.1401 | 1.1504 | 1.0969
2010-06-24 | 21 | 45.0792 | 15.543 | 60.6222 | 6.3929 | 0.76558 | 0.45067 | 7.6091 | 12.55% | 13.36% | 9.025% | 1.1435 | 1.1541 | 1.0992
2010-06-24 | 22 | 44.2329 | 14.6305 | 58.8634 | 6.0273 | 0.76558 | 0.4376 | 7.2305 | 12.28% | 13.07% | 8.832% | 1.14 | 1.1503 | 1.0969
2010-06-24 | 23 | 42.6061 | 13.9241 | 56.5302 | 5.559 | 0.76558 | 0.42025 | 6.7448 | 11.93% | 12.69% | 8.579% | 1.1355 | 1.1454 | 1.0938
2010-06-24 | 24 | 41.2562 | 13.4154 | 54.6716 | 5.1995 | 0.76558 | 0.40644 | 6.3715 | 11.65% | 12.4% | 8.379% | 1.1319 | 1.1416 | 1.0915
2010-06-24 | 25 | 38.47 | 12.5165 | 50.9865 | 4.5222 | 0.76558 | 0.37904 | 5.6668 | 11.11% | 11.83% | 7.991% | 1.125 | 1.1341 | 1.0869
2010-06-24 | 26 | 36.0987 | 11.6875 | 47.7862 | 3.9723 | 0.76558 | 0.35525 | 5.0931 | 10.66% | 11.34% | 7.663% | 1.1193 | 1.1279 | 1.083
2010-06-24 | 27 | 36.4446 | 11.9562 | 48.4008 | 4.0751 | 0.76558 | 0.35982 | 5.2005 | 10.74% | 11.43% | 7.725% | 1.1204 | 1.1291 | 1.0837
2010-06-24 | 28 | 35.9749 | 12.4834 | 48.4583 | 4.0848 | 0.76558 | 0.36025 | 5.2106 | 10.75% | 11.44% | 7.731% | 1.1205 | 1.1292 | 1.0838
2010-06-24 | 29 | 35.3018 | 12.1443 | 47.4461 | 3.9159 | 0.76558 | 0.35272 | 5.0342 | 10.61% | 11.29% | 7.629% | 1.1187 | 1.1273 | 1.0826
2010-06-24 | 30 | 35.6364 | 11.9183 | 47.5547 | 3.9339 | 0.76558 | 0.35353 | 5.053 | 10.63% | 11.31% | 7.64% | 1.1189 | 1.1275 | 1.0827
2010-06-24 | 31 | 38.4379 | 12.1464 | 50.5844 | 4.4511 | 0.76558 | 0.37605 | 5.5927 | 11.06% | 11.76% | 7.949% | 1.1243 | 1.1333 | 1.0864
2010-06-24 | 32 | 39.099 | 12.2685 | 51.3674 | 4.59 | 0.76558 | 0.38187 | 5.7374 | 11.17% | 11.88% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-06-24 | 33 | 38.8988 | 12.7085 | 51.6073 | 4.6329 | 0.76558 | 0.38365 | 5.7822 | 11.2% | 11.92% | 8.056% | 1.1262 | 1.1353 | 1.0876
2010-06-24 | 34 | 40.1341 | 13.2285 | 53.3626 | 4.9535 | 0.76558 | 0.3967 | 6.1157 | 11.46% | 12.19% | 8.24% | 1.1294 | 1.1389 | 1.0898
2010-06-24 | 35 | 42.3313 | 14.1595 | 56.4908 | 5.5512 | 0.76558 | 0.41996 | 6.7368 | 11.93% | 12.69% | 8.574% | 1.1354 | 1.1453 | 1.0938
2010-06-24 | 36 | 44.7566 | 15.5432 | 60.2998 | 6.3251 | 0.76558 | 0.44828 | 7.5389 | 12.5% | 13.3% | 8.989% | 1.1429 | 1.1534 | 1.0988
2010-06-24 | 37 | 46.2068 | 15.6149 | 61.8217 | 6.6484 | 0.76558 | 0.45959 | 7.8736 | 12.74% | 13.55% | 9.157% | 1.1459 | 1.1568 | 1.1008
2010-06-24 | 38 | 46.4457 | 15.3937 | 61.8394 | 6.6522 | 0.76558 | 0.45972 | 7.8775 | 12.74% | 13.55% | 9.159% | 1.146 | 1.1568 | 1.1008
2010-06-24 | 39 | 45.5121 | 14.7984 | 60.3105 | 6.3273 | 0.76558 | 0.44836 | 7.5413 | 12.5% | 13.3% | 8.99% | 1.1429 | 1.1535 | 1.0988
2010-06-24 | 40 | 44.2011 | 14.3815 | 58.5825 | 5.97 | 0.76558 | 0.43551 | 7.171 | 12.24% | 13.02% | 8.801% | 1.1395 | 1.1497 | 1.0965
2010-06-24 | 41 | 45.0191 | 13.9127 | 58.9319 | 6.0414 | 0.76558 | 0.43811 | 7.2451 | 12.29% | 13.08% | 8.839% | 1.1402 | 1.1505 | 1.097
2010-06-24 | 42 | 44.8869 | 13.6648 | 58.5518 | 5.9637 | 0.76558 | 0.43528 | 7.1645 | 12.24% | 13.02% | 8.798% | 1.1394 | 1.1497 | 1.0965
2010-06-24 | 43 | 42.615 | 13.2362 | 55.8512 | 5.4262 | 0.76558 | 0.4152 | 6.607 | 11.83% | 12.59% | 8.506% | 1.1342 | 1.144 | 1.093
2010-06-24 | 44 | 40.7184 | 12.3922 | 53.1106 | 4.9068 | 0.76558 | 0.39483 | 6.0672 | 11.42% | 12.15% | 8.214% | 1.129 | 1.1384 | 1.0895
2010-06-24 | 45 | 36.8378 | 11.2772 | 48.115 | 4.0271 | 0.76558 | 0.35769 | 5.1504 | 10.7% | 11.39% | 7.696% | 1.1199 | 1.1285 | 1.0834
2010-06-24 | 46 | 33.0575 | 9.9674 | 43.0249 | 3.2201 | 0.76558 | 0.31985 | 4.3056 | 10.01% | 10.65% | 7.195% | 1.1112 | 1.1192 | 1.0775
2010-06-24 | 47 | 32.9433 | 10.3005 | 43.2438 | 3.253 | 0.76558 | 0.32148 | 4.34 | 10.04% | 10.68% | 7.216% | 1.1116 | 1.1196 | 1.0778
2010-06-24 | 48 | 32.166 | 11.0888 | 43.2548 | 3.2546 | 0.76558 | 0.32156 | 4.3418 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-06-25 | 1 | 30.3967 | 10.1763 | 40.573 | 2.8636 | 0.76558 | 0.30162 | 3.9308 | 9.688% | 10.31% | 6.966% | 1.1073 | 1.1149 | 1.0749
2010-06-25 | 2 | 32.4068 | 9.8955 | 42.3023 | 3.1129 | 0.76558 | 0.31448 | 4.1929 | 9.912% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-06-25 | 3 | 31.5877 | 9.5581 | 41.1458 | 2.945 | 0.76558 | 0.30588 | 4.0165 | 9.762% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-06-25 | 4 | 29.9353 | 9.3472 | 39.2826 | 2.6843 | 0.76558 | 0.29203 | 3.7419 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-06-25 | 5 | 28.8847 | 9.0204 | 37.9051 | 2.4994 | 0.76558 | 0.28179 | 3.5467 | 9.357% | 9.956% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-06-25 | 6 | 28.2213 | 8.7412 | 36.9625 | 2.3766 | 0.76558 | 0.27478 | 3.417 | 9.244% | 9.836% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-06-25 | 7 | 28.2229 | 8.6481 | 36.8711 | 2.3649 | 0.76558 | 0.2741 | 3.4045 | 9.234% | 9.825% | 6.639% | 1.1017 | 1.1089 | 1.0711
2010-06-25 | 8 | 27.977 | 8.57 | 36.547 | 2.3235 | 0.76558 | 0.27169 | 3.3607 | 9.196% | 9.784% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-06-25 | 9 | 27.8962 | 8.8161 | 36.7123 | 2.3445 | 0.76558 | 0.27292 | 3.383 | 9.215% | 9.805% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-06-25 | 10 | 28.2686 | 8.8029 | 37.0715 | 2.3906 | 0.76558 | 0.27559 | 3.4318 | 9.257% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-06-25 | 11 | 29.2603 | 9.0453 | 38.3057 | 2.5525 | 0.76558 | 0.28477 | 3.6028 | 9.405% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2010-06-25 | 12 | 30.316 | 9.5314 | 39.8474 | 2.7621 | 0.76558 | 0.29623 | 3.8239 | 9.596% | 10.21% | 6.9% | 1.1061 | 1.1137 | 1.0741
2010-06-25 | 13 | 31.9862 | 10.5046 | 42.4908 | 3.1407 | 0.76558 | 0.31588 | 4.2221 | 9.937% | 10.57% | 7.144% | 1.1103 | 1.1182 | 1.0769
2010-06-25 | 14 | 35.1038 | 11.932 | 47.0358 | 3.8485 | 0.76558 | 0.34967 | 4.9638 | 10.55% | 11.23% | 7.588% | 1.118 | 1.1265 | 1.0821
2010-06-25 | 15 | 39.8353 | 14.3914 | 54.2267 | 5.1152 | 0.76558 | 0.40313 | 6.2839 | 11.59% | 12.33% | 8.332% | 1.1311 | 1.1406 | 1.0909
2010-06-25 | 16 | 41.468 | 15.2916 | 56.7596 | 5.6042 | 0.76558 | 0.42196 | 6.7917 | 11.97% | 12.73% | 8.603% | 1.1359 | 1.1459 | 1.0941
2010-06-25 | 17 | 43.4061 | 16.3104 | 59.7165 | 6.2033 | 0.76558 | 0.44394 | 7.4128 | 12.41% | 13.21% | 8.925% | 1.1417 | 1.1522 | 1.098
2010-06-25 | 18 | 43.7349 | 16.2757 | 60.0106 | 6.2646 | 0.76558 | 0.44613 | 7.4763 | 12.46% | 13.26% | 8.957% | 1.1423 | 1.1528 | 1.0984
2010-06-25 | 19 | 43.8742 | 16.2679 | 60.1421 | 6.2921 | 0.76558 | 0.4471 | 7.5047 | 12.48% | 13.28% | 8.972% | 1.1426 | 1.1531 | 1.0986
2010-06-25 | 20 | 43.557 | 16.1059 | 59.6629 | 6.1922 | 0.76558 | 0.44354 | 7.4013 | 12.41% | 13.2% | 8.919% | 1.1416 | 1.1521 | 1.0979
2010-06-25 | 21 | 45.7103 | 16.1333 | 61.8436 | 6.6531 | 0.76558 | 0.45975 | 7.8784 | 12.74% | 13.55% | 9.16% | 1.146 | 1.1568 | 1.1008
2010-06-25 | 22 | 45.1367 | 15.754 | 60.8907 | 6.4497 | 0.76558 | 0.45267 | 7.6679 | 12.59% | 13.4% | 9.054% | 1.1441 | 1.1547 | 1.0996
2010-06-25 | 23 | 43.5713 | 15.2167 | 58.788 | 6.0119 | 0.76558 | 0.43704 | 7.2145 | 12.27% | 13.06% | 8.824% | 1.1399 | 1.1502 | 1.0968
2010-06-25 | 24 | 41.5729 | 14.753 | 56.3259 | 5.5189 | 0.76558 | 0.41873 | 6.7032 | 11.9% | 12.66% | 8.557% | 1.1351 | 1.145 | 1.0936
2010-06-25 | 25 | 39.103 | 14.3356 | 53.4386 | 4.9676 | 0.76558 | 0.39727 | 6.1304 | 11.47% | 12.21% | 8.248% | 1.1296 | 1.139 | 1.0899
2010-06-25 | 26 | 36.8492 | 13.7008 | 50.5499 | 4.445 | 0.76558 | 0.37579 | 5.5864 | 11.05% | 11.76% | 7.946% | 1.1242 | 1.1333 | 1.0863
2010-06-25 | 27 | 36.4345 | 13.8513 | 50.2858 | 4.3987 | 0.76558 | 0.37383 | 5.5381 | 11.01% | 11.72% | 7.919% | 1.1238 | 1.1327 | 1.086
2010-06-25 | 28 | 36.9659 | 14.0862 | 51.0521 | 4.5338 | 0.76558 | 0.37953 | 5.6789 | 11.12% | 11.84% | 7.998% | 1.1252 | 1.1342 | 1.0869
2010-06-25 | 29 | 36.2047 | 13.9841 | 50.1887 | 4.3817 | 0.76558 | 0.37311 | 5.5204 | 11% | 11.7% | 7.909% | 1.1236 | 1.1325 | 1.0859
2010-06-25 | 30 | 35.9048 | 13.5016 | 49.4064 | 4.2462 | 0.76558 | 0.36729 | 5.3791 | 10.89% | 11.58% | 7.828% | 1.1222 | 1.131 | 1.0849
2010-06-25 | 31 | 38.4754 | 13.6361 | 52.1115 | 4.7239 | 0.76558 | 0.3874 | 5.8769 | 11.28% | 12% | 8.109% | 1.1271 | 1.1364 | 1.0882
2010-06-25 | 32 | 39.195 | 13.8775 | 53.0725 | 4.8997 | 0.76558 | 0.39455 | 6.0599 | 11.42% | 12.15% | 8.21% | 1.1289 | 1.1383 | 1.0894
2010-06-25 | 33 | 39.439 | 14.0767 | 53.5157 | 4.9819 | 0.76558 | 0.39784 | 6.1454 | 11.48% | 12.22% | 8.256% | 1.1297 | 1.1392 | 1.09
2010-06-25 | 34 | 40.9474 | 14.49 | 55.4374 | 5.3461 | 0.76558 | 0.41213 | 6.5238 | 11.77% | 12.52% | 8.461% | 1.1334 | 1.1431 | 1.0924
2010-06-25 | 35 | 41.6369 | 15.2906 | 56.9274 | 5.6374 | 0.76558 | 0.42321 | 6.8262 | 11.99% | 12.76% | 8.622% | 1.1362 | 1.1462 | 1.0943
2010-06-25 | 36 | 44.0781 | 16.1061 | 60.1842 | 6.3008 | 0.76558 | 0.44742 | 7.5138 | 12.48% | 13.28% | 8.977% | 1.1427 | 1.1532 | 1.0986
2010-06-25 | 37 | 45.7727 | 15.905 | 61.6776 | 6.6174 | 0.76558 | 0.45852 | 7.8415 | 12.71% | 13.53% | 9.141% | 1.1457 | 1.1564 | 1.1006
2010-06-25 | 38 | 47.0337 | 15.4091 | 62.4428 | 6.7827 | 0.76558 | 0.46421 | 8.0124 | 12.83% | 13.65% | 9.226% | 1.1472 | 1.1581 | 1.1016
2010-06-25 | 39 | 46.4018 | 14.8604 | 61.2622 | 6.5286 | 0.76558 | 0.45543 | 7.7496 | 12.65% | 13.46% | 9.095% | 1.1448 | 1.1555 | 1.1001
2010-06-25 | 40 | 45.6094 | 14.463 | 60.0724 | 6.2775 | 0.76558 | 0.44659 | 7.4896 | 12.47% | 13.27% | 8.964% | 1.1424 | 1.1529 | 1.0985
2010-06-25 | 41 | 46.1091 | 14.2679 | 60.377 | 6.3413 | 0.76558 | 0.44885 | 7.5557 | 12.51% | 13.32% | 8.998% | 1.143 | 1.1536 | 1.0989
2010-06-25 | 42 | 46.0077 | 13.9315 | 59.9392 | 6.2497 | 0.76558 | 0.4456 | 7.4608 | 12.45% | 13.24% | 8.95% | 1.1422 | 1.1527 | 1.0983
2010-06-25 | 43 | 44.585 | 13.1608 | 57.7458 | 5.8006 | 0.76558 | 0.42929 | 6.9955 | 12.11% | 12.89% | 8.71% | 1.1378 | 1.148 | 1.0954
2010-06-25 | 44 | 42.4141 | 12.3345 | 54.7486 | 5.2141 | 0.76558 | 0.40701 | 6.3867 | 11.67% | 12.41% | 8.388% | 1.1321 | 1.1417 | 1.0916
2010-06-25 | 45 | 38.1168 | 10.9767 | 49.0935 | 4.1926 | 0.76558 | 0.36497 | 5.3231 | 10.84% | 11.54% | 7.796% | 1.1216 | 1.1304 | 1.0846
2010-06-25 | 46 | 34.0957 | 9.8642 | 43.9599 | 3.3616 | 0.76558 | 0.3268 | 4.454 | 10.13% | 10.78% | 7.285% | 1.1127 | 1.1208 | 1.0786
2010-06-25 | 47 | 34.0945 | 10.2704 | 44.365 | 3.4239 | 0.76558 | 0.32981 | 4.5192 | 10.19% | 10.84% | 7.324% | 1.1134 | 1.1216 | 1.079
2010-06-25 | 48 | 33.5477 | 10.9556 | 44.5033 | 3.4452 | 0.76558 | 0.33084 | 4.5417 | 10.21% | 10.86% | 7.338% | 1.1137 | 1.1218 | 1.0792
2010-06-26 | 1 | 32.2096 | 10.1874 | 42.397 | 3.1268 | 0.76558 | 0.31518 | 4.2076 | 9.924% | 10.56% | 7.136% | 1.1102 | 1.1181 | 1.0768
2010-06-26 | 2 | 34.0757 | 10.07 | 44.1457 | 3.3901 | 0.76558 | 0.32818 | 4.4839 | 10.16% | 10.81% | 7.303% | 1.1131 | 1.1212 | 1.0788
2010-06-26 | 3 | 32.7537 | 9.5457 | 42.2994 | 3.1125 | 0.76558 | 0.31446 | 4.1925 | 9.911% | 10.55% | 7.126% | 1.11 | 1.1179 | 1.0767
2010-06-26 | 4 | 31.847 | 9.2087 | 41.0557 | 2.9321 | 0.76558 | 0.30521 | 4.0029 | 9.75% | 10.37% | 7.01% | 1.108 | 1.1157 | 1.0754
2010-06-26 | 5 | 31.3179 | 9.0503 | 40.3682 | 2.8347 | 0.76558 | 0.3001 | 3.9004 | 9.662% | 10.28% | 6.947% | 1.107 | 1.1146 | 1.0747
2010-06-26 | 6 | 30.567 | 8.8724 | 39.4394 | 2.7058 | 0.76558 | 0.2932 | 3.7646 | 9.545% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-06-26 | 7 | 30.3242 | 8.7194 | 39.0436 | 2.6518 | 0.76558 | 0.29025 | 3.7076 | 9.496% | 10.1% | 6.828% | 1.1049 | 1.1124 | 1.0733
2010-06-26 | 8 | 30.2953 | 8.6826 | 38.9779 | 2.6428 | 0.76558 | 0.28977 | 3.6982 | 9.488% | 10.1% | 6.822% | 1.1048 | 1.1123 | 1.0732
2010-06-26 | 9 | 30.362 | 8.709 | 39.071 | 2.6555 | 0.76558 | 0.29046 | 3.7115 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-06-26 | 10 | 30.4786 | 8.6684 | 39.147 | 2.6658 | 0.76558 | 0.29102 | 3.7224 | 9.509% | 10.12% | 6.837% | 1.1051 | 1.1126 | 1.0734
2010-06-26 | 11 | 30.8391 | 8.9932 | 39.8323 | 2.76 | 0.76558 | 0.29612 | 3.8217 | 9.594% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-06-26 | 12 | 31.4689 | 9.2984 | 40.7674 | 2.8911 | 0.76558 | 0.30307 | 3.9597 | 9.713% | 10.33% | 6.984% | 1.1076 | 1.1153 | 1.0751
2010-06-26 | 13 | 33.5507 | 10.3981 | 43.9488 | 3.3599 | 0.76558 | 0.32672 | 4.4522 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-06-26 | 14 | 36.7951 | 11.8083 | 48.6033 | 4.1093 | 0.76558 | 0.36132 | 5.2362 | 10.77% | 11.46% | 7.746% | 1.1207 | 1.1295 | 1.084
2010-06-26 | 15 | 40.8892 | 14.121 | 55.0102 | 5.2641 | 0.76558 | 0.40895 | 6.4386 | 11.7% | 12.45% | 8.415% | 1.1326 | 1.1422 | 1.0919
2010-06-26 | 16 | 42.3682 | 15.2426 | 57.6108 | 5.7735 | 0.76558 | 0.42829 | 6.9674 | 12.09% | 12.87% | 8.696% | 1.1376 | 1.1477 | 1.0952
2010-06-26 | 17 | 43.8314 | 16.2382 | 60.0696 | 6.2769 | 0.76558 | 0.44656 | 7.489 | 12.47% | 13.27% | 8.964% | 1.1424 | 1.1529 | 1.0985
2010-06-26 | 18 | 44.9375 | 16.3351 | 61.2727 | 6.5308 | 0.76558 | 0.45551 | 7.7519 | 12.65% | 13.46% | 9.096% | 1.1448 | 1.1556 | 1.1001
2010-06-26 | 19 | 45.4114 | 16.2745 | 61.6859 | 6.6192 | 0.76558 | 0.45858 | 7.8434 | 12.72% | 13.53% | 9.142% | 1.1457 | 1.1565 | 1.1006
2010-06-26 | 20 | 45.0673 | 16.3574 | 61.4247 | 6.5633 | 0.76558 | 0.45664 | 7.7855 | 12.67% | 13.49% | 9.113% | 1.1451 | 1.1559 | 1.1003
2010-06-26 | 21 | 47.1773 | 16.2908 | 63.4681 | 7.0072 | 0.76558 | 0.47183 | 8.2446 | 12.99% | 13.82% | 9.34% | 1.1493 | 1.1604 | 1.103
2010-06-26 | 22 | 46.7634 | 16.2613 | 63.0247 | 6.9096 | 0.76558 | 0.46853 | 8.1438 | 12.92% | 13.75% | 9.291% | 1.1484 | 1.1594 | 1.1024
2010-06-26 | 23 | 45.1244 | 15.5481 | 60.6725 | 6.4035 | 0.76558 | 0.45105 | 7.6201 | 12.56% | 13.36% | 9.03% | 1.1436 | 1.1542 | 1.0993
2010-06-26 | 24 | 43.9894 | 14.9907 | 58.9801 | 6.0513 | 0.76558 | 0.43847 | 7.2553 | 12.3% | 13.09% | 8.845% | 1.1403 | 1.1506 | 1.097
2010-06-26 | 25 | 40.8718 | 14.631 | 55.5028 | 5.3588 | 0.76558 | 0.41261 | 6.537 | 11.78% | 12.53% | 8.468% | 1.1335 | 1.1433 | 1.0925
2010-06-26 | 26 | 38.4467 | 13.9359 | 52.3826 | 4.7732 | 0.76558 | 0.38942 | 5.9282 | 11.32% | 12.04% | 8.137% | 1.1276 | 1.1369 | 1.0886
2010-06-26 | 27 | 38.4188 | 14.4908 | 52.9097 | 4.8697 | 0.76558 | 0.39334 | 6.0286 | 11.39% | 12.12% | 8.192% | 1.1286 | 1.138 | 1.0892
2010-06-26 | 28 | 38.4526 | 14.6218 | 53.0744 | 4.9001 | 0.76558 | 0.39456 | 6.0602 | 11.42% | 12.15% | 8.21% | 1.1289 | 1.1383 | 1.0894
2010-06-26 | 29 | 38.0401 | 14.2958 | 52.3358 | 4.7647 | 0.76558 | 0.38907 | 5.9193 | 11.31% | 12.03% | 8.132% | 1.1275 | 1.1368 | 1.0885
2010-06-26 | 30 | 37.4843 | 13.8717 | 51.3559 | 4.5879 | 0.76558 | 0.38179 | 5.7353 | 11.17% | 11.88% | 8.03% | 1.1257 | 1.1348 | 1.0873
2010-06-26 | 31 | 40.2431 | 13.9703 | 54.2134 | 5.1127 | 0.76558 | 0.40303 | 6.2813 | 11.59% | 12.33% | 8.33% | 1.131 | 1.1406 | 1.0909
2010-06-26 | 32 | 41.3782 | 13.8642 | 55.2424 | 5.3086 | 0.76558 | 0.41068 | 6.4848 | 11.74% | 12.49% | 8.44% | 1.133 | 1.1427 | 1.0922
2010-06-26 | 33 | 41.7198 | 13.9096 | 55.6295 | 5.3833 | 0.76558 | 0.41356 | 6.5624 | 11.8% | 12.55% | 8.482% | 1.1337 | 1.1435 | 1.0927
2010-06-26 | 34 | 42.8967 | 14.1145 | 57.0112 | 5.654 | 0.76558 | 0.42383 | 6.8434 | 12% | 12.77% | 8.631% | 1.1364 | 1.1464 | 1.0945
2010-06-26 | 35 | 43.8863 | 14.6282 | 58.5146 | 5.9561 | 0.76558 | 0.435 | 7.1567 | 12.23% | 13.01% | 8.794% | 1.1393 | 1.1496 | 1.0964
2010-06-26 | 36 | 46.845 | 15.2818 | 62.1269 | 6.7142 | 0.76558 | 0.46186 | 7.9416 | 12.78% | 13.6% | 9.191% | 1.1466 | 1.1574 | 1.1012
2010-06-26 | 37 | 47.4055 | 15.0921 | 62.4976 | 6.7946 | 0.76558 | 0.46461 | 8.0247 | 12.84% | 13.66% | 9.232% | 1.1473 | 1.1582 | 1.1017
2010-06-26 | 38 | 46.1959 | 15.0122 | 61.2081 | 6.5171 | 0.76558 | 0.45503 | 7.7377 | 12.64% | 13.45% | 9.089% | 1.1447 | 1.1554 | 1.1
2010-06-26 | 39 | 43.9538 | 14.6998 | 58.6536 | 5.9844 | 0.76558 | 0.43604 | 7.1861 | 12.25% | 13.04% | 8.809% | 1.1396 | 1.1499 | 1.0966
2010-06-26 | 40 | 42.025 | 14.2332 | 56.2582 | 5.5056 | 0.76558 | 0.41823 | 6.6894 | 11.89% | 12.65% | 8.549% | 1.135 | 1.1448 | 1.0935
2010-06-26 | 41 | 44.0226 | 13.9488 | 57.9715 | 5.8461 | 0.76558 | 0.43097 | 7.0426 | 12.15% | 12.93% | 8.735% | 1.1383 | 1.1484 | 1.0957
2010-06-26 | 42 | 45.3247 | 13.5167 | 58.8414 | 6.0228 | 0.76558 | 0.43743 | 7.2258 | 12.28% | 13.07% | 8.829% | 1.14 | 1.1503 | 1.0968
2010-06-26 | 43 | 44.1178 | 13.0494 | 57.1672 | 5.685 | 0.76558 | 0.42499 | 6.8755 | 12.03% | 12.8% | 8.647% | 1.1367 | 1.1467 | 1.0947
2010-06-26 | 44 | 43.0373 | 12.3359 | 55.3731 | 5.3338 | 0.76558 | 0.41165 | 6.511 | 11.76% | 12.51% | 8.454% | 1.1333 | 1.143 | 1.0924
2010-06-26 | 45 | 40.0464 | 11.2744 | 51.3208 | 4.5816 | 0.76558 | 0.38152 | 5.7287 | 11.16% | 11.88% | 8.026% | 1.1257 | 1.1348 | 1.0873
2010-06-26 | 46 | 37.1161 | 10.177 | 47.293 | 3.8907 | 0.76558 | 0.35158 | 5.0079 | 10.59% | 11.27% | 7.614% | 1.1184 | 1.127 | 1.0824
2010-06-26 | 47 | 36.985 | 10.6173 | 47.6023 | 3.9418 | 0.76558 | 0.35388 | 5.0612 | 10.63% | 11.31% | 7.645% | 1.119 | 1.1276 | 1.0828
2010-06-26 | 48 | 36.3209 | 11.1183 | 47.4392 | 3.9148 | 0.76558 | 0.35267 | 5.033 | 10.61% | 11.29% | 7.628% | 1.1187 | 1.1272 | 1.0826
2010-06-27 | 1 | 34.8963 | 10.2958 | 45.1921 | 3.5527 | 0.76558 | 0.33596 | 4.6542 | 10.3% | 10.96% | 7.405% | 1.1148 | 1.1231 | 1.08
2010-06-27 | 2 | 36.9924 | 10.1494 | 47.1417 | 3.8659 | 0.76558 | 0.35046 | 4.9819 | 10.57% | 11.24% | 7.598% | 1.1182 | 1.1267 | 1.0822
2010-06-27 | 3 | 35.8511 | 9.699 | 45.5502 | 3.6092 | 0.76558 | 0.33863 | 4.7134 | 10.35% | 11.01% | 7.44% | 1.1154 | 1.1237 | 1.0804
2010-06-27 | 4 | 34.2698 | 9.3804 | 43.6502 | 3.3144 | 0.76558 | 0.3245 | 4.4045 | 10.09% | 10.74% | 7.255% | 1.1122 | 1.1203 | 1.0782
2010-06-27 | 5 | 33.5168 | 9.0918 | 42.6086 | 3.1581 | 0.76558 | 0.31676 | 4.2405 | 9.952% | 10.59% | 7.156% | 1.1105 | 1.1184 | 1.0771
2010-06-27 | 6 | 33.211 | 8.7473 | 41.9582 | 3.0624 | 0.76558 | 0.31192 | 4.1399 | 9.867% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-06-27 | 7 | 32.6726 | 8.6653 | 41.3378 | 2.9726 | 0.76558 | 0.30731 | 4.0454 | 9.786% | 10.41% | 7.036% | 1.1085 | 1.1162 | 1.0757
2010-06-27 | 8 | 31.9655 | 8.5341 | 40.4997 | 2.8532 | 0.76558 | 0.30108 | 3.9199 | 9.679% | 10.3% | 6.959% | 1.1072 | 1.1148 | 1.0748
2010-06-27 | 9 | 31.6748 | 8.5814 | 40.2562 | 2.819 | 0.76558 | 0.29927 | 3.8839 | 9.648% | 10.27% | 6.937% | 1.1068 | 1.1144 | 1.0745
2010-06-27 | 10 | 31.8317 | 8.6728 | 40.5044 | 2.8539 | 0.76558 | 0.30111 | 3.9206 | 9.679% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-06-27 | 11 | 32.5359 | 8.7671 | 41.303 | 2.9676 | 0.76558 | 0.30705 | 4.0402 | 9.782% | 10.41% | 7.033% | 1.1084 | 1.1162 | 1.0757
2010-06-27 | 12 | 32.6184 | 8.9395 | 41.5579 | 3.0043 | 0.76558 | 0.30895 | 4.0788 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-06-27 | 13 | 34.1715 | 9.4327 | 43.6042 | 3.3074 | 0.76558 | 0.32416 | 4.3972 | 10.08% | 10.73% | 7.251% | 1.1122 | 1.1202 | 1.0782
2010-06-27 | 14 | 36.6705 | 9.9973 | 46.6678 | 3.7885 | 0.76558 | 0.34693 | 4.901 | 10.5% | 11.17% | 7.551% | 1.1173 | 1.1258 | 1.0817
2010-06-27 | 15 | 38.0629 | 10.3764 | 48.4393 | 4.0816 | 0.76558 | 0.3601 | 5.2073 | 10.75% | 11.44% | 7.729% | 1.1204 | 1.1292 | 1.0838
2010-06-27 | 16 | 37.4584 | 10.9334 | 48.3918 | 4.0736 | 0.76558 | 0.35975 | 5.1989 | 10.74% | 11.43% | 7.725% | 1.1204 | 1.1291 | 1.0837
2010-06-27 | 17 | 38.4181 | 12.1235 | 50.5416 | 4.4436 | 0.76558 | 0.37573 | 5.5849 | 11.05% | 11.76% | 7.945% | 1.1242 | 1.1332 | 1.0863
2010-06-27 | 18 | 39.6375 | 13.4782 | 53.1157 | 4.9077 | 0.76558 | 0.39487 | 6.0682 | 11.42% | 12.16% | 8.214% | 1.129 | 1.1384 | 1.0895
2010-06-27 | 19 | 42.652 | 14.5293 | 57.1813 | 5.6878 | 0.76558 | 0.42509 | 6.8784 | 12.03% | 12.8% | 8.649% | 1.1367 | 1.1468 | 1.0947
2010-06-27 | 20 | 43.7424 | 15.2034 | 58.9458 | 6.0442 | 0.76558 | 0.43821 | 7.248 | 12.3% | 13.08% | 8.841% | 1.1402 | 1.1505 | 1.097
2010-06-27 | 21 | 47.0889 | 15.5684 | 62.6573 | 6.8293 | 0.76558 | 0.4658 | 8.0607 | 12.86% | 13.69% | 9.25% | 1.1476 | 1.1586 | 1.1019
2010-06-27 | 22 | 47.1048 | 15.6883 | 62.7931 | 6.859 | 0.76558 | 0.46681 | 8.0913 | 12.89% | 13.71% | 9.265% | 1.1479 | 1.1589 | 1.1021
2010-06-27 | 23 | 46.1563 | 15.2371 | 61.3934 | 6.5566 | 0.76558 | 0.45641 | 7.7786 | 12.67% | 13.48% | 9.11% | 1.1451 | 1.1558 | 1.1002
2010-06-27 | 24 | 44.752 | 14.9634 | 59.7154 | 6.2031 | 0.76558 | 0.44393 | 7.4126 | 12.41% | 13.21% | 8.925% | 1.1417 | 1.1522 | 1.098
2010-06-27 | 25 | 41.7243 | 14.4173 | 56.1415 | 5.4828 | 0.76558 | 0.41736 | 6.6657 | 11.87% | 12.63% | 8.537% | 1.1347 | 1.1446 | 1.0933
2010-06-27 | 26 | 39.7078 | 13.7901 | 53.4979 | 4.9786 | 0.76558 | 0.39771 | 6.1419 | 11.48% | 12.22% | 8.255% | 1.1297 | 1.1392 | 1.09
2010-06-27 | 27 | 40.1325 | 14.165 | 54.2974 | 5.1285 | 0.76558 | 0.40365 | 6.2978 | 11.6% | 12.34% | 8.339% | 1.1312 | 1.1408 | 1.091
2010-06-27 | 28 | 39.6429 | 14.246 | 53.8889 | 5.0517 | 0.76558 | 0.40062 | 6.2178 | 11.54% | 12.28% | 8.296% | 1.1304 | 1.1399 | 1.0905
2010-06-27 | 29 | 39.332 | 13.7916 | 53.1235 | 4.9092 | 0.76558 | 0.39493 | 6.0697 | 11.43% | 12.16% | 8.215% | 1.129 | 1.1384 | 1.0895
2010-06-27 | 30 | 38.6535 | 13.503 | 52.1565 | 4.7321 | 0.76558 | 0.38774 | 5.8854 | 11.28% | 12.01% | 8.113% | 1.1272 | 1.1364 | 1.0883
2010-06-27 | 31 | 40.5947 | 13.5719 | 54.1665 | 5.1038 | 0.76558 | 0.40268 | 6.2721 | 11.58% | 12.32% | 8.326% | 1.131 | 1.1405 | 1.0908
2010-06-27 | 32 | 41.2122 | 13.456 | 54.6682 | 5.1988 | 0.76558 | 0.40641 | 6.3708 | 11.65% | 12.4% | 8.379% | 1.1319 | 1.1415 | 1.0915
2010-06-27 | 33 | 41.4323 | 13.3347 | 54.767 | 5.2176 | 0.76558 | 0.40714 | 6.3903 | 11.67% | 12.42% | 8.389% | 1.1321 | 1.1417 | 1.0916
2010-06-27 | 34 | 43.602 | 13.2544 | 56.8564 | 5.6233 | 0.76558 | 0.42268 | 6.8116 | 11.98% | 12.75% | 8.614% | 1.1361 | 1.1461 | 1.0943
2010-06-27 | 35 | 45.7027 | 14.0991 | 59.8018 | 6.221 | 0.76558 | 0.44457 | 7.4312 | 12.43% | 13.22% | 8.935% | 1.1419 | 1.1524 | 1.0981
2010-06-27 | 36 | 47.46 | 15.1523 | 62.6123 | 6.8195 | 0.76558 | 0.46547 | 8.0506 | 12.86% | 13.68% | 9.245% | 1.1475 | 1.1585 | 1.1019
2010-06-27 | 37 | 47.4589 | 14.9797 | 62.4386 | 6.7817 | 0.76558 | 0.46418 | 8.0115 | 12.83% | 13.65% | 9.225% | 1.1472 | 1.1581 | 1.1016
2010-06-27 | 38 | 47.4009 | 14.7326 | 62.1335 | 6.7156 | 0.76558 | 0.46191 | 7.9431 | 12.78% | 13.6% | 9.192% | 1.1466 | 1.1574 | 1.1012
2010-06-27 | 39 | 47.4698 | 13.981 | 61.4508 | 6.5689 | 0.76558 | 0.45683 | 7.7913 | 12.68% | 13.49% | 9.116% | 1.1452 | 1.1559 | 1.1003
2010-06-27 | 40 | 46.7182 | 13.2518 | 59.97 | 6.2561 | 0.76558 | 0.44582 | 7.4675 | 12.45% | 13.25% | 8.953% | 1.1422 | 1.1527 | 1.0983
2010-06-27 | 41 | 47.2755 | 13.0002 | 60.2757 | 6.32 | 0.76558 | 0.4481 | 7.5337 | 12.5% | 13.3% | 8.987% | 1.1428 | 1.1534 | 1.0987
2010-06-27 | 42 | 46.843 | 12.7086 | 59.5516 | 6.1691 | 0.76558 | 0.44271 | 7.3774 | 12.39% | 13.18% | 8.907% | 1.1414 | 1.1518 | 1.0978
2010-06-27 | 43 | 45.576 | 12.2492 | 57.8252 | 5.8166 | 0.76558 | 0.42988 | 7.012 | 12.13% | 12.9% | 8.719% | 1.138 | 1.1481 | 1.0955
2010-06-27 | 44 | 44.1539 | 11.854 | 56.0079 | 5.4567 | 0.76558 | 0.41637 | 6.6387 | 11.85% | 12.61% | 8.522% | 1.1345 | 1.1443 | 1.0932
2010-06-27 | 45 | 40.8374 | 11.0782 | 51.9156 | 4.6885 | 0.76558 | 0.38595 | 5.84 | 11.25% | 11.97% | 8.088% | 1.1267 | 1.136 | 1.088
2010-06-27 | 46 | 38.692 | 10.4009 | 49.0929 | 4.1925 | 0.76558 | 0.36496 | 5.323 | 10.84% | 11.54% | 7.796% | 1.1216 | 1.1304 | 1.0846
2010-06-27 | 47 | 39.1914 | 10.8653 | 50.0567 | 4.3587 | 0.76558 | 0.37213 | 5.4964 | 10.98% | 11.68% | 7.895% | 1.1233 | 1.1323 | 1.0857
2010-06-27 | 48 | 38.0268 | 11.4337 | 49.4604 | 4.2555 | 0.76558 | 0.36769 | 5.3888 | 10.9% | 11.59% | 7.834% | 1.1223 | 1.1311 | 1.085
2010-06-28 | 1 | 36.1301 | 10.5444 | 46.6745 | 3.7896 | 0.76558 | 0.34698 | 4.9022 | 10.5% | 11.18% | 7.552% | 1.1174 | 1.1258 | 1.0817
2010-06-28 | 2 | 38.1828 | 10.3877 | 48.5705 | 4.1037 | 0.76558 | 0.36108 | 5.2304 | 10.77% | 11.46% | 7.743% | 1.1207 | 1.1294 | 1.0839
2010-06-28 | 3 | 37.1322 | 9.9661 | 47.0983 | 3.8587 | 0.76558 | 0.35013 | 4.9745 | 10.56% | 11.24% | 7.594% | 1.1181 | 1.1266 | 1.0822
2010-06-28 | 4 | 35.0311 | 9.4788 | 44.5099 | 3.4463 | 0.76558 | 0.33089 | 4.5427 | 10.21% | 10.86% | 7.338% | 1.1137 | 1.1218 | 1.0792
2010-06-28 | 5 | 34.1381 | 9.0309 | 43.169 | 3.2417 | 0.76558 | 0.32092 | 4.3282 | 10.03% | 10.67% | 7.209% | 1.1114 | 1.1194 | 1.0777
2010-06-28 | 6 | 34.1218 | 8.8456 | 42.9675 | 3.2115 | 0.76558 | 0.31943 | 4.2965 | 10% | 10.64% | 7.19% | 1.1111 | 1.1191 | 1.0775
2010-06-28 | 7 | 34.0128 | 8.6201 | 42.633 | 3.1617 | 0.76558 | 0.31694 | 4.2443 | 9.955% | 10.59% | 7.158% | 1.1106 | 1.1185 | 1.0771
2010-06-28 | 8 | 33.7611 | 8.6287 | 42.3898 | 3.1258 | 0.76558 | 0.31513 | 4.2065 | 9.923% | 10.56% | 7.135% | 1.1102 | 1.118 | 1.0768
2010-06-28 | 9 | 33.4013 | 8.6127 | 42.014 | 3.0706 | 0.76558 | 0.31234 | 4.1485 | 9.874% | 10.51% | 7.099% | 1.1096 | 1.1174 | 1.0764
2010-06-28 | 10 | 33.6971 | 8.6699 | 42.367 | 3.1224 | 0.76558 | 0.31496 | 4.203 | 9.92% | 10.56% | 7.133% | 1.1101 | 1.118 | 1.0768
2010-06-28 | 11 | 33.9658 | 8.7996 | 42.7654 | 3.1814 | 0.76558 | 0.31792 | 4.2649 | 9.973% | 10.61% | 7.17% | 1.1108 | 1.1187 | 1.0772
2010-06-28 | 12 | 34.5337 | 8.975 | 43.5087 | 3.293 | 0.76558 | 0.32345 | 4.382 | 10.07% | 10.72% | 7.241% | 1.112 | 1.12 | 1.0781
2010-06-28 | 13 | 35.3191 | 9.2965 | 44.6156 | 3.4626 | 0.76558 | 0.33168 | 4.5599 | 10.22% | 10.87% | 7.348% | 1.1138 | 1.122 | 1.0793
2010-06-28 | 14 | 36.4173 | 9.5768 | 45.9941 | 3.6799 | 0.76558 | 0.34193 | 4.7874 | 10.41% | 11.07% | 7.484% | 1.1162 | 1.1245 | 1.0809
2010-06-28 | 15 | 37.417 | 9.7897 | 47.2067 | 3.8765 | 0.76558 | 0.35094 | 4.993 | 10.58% | 11.25% | 7.605% | 1.1183 | 1.1268 | 1.0823
2010-06-28 | 16 | 37.0858 | 9.7845 | 46.8703 | 3.8215 | 0.76558 | 0.34844 | 4.9355 | 10.53% | 11.2% | 7.571% | 1.1177 | 1.1262 | 1.0819
2010-06-28 | 17 | 37.5441 | 11.0053 | 48.5494 | 4.1002 | 0.76558 | 0.36092 | 5.2267 | 10.77% | 11.45% | 7.741% | 1.1206 | 1.1294 | 1.0839
2010-06-28 | 18 | 38.6452 | 12.2117 | 50.8569 | 4.4992 | 0.76558 | 0.37808 | 5.6428 | 11.1% | 11.81% | 7.978% | 1.1248 | 1.1339 | 1.0867
2010-06-28 | 19 | 41.9217 | 13.4101 | 55.3318 | 5.3258 | 0.76558 | 0.41134 | 6.5027 | 11.75% | 12.5% | 8.45% | 1.1332 | 1.1429 | 1.0923
2010-06-28 | 20 | 43.5739 | 14.1112 | 57.6851 | 5.7884 | 0.76558 | 0.42884 | 6.9829 | 12.11% | 12.88% | 8.704% | 1.1377 | 1.1478 | 1.0953
2010-06-28 | 21 | 47.0106 | 14.7633 | 61.7739 | 6.6381 | 0.76558 | 0.45923 | 7.8629 | 12.73% | 13.54% | 9.152% | 1.1459 | 1.1566 | 1.1007
2010-06-28 | 22 | 46.9853 | 14.9053 | 61.8905 | 6.6632 | 0.76558 | 0.4601 | 7.8889 | 12.75% | 13.56% | 9.165% | 1.1461 | 1.1569 | 1.1009
2010-06-28 | 23 | 45.8963 | 14.5106 | 60.4068 | 6.3476 | 0.76558 | 0.44907 | 7.5622 | 12.52% | 13.32% | 9.001% | 1.1431 | 1.1537 | 1.0989
2010-06-28 | 24 | 44.5093 | 14.2571 | 58.7664 | 6.0075 | 0.76558 | 0.43688 | 7.2099 | 12.27% | 13.05% | 8.821% | 1.1398 | 1.1501 | 1.0967
2010-06-28 | 25 | 41.0931 | 13.9448 | 55.0379 | 5.2694 | 0.76558 | 0.40916 | 6.4441 | 11.71% | 12.46% | 8.418% | 1.1326 | 1.1423 | 1.0919
2010-06-28 | 26 | 37.9574 | 13.2874 | 51.2448 | 4.5681 | 0.76558 | 0.38096 | 5.7146 | 11.15% | 11.87% | 8.018% | 1.1255 | 1.1346 | 1.0872
2010-06-28 | 27 | 37.9454 | 13.8157 | 51.7611 | 4.6606 | 0.76558 | 0.3848 | 5.811 | 11.23% | 11.95% | 8.072% | 1.1265 | 1.1357 | 1.0878
2010-06-28 | 28 | 37.8189 | 13.8942 | 51.7131 | 4.652 | 0.76558 | 0.38444 | 5.802 | 11.22% | 11.94% | 8.067% | 1.1264 | 1.1356 | 1.0877
2010-06-28 | 29 | 37.1885 | 13.454 | 50.6425 | 4.4613 | 0.76558 | 0.37648 | 5.6034 | 11.06% | 11.77% | 7.955% | 1.1244 | 1.1334 | 1.0864
2010-06-28 | 30 | 36.3528 | 13.2835 | 49.6363 | 4.2858 | 0.76558 | 0.369 | 5.4204 | 10.92% | 11.62% | 7.852% | 1.1226 | 1.1315 | 1.0852
2010-06-28 | 31 | 39.2877 | 13.3279 | 52.6156 | 4.8158 | 0.76558 | 0.39115 | 5.9725 | 11.35% | 12.08% | 8.161% | 1.128 | 1.1374 | 1.0889
2010-06-28 | 32 | 40.8312 | 13.1398 | 53.971 | 5.0671 | 0.76558 | 0.40123 | 6.2339 | 11.55% | 12.29% | 8.305% | 1.1306 | 1.1401 | 1.0906
2010-06-28 | 33 | 41.6961 | 13.4631 | 55.1592 | 5.2926 | 0.76558 | 0.41006 | 6.4683 | 11.73% | 12.48% | 8.431% | 1.1328 | 1.1426 | 1.0921
2010-06-28 | 34 | 43.95 | 13.8971 | 57.8471 | 5.821 | 0.76558 | 0.43004 | 7.0166 | 12.13% | 12.91% | 8.721% | 1.138 | 1.1482 | 1.0955
2010-06-28 | 35 | 45.6007 | 14.6335 | 60.2342 | 6.3113 | 0.76558 | 0.44779 | 7.5247 | 12.49% | 13.29% | 8.982% | 1.1428 | 1.1533 | 1.0987
2010-06-28 | 36 | 47.4109 | 15.7404 | 63.1514 | 6.9375 | 0.76558 | 0.46947 | 8.1725 | 12.94% | 13.77% | 9.305% | 1.1486 | 1.1597 | 1.1026
2010-06-28 | 37 | 47.4573 | 15.48 | 62.9373 | 6.8905 | 0.76558 | 0.46788 | 8.124 | 12.91% | 13.73% | 9.281% | 1.1482 | 1.1592 | 1.1023
2010-06-28 | 38 | 47.3145 | 15.194 | 62.5085 | 6.7969 | 0.76558 | 0.4647 | 8.0272 | 12.84% | 13.66% | 9.233% | 1.1473 | 1.1583 | 1.1017
2010-06-28 | 39 | 46.4738 | 14.6502 | 61.124 | 6.4992 | 0.76558 | 0.4544 | 7.7192 | 12.63% | 13.44% | 9.08% | 1.1445 | 1.1552 | 1.0999
2010-06-28 | 40 | 45.3612 | 14.1989 | 59.5601 | 6.1709 | 0.76558 | 0.44278 | 7.3792 | 12.39% | 13.18% | 8.908% | 1.1414 | 1.1518 | 1.0978
2010-06-28 | 41 | 46.4664 | 14.0083 | 60.4747 | 6.3618 | 0.76558 | 0.44958 | 7.577 | 12.53% | 13.33% | 9.008% | 1.1432 | 1.1538 | 1.099
2010-06-28 | 42 | 46.6812 | 13.4838 | 60.1651 | 6.2969 | 0.76558 | 0.44727 | 7.5097 | 12.48% | 13.28% | 8.974% | 1.1426 | 1.1531 | 1.0986
2010-06-28 | 43 | 44.5047 | 12.7802 | 57.2849 | 5.7084 | 0.76558 | 0.42586 | 6.8998 | 12.04% | 12.82% | 8.66% | 1.1369 | 1.147 | 1.0948
2010-06-28 | 44 | 42.2615 | 11.8843 | 54.1458 | 5.0999 | 0.76558 | 0.40253 | 6.268 | 11.58% | 12.32% | 8.323% | 1.1309 | 1.1405 | 1.0908
2010-06-28 | 45 | 38.1271 | 10.7187 | 48.8459 | 4.1504 | 0.76558 | 0.36313 | 5.2791 | 10.81% | 11.5% | 7.771% | 1.1212 | 1.1299 | 1.0843
2010-06-28 | 46 | 34.836 | 9.6165 | 44.4525 | 3.4374 | 0.76558 | 0.33047 | 4.5334 | 10.2% | 10.85% | 7.333% | 1.1136 | 1.1217 | 1.0791
2010-06-28 | 47 | 34.334 | 10.0437 | 44.3776 | 3.4258 | 0.76558 | 0.32991 | 4.5213 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-06-28 | 48 | 33.5595 | 10.8056 | 44.3652 | 3.4239 | 0.76558 | 0.32982 | 4.5193 | 10.19% | 10.84% | 7.324% | 1.1134 | 1.1216 | 1.079
2010-06-29 | 1 | 31.7625 | 9.9953 | 41.7578 | 3.0333 | 0.76558 | 0.31043 | 4.1093 | 9.841% | 10.47% | 7.075% | 1.1091 | 1.117 | 1.0761
2010-06-29 | 2 | 33.5846 | 9.8557 | 43.4403 | 3.2826 | 0.76558 | 0.32294 | 4.3711 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-06-29 | 3 | 31.9877 | 9.5328 | 41.5204 | 2.9989 | 0.76558 | 0.30867 | 4.0731 | 9.81% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-06-29 | 4 | 30.8656 | 9.1372 | 40.0028 | 2.7837 | 0.76558 | 0.29739 | 3.8466 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-06-29 | 5 | 30.4876 | 8.8818 | 39.3694 | 2.6962 | 0.76558 | 0.29268 | 3.7545 | 9.536% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-06-29 | 6 | 29.8383 | 8.8226 | 38.6609 | 2.6 | 0.76558 | 0.28741 | 3.653 | 9.449% | 10.05% | 6.794% | 1.1043 | 1.1118 | 1.0729
2010-06-29 | 7 | 29.574 | 8.7651 | 38.3391 | 2.5569 | 0.76558 | 0.28502 | 3.6075 | 9.41% | 10.01% | 6.765% | 1.1039 | 1.1113 | 1.0726
2010-06-29 | 8 | 29.5257 | 8.5588 | 38.0844 | 2.5231 | 0.76558 | 0.28312 | 3.5718 | 9.379% | 9.979% | 6.743% | 1.1035 | 1.1108 | 1.0723
2010-06-29 | 9 | 29.6532 | 8.58 | 38.2331 | 2.5428 | 0.76558 | 0.28423 | 3.5926 | 9.397% | 9.998% | 6.756% | 1.1037 | 1.1111 | 1.0725
2010-06-29 | 10 | 29.6906 | 8.7365 | 38.4271 | 2.5687 | 0.76558 | 0.28567 | 3.6199 | 9.42% | 10.02% | 6.773% | 1.104 | 1.1114 | 1.0727
2010-06-29 | 11 | 30.0648 | 8.898 | 38.9628 | 2.6408 | 0.76558 | 0.28965 | 3.696 | 9.486% | 10.09% | 6.82% | 1.1048 | 1.1123 | 1.0732
2010-06-29 | 12 | 30.8516 | 9.2516 | 40.1032 | 2.7976 | 0.76558 | 0.29813 | 3.8614 | 9.629% | 10.24% | 6.923% | 1.1065 | 1.1141 | 1.0744
2010-06-29 | 13 | 33.4188 | 10.4238 | 43.8426 | 3.3437 | 0.76558 | 0.32593 | 4.4352 | 10.12% | 10.76% | 7.274% | 1.1125 | 1.1206 | 1.0784
2010-06-29 | 14 | 36.775 | 11.9099 | 48.6849 | 4.1231 | 0.76558 | 0.36193 | 5.2506 | 10.78% | 11.48% | 7.754% | 1.1209 | 1.1296 | 1.0841
2010-06-29 | 15 | 40.7612 | 13.8764 | 54.6375 | 5.193 | 0.76558 | 0.40618 | 6.3647 | 11.65% | 12.39% | 8.376% | 1.1318 | 1.1415 | 1.0914
2010-06-29 | 16 | 42.466 | 14.9489 | 57.4149 | 5.7343 | 0.76558 | 0.42683 | 6.9267 | 12.06% | 12.84% | 8.674% | 1.1372 | 1.1473 | 1.095
2010-06-29 | 17 | 44.3017 | 15.9927 | 60.2944 | 6.3239 | 0.76558 | 0.44824 | 7.5378 | 12.5% | 13.3% | 8.989% | 1.1429 | 1.1534 | 1.0988
2010-06-29 | 18 | 44.5571 | 16.3226 | 60.8797 | 6.4473 | 0.76558 | 0.45259 | 7.6655 | 12.59% | 13.4% | 9.053% | 1.144 | 1.1547 | 1.0995
2010-06-29 | 19 | 44.3826 | 15.8392 | 60.2218 | 6.3087 | 0.76558 | 0.4477 | 7.522 | 12.49% | 13.29% | 8.981% | 1.1427 | 1.1533 | 1.0987
2010-06-29 | 20 | 44.8259 | 15.9869 | 60.8128 | 6.4332 | 0.76558 | 0.45209 | 7.6508 | 12.58% | 13.39% | 9.046% | 1.1439 | 1.1545 | 1.0995
2010-06-29 | 21 | 47.0958 | 15.9282 | 63.024 | 6.9095 | 0.76558 | 0.46853 | 8.1436 | 12.92% | 13.75% | 9.291% | 1.1484 | 1.1594 | 1.1024
2010-06-29 | 22 | 46.2654 | 15.7963 | 62.0617 | 6.7001 | 0.76558 | 0.46137 | 7.9271 | 12.77% | 13.59% | 9.184% | 1.1464 | 1.1573 | 1.1011
2010-06-29 | 23 | 44.8014 | 14.9525 | 59.7539 | 6.2111 | 0.76558 | 0.44422 | 7.4209 | 12.42% | 13.21% | 8.929% | 1.1418 | 1.1523 | 1.098
2010-06-29 | 24 | 43.3233 | 14.22 | 57.5433 | 5.76 | 0.76558 | 0.42778 | 6.9534 | 12.08% | 12.86% | 8.688% | 1.1374 | 1.1475 | 1.0951
2010-06-29 | 25 | 40.1846 | 13.5491 | 53.7337 | 5.0226 | 0.76558 | 0.39946 | 6.1876 | 11.52% | 12.25% | 8.28% | 1.1301 | 1.1396 | 1.0903
2010-06-29 | 26 | 37.8765 | 12.5993 | 50.4757 | 4.432 | 0.76558 | 0.37524 | 5.5728 | 11.04% | 11.75% | 7.938% | 1.1241 | 1.1331 | 1.0862
2010-06-29 | 27 | 38.552 | 12.8872 | 51.4392 | 4.6028 | 0.76558 | 0.38241 | 5.7508 | 11.18% | 11.9% | 8.038% | 1.1259 | 1.135 | 1.0874
2010-06-29 | 28 | 38.6374 | 13.0499 | 51.6874 | 4.6473 | 0.76558 | 0.38425 | 5.7972 | 11.22% | 11.93% | 8.064% | 1.1263 | 1.1355 | 1.0877
2010-06-29 | 29 | 38.5942 | 12.7122 | 51.3063 | 4.5791 | 0.76558 | 0.38142 | 5.7261 | 11.16% | 11.87% | 8.024% | 1.1256 | 1.1347 | 1.0872
2010-06-29 | 30 | 37.87 | 12.1164 | 49.9865 | 4.3465 | 0.76558 | 0.37161 | 5.4837 | 10.97% | 11.67% | 7.888% | 1.1232 | 1.1321 | 1.0856
2010-06-29 | 31 | 40.7486 | 12.7364 | 53.485 | 4.9762 | 0.76558 | 0.39761 | 6.1394 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.09
2010-06-29 | 32 | 41.6147 | 12.7933 | 54.408 | 5.1495 | 0.76558 | 0.40448 | 6.3195 | 11.62% | 12.36% | 8.351% | 1.1314 | 1.141 | 1.0911
2010-06-29 | 33 | 41.9955 | 13.2045 | 55.2 | 5.3004 | 0.76558 | 0.41036 | 6.4764 | 11.73% | 12.48% | 8.436% | 1.1329 | 1.1426 | 1.0921
2010-06-29 | 34 | 43.6746 | 13.7781 | 57.4527 | 5.7419 | 0.76558 | 0.42711 | 6.9346 | 12.07% | 12.84% | 8.678% | 1.1373 | 1.1473 | 1.095
2010-06-29 | 35 | 45.0632 | 14.6046 | 59.6678 | 6.1932 | 0.76558 | 0.44358 | 7.4024 | 12.41% | 13.2% | 8.92% | 1.1416 | 1.1521 | 1.0979
2010-06-29 | 36 | 47.3513 | 15.8029 | 63.1543 | 6.9381 | 0.76558 | 0.4695 | 8.1732 | 12.94% | 13.77% | 9.305% | 1.1487 | 1.1597 | 1.1026
2010-06-29 | 37 | 47.3985 | 15.5956 | 62.994 | 6.9029 | 0.76558 | 0.46831 | 8.1368 | 12.92% | 13.74% | 9.287% | 1.1483 | 1.1593 | 1.1024
2010-06-29 | 38 | 47.375 | 15.2785 | 62.6535 | 6.8285 | 0.76558 | 0.46577 | 8.0599 | 12.86% | 13.69% | 9.249% | 1.1476 | 1.1586 | 1.1019
2010-06-29 | 39 | 47.3519 | 14.6619 | 62.0139 | 6.6898 | 0.76558 | 0.46102 | 7.9164 | 12.77% | 13.58% | 9.178% | 1.1463 | 1.1572 | 1.1011
2010-06-29 | 40 | 47.36 | 14.1567 | 61.5167 | 6.583 | 0.76558 | 0.45732 | 7.8059 | 12.69% | 13.5% | 9.123% | 1.1453 | 1.1561 | 1.1004
2010-06-29 | 41 | 47.3705 | 13.9851 | 61.3556 | 6.5485 | 0.76558 | 0.45612 | 7.7702 | 12.66% | 13.47% | 9.106% | 1.145 | 1.1557 | 1.1002
2010-06-29 | 42 | 47.2989 | 13.6642 | 60.9631 | 6.465 | 0.76558 | 0.45321 | 7.6838 | 12.6% | 13.41% | 9.062% | 1.1442 | 1.1549 | 1.0997
2010-06-29 | 43 | 46.8612 | 13.0521 | 59.9134 | 6.2443 | 0.76558 | 0.4454 | 7.4553 | 12.44% | 13.24% | 8.947% | 1.1421 | 1.1526 | 1.0983
2010-06-29 | 44 | 45.3526 | 12.1181 | 57.4707 | 5.7455 | 0.76558 | 0.42724 | 6.9383 | 12.07% | 12.85% | 8.68% | 1.1373 | 1.1474 | 1.0951
2010-06-29 | 45 | 41.0173 | 10.9245 | 51.9418 | 4.6932 | 0.76558 | 0.38614 | 5.8449 | 11.25% | 11.97% | 8.091% | 1.1268 | 1.136 | 1.088
2010-06-29 | 46 | 37.2378 | 9.8692 | 47.1069 | 3.8602 | 0.76558 | 0.3502 | 4.9759 | 10.56% | 11.24% | 7.595% | 1.1181 | 1.1266 | 1.0822
2010-06-29 | 47 | 36.4449 | 10.3065 | 46.7514 | 3.8021 | 0.76558 | 0.34756 | 4.9152 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.126 | 1.0818
2010-06-29 | 48 | 35.0484 | 10.9013 | 45.9497 | 3.6728 | 0.76558 | 0.3416 | 4.78 | 10.4% | 11.07% | 7.48% | 1.1161 | 1.1245 | 1.0808
2010-06-30 | 1 | 33.05 | 10.1967 | 43.2467 | 3.2534 | 0.76558 | 0.3215 | 4.3405 | 10.04% | 10.68% | 7.216% | 1.1116 | 1.1196 | 1.0778
2010-06-30 | 2 | 35.2735 | 10.0845 | 45.358 | 3.5788 | 0.76558 | 0.3372 | 4.6816 | 10.32% | 10.98% | 7.421% | 1.1151 | 1.1234 | 1.0802
2010-06-30 | 3 | 34.2081 | 9.7347 | 43.9428 | 3.359 | 0.76558 | 0.32668 | 4.4513 | 10.13% | 10.78% | 7.283% | 1.1127 | 1.1208 | 1.0786
2010-06-30 | 4 | 32.4837 | 9.5669 | 42.0506 | 3.076 | 0.76558 | 0.31261 | 4.1541 | 9.879% | 10.51% | 7.103% | 1.1096 | 1.1175 | 1.0765
2010-06-30 | 5 | 31.5646 | 9.2482 | 40.8128 | 2.8975 | 0.76558 | 0.30341 | 3.9665 | 9.719% | 10.34% | 6.988% | 1.1077 | 1.1153 | 1.0751
2010-06-30 | 6 | 31.1029 | 8.8476 | 39.9505 | 2.7764 | 0.76558 | 0.297 | 3.839 | 9.609% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-06-30 | 7 | 31.2625 | 8.8375 | 40.1 | 2.7972 | 0.76558 | 0.29811 | 3.8609 | 9.628% | 10.24% | 6.923% | 1.1065 | 1.1141 | 1.0744
2010-06-30 | 8 | 31.2051 | 8.8879 | 40.093 | 2.7962 | 0.76558 | 0.29806 | 3.8599 | 9.627% | 10.24% | 6.922% | 1.1065 | 1.1141 | 1.0744
2010-06-30 | 9 | 31.1647 | 8.9552 | 40.1199 | 2.8 | 0.76558 | 0.29826 | 3.8638 | 9.631% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-06-30 | 10 | 31.6383 | 8.9789 | 40.6172 | 2.8698 | 0.76558 | 0.30195 | 3.9374 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2010-06-30 | 11 | 33.0026 | 9.3933 | 42.3958 | 3.1267 | 0.76558 | 0.31518 | 4.2074 | 9.924% | 10.56% | 7.135% | 1.1102 | 1.1181 | 1.0768
2010-06-30 | 12 | 34.1807 | 9.6667 | 43.8474 | 3.3444 | 0.76558 | 0.32597 | 4.436 | 10.12% | 10.76% | 7.274% | 1.1126 | 1.1206 | 1.0784
2010-06-30 | 13 | 36.162 | 10.774 | 46.936 | 3.8322 | 0.76558 | 0.34893 | 4.9467 | 10.54% | 11.21% | 7.578% | 1.1178 | 1.1263 | 1.082
2010-06-30 | 14 | 39.6202 | 12.257 | 51.8773 | 4.6815 | 0.76558 | 0.38566 | 5.8328 | 11.24% | 11.96% | 8.084% | 1.1267 | 1.1359 | 1.088
2010-06-30 | 15 | 44.4743 | 14.3929 | 58.8671 | 6.0281 | 0.76558 | 0.43763 | 7.2313 | 12.28% | 13.07% | 8.832% | 1.14 | 1.1504 | 1.0969
2010-06-30 | 16 | 45.9227 | 15.4494 | 61.3721 | 6.5521 | 0.76558 | 0.45625 | 7.7739 | 12.67% | 13.48% | 9.107% | 1.145 | 1.1558 | 1.1002
2010-06-30 | 17 | 43.9806 | 15.978 | 59.9586 | 6.2537 | 0.76558 | 0.44574 | 7.465 | 12.45% | 13.25% | 8.952% | 1.1422 | 1.1527 | 1.0983
2010-06-30 | 18 | 41.8314 | 14.6791 | 56.5105 | 5.5551 | 0.76558 | 0.42011 | 6.7408 | 11.93% | 12.69% | 8.577% | 1.1354 | 1.1454 | 1.0938
2010-06-30 | 19 | 41.9192 | 15.1581 | 57.0773 | 5.6671 | 0.76558 | 0.42432 | 6.857 | 12.01% | 12.78% | 8.638% | 1.1365 | 1.1466 | 1.0945
2010-06-30 | 20 | 42.0775 | 14.6284 | 56.7059 | 5.5936 | 0.76558 | 0.42156 | 6.7807 | 11.96% | 12.72% | 8.598% | 1.1358 | 1.1458 | 1.0941
2010-06-30 | 21 | 44.6996 | 14.6501 | 59.3497 | 6.1273 | 0.76558 | 0.44121 | 7.3341 | 12.36% | 13.15% | 8.885% | 1.141 | 1.1514 | 1.0975
2010-06-30 | 22 | 44.9018 | 14.0729 | 58.9747 | 6.0501 | 0.76558 | 0.43842 | 7.2541 | 12.3% | 13.09% | 8.844% | 1.1403 | 1.1506 | 1.097
2010-06-30 | 23 | 46.6652 | 14.843 | 61.5082 | 6.5811 | 0.76558 | 0.45726 | 7.804 | 12.69% | 13.5% | 9.122% | 1.1453 | 1.1561 | 1.1004
2010-06-30 | 24 | 46.0674 | 15.56 | 61.6273 | 6.6067 | 0.76558 | 0.45815 | 7.8304 | 12.71% | 13.52% | 9.136% | 1.1456 | 1.1563 | 1.1005
2010-06-30 | 25 | 42.4058 | 14.6619 | 57.0677 | 5.6652 | 0.76558 | 0.42425 | 6.855 | 12.01% | 12.78% | 8.637% | 1.1365 | 1.1465 | 1.0945
2010-06-30 | 26 | 39.3717 | 13.3975 | 52.7692 | 4.8439 | 0.76558 | 0.39229 | 6.0018 | 11.37% | 12.1% | 8.178% | 1.1283 | 1.1377 | 1.0891
2010-06-30 | 27 | 39.2286 | 13.4993 | 52.7279 | 4.8363 | 0.76558 | 0.39199 | 5.9939 | 11.37% | 12.1% | 8.173% | 1.1283 | 1.1376 | 1.089
2010-06-30 | 28 | 38.7305 | 13.5405 | 52.271 | 4.7529 | 0.76558 | 0.38859 | 5.907 | 11.3% | 12.02% | 8.125% | 1.1274 | 1.1367 | 1.0884
2010-06-30 | 29 | 38.0943 | 12.8832 | 50.9775 | 4.5206 | 0.76558 | 0.37897 | 5.6651 | 11.11% | 11.82% | 7.99% | 1.125 | 1.1341 | 1.0868
2010-06-30 | 30 | 37.7152 | 12.2606 | 49.9758 | 4.3446 | 0.76558 | 0.37153 | 5.4817 | 10.97% | 11.67% | 7.887% | 1.1232 | 1.1321 | 1.0856
2010-06-30 | 31 | 40.6113 | 12.0897 | 52.701 | 4.8314 | 0.76558 | 0.39179 | 5.9888 | 11.36% | 12.09% | 8.17% | 1.1282 | 1.1375 | 1.089
2010-06-30 | 32 | 41.6202 | 11.9025 | 53.5227 | 4.9832 | 0.76558 | 0.39789 | 6.1467 | 11.48% | 12.22% | 8.257% | 1.1297 | 1.1392 | 1.09
2010-06-30 | 33 | 41.7989 | 12.2441 | 54.043 | 5.0806 | 0.76558 | 0.40176 | 6.2479 | 11.56% | 12.3% | 8.312% | 1.1307 | 1.1403 | 1.0907
2010-06-30 | 34 | 43.2031 | 12.6575 | 55.8606 | 5.4281 | 0.76558 | 0.41527 | 6.6089 | 11.83% | 12.59% | 8.507% | 1.1342 | 1.144 | 1.093
2010-06-30 | 35 | 44.2043 | 14.0397 | 58.244 | 5.9012 | 0.76558 | 0.43299 | 7.0997 | 12.19% | 12.97% | 8.764% | 1.1388 | 1.149 | 1.0961
2010-06-30 | 36 | 44.8159 | 14.823 | 59.6389 | 6.1872 | 0.76558 | 0.44336 | 7.3961 | 12.4% | 13.2% | 8.917% | 1.1416 | 1.152 | 1.0979
2010-06-30 | 37 | 44.282 | 14.3295 | 58.6115 | 5.9759 | 0.76558 | 0.43572 | 7.1772 | 12.25% | 13.03% | 8.804% | 1.1395 | 1.1498 | 1.0965
2010-06-30 | 38 | 46.5894 | 15.346 | 61.9354 | 6.6729 | 0.76558 | 0.46044 | 7.8989 | 12.75% | 13.57% | 9.17% | 1.1462 | 1.157 | 1.101
2010-06-30 | 39 | 45.6532 | 14.9745 | 60.6276 | 6.394 | 0.76558 | 0.45071 | 7.6103 | 12.55% | 13.36% | 9.025% | 1.1435 | 1.1541 | 1.0992
2010-06-30 | 40 | 43.4542 | 14.0878 | 57.5419 | 5.7598 | 0.76558 | 0.42777 | 6.9531 | 12.08% | 12.86% | 8.688% | 1.1374 | 1.1475 | 1.0951
2010-06-30 | 41 | 47.0257 | 15.0439 | 62.0697 | 6.7018 | 0.76558 | 0.46143 | 7.9288 | 12.77% | 13.59% | 9.185% | 1.1464 | 1.1573 | 1.1011
2010-06-30 | 42 | 47.3125 | 14.6376 | 61.9501 | 6.676 | 0.76558 | 0.46054 | 7.9022 | 12.76% | 13.57% | 9.171% | 1.1462 | 1.157 | 1.101
2010-06-30 | 43 | 47.0801 | 13.8317 | 60.9118 | 6.4541 | 0.76558 | 0.45283 | 7.6725 | 12.6% | 13.4% | 9.057% | 1.1441 | 1.1548 | 1.0996
2010-06-30 | 44 | 46.3173 | 13.0305 | 59.3478 | 6.1269 | 0.76558 | 0.4412 | 7.3337 | 12.36% | 13.15% | 8.885% | 1.141 | 1.1514 | 1.0975
2010-06-30 | 45 | 42.492 | 11.8941 | 54.3861 | 5.1453 | 0.76558 | 0.40431 | 6.3152 | 11.61% | 12.35% | 8.349% | 1.1314 | 1.141 | 1.0911
2010-06-30 | 46 | 38.0825 | 10.588 | 48.6705 | 4.1207 | 0.76558 | 0.36182 | 5.2481 | 10.78% | 11.47% | 7.753% | 1.1209 | 1.1296 | 1.084
2010-06-30 | 47 | 37.4462 | 10.9266 | 48.3728 | 4.0704 | 0.76558 | 0.35961 | 5.1956 | 10.74% | 11.43% | 7.723% | 1.1203 | 1.129 | 1.0837
2010-06-30 | 48 | 36.8684 | 11.3265 | 48.1949 | 4.0405 | 0.76558 | 0.35829 | 5.1644 | 10.72% | 11.4% | 7.705% | 1.12 | 1.1287 | 1.0835
2010-07-01 | 1 | 34.8989 | 10.6616 | 45.5605 | 3.6109 | 0.76558 | 0.3387 | 4.7151 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-07-01 | 2 | 36.8947 | 10.5666 | 47.4613 | 3.9184 | 0.76558 | 0.35283 | 5.0369 | 10.61% | 11.29% | 7.63% | 1.1187 | 1.1273 | 1.0826
2010-07-01 | 3 | 35.6979 | 10.1571 | 45.855 | 3.6577 | 0.76558 | 0.34089 | 4.7642 | 10.39% | 11.05% | 7.47% | 1.1159 | 1.1243 | 1.0807
2010-07-01 | 4 | 34.2312 | 9.805 | 44.0361 | 3.3733 | 0.76558 | 0.32737 | 4.4662 | 10.14% | 10.79% | 7.292% | 1.1129 | 1.121 | 1.0787
2010-07-01 | 5 | 33.5106 | 9.4632 | 42.9737 | 3.2125 | 0.76558 | 0.31947 | 4.2975 | 10% | 10.64% | 7.19% | 1.1111 | 1.1191 | 1.0775
2010-07-01 | 6 | 32.9921 | 9.2582 | 42.2502 | 3.1052 | 0.76558 | 0.31409 | 4.1849 | 9.905% | 10.54% | 7.122% | 1.1099 | 1.1178 | 1.0767
2010-07-01 | 7 | 32.3012 | 9.2173 | 41.5184 | 2.9986 | 0.76558 | 0.30865 | 4.0728 | 9.81% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-07-01 | 8 | 32.3702 | 9.163 | 41.5332 | 3.0007 | 0.76558 | 0.30876 | 4.0751 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-07-01 | 9 | 33.001 | 9.2108 | 42.2118 | 3.0996 | 0.76558 | 0.31381 | 4.179 | 9.9% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-07-01 | 10 | 34.2197 | 9.2449 | 43.4645 | 3.2863 | 0.76558 | 0.32312 | 4.375 | 10.07% | 10.71% | 7.237% | 1.1119 | 1.1199 | 1.078
2010-07-01 | 11 | 34.5457 | 9.4982 | 44.0439 | 3.3745 | 0.76558 | 0.32743 | 4.4675 | 10.14% | 10.79% | 7.293% | 1.1129 | 1.121 | 1.0787
2010-07-01 | 12 | 34.989 | 9.9261 | 44.9152 | 3.5093 | 0.76558 | 0.3339 | 4.6088 | 10.26% | 10.92% | 7.378% | 1.1143 | 1.1226 | 1.0797
2010-07-01 | 13 | 36.5521 | 11.049 | 47.6012 | 3.9416 | 0.76558 | 0.35387 | 5.061 | 10.63% | 11.31% | 7.645% | 1.119 | 1.1276 | 1.0828
2010-07-01 | 14 | 40.3695 | 12.6854 | 53.0549 | 4.8965 | 0.76558 | 0.39442 | 6.0565 | 11.42% | 12.15% | 8.208% | 1.1289 | 1.1383 | 1.0894
2010-07-01 | 15 | 45.0603 | 14.9834 | 60.0437 | 6.2715 | 0.76558 | 0.44637 | 7.4834 | 12.46% | 13.26% | 8.961% | 1.1424 | 1.1529 | 1.0984
2010-07-01 | 16 | 46.7085 | 16.1382 | 62.8467 | 6.8707 | 0.76558 | 0.46721 | 8.1035 | 12.89% | 13.72% | 9.271% | 1.148 | 1.159 | 1.1022
2010-07-01 | 17 | 45.3706 | 16.056 | 61.4265 | 6.5637 | 0.76558 | 0.45665 | 7.7859 | 12.68% | 13.49% | 9.113% | 1.1451 | 1.1559 | 1.1003
2010-07-01 | 18 | 46.8492 | 16.28 | 63.1292 | 6.9326 | 0.76558 | 0.46931 | 8.1675 | 12.94% | 13.77% | 9.302% | 1.1486 | 1.1596 | 1.1026
2010-07-01 | 19 | 46.0737 | 15.6042 | 61.6779 | 6.6175 | 0.76558 | 0.45852 | 7.8416 | 12.71% | 13.53% | 9.141% | 1.1457 | 1.1564 | 1.1006
2010-07-01 | 20 | 44.8683 | 15.9375 | 60.8058 | 6.4317 | 0.76558 | 0.45204 | 7.6493 | 12.58% | 13.38% | 9.045% | 1.1439 | 1.1545 | 1.0994
2010-07-01 | 21 | 47.325 | 16.1702 | 63.4952 | 7.0132 | 0.76558 | 0.47203 | 8.2508 | 12.99% | 13.83% | 9.343% | 1.1494 | 1.1604 | 1.1031
2010-07-01 | 22 | 47.1784 | 15.9799 | 63.1583 | 6.939 | 0.76558 | 0.46953 | 8.1741 | 12.94% | 13.77% | 9.305% | 1.1487 | 1.1597 | 1.1026
2010-07-01 | 23 | 47.0829 | 15.6174 | 62.7002 | 6.8387 | 0.76558 | 0.46612 | 8.0704 | 12.87% | 13.7% | 9.255% | 1.1477 | 1.1587 | 1.102
2010-07-01 | 24 | 47.0418 | 15.5445 | 62.5863 | 6.8139 | 0.76558 | 0.46527 | 8.0447 | 12.85% | 13.68% | 9.242% | 1.1475 | 1.1584 | 1.1018
2010-07-01 | 25 | 43.7707 | 13.9176 | 57.6883 | 5.7891 | 0.76558 | 0.42886 | 6.9835 | 12.11% | 12.88% | 8.704% | 1.1377 | 1.1478 | 1.0953
2010-07-01 | 26 | 40.4304 | 12.7881 | 53.2186 | 4.9268 | 0.76558 | 0.39563 | 6.088 | 11.44% | 12.17% | 8.225% | 1.1292 | 1.1386 | 1.0896
2010-07-01 | 27 | 40.3751 | 12.9802 | 53.3552 | 4.9521 | 0.76558 | 0.39665 | 6.1143 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1389 | 1.0898
2010-07-01 | 28 | 40.3951 | 13.1714 | 53.5665 | 4.9914 | 0.76558 | 0.39822 | 6.1552 | 11.49% | 12.23% | 8.262% | 1.1298 | 1.1393 | 1.0901
2010-07-01 | 29 | 40.1068 | 13.0394 | 53.1462 | 4.9134 | 0.76558 | 0.3951 | 6.074 | 11.43% | 12.16% | 8.217% | 1.129 | 1.1384 | 1.0895
2010-07-01 | 30 | 39.92 | 12.8406 | 52.7606 | 4.8423 | 0.76558 | 0.39223 | 6.0001 | 11.37% | 12.1% | 8.177% | 1.1283 | 1.1377 | 1.089
2010-07-01 | 31 | 43.0253 | 13.1414 | 56.1667 | 5.4877 | 0.76558 | 0.41755 | 6.6709 | 11.88% | 12.64% | 8.539% | 1.1348 | 1.1446 | 1.0934
2010-07-01 | 32 | 44.262 | 12.8636 | 57.1256 | 5.6767 | 0.76558 | 0.42468 | 6.867 | 12.02% | 12.79% | 8.643% | 1.1366 | 1.1467 | 1.0946
2010-07-01 | 33 | 44.71 | 12.9565 | 57.6665 | 5.7847 | 0.76558 | 0.4287 | 6.979 | 12.1% | 12.88% | 8.702% | 1.1377 | 1.1478 | 1.0953
2010-07-01 | 34 | 47.2406 | 13.2936 | 60.5343 | 6.3744 | 0.76558 | 0.45002 | 7.59 | 12.54% | 13.34% | 9.015% | 1.1434 | 1.1539 | 1.0991
2010-07-01 | 35 | 47.3436 | 14.4672 | 61.8108 | 6.6461 | 0.76558 | 0.45951 | 7.8711 | 12.73% | 13.55% | 9.156% | 1.1459 | 1.1567 | 1.1008
2010-07-01 | 36 | 47.2743 | 15.6828 | 62.9571 | 6.8948 | 0.76558 | 0.46803 | 8.1285 | 12.91% | 13.74% | 9.283% | 1.1483 | 1.1593 | 1.1023
2010-07-01 | 37 | 45.3471 | 14.7859 | 60.133 | 6.2901 | 0.76558 | 0.44704 | 7.5028 | 12.48% | 13.28% | 8.971% | 1.1426 | 1.1531 | 1.0986
2010-07-01 | 38 | 47.1552 | 15.8524 | 63.0076 | 6.9059 | 0.76558 | 0.46841 | 8.1399 | 12.92% | 13.75% | 9.289% | 1.1484 | 1.1594 | 1.1024
2010-07-01 | 39 | 45.7157 | 15.2318 | 60.9475 | 6.4617 | 0.76558 | 0.45309 | 7.6804 | 12.6% | 13.41% | 9.061% | 1.1442 | 1.1548 | 1.0996
2010-07-01 | 40 | 45.1926 | 14.9763 | 60.1688 | 6.2976 | 0.76558 | 0.4473 | 7.5105 | 12.48% | 13.28% | 8.975% | 1.1426 | 1.1532 | 1.0986
2010-07-01 | 41 | 47.2575 | 14.9966 | 62.2542 | 6.7417 | 0.76558 | 0.46281 | 7.9701 | 12.8% | 13.62% | 9.205% | 1.1468 | 1.1577 | 1.1014
2010-07-01 | 42 | 47.1407 | 14.523 | 61.6638 | 6.6145 | 0.76558 | 0.45842 | 7.8385 | 12.71% | 13.53% | 9.14% | 1.1456 | 1.1564 | 1.1006
2010-07-01 | 43 | 47.1361 | 14.0524 | 61.1885 | 6.5129 | 0.76558 | 0.45488 | 7.7334 | 12.64% | 13.45% | 9.087% | 1.1447 | 1.1554 | 1.1
2010-07-01 | 44 | 47.0781 | 13.0432 | 60.1212 | 6.2877 | 0.76558 | 0.44695 | 7.5002 | 12.48% | 13.27% | 8.97% | 1.1425 | 1.1531 | 1.0985
2010-07-01 | 45 | 45.7378 | 11.5554 | 57.2932 | 5.7101 | 0.76558 | 0.42592 | 6.9016 | 12.05% | 12.82% | 8.661% | 1.137 | 1.147 | 1.0948
2010-07-01 | 46 | 41.6012 | 10.3622 | 51.9634 | 4.6971 | 0.76558 | 0.3863 | 5.849 | 11.26% | 11.98% | 8.093% | 1.1268 | 1.1361 | 1.0881
2010-07-01 | 47 | 40.8629 | 10.8542 | 51.717 | 4.6527 | 0.76558 | 0.38447 | 5.8027 | 11.22% | 11.94% | 8.067% | 1.1264 | 1.1356 | 1.0878
2010-07-01 | 48 | 39.2562 | 11.6441 | 50.9003 | 4.5069 | 0.76558 | 0.3784 | 5.6509 | 11.1% | 11.81% | 7.982% | 1.1249 | 1.1339 | 1.0867
2010-07-02 | 1 | 36.6837 | 10.6957 | 47.3794 | 3.9049 | 0.76558 | 0.35222 | 5.0227 | 10.6% | 11.28% | 7.622% | 1.1186 | 1.1271 | 1.0825
2010-07-02 | 2 | 38.3187 | 10.63 | 48.9487 | 4.1679 | 0.76558 | 0.36389 | 5.2974 | 10.82% | 11.51% | 7.781% | 1.1214 | 1.1301 | 1.0844
2010-07-02 | 3 | 37.123 | 10.3682 | 47.4912 | 3.9234 | 0.76558 | 0.35306 | 5.042 | 10.62% | 11.3% | 7.633% | 1.1188 | 1.1273 | 1.0826
2010-07-02 | 4 | 35.0948 | 10.0187 | 45.1135 | 3.5404 | 0.76558 | 0.33538 | 4.6413 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-07-02 | 5 | 34.0967 | 9.7888 | 43.8854 | 3.3502 | 0.76558 | 0.32625 | 4.4421 | 10.12% | 10.77% | 7.278% | 1.1126 | 1.1207 | 1.0785
2010-07-02 | 6 | 33.3084 | 9.668 | 42.9765 | 3.2129 | 0.76558 | 0.31949 | 4.298 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-07-02 | 7 | 32.9118 | 9.6199 | 42.5318 | 3.1467 | 0.76558 | 0.31619 | 4.2285 | 9.942% | 10.58% | 7.148% | 1.1104 | 1.1183 | 1.077
2010-07-02 | 8 | 32.566 | 9.4982 | 42.0642 | 3.0779 | 0.76558 | 0.31271 | 4.1562 | 9.881% | 10.51% | 7.104% | 1.1096 | 1.1175 | 1.0765
2010-07-02 | 9 | 32.9265 | 9.4046 | 42.3311 | 3.1171 | 0.76558 | 0.31469 | 4.1974 | 9.916% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-07-02 | 10 | 33.9749 | 9.5398 | 43.5147 | 3.2939 | 0.76558 | 0.32349 | 4.3829 | 10.07% | 10.72% | 7.242% | 1.112 | 1.12 | 1.0781
2010-07-02 | 11 | 34.7499 | 9.7686 | 44.5185 | 3.4476 | 0.76558 | 0.33096 | 4.5441 | 10.21% | 10.86% | 7.339% | 1.1137 | 1.1218 | 1.0792
2010-07-02 | 12 | 35.4231 | 10.2686 | 45.6917 | 3.6317 | 0.76558 | 0.33968 | 4.7369 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-07-02 | 13 | 36.4981 | 11.3089 | 47.8069 | 3.9757 | 0.76558 | 0.3554 | 5.0967 | 10.66% | 11.34% | 7.665% | 1.1193 | 1.1279 | 1.083
2010-07-02 | 14 | 39.7302 | 12.9045 | 52.6348 | 4.8193 | 0.76558 | 0.39129 | 5.9761 | 11.35% | 12.08% | 8.163% | 1.1281 | 1.1374 | 1.0889
2010-07-02 | 15 | 45.0276 | 15.237 | 60.2646 | 6.3177 | 0.76558 | 0.44801 | 7.5313 | 12.5% | 13.3% | 8.985% | 1.1428 | 1.1534 | 1.0987
2010-07-02 | 16 | 45.9321 | 16.3338 | 62.266 | 6.7443 | 0.76558 | 0.46289 | 7.9728 | 12.8% | 13.62% | 9.206% | 1.1468 | 1.1577 | 1.1014
2010-07-02 | 17 | 45.605 | 16.1571 | 61.7622 | 6.6356 | 0.76558 | 0.45915 | 7.8603 | 12.73% | 13.54% | 9.151% | 1.1458 | 1.1566 | 1.1007
2010-07-02 | 18 | 45.461 | 16.0714 | 61.5324 | 6.5863 | 0.76558 | 0.45744 | 7.8093 | 12.69% | 13.5% | 9.125% | 1.1454 | 1.1561 | 1.1004
2010-07-02 | 19 | 47.3889 | 16.3619 | 63.7508 | 7.0698 | 0.76558 | 0.47393 | 8.3093 | 13.03% | 13.87% | 9.371% | 1.1499 | 1.161 | 1.1034
2010-07-02 | 20 | 47.3128 | 16.2868 | 63.5995 | 7.0363 | 0.76558 | 0.47281 | 8.2747 | 13.01% | 13.84% | 9.355% | 1.1496 | 1.1607 | 1.1032
2010-07-02 | 21 | 47.3297 | 16.3241 | 63.6538 | 7.0483 | 0.76558 | 0.47321 | 8.2871 | 13.02% | 13.85% | 9.361% | 1.1497 | 1.1608 | 1.1033
2010-07-02 | 22 | 47.2693 | 16.3167 | 63.586 | 7.0333 | 0.76558 | 0.47271 | 8.2716 | 13.01% | 13.84% | 9.353% | 1.1495 | 1.1606 | 1.1032
2010-07-02 | 23 | 47.2498 | 16.2906 | 63.5404 | 7.0232 | 0.76558 | 0.47237 | 8.2611 | 13% | 13.83% | 9.348% | 1.1494 | 1.1605 | 1.1031
2010-07-02 | 24 | 47.2957 | 16.2952 | 63.591 | 7.0344 | 0.76558 | 0.47274 | 8.2727 | 13.01% | 13.84% | 9.354% | 1.1495 | 1.1607 | 1.1032
2010-07-02 | 25 | 46.6458 | 16.1825 | 62.8283 | 6.8667 | 0.76558 | 0.46707 | 8.0993 | 12.89% | 13.72% | 9.269% | 1.148 | 1.159 | 1.1022
2010-07-02 | 26 | 44.9718 | 16.2871 | 61.2589 | 6.5279 | 0.76558 | 0.45541 | 7.7489 | 12.65% | 13.46% | 9.095% | 1.1448 | 1.1555 | 1.1
2010-07-02 | 27 | 45.2845 | 16.5011 | 61.7855 | 6.6406 | 0.76558 | 0.45932 | 7.8655 | 12.73% | 13.55% | 9.153% | 1.1459 | 1.1567 | 1.1008
2010-07-02 | 28 | 46.2698 | 16.5576 | 62.8273 | 6.8664 | 0.76558 | 0.46707 | 8.0991 | 12.89% | 13.72% | 9.269% | 1.148 | 1.159 | 1.1022
2010-07-02 | 29 | 46.5275 | 16.7115 | 63.239 | 6.9567 | 0.76558 | 0.47013 | 8.1924 | 12.95% | 13.78% | 9.314% | 1.1488 | 1.1599 | 1.1027
2010-07-02 | 30 | 45.5082 | 16.6434 | 62.1516 | 6.7195 | 0.76558 | 0.46204 | 7.9472 | 12.79% | 13.61% | 9.194% | 1.1466 | 1.1575 | 1.1012
2010-07-02 | 31 | 47.04 | 16.7633 | 63.8033 | 7.0814 | 0.76558 | 0.47432 | 8.3213 | 13.04% | 13.88% | 9.377% | 1.15 | 1.1611 | 1.1035
2010-07-02 | 32 | 47.2769 | 16.6719 | 63.9488 | 7.1138 | 0.76558 | 0.4754 | 8.3547 | 13.06% | 13.9% | 9.394% | 1.1503 | 1.1615 | 1.1037
2010-07-02 | 33 | 47.7917 | 16.5734 | 64.3651 | 7.2067 | 0.76558 | 0.4785 | 8.4508 | 13.13% | 13.97% | 9.44% | 1.1511 | 1.1624 | 1.1042
2010-07-02 | 34 | 47.8646 | 16.5414 | 64.406 | 7.2159 | 0.76558 | 0.4788 | 8.4602 | 13.14% | 13.98% | 9.445% | 1.1512 | 1.1625 | 1.1043
2010-07-02 | 35 | 46.7551 | 16.73 | 63.4851 | 7.011 | 0.76558 | 0.47196 | 8.2485 | 12.99% | 13.82% | 9.342% | 1.1493 | 1.1604 | 1.103
2010-07-02 | 36 | 45.0373 | 16.4136 | 61.4509 | 6.5689 | 0.76558 | 0.45683 | 7.7913 | 12.68% | 13.49% | 9.116% | 1.1452 | 1.1559 | 1.1003
2010-07-02 | 37 | 45.9721 | 15.979 | 61.9511 | 6.6763 | 0.76558 | 0.46055 | 7.9024 | 12.76% | 13.57% | 9.171% | 1.1462 | 1.157 | 1.101
2010-07-02 | 38 | 47.8195 | 16.7476 | 64.5671 | 7.252 | 0.76558 | 0.48 | 8.4976 | 13.16% | 14% | 9.463% | 1.1516 | 1.1628 | 1.1045
2010-07-02 | 39 | 47.7188 | 16.1029 | 63.8217 | 7.0855 | 0.76558 | 0.47446 | 8.3256 | 13.05% | 13.88% | 9.379% | 1.15 | 1.1612 | 1.1035
2010-07-02 | 40 | 47.5852 | 15.2721 | 62.8573 | 6.873 | 0.76558 | 0.46729 | 8.1059 | 12.9% | 13.72% | 9.272% | 1.148 | 1.159 | 1.1022
2010-07-02 | 41 | 47.6707 | 14.9603 | 62.631 | 6.8236 | 0.76558 | 0.46561 | 8.0548 | 12.86% | 13.68% | 9.247% | 1.1476 | 1.1585 | 1.1019
2010-07-02 | 42 | 47.552 | 14.6211 | 62.1731 | 6.7242 | 0.76558 | 0.4622 | 7.952 | 12.79% | 13.61% | 9.196% | 1.1467 | 1.1575 | 1.1013
2010-07-02 | 43 | 47.6084 | 13.9368 | 61.5452 | 6.5891 | 0.76558 | 0.45753 | 7.8122 | 12.69% | 13.51% | 9.127% | 1.1454 | 1.1561 | 1.1004
2010-07-02 | 44 | 47.2756 | 13.0665 | 60.3421 | 6.334 | 0.76558 | 0.44859 | 7.5481 | 12.51% | 13.31% | 8.994% | 1.143 | 1.1535 | 1.0988
2010-07-02 | 45 | 42.6785 | 11.8341 | 54.5125 | 5.1692 | 0.76558 | 0.40525 | 6.3401 | 11.63% | 12.37% | 8.362% | 1.1316 | 1.1412 | 1.0913
2010-07-02 | 46 | 37.8067 | 10.8194 | 48.6261 | 4.1131 | 0.76558 | 0.36149 | 5.2402 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-07-02 | 47 | 36.5864 | 11.0748 | 47.6612 | 3.9515 | 0.76558 | 0.35432 | 5.0714 | 10.64% | 11.32% | 7.651% | 1.1191 | 1.1277 | 1.0828
2010-07-02 | 48 | 35.5703 | 11.7706 | 47.3409 | 3.8986 | 0.76558 | 0.35194 | 5.0161 | 10.6% | 11.27% | 7.618% | 1.1185 | 1.1271 | 1.0825
2010-07-03 | 1 | 33.7336 | 11.0702 | 44.8037 | 3.4919 | 0.76558 | 0.33308 | 4.5906 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-07-03 | 2 | 35.3403 | 10.837 | 46.1773 | 3.7093 | 0.76558 | 0.34329 | 4.8182 | 10.43% | 11.1% | 7.502% | 1.1165 | 1.1249 | 1.0811
2010-07-03 | 3 | 33.8342 | 10.4176 | 44.2518 | 3.4064 | 0.76558 | 0.32897 | 4.501 | 10.17% | 10.82% | 7.313% | 1.1132 | 1.1214 | 1.0789
2010-07-03 | 4 | 32.2534 | 10.0144 | 42.2678 | 3.1078 | 0.76558 | 0.31422 | 4.1876 | 9.907% | 10.54% | 7.123% | 1.11 | 1.1178 | 1.0767
2010-07-03 | 5 | 31.493 | 9.8148 | 41.3078 | 2.9682 | 0.76558 | 0.30709 | 4.0409 | 9.782% | 10.41% | 7.034% | 1.1084 | 1.1162 | 1.0757
2010-07-03 | 6 | 30.8912 | 9.5603 | 40.4515 | 2.8465 | 0.76558 | 0.30072 | 3.9128 | 9.673% | 10.29% | 6.955% | 1.1071 | 1.1147 | 1.0747
2010-07-03 | 7 | 30.5004 | 9.4545 | 39.9549 | 2.777 | 0.76558 | 0.29703 | 3.8396 | 9.61% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-07-03 | 8 | 30.2242 | 9.3659 | 39.59 | 2.7265 | 0.76558 | 0.29432 | 3.7864 | 9.564% | 10.18% | 6.877% | 1.1058 | 1.1133 | 1.0738
2010-07-03 | 9 | 30.4279 | 9.4246 | 39.8525 | 2.7628 | 0.76558 | 0.29627 | 3.8246 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-07-03 | 10 | 30.6254 | 9.3409 | 39.9663 | 2.7786 | 0.76558 | 0.29711 | 3.8413 | 9.611% | 10.23% | 6.911% | 1.1063 | 1.1139 | 1.0742
2010-07-03 | 11 | 31.1881 | 9.4431 | 40.6313 | 2.8718 | 0.76558 | 0.30206 | 3.9394 | 9.696% | 10.32% | 6.971% | 1.1074 | 1.115 | 1.0749
2010-07-03 | 12 | 31.7911 | 9.7612 | 41.5523 | 3.0035 | 0.76558 | 0.3089 | 4.078 | 9.814% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-07-03 | 13 | 33.7725 | 10.5446 | 44.317 | 3.4165 | 0.76558 | 0.32946 | 4.5115 | 10.18% | 10.83% | 7.319% | 1.1133 | 1.1215 | 1.079
2010-07-03 | 14 | 37.6939 | 11.8117 | 49.5056 | 4.2633 | 0.76558 | 0.36803 | 5.3969 | 10.9% | 11.6% | 7.838% | 1.1224 | 1.1312 | 1.085
2010-07-03 | 15 | 42.1441 | 13.4384 | 55.5824 | 5.3742 | 0.76558 | 0.41321 | 6.5529 | 11.79% | 12.54% | 8.477% | 1.1337 | 1.1434 | 1.0926
2010-07-03 | 16 | 43.2357 | 14.3134 | 57.5491 | 5.7612 | 0.76558 | 0.42783 | 6.9546 | 12.08% | 12.86% | 8.689% | 1.1375 | 1.1476 | 1.0952
2010-07-03 | 17 | 44.8464 | 15.7434 | 60.5897 | 6.3861 | 0.76558 | 0.45043 | 7.6021 | 12.55% | 13.35% | 9.021% | 1.1435 | 1.1541 | 1.0992
2010-07-03 | 18 | 46.7559 | 16.8412 | 63.5971 | 7.0357 | 0.76558 | 0.47279 | 8.2741 | 13.01% | 13.84% | 9.354% | 1.1496 | 1.1607 | 1.1032
2010-07-03 | 19 | 47.472 | 16.8044 | 64.2764 | 7.1868 | 0.76558 | 0.47784 | 8.4302 | 13.12% | 13.96% | 9.43% | 1.151 | 1.1622 | 1.1041
2010-07-03 | 20 | 47.0431 | 16.6231 | 63.6661 | 7.051 | 0.76558 | 0.4733 | 8.2899 | 13.02% | 13.85% | 9.362% | 1.1497 | 1.1608 | 1.1033
2010-07-03 | 21 | 47.3289 | 16.62 | 63.9489 | 7.1138 | 0.76558 | 0.4754 | 8.3548 | 13.06% | 13.9% | 9.394% | 1.1503 | 1.1615 | 1.1037
2010-07-03 | 22 | 47.1703 | 16.6467 | 63.8171 | 7.0845 | 0.76558 | 0.47442 | 8.3245 | 13.04% | 13.88% | 9.379% | 1.15 | 1.1612 | 1.1035
2010-07-03 | 23 | 46.4401 | 16.5367 | 62.9768 | 6.8992 | 0.76558 | 0.46818 | 8.1329 | 12.91% | 13.74% | 9.285% | 1.1483 | 1.1593 | 1.1024
2010-07-03 | 24 | 44.9457 | 16.1185 | 61.0642 | 6.4865 | 0.76558 | 0.45396 | 7.706 | 12.62% | 13.43% | 9.073% | 1.1444 | 1.1551 | 1.0998
2010-07-03 | 25 | 41.3842 | 15.5246 | 56.9088 | 5.6337 | 0.76558 | 0.42307 | 6.8223 | 11.99% | 12.76% | 8.62% | 1.1362 | 1.1462 | 1.0943
2010-07-03 | 26 | 39.0576 | 14.2454 | 53.303 | 4.9424 | 0.76558 | 0.39626 | 6.1042 | 11.45% | 12.18% | 8.234% | 1.1293 | 1.1388 | 1.0897
2010-07-03 | 27 | 38.569 | 14.7619 | 53.331 | 4.9476 | 0.76558 | 0.39647 | 6.1096 | 11.46% | 12.19% | 8.237% | 1.1294 | 1.1388 | 1.0898
2010-07-03 | 28 | 39.5041 | 15.3366 | 54.8407 | 5.2317 | 0.76558 | 0.40769 | 6.4049 | 11.68% | 12.43% | 8.397% | 1.1322 | 1.1419 | 1.0917
2010-07-03 | 29 | 39.1921 | 14.7445 | 53.9366 | 5.0606 | 0.76558 | 0.40097 | 6.2272 | 11.55% | 12.28% | 8.301% | 1.1305 | 1.14 | 1.0905
2010-07-03 | 30 | 39.2972 | 14.216 | 53.5132 | 4.9815 | 0.76558 | 0.39782 | 6.1449 | 11.48% | 12.22% | 8.256% | 1.1297 | 1.1392 | 1.09
2010-07-03 | 31 | 42.2287 | 14.6064 | 56.8351 | 5.6191 | 0.76558 | 0.42252 | 6.8072 | 11.98% | 12.74% | 8.612% | 1.1361 | 1.146 | 1.0942
2010-07-03 | 32 | 42.9522 | 14.4872 | 57.4394 | 5.7392 | 0.76558 | 0.42701 | 6.9318 | 12.07% | 12.84% | 8.677% | 1.1372 | 1.1473 | 1.095
2010-07-03 | 33 | 43.8285 | 14.521 | 58.3495 | 5.9225 | 0.76558 | 0.43378 | 7.1219 | 12.21% | 12.99% | 8.776% | 1.139 | 1.1493 | 1.0962
2010-07-03 | 34 | 45.6526 | 14.4616 | 60.1143 | 6.2862 | 0.76558 | 0.4469 | 7.4987 | 12.47% | 13.27% | 8.969% | 1.1425 | 1.153 | 1.0985
2010-07-03 | 35 | 45.9256 | 14.894 | 60.8196 | 6.4346 | 0.76558 | 0.45214 | 7.6523 | 12.58% | 13.39% | 9.046% | 1.1439 | 1.1546 | 1.0995
2010-07-03 | 36 | 47.3585 | 15.3829 | 62.7414 | 6.8477 | 0.76558 | 0.46643 | 8.0797 | 12.88% | 13.7% | 9.259% | 1.1478 | 1.1588 | 1.102
2010-07-03 | 37 | 47.3881 | 15.0204 | 62.4085 | 6.7752 | 0.76558 | 0.46395 | 8.0047 | 12.83% | 13.65% | 9.222% | 1.1471 | 1.158 | 1.1016
2010-07-03 | 38 | 47.3141 | 14.7895 | 62.1036 | 6.7092 | 0.76558 | 0.46169 | 7.9364 | 12.78% | 13.6% | 9.188% | 1.1465 | 1.1574 | 1.1012
2010-07-03 | 39 | 47.0128 | 14.2982 | 61.311 | 6.539 | 0.76558 | 0.45579 | 7.7604 | 12.66% | 13.47% | 9.101% | 1.1449 | 1.1556 | 1.1001
2010-07-03 | 40 | 46.0502 | 13.9603 | 60.0105 | 6.2645 | 0.76558 | 0.44613 | 7.4762 | 12.46% | 13.26% | 8.957% | 1.1423 | 1.1528 | 1.0984
2010-07-03 | 41 | 47.0684 | 13.5767 | 60.6451 | 6.3977 | 0.76558 | 0.45084 | 7.6142 | 12.56% | 13.36% | 9.027% | 1.1436 | 1.1542 | 1.0992
2010-07-03 | 42 | 46.7246 | 13.2316 | 59.9562 | 6.2532 | 0.76558 | 0.44572 | 7.4645 | 12.45% | 13.25% | 8.952% | 1.1422 | 1.1527 | 1.0983
2010-07-03 | 43 | 44.9295 | 12.525 | 57.4544 | 5.7422 | 0.76558 | 0.42712 | 6.9349 | 12.07% | 12.84% | 8.679% | 1.1373 | 1.1474 | 1.095
2010-07-03 | 44 | 42.8015 | 11.7506 | 54.5521 | 5.1768 | 0.76558 | 0.40555 | 6.3479 | 11.64% | 12.38% | 8.367% | 1.1317 | 1.1413 | 1.0913
2010-07-03 | 45 | 38.8355 | 10.6313 | 49.4668 | 4.2566 | 0.76558 | 0.36774 | 5.3899 | 10.9% | 11.59% | 7.834% | 1.1223 | 1.1311 | 1.085
2010-07-03 | 46 | 35.2151 | 9.7046 | 44.9196 | 3.51 | 0.76558 | 0.33394 | 4.6095 | 10.26% | 10.92% | 7.378% | 1.1144 | 1.1226 | 1.0797
2010-07-03 | 47 | 35.1438 | 10.6419 | 45.7858 | 3.6467 | 0.76558 | 0.34038 | 4.7526 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0807
2010-07-03 | 48 | 34.1237 | 11.1642 | 45.2879 | 3.5678 | 0.76558 | 0.33668 | 4.67 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-07-04 | 1 | 32.2677 | 10.2773 | 42.545 | 3.1487 | 0.76558 | 0.31628 | 4.2306 | 9.944% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-07-04 | 2 | 34.1504 | 10.117 | 44.2674 | 3.4088 | 0.76558 | 0.32909 | 4.5035 | 10.17% | 10.82% | 7.315% | 1.1133 | 1.1214 | 1.0789
2010-07-04 | 3 | 32.8541 | 9.7083 | 42.5624 | 3.1513 | 0.76558 | 0.31641 | 4.2333 | 9.946% | 10.58% | 7.151% | 1.1104 | 1.1184 | 1.077
2010-07-04 | 4 | 31.2753 | 9.277 | 40.5523 | 2.8607 | 0.76558 | 0.30147 | 3.9277 | 9.686% | 10.31% | 6.964% | 1.1072 | 1.1149 | 1.0749
2010-07-04 | 5 | 30.1833 | 9.0285 | 39.2118 | 2.6747 | 0.76558 | 0.29151 | 3.7317 | 9.517% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-07-04 | 6 | 30.1083 | 8.7851 | 38.8934 | 2.6314 | 0.76558 | 0.28914 | 3.6861 | 9.477% | 10.08% | 6.814% | 1.1047 | 1.1121 | 1.0731
2010-07-04 | 7 | 29.8924 | 8.6819 | 38.5743 | 2.5884 | 0.76558 | 0.28677 | 3.6407 | 9.438% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-07-04 | 8 | 29.6772 | 8.4823 | 38.1595 | 2.533 | 0.76558 | 0.28368 | 3.5823 | 9.388% | 9.988% | 6.75% | 1.1036 | 1.111 | 1.0724
2010-07-04 | 9 | 29.0729 | 8.5127 | 37.5857 | 2.4574 | 0.76558 | 0.27942 | 3.5024 | 9.318% | 9.915% | 6.7% | 1.1028 | 1.1101 | 1.0718
2010-07-04 | 10 | 29.2569 | 8.6264 | 37.8833 | 2.4965 | 0.76558 | 0.28163 | 3.5437 | 9.354% | 9.953% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-07-04 | 11 | 29.9641 | 8.7052 | 38.6693 | 2.6012 | 0.76558 | 0.28747 | 3.6542 | 9.45% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-07-04 | 12 | 30.5664 | 8.8961 | 39.4626 | 2.709 | 0.76558 | 0.29337 | 3.7679 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-07-04 | 13 | 31.9006 | 9.2275 | 41.1281 | 2.9425 | 0.76558 | 0.30575 | 4.0138 | 9.759% | 10.38% | 7.017% | 1.1081 | 1.1159 | 1.0755
2010-07-04 | 14 | 33.4506 | 9.5969 | 43.0474 | 3.2235 | 0.76558 | 0.32002 | 4.3091 | 10.01% | 10.65% | 7.197% | 1.1112 | 1.1192 | 1.0776
2010-07-04 | 15 | 35.1476 | 9.9316 | 45.0791 | 3.535 | 0.76558 | 0.33512 | 4.6357 | 10.28% | 10.94% | 7.394% | 1.1146 | 1.1229 | 1.0798
2010-07-04 | 16 | 34.6599 | 10.286 | 44.9459 | 3.5141 | 0.76558 | 0.33413 | 4.6138 | 10.27% | 10.92% | 7.381% | 1.1144 | 1.1226 | 1.0797
2010-07-04 | 17 | 36.5103 | 11.4688 | 47.9792 | 4.0044 | 0.76558 | 0.35668 | 5.1267 | 10.69% | 11.37% | 7.683% | 1.1196 | 1.1283 | 1.0832
2010-07-04 | 18 | 39.31 | 12.8335 | 52.1435 | 4.7297 | 0.76558 | 0.38764 | 5.8829 | 11.28% | 12% | 8.112% | 1.1272 | 1.1364 | 1.0883
2010-07-04 | 19 | 42.0386 | 13.946 | 55.9846 | 5.4522 | 0.76558 | 0.4162 | 6.634 | 11.85% | 12.61% | 8.52% | 1.1344 | 1.1443 | 1.0931
2010-07-04 | 20 | 43.174 | 14.6675 | 57.8416 | 5.8199 | 0.76558 | 0.43 | 7.0155 | 12.13% | 12.91% | 8.721% | 1.138 | 1.1482 | 1.0955
2010-07-04 | 21 | 46.2029 | 15.1618 | 61.3647 | 6.5505 | 0.76558 | 0.45619 | 7.7722 | 12.67% | 13.48% | 9.107% | 1.145 | 1.1558 | 1.1002
2010-07-04 | 22 | 46.5758 | 15.3403 | 61.9161 | 6.6687 | 0.76558 | 0.46029 | 7.8946 | 12.75% | 13.57% | 9.168% | 1.1461 | 1.157 | 1.1009
2010-07-04 | 23 | 45.6295 | 14.9637 | 60.5932 | 6.3868 | 0.76558 | 0.45046 | 7.6028 | 12.55% | 13.35% | 9.022% | 1.1435 | 1.1541 | 1.0992
2010-07-04 | 24 | 44.1774 | 14.7413 | 58.9187 | 6.0387 | 0.76558 | 0.43801 | 7.2422 | 12.29% | 13.08% | 8.838% | 1.1401 | 1.1505 | 1.0969
2010-07-04 | 25 | 41.4201 | 14.1856 | 55.6057 | 5.3787 | 0.76558 | 0.41338 | 6.5576 | 11.79% | 12.55% | 8.479% | 1.1337 | 1.1435 | 1.0926
2010-07-04 | 26 | 38.9624 | 13.2263 | 52.1888 | 4.7379 | 0.76558 | 0.38798 | 5.8915 | 11.29% | 12.01% | 8.117% | 1.1273 | 1.1365 | 1.0883
2010-07-04 | 27 | 39.3117 | 13.4343 | 52.7459 | 4.8396 | 0.76558 | 0.39212 | 5.9973 | 11.37% | 12.1% | 8.175% | 1.1283 | 1.1376 | 1.089
2010-07-04 | 28 | 39.6003 | 13.5099 | 53.1103 | 4.9067 | 0.76558 | 0.39483 | 6.0671 | 11.42% | 12.15% | 8.214% | 1.129 | 1.1384 | 1.0895
2010-07-04 | 29 | 39.3865 | 12.9407 | 52.3271 | 4.7631 | 0.76558 | 0.38901 | 5.9177 | 11.31% | 12.03% | 8.131% | 1.1275 | 1.1368 | 1.0885
2010-07-04 | 30 | 38.4698 | 12.3533 | 50.8231 | 4.4932 | 0.76558 | 0.37782 | 5.6366 | 11.09% | 11.8% | 7.974% | 1.1247 | 1.1338 | 1.0867
2010-07-04 | 31 | 41.5723 | 12.4525 | 54.0247 | 5.0772 | 0.76558 | 0.40163 | 6.2444 | 11.56% | 12.3% | 8.31% | 1.1307 | 1.1402 | 1.0906
2010-07-04 | 32 | 42.6503 | 12.0718 | 54.7222 | 5.2091 | 0.76558 | 0.40681 | 6.3815 | 11.66% | 12.41% | 8.385% | 1.132 | 1.1417 | 1.0915
2010-07-04 | 33 | 42.8376 | 12.1149 | 54.9525 | 5.253 | 0.76558 | 0.40852 | 6.4271 | 11.7% | 12.44% | 8.409% | 1.1324 | 1.1421 | 1.0918
2010-07-04 | 34 | 43.7126 | 12.2996 | 56.0122 | 5.4576 | 0.76558 | 0.4164 | 6.6396 | 11.85% | 12.61% | 8.523% | 1.1345 | 1.1443 | 1.0932
2010-07-04 | 35 | 45.0614 | 13.1362 | 58.1976 | 5.8918 | 0.76558 | 0.43265 | 7.09 | 12.18% | 12.96% | 8.759% | 1.1387 | 1.1489 | 1.096
2010-07-04 | 36 | 47.3044 | 14.1212 | 61.4256 | 6.5635 | 0.76558 | 0.45665 | 7.7857 | 12.67% | 13.49% | 9.113% | 1.1451 | 1.1559 | 1.1003
2010-07-04 | 37 | 47.288 | 14.0078 | 61.2958 | 6.5358 | 0.76558 | 0.45568 | 7.757 | 12.66% | 13.46% | 9.099% | 1.1449 | 1.1556 | 1.1001
2010-07-04 | 38 | 47.2865 | 13.6433 | 60.9298 | 6.4579 | 0.76558 | 0.45296 | 7.6765 | 12.6% | 13.41% | 9.059% | 1.1442 | 1.1548 | 1.0996
2010-07-04 | 39 | 46.8847 | 13.0481 | 59.9328 | 6.2483 | 0.76558 | 0.44555 | 7.4595 | 12.45% | 13.24% | 8.949% | 1.1422 | 1.1526 | 1.0983
2010-07-04 | 40 | 45.6358 | 12.5214 | 58.1572 | 5.8836 | 0.76558 | 0.43235 | 7.0815 | 12.18% | 12.96% | 8.755% | 1.1386 | 1.1488 | 1.0959
2010-07-04 | 41 | 46.0422 | 12.2728 | 58.315 | 5.9155 | 0.76558 | 0.43352 | 7.1146 | 12.2% | 12.98% | 8.772% | 1.139 | 1.1492 | 1.0962
2010-07-04 | 42 | 45.957 | 11.7863 | 57.7433 | 5.8001 | 0.76558 | 0.42927 | 6.995 | 12.11% | 12.89% | 8.71% | 1.1378 | 1.148 | 1.0954
2010-07-04 | 43 | 44.3634 | 11.3963 | 55.7597 | 5.4085 | 0.76558 | 0.41452 | 6.5886 | 11.82% | 12.57% | 8.496% | 1.134 | 1.1438 | 1.0928
2010-07-04 | 44 | 41.7447 | 10.7851 | 52.5298 | 4.8001 | 0.76558 | 0.39051 | 5.9561 | 11.34% | 12.06% | 8.152% | 1.1279 | 1.1372 | 1.0888
2010-07-04 | 45 | 37.7081 | 10.0644 | 47.7724 | 3.97 | 0.76558 | 0.35515 | 5.0907 | 10.66% | 11.34% | 7.662% | 1.1193 | 1.1279 | 1.083
2010-07-04 | 46 | 34.4627 | 9.3647 | 43.8273 | 3.3414 | 0.76558 | 0.32582 | 4.4328 | 10.11% | 10.76% | 7.272% | 1.1125 | 1.1206 | 1.0784
2010-07-04 | 47 | 34.6778 | 9.8242 | 44.502 | 3.445 | 0.76558 | 0.33083 | 4.5415 | 10.21% | 10.86% | 7.337% | 1.1136 | 1.1218 | 1.0792
2010-07-04 | 48 | 33.9866 | 10.5854 | 44.572 | 3.4559 | 0.76558 | 0.33135 | 4.5528 | 10.21% | 10.87% | 7.344% | 1.1138 | 1.1219 | 1.0793
2010-07-05 | 1 | 31.9036 | 9.8379 | 41.7414 | 3.0309 | 0.76558 | 0.31031 | 4.1068 | 9.839% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-07-05 | 2 | 33.956 | 9.7808 | 43.7368 | 3.3276 | 0.76558 | 0.32514 | 4.4183 | 10.1% | 10.75% | 7.263% | 1.1124 | 1.1204 | 1.0783
2010-07-05 | 3 | 32.8635 | 9.344 | 42.2075 | 3.0989 | 0.76558 | 0.31378 | 4.1783 | 9.899% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-07-05 | 4 | 31.2671 | 8.8081 | 40.0752 | 2.7937 | 0.76558 | 0.29792 | 3.8572 | 9.625% | 10.24% | 6.92% | 1.1065 | 1.1141 | 1.0743
2010-07-05 | 5 | 29.9161 | 8.4191 | 38.3352 | 2.5564 | 0.76558 | 0.28499 | 3.607 | 9.409% | 10.01% | 6.765% | 1.1039 | 1.1112 | 1.0726
2010-07-05 | 6 | 29.4579 | 8.2367 | 37.6946 | 2.4717 | 0.76558 | 0.28023 | 3.5175 | 9.332% | 9.929% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-07-05 | 7 | 29.3678 | 8.1666 | 37.5344 | 2.4507 | 0.76558 | 0.27904 | 3.4953 | 9.312% | 9.908% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-07-05 | 8 | 29.141 | 8.1079 | 37.2489 | 2.4136 | 0.76558 | 0.27691 | 3.4561 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-07-05 | 9 | 28.9392 | 8.0536 | 36.9928 | 2.3805 | 0.76558 | 0.27501 | 3.4211 | 9.248% | 9.84% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-07-05 | 10 | 28.7971 | 8.0817 | 36.8787 | 2.3658 | 0.76558 | 0.27416 | 3.4056 | 9.235% | 9.826% | 6.64% | 1.1017 | 1.109 | 1.0711
2010-07-05 | 11 | 29.0453 | 8.0635 | 37.1088 | 2.3955 | 0.76558 | 0.27587 | 3.4369 | 9.262% | 9.854% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-07-05 | 12 | 29.6484 | 8.2468 | 37.8952 | 2.4981 | 0.76558 | 0.28172 | 3.5454 | 9.356% | 9.954% | 6.727% | 1.1032 | 1.1105 | 1.0721
2010-07-05 | 13 | 30.5353 | 8.5716 | 39.1069 | 2.6604 | 0.76558 | 0.29073 | 3.7167 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-07-05 | 14 | 31.6581 | 8.8506 | 40.5086 | 2.8545 | 0.76558 | 0.30115 | 3.9212 | 9.68% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-07-05 | 15 | 32.7184 | 9.0284 | 41.7469 | 3.0317 | 0.76558 | 0.31035 | 4.1076 | 9.839% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-07-05 | 16 | 32.304 | 9.3163 | 41.6203 | 3.0133 | 0.76558 | 0.30941 | 4.0883 | 9.823% | 10.45% | 7.063% | 1.1089 | 1.1167 | 1.076
2010-07-05 | 17 | 34.2684 | 10.2672 | 44.5356 | 3.4502 | 0.76558 | 0.33108 | 4.5469 | 10.21% | 10.86% | 7.341% | 1.1137 | 1.1219 | 1.0792
2010-07-05 | 18 | 36.7388 | 11.2967 | 48.0355 | 4.0138 | 0.76558 | 0.3571 | 5.1365 | 10.69% | 11.38% | 7.688% | 1.1197 | 1.1284 | 1.0833
2010-07-05 | 19 | 39.1088 | 12.264 | 51.3729 | 4.5909 | 0.76558 | 0.38191 | 5.7384 | 11.17% | 11.89% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-07-05 | 20 | 40.6616 | 12.8414 | 53.5029 | 4.9795 | 0.76558 | 0.39775 | 6.1429 | 11.48% | 12.22% | 8.255% | 1.1297 | 1.1392 | 1.09
2010-07-05 | 21 | 44.6969 | 13.3903 | 58.0872 | 5.8694 | 0.76558 | 0.43183 | 7.0668 | 12.17% | 12.94% | 8.747% | 1.1385 | 1.1487 | 1.0959
2010-07-05 | 22 | 45.3169 | 13.559 | 58.8759 | 6.0299 | 0.76558 | 0.43769 | 7.2332 | 12.29% | 13.07% | 8.833% | 1.1401 | 1.1504 | 1.0969
2010-07-05 | 23 | 44.2653 | 13.2031 | 57.4684 | 5.745 | 0.76558 | 0.42723 | 6.9378 | 12.07% | 12.85% | 8.68% | 1.1373 | 1.1474 | 1.0951
2010-07-05 | 24 | 42.8755 | 12.9025 | 55.7779 | 5.412 | 0.76558 | 0.41466 | 6.5923 | 11.82% | 12.58% | 8.498% | 1.134 | 1.1438 | 1.0929
2010-07-05 | 25 | 40.5487 | 12.4719 | 53.0206 | 4.8902 | 0.76558 | 0.39416 | 6.0499 | 11.41% | 12.14% | 8.204% | 1.1288 | 1.1382 | 1.0894
2010-07-05 | 26 | 39.0855 | 11.7975 | 50.8829 | 4.5038 | 0.76558 | 0.37827 | 5.6476 | 11.1% | 11.81% | 7.98% | 1.1249 | 1.1339 | 1.0867
2010-07-05 | 27 | 39.503 | 12.2596 | 51.7626 | 4.6609 | 0.76558 | 0.38481 | 5.8113 | 11.23% | 11.95% | 8.072% | 1.1265 | 1.1357 | 1.0878
2010-07-05 | 28 | 40.0205 | 12.4455 | 52.466 | 4.7884 | 0.76558 | 0.39004 | 5.944 | 11.33% | 12.05% | 8.146% | 1.1278 | 1.1371 | 1.0887
2010-07-05 | 29 | 39.4604 | 11.9816 | 51.442 | 4.6033 | 0.76558 | 0.38243 | 5.7513 | 11.18% | 11.9% | 8.039% | 1.1259 | 1.135 | 1.0874
2010-07-05 | 30 | 38.9738 | 11.6297 | 50.6035 | 4.4545 | 0.76558 | 0.37619 | 5.5962 | 11.06% | 11.77% | 7.951% | 1.1243 | 1.1334 | 1.0864
2010-07-05 | 31 | 41.5883 | 11.7711 | 53.3594 | 4.9529 | 0.76558 | 0.39668 | 6.1151 | 11.46% | 12.19% | 8.24% | 1.1294 | 1.1389 | 1.0898
2010-07-05 | 32 | 42.5543 | 11.6262 | 54.1805 | 5.1065 | 0.76558 | 0.40278 | 6.2748 | 11.58% | 12.32% | 8.327% | 1.131 | 1.1405 | 1.0908
2010-07-05 | 33 | 42.7133 | 11.7703 | 54.4836 | 5.1638 | 0.76558 | 0.40504 | 6.3344 | 11.63% | 12.37% | 8.359% | 1.1316 | 1.1412 | 1.0912
2010-07-05 | 34 | 43.5443 | 11.9781 | 55.5224 | 5.3625 | 0.76558 | 0.41276 | 6.5409 | 11.78% | 12.53% | 8.47% | 1.1335 | 1.1433 | 1.0925
2010-07-05 | 35 | 44.1475 | 12.847 | 56.9945 | 5.6507 | 0.76558 | 0.4237 | 6.84 | 12% | 12.77% | 8.629% | 1.1364 | 1.1464 | 1.0944
2010-07-05 | 36 | 46.4594 | 13.9991 | 60.4585 | 6.3584 | 0.76558 | 0.44946 | 7.5735 | 12.53% | 13.33% | 9.007% | 1.1432 | 1.1538 | 1.099
2010-07-05 | 37 | 47.3785 | 13.8683 | 61.2468 | 6.5253 | 0.76558 | 0.45532 | 7.7462 | 12.65% | 13.46% | 9.094% | 1.1448 | 1.1555 | 1.1
2010-07-05 | 38 | 47.3194 | 13.6111 | 60.9305 | 6.4581 | 0.76558 | 0.45296 | 7.6766 | 12.6% | 13.41% | 9.059% | 1.1442 | 1.1548 | 1.0996
2010-07-05 | 39 | 46.9897 | 13.1987 | 60.1884 | 6.3017 | 0.76558 | 0.44745 | 7.5148 | 12.49% | 13.28% | 8.977% | 1.1427 | 1.1532 | 1.0986
2010-07-05 | 40 | 45.8111 | 12.8689 | 58.68 | 5.9898 | 0.76558 | 0.43623 | 7.1916 | 12.26% | 13.04% | 8.812% | 1.1397 | 1.15 | 1.0966
2010-07-05 | 41 | 46.427 | 12.7564 | 59.1834 | 6.0931 | 0.76558 | 0.43998 | 7.2986 | 12.33% | 13.12% | 8.867% | 1.1407 | 1.151 | 1.0973
2010-07-05 | 42 | 46.3251 | 12.2517 | 58.5768 | 5.9688 | 0.76558 | 0.43547 | 7.1698 | 12.24% | 13.02% | 8.801% | 1.1395 | 1.1497 | 1.0965
2010-07-05 | 43 | 44.183 | 11.6938 | 55.8769 | 5.4312 | 0.76558 | 0.4154 | 6.6122 | 11.83% | 12.59% | 8.508% | 1.1342 | 1.144 | 1.093
2010-07-05 | 44 | 41.6254 | 10.9933 | 52.6187 | 4.8163 | 0.76558 | 0.39117 | 5.9731 | 11.35% | 12.08% | 8.162% | 1.1281 | 1.1374 | 1.0889
2010-07-05 | 45 | 36.9594 | 10.1323 | 47.0918 | 3.8577 | 0.76558 | 0.35009 | 4.9733 | 10.56% | 11.24% | 7.593% | 1.1181 | 1.1266 | 1.0822
2010-07-05 | 46 | 33.2369 | 9.3053 | 42.5422 | 3.1483 | 0.76558 | 0.31626 | 4.2301 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-07-05 | 47 | 33.107 | 9.8345 | 42.9415 | 3.2077 | 0.76558 | 0.31923 | 4.2925 | 9.996% | 10.64% | 7.187% | 1.1111 | 1.119 | 1.0774
2010-07-05 | 48 | 32.258 | 10.6217 | 42.8797 | 3.1984 | 0.76558 | 0.31877 | 4.2828 | 9.988% | 10.63% | 7.181% | 1.111 | 1.1189 | 1.0774
2010-07-06 | 1 | 30.3755 | 9.845 | 40.2205 | 2.814 | 0.76558 | 0.299 | 3.8786 | 9.643% | 10.26% | 6.934% | 1.1067 | 1.1143 | 1.0745
2010-07-06 | 2 | 32.6878 | 9.7258 | 42.4136 | 3.1293 | 0.76558 | 0.31531 | 4.2102 | 9.926% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-07-06 | 3 | 31.9703 | 9.3489 | 41.3191 | 2.9699 | 0.76558 | 0.30717 | 4.0426 | 9.784% | 10.41% | 7.035% | 1.1084 | 1.1162 | 1.0757
2010-07-06 | 4 | 30.602 | 9.1421 | 39.7441 | 2.7478 | 0.76558 | 0.29546 | 3.8088 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-07-06 | 5 | 30.0711 | 8.8431 | 38.9142 | 2.6342 | 0.76558 | 0.28929 | 3.6891 | 9.48% | 10.09% | 6.816% | 1.1047 | 1.1122 | 1.0731
2010-07-06 | 6 | 29.5528 | 8.6748 | 38.2275 | 2.5421 | 0.76558 | 0.28419 | 3.5918 | 9.396% | 9.997% | 6.756% | 1.1037 | 1.1111 | 1.0725
2010-07-06 | 7 | 29.2934 | 8.5933 | 37.8867 | 2.4969 | 0.76558 | 0.28165 | 3.5442 | 9.355% | 9.953% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-07-06 | 8 | 30.2267 | 8.5117 | 38.7384 | 2.6105 | 0.76558 | 0.28799 | 3.664 | 9.458% | 10.06% | 6.801% | 1.1045 | 1.1119 | 1.073
2010-07-06 | 9 | 30.6699 | 8.623 | 39.2929 | 2.6857 | 0.76558 | 0.29211 | 3.7434 | 9.527% | 10.14% | 6.85% | 1.1053 | 1.1128 | 1.0735
2010-07-06 | 10 | 31.6027 | 8.7142 | 40.3169 | 2.8275 | 0.76558 | 0.29972 | 3.8928 | 9.656% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-07-06 | 11 | 32.3651 | 8.8663 | 41.2313 | 2.9573 | 0.76558 | 0.30652 | 4.0294 | 9.773% | 10.4% | 7.026% | 1.1083 | 1.116 | 1.0756
2010-07-06 | 12 | 33.4103 | 9.4392 | 42.8495 | 3.1939 | 0.76558 | 0.31855 | 4.2781 | 9.984% | 10.62% | 7.178% | 1.1109 | 1.1189 | 1.0773
2010-07-06 | 13 | 35.0493 | 10.4303 | 45.4796 | 3.5981 | 0.76558 | 0.3381 | 4.7017 | 10.34% | 11% | 7.433% | 1.1153 | 1.1236 | 1.0803
2010-07-06 | 14 | 38.2223 | 11.5769 | 49.7992 | 4.314 | 0.76558 | 0.37021 | 5.4498 | 10.94% | 11.64% | 7.868% | 1.1229 | 1.1318 | 1.0854
2010-07-06 | 15 | 41.7973 | 13.0495 | 54.8469 | 5.2329 | 0.76558 | 0.40774 | 6.4062 | 11.68% | 12.43% | 8.398% | 1.1322 | 1.1419 | 1.0917
2010-07-06 | 16 | 41.811 | 13.7647 | 55.5756 | 5.3728 | 0.76558 | 0.41316 | 6.5516 | 11.79% | 12.54% | 8.476% | 1.1336 | 1.1434 | 1.0926
2010-07-06 | 17 | 43.9219 | 15.0637 | 58.9856 | 6.0524 | 0.76558 | 0.43851 | 7.2565 | 12.3% | 13.09% | 8.845% | 1.1403 | 1.1506 | 1.097
2010-07-06 | 18 | 46.0774 | 16.0991 | 62.1764 | 6.7249 | 0.76558 | 0.46223 | 7.9527 | 12.79% | 13.61% | 9.196% | 1.1467 | 1.1575 | 1.1013
2010-07-06 | 19 | 46.7636 | 16.2807 | 63.0443 | 6.914 | 0.76558 | 0.46868 | 8.1482 | 12.92% | 13.75% | 9.293% | 1.1484 | 1.1594 | 1.1024
2010-07-06 | 20 | 46.6053 | 16.2544 | 62.8597 | 6.8735 | 0.76558 | 0.46731 | 8.1064 | 12.9% | 13.72% | 9.272% | 1.1481 | 1.159 | 1.1022
2010-07-06 | 21 | 47.1633 | 15.8629 | 63.0263 | 6.91 | 0.76558 | 0.46854 | 8.1441 | 12.92% | 13.75% | 9.291% | 1.1484 | 1.1594 | 1.1024
2010-07-06 | 22 | 46.2732 | 15.3461 | 61.6193 | 6.6049 | 0.76558 | 0.45809 | 7.8286 | 12.7% | 13.52% | 9.135% | 1.1455 | 1.1563 | 1.1005
2010-07-06 | 23 | 47.2353 | 15.0805 | 62.3158 | 6.7551 | 0.76558 | 0.46326 | 7.9839 | 12.81% | 13.63% | 9.212% | 1.1469 | 1.1578 | 1.1015
2010-07-06 | 24 | 46.8762 | 14.222 | 61.0982 | 6.4937 | 0.76558 | 0.45421 | 7.7135 | 12.62% | 13.43% | 9.077% | 1.1445 | 1.1552 | 1.0998
2010-07-06 | 25 | 43.3586 | 13.7362 | 57.0948 | 5.6706 | 0.76558 | 0.42445 | 6.8606 | 12.02% | 12.79% | 8.64% | 1.1366 | 1.1466 | 1.0946
2010-07-06 | 26 | 40.0255 | 12.7552 | 52.7808 | 4.846 | 0.76558 | 0.39238 | 6.004 | 11.38% | 12.1% | 8.179% | 1.1284 | 1.1377 | 1.0891
2010-07-06 | 27 | 40.0956 | 12.9959 | 53.0915 | 4.9033 | 0.76558 | 0.39469 | 6.0635 | 11.42% | 12.15% | 8.212% | 1.1289 | 1.1383 | 1.0895
2010-07-06 | 28 | 40.729 | 13.3762 | 54.1052 | 5.0923 | 0.76558 | 0.40222 | 6.2601 | 11.57% | 12.31% | 8.319% | 1.1308 | 1.1404 | 1.0907
2010-07-06 | 29 | 39.6804 | 13.2264 | 52.9068 | 4.8692 | 0.76558 | 0.39332 | 6.0281 | 11.39% | 12.12% | 8.192% | 1.1286 | 1.138 | 1.0892
2010-07-06 | 30 | 39.3076 | 12.9884 | 52.2961 | 4.7574 | 0.76558 | 0.38878 | 5.9118 | 11.3% | 12.03% | 8.128% | 1.1275 | 1.1367 | 1.0885
2010-07-06 | 31 | 41.5216 | 13.1993 | 54.7209 | 5.2088 | 0.76558 | 0.4068 | 6.3812 | 11.66% | 12.41% | 8.385% | 1.132 | 1.1417 | 1.0915
2010-07-06 | 32 | 42.4859 | 13.099 | 55.5849 | 5.3746 | 0.76558 | 0.41322 | 6.5534 | 11.79% | 12.54% | 8.477% | 1.1337 | 1.1434 | 1.0926
2010-07-06 | 33 | 42.6597 | 13.091 | 55.7507 | 5.4067 | 0.76558 | 0.41446 | 6.5868 | 11.81% | 12.57% | 8.495% | 1.134 | 1.1438 | 1.0928
2010-07-06 | 34 | 43.9573 | 13.2686 | 57.2259 | 5.6967 | 0.76558 | 0.42542 | 6.8877 | 12.04% | 12.81% | 8.654% | 1.1368 | 1.1469 | 1.0947
2010-07-06 | 35 | 44.5748 | 14.2813 | 58.856 | 6.0258 | 0.76558 | 0.43754 | 7.2289 | 12.28% | 13.07% | 8.831% | 1.14 | 1.1503 | 1.0969
2010-07-06 | 36 | 47.1587 | 15.4698 | 62.6284 | 6.823 | 0.76558 | 0.46559 | 8.0542 | 12.86% | 13.68% | 9.247% | 1.1476 | 1.1585 | 1.1019
2010-07-06 | 37 | 46.5265 | 14.8678 | 61.3943 | 6.5568 | 0.76558 | 0.45641 | 7.7788 | 12.67% | 13.48% | 9.11% | 1.1451 | 1.1558 | 1.1002
2010-07-06 | 38 | 47.1846 | 15.4622 | 62.6469 | 6.8271 | 0.76558 | 0.46572 | 8.0584 | 12.86% | 13.69% | 9.249% | 1.1476 | 1.1586 | 1.1019
2010-07-06 | 39 | 45.9488 | 14.8914 | 60.8402 | 6.439 | 0.76558 | 0.45229 | 7.6568 | 12.59% | 13.39% | 9.049% | 1.144 | 1.1546 | 1.0995
2010-07-06 | 40 | 47.1379 | 14.5018 | 61.6397 | 6.6093 | 0.76558 | 0.45824 | 7.8331 | 12.71% | 13.52% | 9.137% | 1.1456 | 1.1564 | 1.1006
2010-07-06 | 41 | 47.3072 | 14.352 | 61.6592 | 6.6135 | 0.76558 | 0.45838 | 7.8375 | 12.71% | 13.52% | 9.139% | 1.1456 | 1.1564 | 1.1006
2010-07-06 | 42 | 47.1079 | 13.8597 | 60.9676 | 6.466 | 0.76558 | 0.45324 | 7.6848 | 12.6% | 13.41% | 9.063% | 1.1442 | 1.1549 | 1.0997
2010-07-06 | 43 | 47.0736 | 13.4048 | 60.4784 | 6.3626 | 0.76558 | 0.4496 | 7.5778 | 12.53% | 13.33% | 9.009% | 1.1432 | 1.1538 | 1.099
2010-07-06 | 44 | 47.0878 | 12.7434 | 59.8312 | 6.2272 | 0.76558 | 0.44479 | 7.4375 | 12.43% | 13.23% | 8.938% | 1.142 | 1.1524 | 1.0982
2010-07-06 | 45 | 43.3663 | 11.5069 | 54.8732 | 5.2379 | 0.76558 | 0.40793 | 6.4114 | 11.68% | 12.43% | 8.401% | 1.1323 | 1.142 | 1.0917
2010-07-06 | 46 | 39.2852 | 10.2933 | 49.5784 | 4.2758 | 0.76558 | 0.36857 | 5.41 | 10.91% | 11.61% | 7.846% | 1.1225 | 1.1314 | 1.0851
2010-07-06 | 47 | 38.6236 | 10.7477 | 49.3713 | 4.2402 | 0.76558 | 0.36703 | 5.3728 | 10.88% | 11.58% | 7.824% | 1.1221 | 1.131 | 1.0849
2010-07-06 | 48 | 37.4148 | 11.3287 | 48.7435 | 4.133 | 0.76558 | 0.36236 | 5.261 | 10.79% | 11.48% | 7.76% | 1.121 | 1.1297 | 1.0841
2010-07-07 | 1 | 35.4731 | 10.4757 | 45.9488 | 3.6727 | 0.76558 | 0.34159 | 4.7798 | 10.4% | 11.07% | 7.479% | 1.1161 | 1.1245 | 1.0808
2010-07-07 | 2 | 37.2247 | 10.4329 | 47.6576 | 3.9509 | 0.76558 | 0.35429 | 5.0708 | 10.64% | 11.32% | 7.65% | 1.1191 | 1.1277 | 1.0828
2010-07-07 | 3 | 35.6577 | 10.1397 | 45.7974 | 3.6485 | 0.76558 | 0.34046 | 4.7546 | 10.38% | 11.05% | 7.464% | 1.1158 | 1.1242 | 1.0807
2010-07-07 | 4 | 34.4214 | 9.7932 | 44.2146 | 3.4007 | 0.76558 | 0.3287 | 4.495 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-07-07 | 5 | 33.4004 | 9.476 | 42.8764 | 3.198 | 0.76558 | 0.31875 | 4.2823 | 9.987% | 10.63% | 7.181% | 1.111 | 1.1189 | 1.0774
2010-07-07 | 6 | 32.795 | 9.3155 | 42.1105 | 3.0847 | 0.76558 | 0.31305 | 4.1634 | 9.887% | 10.52% | 7.109% | 1.1097 | 1.1176 | 1.0765
2010-07-07 | 7 | 32.4518 | 9.4427 | 41.8945 | 3.0531 | 0.76558 | 0.31145 | 4.1302 | 9.859% | 10.49% | 7.088% | 1.1094 | 1.1172 | 1.0763
2010-07-07 | 8 | 32.1336 | 9.6243 | 41.7579 | 3.0333 | 0.76558 | 0.31043 | 4.1093 | 9.841% | 10.47% | 7.075% | 1.1091 | 1.117 | 1.0761
2010-07-07 | 9 | 32.8233 | 9.6216 | 42.445 | 3.1339 | 0.76558 | 0.31554 | 4.215 | 9.931% | 10.57% | 7.14% | 1.1103 | 1.1181 | 1.0769
2010-07-07 | 10 | 33.2684 | 9.588 | 42.8564 | 3.195 | 0.76558 | 0.3186 | 4.2791 | 9.985% | 10.62% | 7.179% | 1.1109 | 1.1189 | 1.0773
2010-07-07 | 11 | 34.0133 | 9.9095 | 43.9228 | 3.3559 | 0.76558 | 0.32653 | 4.448 | 10.13% | 10.78% | 7.281% | 1.1127 | 1.1208 | 1.0785
2010-07-07 | 12 | 34.6807 | 10.3958 | 45.0765 | 3.5346 | 0.76558 | 0.3351 | 4.6352 | 10.28% | 10.94% | 7.394% | 1.1146 | 1.1229 | 1.0798
2010-07-07 | 13 | 36.1382 | 11.2217 | 47.3598 | 3.9017 | 0.76558 | 0.35208 | 5.0194 | 10.6% | 11.28% | 7.62% | 1.1185 | 1.1271 | 1.0825
2010-07-07 | 14 | 40.0249 | 12.5632 | 52.5882 | 4.8107 | 0.76558 | 0.39095 | 5.9673 | 11.35% | 12.07% | 8.159% | 1.128 | 1.1373 | 1.0888
2010-07-07 | 15 | 44.1585 | 14.1234 | 58.2819 | 5.9088 | 0.76558 | 0.43327 | 7.1077 | 12.2% | 12.98% | 8.768% | 1.1389 | 1.1491 | 1.0961
2010-07-07 | 16 | 43.6363 | 14.7206 | 58.3569 | 5.9241 | 0.76558 | 0.43383 | 7.1235 | 12.21% | 12.99% | 8.777% | 1.139 | 1.1493 | 1.0962
2010-07-07 | 17 | 44.9441 | 15.9102 | 60.8543 | 6.4419 | 0.76558 | 0.4524 | 7.6599 | 12.59% | 13.39% | 9.05% | 1.144 | 1.1546 | 1.0995
2010-07-07 | 18 | 46.291 | 16.3173 | 62.6083 | 6.8187 | 0.76558 | 0.46544 | 8.0497 | 12.86% | 13.68% | 9.244% | 1.1475 | 1.1585 | 1.1019
2010-07-07 | 19 | 42.944 | 15.0523 | 57.9963 | 5.8511 | 0.76558 | 0.43115 | 7.0478 | 12.15% | 12.93% | 8.737% | 1.1383 | 1.1485 | 1.0957
2010-07-07 | 20 | 42.5835 | 14.8791 | 57.4626 | 5.7439 | 0.76558 | 0.42718 | 6.9366 | 12.07% | 12.84% | 8.679% | 1.1373 | 1.1474 | 1.095
2010-07-07 | 21 | 47.0802 | 16.5383 | 63.6185 | 7.0405 | 0.76558 | 0.47295 | 8.279 | 13.01% | 13.85% | 9.357% | 1.1496 | 1.1607 | 1.1032
2010-07-07 | 22 | 47.1662 | 16.6647 | 63.8309 | 7.0876 | 0.76558 | 0.47453 | 8.3277 | 13.05% | 13.88% | 9.38% | 1.15 | 1.1612 | 1.1035
2010-07-07 | 23 | 47.2031 | 16.4648 | 63.6679 | 7.0514 | 0.76558 | 0.47331 | 8.2903 | 13.02% | 13.85% | 9.362% | 1.1497 | 1.1608 | 1.1033
2010-07-07 | 24 | 47.2368 | 16.0092 | 63.2461 | 6.9583 | 0.76558 | 0.47018 | 8.194 | 12.96% | 13.78% | 9.315% | 1.1488 | 1.1599 | 1.1027
2010-07-07 | 25 | 46.3192 | 15.5367 | 61.8559 | 6.6557 | 0.76558 | 0.45984 | 7.8812 | 12.74% | 13.56% | 9.161% | 1.146 | 1.1568 | 1.1008
2010-07-07 | 26 | 44.0938 | 14.3046 | 58.3984 | 5.9325 | 0.76558 | 0.43414 | 7.1322 | 12.21% | 12.99% | 8.781% | 1.1391 | 1.1494 | 1.0963
2010-07-07 | 27 | 43.3461 | 14.5536 | 57.8997 | 5.8316 | 0.76558 | 0.43043 | 7.0276 | 12.14% | 12.91% | 8.727% | 1.1381 | 1.1483 | 1.0956
2010-07-07 | 28 | 43.0636 | 14.7036 | 57.7672 | 5.8049 | 0.76558 | 0.42945 | 7 | 12.12% | 12.89% | 8.713% | 1.1379 | 1.148 | 1.0954
2010-07-07 | 29 | 42.3766 | 14.5688 | 56.9454 | 5.6409 | 0.76558 | 0.42334 | 6.8299 | 11.99% | 12.76% | 8.623% | 1.1363 | 1.1463 | 1.0944
2010-07-07 | 30 | 41.7881 | 14.141 | 55.9291 | 5.4414 | 0.76558 | 0.41578 | 6.6228 | 11.84% | 12.6% | 8.514% | 1.1343 | 1.1442 | 1.0931
2010-07-07 | 31 | 44.1872 | 14.1878 | 58.3751 | 5.9277 | 0.76558 | 0.43397 | 7.1273 | 12.21% | 12.99% | 8.779% | 1.1391 | 1.1493 | 1.0962
2010-07-07 | 32 | 45.0388 | 14.1507 | 59.1895 | 6.0943 | 0.76558 | 0.44002 | 7.2999 | 12.33% | 13.12% | 8.867% | 1.1407 | 1.151 | 1.0973
2010-07-07 | 33 | 45.1336 | 14.3154 | 59.449 | 6.1479 | 0.76558 | 0.44195 | 7.3554 | 12.37% | 13.16% | 8.896% | 1.1412 | 1.1516 | 1.0976
2010-07-07 | 34 | 45.7672 | 14.4354 | 60.2027 | 6.3047 | 0.76558 | 0.44755 | 7.5179 | 12.49% | 13.29% | 8.979% | 1.1427 | 1.1532 | 1.0986
2010-07-07 | 35 | 46.3837 | 15.1077 | 61.4914 | 6.5775 | 0.76558 | 0.45713 | 7.8003 | 12.69% | 13.5% | 9.121% | 1.1453 | 1.156 | 1.1004
2010-07-07 | 36 | 46.8842 | 15.5745 | 62.4586 | 6.7861 | 0.76558 | 0.46433 | 8.016 | 12.83% | 13.66% | 9.228% | 1.1472 | 1.1582 | 1.1017
2010-07-07 | 37 | 45.7046 | 14.5083 | 60.2129 | 6.3069 | 0.76558 | 0.44763 | 7.5201 | 12.49% | 13.29% | 8.98% | 1.1427 | 1.1532 | 1.0987
2010-07-07 | 38 | 46.1353 | 14.4009 | 60.5362 | 6.3748 | 0.76558 | 0.45003 | 7.5904 | 12.54% | 13.34% | 9.015% | 1.1434 | 1.1539 | 1.0991
2010-07-07 | 39 | 47.0971 | 15.1516 | 62.2486 | 6.7405 | 0.76558 | 0.46276 | 7.9689 | 12.8% | 13.62% | 9.204% | 1.1468 | 1.1577 | 1.1014
2010-07-07 | 40 | 47.195 | 15.9592 | 63.1542 | 6.9381 | 0.76558 | 0.4695 | 8.1731 | 12.94% | 13.77% | 9.305% | 1.1487 | 1.1597 | 1.1026
2010-07-07 | 41 | 47.1936 | 15.5875 | 62.7812 | 6.8564 | 0.76558 | 0.46672 | 8.0887 | 12.88% | 13.71% | 9.264% | 1.1479 | 1.1589 | 1.1021
2010-07-07 | 42 | 47.0061 | 14.7789 | 61.785 | 6.6405 | 0.76558 | 0.45932 | 7.8654 | 12.73% | 13.55% | 9.153% | 1.1459 | 1.1567 | 1.1008
2010-07-07 | 43 | 47.0468 | 14.1983 | 61.2452 | 6.525 | 0.76558 | 0.4553 | 7.7458 | 12.65% | 13.46% | 9.093% | 1.1448 | 1.1555 | 1.1
2010-07-07 | 44 | 46.9302 | 13.352 | 60.2822 | 6.3214 | 0.76558 | 0.44815 | 7.5351 | 12.5% | 13.3% | 8.987% | 1.1429 | 1.1534 | 1.0987
2010-07-07 | 45 | 44.8165 | 12.0574 | 56.874 | 5.6268 | 0.76558 | 0.42281 | 6.8152 | 11.98% | 12.75% | 8.616% | 1.1361 | 1.1461 | 1.0943
2010-07-07 | 46 | 39.7016 | 10.878 | 50.5796 | 4.4503 | 0.76558 | 0.37601 | 5.5919 | 11.06% | 11.76% | 7.949% | 1.1243 | 1.1333 | 1.0864
2010-07-07 | 47 | 37.9464 | 11.0268 | 48.9732 | 4.1721 | 0.76558 | 0.36407 | 5.3017 | 10.83% | 11.52% | 7.784% | 1.1214 | 1.1302 | 1.0844
2010-07-07 | 48 | 36.5808 | 11.5892 | 48.17 | 4.0363 | 0.76558 | 0.3581 | 5.16 | 10.71% | 11.4% | 7.702% | 1.12 | 1.1286 | 1.0834
2010-07-08 | 1 | 34.6112 | 10.9446 | 45.5558 | 3.6101 | 0.76558 | 0.33867 | 4.7144 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-07-08 | 2 | 36.0751 | 10.5749 | 46.65 | 3.7856 | 0.76558 | 0.3468 | 4.898 | 10.5% | 11.17% | 7.549% | 1.1173 | 1.1258 | 1.0817
2010-07-08 | 3 | 34.5472 | 10.2168 | 44.7641 | 3.4857 | 0.76558 | 0.33278 | 4.5841 | 10.24% | 10.9% | 7.363% | 1.1141 | 1.1223 | 1.0795
2010-07-08 | 4 | 33.7078 | 10.0945 | 43.8023 | 3.3376 | 0.76558 | 0.32563 | 4.4288 | 10.11% | 10.76% | 7.27% | 1.1125 | 1.1205 | 1.0784
2010-07-08 | 5 | 34.0073 | 9.7821 | 43.7894 | 3.3356 | 0.76558 | 0.32554 | 4.4267 | 10.11% | 10.76% | 7.268% | 1.1125 | 1.1205 | 1.0784
2010-07-08 | 6 | 34.0032 | 9.4947 | 43.4979 | 3.2913 | 0.76558 | 0.32337 | 4.3803 | 10.07% | 10.71% | 7.24% | 1.112 | 1.12 | 1.0781
2010-07-08 | 7 | 33.4079 | 9.4365 | 42.8444 | 3.1932 | 0.76558 | 0.31851 | 4.2773 | 9.983% | 10.62% | 7.178% | 1.1109 | 1.1188 | 1.0773
2010-07-08 | 8 | 33.2222 | 9.3879 | 42.6101 | 3.1583 | 0.76558 | 0.31677 | 4.2407 | 9.952% | 10.59% | 7.156% | 1.1105 | 1.1184 | 1.0771
2010-07-08 | 9 | 33.7789 | 9.4857 | 43.2646 | 3.2561 | 0.76558 | 0.32163 | 4.3433 | 10.04% | 10.68% | 7.218% | 1.1116 | 1.1196 | 1.0778
2010-07-08 | 10 | 35.0068 | 9.589 | 44.5958 | 3.4596 | 0.76558 | 0.33153 | 4.5567 | 10.22% | 10.87% | 7.347% | 1.1138 | 1.122 | 1.0793
2010-07-08 | 11 | 35.8613 | 9.793 | 45.6543 | 3.6258 | 0.76558 | 0.3394 | 4.7307 | 10.36% | 11.03% | 7.45% | 1.1156 | 1.1239 | 1.0805
2010-07-08 | 12 | 36.6652 | 10.1431 | 46.8082 | 3.8114 | 0.76558 | 0.34798 | 4.9249 | 10.52% | 11.19% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-07-08 | 13 | 37.6809 | 11.12 | 48.801 | 4.1428 | 0.76558 | 0.36279 | 5.2711 | 10.8% | 11.49% | 7.766% | 1.1211 | 1.1298 | 1.0842
2010-07-08 | 14 | 41.6381 | 12.5684 | 54.2065 | 5.1114 | 0.76558 | 0.40298 | 6.2799 | 11.59% | 12.33% | 8.33% | 1.131 | 1.1406 | 1.0909
2010-07-08 | 15 | 46.0727 | 14.0089 | 60.0816 | 6.2794 | 0.76558 | 0.44665 | 7.4916 | 12.47% | 13.27% | 8.965% | 1.1425 | 1.153 | 1.0985
2010-07-08 | 16 | 45.663 | 14.4881 | 60.1512 | 6.2939 | 0.76558 | 0.44717 | 7.5067 | 12.48% | 13.28% | 8.973% | 1.1426 | 1.1531 | 1.0986
2010-07-08 | 17 | 47.1147 | 15.8729 | 62.9876 | 6.9015 | 0.76558 | 0.46826 | 8.1354 | 12.92% | 13.74% | 9.286% | 1.1483 | 1.1593 | 1.1024
2010-07-08 | 18 | 46.9924 | 16.3414 | 63.3338 | 6.9776 | 0.76558 | 0.47083 | 8.214 | 12.97% | 13.8% | 9.325% | 1.149 | 1.1601 | 1.1028
2010-07-08 | 19 | 46.7166 | 16.0601 | 62.7767 | 6.8554 | 0.76558 | 0.46669 | 8.0876 | 12.88% | 13.71% | 9.263% | 1.1479 | 1.1589 | 1.1021
2010-07-08 | 20 | 47.1318 | 16.6072 | 63.739 | 7.0672 | 0.76558 | 0.47384 | 8.3066 | 13.03% | 13.87% | 9.37% | 1.1499 | 1.161 | 1.1034
2010-07-08 | 21 | 46.4945 | 16.0591 | 62.5536 | 6.8067 | 0.76558 | 0.46503 | 8.0373 | 12.85% | 13.67% | 9.238% | 1.1474 | 1.1584 | 1.1018
2010-07-08 | 22 | 46.744 | 15.9527 | 62.6967 | 6.8379 | 0.76558 | 0.46609 | 8.0696 | 12.87% | 13.69% | 9.254% | 1.1477 | 1.1587 | 1.102
2010-07-08 | 23 | 47.227 | 16.5888 | 63.8158 | 7.0842 | 0.76558 | 0.47441 | 8.3242 | 13.04% | 13.88% | 9.379% | 1.15 | 1.1612 | 1.1035
2010-07-08 | 24 | 47.1251 | 16.2322 | 63.3573 | 6.9828 | 0.76558 | 0.47101 | 8.2193 | 12.97% | 13.8% | 9.328% | 1.1491 | 1.1601 | 1.1029
2010-07-08 | 25 | 45.5412 | 15.6094 | 61.1505 | 6.5048 | 0.76558 | 0.4546 | 7.725 | 12.63% | 13.44% | 9.083% | 1.1446 | 1.1553 | 1.0999
2010-07-08 | 26 | 44.7036 | 14.8631 | 59.5667 | 6.1722 | 0.76558 | 0.44283 | 7.3806 | 12.39% | 13.18% | 8.909% | 1.1414 | 1.1519 | 1.0978
2010-07-08 | 27 | 44.4892 | 15.0326 | 59.5217 | 6.1629 | 0.76558 | 0.44249 | 7.371 | 12.38% | 13.18% | 8.904% | 1.1413 | 1.1518 | 1.0977
2010-07-08 | 28 | 43.3346 | 15.0875 | 58.4222 | 5.9373 | 0.76558 | 0.43432 | 7.1372 | 12.22% | 13% | 8.784% | 1.1392 | 1.1494 | 1.0963
2010-07-08 | 29 | 42.0751 | 14.7098 | 56.7848 | 5.6092 | 0.76558 | 0.42215 | 6.7969 | 11.97% | 12.74% | 8.606% | 1.136 | 1.1459 | 1.0942
2010-07-08 | 30 | 41.7611 | 14.1335 | 55.8946 | 5.4347 | 0.76558 | 0.41553 | 6.6158 | 11.84% | 12.59% | 8.51% | 1.1343 | 1.1441 | 1.093
2010-07-08 | 31 | 44.4726 | 13.9345 | 58.4071 | 5.9342 | 0.76558 | 0.43421 | 7.134 | 12.21% | 13% | 8.782% | 1.1391 | 1.1494 | 1.0963
2010-07-08 | 32 | 44.5635 | 13.5035 | 58.067 | 5.8653 | 0.76558 | 0.43168 | 7.0626 | 12.16% | 12.94% | 8.745% | 1.1385 | 1.1486 | 1.0958
2010-07-08 | 33 | 44.1729 | 13.6043 | 57.7772 | 5.8069 | 0.76558 | 0.42952 | 7.002 | 12.12% | 12.89% | 8.714% | 1.1379 | 1.148 | 1.0955
2010-07-08 | 34 | 45.145 | 13.9383 | 59.0833 | 6.0725 | 0.76558 | 0.43923 | 7.2773 | 12.32% | 13.11% | 8.856% | 1.1405 | 1.1508 | 1.0972
2010-07-08 | 35 | 46.0789 | 14.7354 | 60.8143 | 6.4335 | 0.76558 | 0.4521 | 7.6512 | 12.58% | 13.39% | 9.046% | 1.1439 | 1.1546 | 1.0995
2010-07-08 | 36 | 47.0111 | 15.147 | 62.1581 | 6.721 | 0.76558 | 0.46209 | 7.9486 | 12.79% | 13.61% | 9.194% | 1.1466 | 1.1575 | 1.1013
2010-07-08 | 37 | 45.9736 | 14.1889 | 60.1625 | 6.2963 | 0.76558 | 0.44726 | 7.5092 | 12.48% | 13.28% | 8.974% | 1.1426 | 1.1531 | 1.0986
2010-07-08 | 38 | 46.8768 | 14.2874 | 61.1642 | 6.5077 | 0.76558 | 0.4547 | 7.728 | 12.63% | 13.44% | 9.084% | 1.1446 | 1.1553 | 1.0999
2010-07-08 | 39 | 47.1377 | 15.7635 | 62.9012 | 6.8826 | 0.76558 | 0.46761 | 8.1158 | 12.9% | 13.73% | 9.277% | 1.1481 | 1.1591 | 1.1023
2010-07-08 | 40 | 47.1361 | 14.911 | 62.0471 | 6.697 | 0.76558 | 0.46127 | 7.9238 | 12.77% | 13.59% | 9.182% | 1.1464 | 1.1572 | 1.1011
2010-07-08 | 41 | 47.3213 | 14.596 | 61.9173 | 6.669 | 0.76558 | 0.4603 | 7.8949 | 12.75% | 13.57% | 9.168% | 1.1461 | 1.157 | 1.1009
2010-07-08 | 42 | 47.0895 | 14.1333 | 61.2229 | 6.5202 | 0.76558 | 0.45514 | 7.7409 | 12.64% | 13.45% | 9.091% | 1.1447 | 1.1554 | 1.1
2010-07-08 | 43 | 47.0749 | 13.4534 | 60.5283 | 6.3731 | 0.76558 | 0.44997 | 7.5887 | 12.54% | 13.34% | 9.014% | 1.1433 | 1.1539 | 1.0991
2010-07-08 | 44 | 46.9875 | 12.842 | 59.8295 | 6.2268 | 0.76558 | 0.44478 | 7.4372 | 12.43% | 13.23% | 8.938% | 1.142 | 1.1524 | 1.0981
2010-07-08 | 45 | 46.1791 | 11.4734 | 57.6525 | 5.7819 | 0.76558 | 0.4286 | 6.9761 | 12.1% | 12.87% | 8.7% | 1.1377 | 1.1478 | 1.0953
2010-07-08 | 46 | 41.9705 | 10.3863 | 52.3568 | 4.7685 | 0.76558 | 0.38923 | 5.9233 | 11.31% | 12.04% | 8.134% | 1.1276 | 1.1368 | 1.0885
2010-07-08 | 47 | 40.3171 | 10.8026 | 51.1197 | 4.5458 | 0.76558 | 0.38003 | 5.6914 | 11.13% | 11.85% | 8.005% | 1.1253 | 1.1344 | 1.087
2010-07-08 | 48 | 38.3348 | 11.3975 | 49.7323 | 4.3024 | 0.76558 | 0.36972 | 5.4377 | 10.93% | 11.63% | 7.862% | 1.1228 | 1.1317 | 1.0853
2010-07-09 | 1 | 35.9749 | 10.6301 | 46.605 | 3.7783 | 0.76558 | 0.34647 | 4.8904 | 10.49% | 11.16% | 7.545% | 1.1172 | 1.1257 | 1.0816
2010-07-09 | 2 | 37.14 | 10.5137 | 47.6536 | 3.9503 | 0.76558 | 0.35426 | 5.0701 | 10.64% | 11.32% | 7.65% | 1.1191 | 1.1277 | 1.0828
2010-07-09 | 3 | 35.9185 | 10.0926 | 46.0111 | 3.6827 | 0.76558 | 0.34205 | 4.7903 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-07-09 | 4 | 34.0062 | 9.747 | 43.7531 | 3.3301 | 0.76558 | 0.32527 | 4.4209 | 10.1% | 10.75% | 7.265% | 1.1124 | 1.1205 | 1.0783
2010-07-09 | 5 | 33.0862 | 9.4904 | 42.5766 | 3.1534 | 0.76558 | 0.31652 | 4.2355 | 9.948% | 10.58% | 7.153% | 1.1105 | 1.1184 | 1.077
2010-07-09 | 6 | 32.825 | 9.4025 | 42.2275 | 3.1019 | 0.76558 | 0.31392 | 4.1814 | 9.902% | 10.54% | 7.12% | 1.1099 | 1.1178 | 1.0767
2010-07-09 | 7 | 33.0845 | 9.3136 | 42.3981 | 3.127 | 0.76558 | 0.31519 | 4.2078 | 9.924% | 10.56% | 7.136% | 1.1102 | 1.1181 | 1.0768
2010-07-09 | 8 | 32.7082 | 9.3285 | 42.0366 | 3.0739 | 0.76558 | 0.31251 | 4.152 | 9.877% | 10.51% | 7.102% | 1.1096 | 1.1174 | 1.0764
2010-07-09 | 9 | 32.9388 | 9.469 | 42.4078 | 3.1284 | 0.76558 | 0.31526 | 4.2093 | 9.926% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-07-09 | 10 | 34.1869 | 9.5427 | 43.7296 | 3.3265 | 0.76558 | 0.32509 | 4.4172 | 10.1% | 10.75% | 7.263% | 1.1124 | 1.1204 | 1.0783
2010-07-09 | 11 | 34.7466 | 9.7521 | 44.4987 | 3.4445 | 0.76558 | 0.33081 | 4.5409 | 10.2% | 10.86% | 7.337% | 1.1136 | 1.1218 | 1.0792
2010-07-09 | 12 | 35.5938 | 10.1808 | 45.7745 | 3.6449 | 0.76558 | 0.34029 | 4.7507 | 10.38% | 11.04% | 7.462% | 1.1158 | 1.1241 | 1.0806
2010-07-09 | 13 | 36.6536 | 11.2269 | 47.8806 | 3.988 | 0.76558 | 0.35595 | 5.1095 | 10.67% | 11.35% | 7.673% | 1.1195 | 1.1281 | 1.0831
2010-07-09 | 14 | 39.8286 | 12.6198 | 52.4484 | 4.7852 | 0.76558 | 0.38991 | 5.9407 | 11.33% | 12.05% | 8.144% | 1.1277 | 1.137 | 1.0887
2010-07-09 | 15 | 44.1815 | 14.0532 | 58.2347 | 5.8993 | 0.76558 | 0.43292 | 7.0978 | 12.19% | 12.97% | 8.763% | 1.1388 | 1.149 | 1.0961
2010-07-09 | 16 | 45.6299 | 15.0017 | 60.6316 | 6.3949 | 0.76558 | 0.45074 | 7.6112 | 12.55% | 13.36% | 9.026% | 1.1436 | 1.1542 | 1.0992
2010-07-09 | 17 | 47.2517 | 16.2351 | 63.4868 | 7.0113 | 0.76558 | 0.47197 | 8.2489 | 12.99% | 13.82% | 9.342% | 1.1493 | 1.1604 | 1.103
2010-07-09 | 18 | 47.2374 | 16.6695 | 63.9069 | 7.1044 | 0.76558 | 0.47509 | 8.3451 | 13.06% | 13.89% | 9.389% | 1.1502 | 1.1614 | 1.1036
2010-07-09 | 19 | 47.1318 | 16.6109 | 63.7427 | 7.068 | 0.76558 | 0.47387 | 8.3074 | 13.03% | 13.87% | 9.371% | 1.1499 | 1.161 | 1.1034
2010-07-09 | 20 | 47.1744 | 16.5487 | 63.7231 | 7.0636 | 0.76558 | 0.47373 | 8.3029 | 13.03% | 13.86% | 9.368% | 1.1498 | 1.1609 | 1.1034
2010-07-09 | 21 | 47.2592 | 16.5512 | 63.8104 | 7.083 | 0.76558 | 0.47437 | 8.323 | 13.04% | 13.88% | 9.378% | 1.15 | 1.1611 | 1.1035
2010-07-09 | 22 | 47.1257 | 16.1911 | 63.3168 | 6.9739 | 0.76558 | 0.4707 | 8.2101 | 12.97% | 13.8% | 9.323% | 1.149 | 1.16 | 1.1028
2010-07-09 | 23 | 47.1376 | 15.2463 | 62.3839 | 6.7699 | 0.76558 | 0.46377 | 7.9992 | 12.82% | 13.64% | 9.219% | 1.1471 | 1.158 | 1.1016
2010-07-09 | 24 | 47.1537 | 14.3824 | 61.536 | 6.5871 | 0.76558 | 0.45747 | 7.8101 | 12.69% | 13.5% | 9.126% | 1.1454 | 1.1561 | 1.1004
2010-07-09 | 25 | 45.1128 | 13.5862 | 58.699 | 5.9937 | 0.76558 | 0.43638 | 7.1957 | 12.26% | 13.04% | 8.814% | 1.1397 | 1.15 | 1.0967
2010-07-09 | 26 | 41.9697 | 12.5033 | 54.473 | 5.1618 | 0.76558 | 0.40496 | 6.3323 | 11.62% | 12.37% | 8.358% | 1.1315 | 1.1411 | 1.0912
2010-07-09 | 27 | 41.5533 | 12.7216 | 54.2749 | 5.1243 | 0.76558 | 0.40349 | 6.2933 | 11.6% | 12.34% | 8.337% | 1.1312 | 1.1407 | 1.091
2010-07-09 | 28 | 40.9974 | 12.8821 | 53.8795 | 5.0499 | 0.76558 | 0.40055 | 6.216 | 11.54% | 12.28% | 8.295% | 1.1304 | 1.1399 | 1.0905
2010-07-09 | 29 | 40.2357 | 12.5015 | 52.7372 | 4.838 | 0.76558 | 0.39206 | 5.9957 | 11.37% | 12.1% | 8.174% | 1.1283 | 1.1376 | 1.089
2010-07-09 | 30 | 39.8076 | 11.9691 | 51.7767 | 4.6634 | 0.76558 | 0.38491 | 5.8139 | 11.23% | 11.95% | 8.074% | 1.1265 | 1.1357 | 1.0878
2010-07-09 | 31 | 42.8332 | 12.088 | 54.9212 | 5.247 | 0.76558 | 0.40829 | 6.4209 | 11.69% | 12.44% | 8.406% | 1.1324 | 1.1421 | 1.0918
2010-07-09 | 32 | 43.6322 | 11.8286 | 55.4608 | 5.3507 | 0.76558 | 0.4123 | 6.5285 | 11.77% | 12.52% | 8.464% | 1.1334 | 1.1432 | 1.0925
2010-07-09 | 33 | 43.6642 | 12.1891 | 55.8533 | 5.4267 | 0.76558 | 0.41522 | 6.6075 | 11.83% | 12.59% | 8.506% | 1.1342 | 1.144 | 1.093
2010-07-09 | 34 | 45.1007 | 12.4451 | 57.5458 | 5.7605 | 0.76558 | 0.4278 | 6.9539 | 12.08% | 12.86% | 8.688% | 1.1375 | 1.1475 | 1.0952
2010-07-09 | 35 | 45.7363 | 13.6214 | 59.3577 | 6.129 | 0.76558 | 0.44127 | 7.3358 | 12.36% | 13.15% | 8.886% | 1.141 | 1.1514 | 1.0975
2010-07-09 | 36 | 47.2537 | 15.1373 | 62.391 | 6.7714 | 0.76558 | 0.46382 | 8.0008 | 12.82% | 13.64% | 9.22% | 1.1471 | 1.158 | 1.1016
2010-07-09 | 37 | 47.2147 | 15.3043 | 62.519 | 6.7992 | 0.76558 | 0.46477 | 8.0296 | 12.84% | 13.67% | 9.234% | 1.1474 | 1.1583 | 1.1017
2010-07-09 | 38 | 47.2677 | 15.2403 | 62.508 | 6.7968 | 0.76558 | 0.46469 | 8.0271 | 12.84% | 13.66% | 9.233% | 1.1473 | 1.1583 | 1.1017
2010-07-09 | 39 | 47.1662 | 14.8563 | 62.0224 | 6.6916 | 0.76558 | 0.46108 | 7.9183 | 12.77% | 13.58% | 9.179% | 1.1464 | 1.1572 | 1.1011
2010-07-09 | 40 | 47.2093 | 14.4436 | 61.6529 | 6.6121 | 0.76558 | 0.45834 | 7.836 | 12.71% | 13.52% | 9.138% | 1.1456 | 1.1564 | 1.1006
2010-07-09 | 41 | 47.3638 | 14.3701 | 61.7339 | 6.6295 | 0.76558 | 0.45894 | 7.854 | 12.72% | 13.54% | 9.147% | 1.1458 | 1.1566 | 1.1007
2010-07-09 | 42 | 47.0455 | 14.1143 | 61.1598 | 6.5068 | 0.76558 | 0.45467 | 7.727 | 12.63% | 13.44% | 9.084% | 1.1446 | 1.1553 | 1.0999
2010-07-09 | 43 | 47.0008 | 13.5532 | 60.554 | 6.3785 | 0.76558 | 0.45017 | 7.5943 | 12.54% | 13.34% | 9.017% | 1.1434 | 1.154 | 1.0991
2010-07-09 | 44 | 46.9983 | 12.9241 | 59.9224 | 6.2462 | 0.76558 | 0.44547 | 7.4572 | 12.44% | 13.24% | 8.948% | 1.1421 | 1.1526 | 1.0983
2010-07-09 | 45 | 46.6523 | 11.8357 | 58.4879 | 5.9507 | 0.76558 | 0.43481 | 7.1511 | 12.23% | 13.01% | 8.791% | 1.1393 | 1.1495 | 1.0964
2010-07-09 | 46 | 44.1105 | 10.578 | 54.6885 | 5.2027 | 0.76558 | 0.40656 | 6.3748 | 11.66% | 12.4% | 8.381% | 1.1319 | 1.1416 | 1.0915
2010-07-09 | 47 | 41.6646 | 11.0579 | 52.7225 | 4.8353 | 0.76558 | 0.39195 | 5.9929 | 11.37% | 12.09% | 8.173% | 1.1282 | 1.1376 | 1.089
2010-07-09 | 48 | 39.9669 | 11.6716 | 51.6384 | 4.6385 | 0.76558 | 0.38389 | 5.788 | 11.21% | 11.93% | 8.059% | 1.1262 | 1.1354 | 1.0877
2010-07-10 | 1 | 37.3814 | 10.9124 | 48.2938 | 4.0571 | 0.76558 | 0.35902 | 5.1817 | 10.73% | 11.42% | 7.715% | 1.1202 | 1.1289 | 1.0836
2010-07-10 | 2 | 39.2042 | 10.711 | 49.9151 | 4.3341 | 0.76558 | 0.37108 | 5.4708 | 10.96% | 11.66% | 7.88% | 1.1231 | 1.132 | 1.0855
2010-07-10 | 3 | 37.1199 | 10.3914 | 47.5113 | 3.9267 | 0.76558 | 0.3532 | 5.0455 | 10.62% | 11.3% | 7.635% | 1.1188 | 1.1274 | 1.0827
2010-07-10 | 4 | 34.9328 | 10.0417 | 44.9745 | 3.5186 | 0.76558 | 0.33435 | 4.6185 | 10.27% | 10.93% | 7.384% | 1.1144 | 1.1227 | 1.0797
2010-07-10 | 5 | 34.366 | 9.7354 | 44.1013 | 3.3833 | 0.76558 | 0.32785 | 4.4767 | 10.15% | 10.8% | 7.299% | 1.113 | 1.1211 | 1.0787
2010-07-10 | 6 | 33.186 | 9.5219 | 42.7079 | 3.1729 | 0.76558 | 0.3175 | 4.2559 | 9.965% | 10.6% | 7.165% | 1.1107 | 1.1186 | 1.0772
2010-07-10 | 7 | 32.6743 | 9.4321 | 42.1064 | 3.0841 | 0.76558 | 0.31302 | 4.1627 | 9.886% | 10.52% | 7.108% | 1.1097 | 1.1176 | 1.0765
2010-07-10 | 8 | 32.0826 | 9.317 | 41.3996 | 2.9814 | 0.76558 | 0.30777 | 4.0548 | 9.794% | 10.42% | 7.042% | 1.1086 | 1.1163 | 1.0758
2010-07-10 | 9 | 33.0432 | 9.4041 | 42.4473 | 3.1343 | 0.76558 | 0.31556 | 4.2154 | 9.931% | 10.57% | 7.14% | 1.1103 | 1.1181 | 1.0769
2010-07-10 | 10 | 34.3759 | 9.4262 | 43.8021 | 3.3375 | 0.76558 | 0.32563 | 4.4287 | 10.11% | 10.76% | 7.27% | 1.1125 | 1.1205 | 1.0784
2010-07-10 | 11 | 35.2416 | 9.6913 | 44.933 | 3.5121 | 0.76558 | 0.33404 | 4.6117 | 10.26% | 10.92% | 7.379% | 1.1144 | 1.1226 | 1.0797
2010-07-10 | 12 | 35.7142 | 10.0135 | 45.7277 | 3.6374 | 0.76558 | 0.33995 | 4.7429 | 10.37% | 11.04% | 7.458% | 1.1157 | 1.124 | 1.0806
2010-07-10 | 13 | 37.2627 | 10.8945 | 48.1571 | 4.0342 | 0.76558 | 0.35801 | 5.1578 | 10.71% | 11.4% | 7.701% | 1.1199 | 1.1286 | 1.0834
2010-07-10 | 14 | 41.1314 | 12.3259 | 53.4574 | 4.9711 | 0.76558 | 0.39741 | 6.1341 | 11.47% | 12.21% | 8.25% | 1.1296 | 1.1391 | 1.0899
2010-07-10 | 15 | 45.2266 | 13.9034 | 59.13 | 6.082 | 0.76558 | 0.43958 | 7.2872 | 12.32% | 13.11% | 8.861% | 1.1406 | 1.1509 | 1.0972
2010-07-10 | 16 | 45.2674 | 14.6248 | 59.8922 | 6.2399 | 0.76558 | 0.44525 | 7.4507 | 12.44% | 13.24% | 8.944% | 1.1421 | 1.1526 | 1.0982
2010-07-10 | 17 | 47.1324 | 15.8574 | 62.9898 | 6.902 | 0.76558 | 0.46827 | 8.1359 | 12.92% | 13.74% | 9.287% | 1.1483 | 1.1593 | 1.1024
2010-07-10 | 18 | 47.3828 | 16.6266 | 64.0093 | 7.1272 | 0.76558 | 0.47585 | 8.3687 | 13.07% | 13.91% | 9.4% | 1.1504 | 1.1616 | 1.1038
2010-07-10 | 19 | 47.1844 | 16.6754 | 63.8598 | 7.094 | 0.76558 | 0.47474 | 8.3343 | 13.05% | 13.89% | 9.384% | 1.1501 | 1.1613 | 1.1036
2010-07-10 | 20 | 47.2172 | 16.6017 | 63.8189 | 7.0849 | 0.76558 | 0.47444 | 8.3249 | 13.04% | 13.88% | 9.379% | 1.15 | 1.1612 | 1.1035
2010-07-10 | 21 | 47.1478 | 16.6506 | 63.7983 | 7.0803 | 0.76558 | 0.47428 | 8.3202 | 13.04% | 13.88% | 9.377% | 1.15 | 1.1611 | 1.1035
2010-07-10 | 22 | 47.1807 | 16.6553 | 63.836 | 7.0887 | 0.76558 | 0.47456 | 8.3288 | 13.05% | 13.88% | 9.381% | 1.15 | 1.1612 | 1.1035
2010-07-10 | 23 | 47.1135 | 16.605 | 63.7185 | 7.0626 | 0.76558 | 0.47369 | 8.3019 | 13.03% | 13.86% | 9.368% | 1.1498 | 1.1609 | 1.1034
2010-07-10 | 24 | 47.1105 | 16.2749 | 63.3855 | 6.989 | 0.76558 | 0.47122 | 8.2258 | 12.98% | 13.81% | 9.331% | 1.1491 | 1.1602 | 1.1029
2010-07-10 | 25 | 45.4361 | 15.7068 | 61.1428 | 6.5032 | 0.76558 | 0.45454 | 7.7233 | 12.63% | 13.44% | 9.082% | 1.1446 | 1.1553 | 1.0999
2010-07-10 | 26 | 42.2443 | 14.8568 | 57.1011 | 5.6718 | 0.76558 | 0.4245 | 6.8619 | 12.02% | 12.79% | 8.64% | 1.1366 | 1.1466 | 1.0946
2010-07-10 | 27 | 41.957 | 15.2934 | 57.2503 | 5.7015 | 0.76558 | 0.42561 | 6.8927 | 12.04% | 12.81% | 8.656% | 1.1369 | 1.1469 | 1.0948
2010-07-10 | 28 | 41.5684 | 15.2568 | 56.8252 | 5.6172 | 0.76558 | 0.42245 | 6.8052 | 11.98% | 12.74% | 8.61% | 1.136 | 1.146 | 1.0942
2010-07-10 | 29 | 40.2505 | 14.7613 | 55.0119 | 5.2644 | 0.76558 | 0.40897 | 6.4389 | 11.7% | 12.45% | 8.416% | 1.1326 | 1.1423 | 1.0919
2010-07-10 | 30 | 39.5238 | 14.2855 | 53.8093 | 5.0367 | 0.76558 | 0.40002 | 6.2023 | 11.53% | 12.26% | 8.288% | 1.1303 | 1.1398 | 1.0904
2010-07-10 | 31 | 43.0545 | 14.3181 | 57.3726 | 5.7259 | 0.76558 | 0.42651 | 6.918 | 12.06% | 12.83% | 8.67% | 1.1371 | 1.1472 | 1.0949
2010-07-10 | 32 | 43.8128 | 14.1601 | 57.9729 | 5.8464 | 0.76558 | 0.43098 | 7.0429 | 12.15% | 12.93% | 8.735% | 1.1383 | 1.1485 | 1.0957
2010-07-10 | 33 | 43.1061 | 14.0918 | 57.1979 | 5.6911 | 0.76558 | 0.42522 | 6.8819 | 12.03% | 12.8% | 8.651% | 1.1368 | 1.1468 | 1.0947
2010-07-10 | 34 | 44.1282 | 14.0124 | 58.1406 | 5.8802 | 0.76558 | 0.43222 | 7.078 | 12.17% | 12.95% | 8.753% | 1.1386 | 1.1488 | 1.0959
2010-07-10 | 35 | 44.8309 | 14.2864 | 59.1173 | 6.0794 | 0.76558 | 0.43949 | 7.2845 | 12.32% | 13.11% | 8.86% | 1.1405 | 1.1509 | 1.0972
2010-07-10 | 36 | 47.2593 | 15.2358 | 62.4951 | 6.794 | 0.76558 | 0.4646 | 8.0242 | 12.84% | 13.66% | 9.232% | 1.1473 | 1.1582 | 1.1017
2010-07-10 | 37 | 47.0841 | 15.289 | 62.3731 | 6.7675 | 0.76558 | 0.46369 | 7.9968 | 12.82% | 13.64% | 9.218% | 1.1471 | 1.158 | 1.1015
2010-07-10 | 38 | 47.2585 | 14.9972 | 62.2557 | 6.7421 | 0.76558 | 0.46282 | 7.9705 | 12.8% | 13.62% | 9.205% | 1.1468 | 1.1577 | 1.1014
2010-07-10 | 39 | 47.1552 | 14.6668 | 61.822 | 6.6485 | 0.76558 | 0.45959 | 7.8736 | 12.74% | 13.55% | 9.157% | 1.1459 | 1.1568 | 1.1008
2010-07-10 | 40 | 47.1558 | 14.3091 | 61.4649 | 6.5719 | 0.76558 | 0.45694 | 7.7944 | 12.68% | 13.49% | 9.118% | 1.1452 | 1.156 | 1.1003
2010-07-10 | 41 | 47.1814 | 14.098 | 61.2794 | 6.5323 | 0.76558 | 0.45556 | 7.7534 | 12.65% | 13.46% | 9.097% | 1.1449 | 1.1556 | 1.1001
2010-07-10 | 42 | 47.2107 | 13.8065 | 61.0172 | 6.4765 | 0.76558 | 0.45361 | 7.6957 | 12.61% | 13.42% | 9.068% | 1.1443 | 1.155 | 1.0997
2010-07-10 | 43 | 47.0364 | 13.3605 | 60.3969 | 6.3455 | 0.76558 | 0.449 | 7.56 | 12.52% | 13.32% | 9% | 1.1431 | 1.1536 | 1.0989
2010-07-10 | 44 | 47.0365 | 12.2471 | 59.2836 | 6.1137 | 0.76558 | 0.44072 | 7.32 | 12.35% | 13.14% | 8.878% | 1.1409 | 1.1512 | 1.0974
2010-07-10 | 45 | 45.6138 | 11.1626 | 56.7764 | 5.6075 | 0.76558 | 0.42208 | 6.7952 | 11.97% | 12.73% | 8.605% | 1.136 | 1.1459 | 1.0942
2010-07-10 | 46 | 42.2068 | 10.2461 | 52.4529 | 4.786 | 0.76558 | 0.38994 | 5.9415 | 11.33% | 12.05% | 8.144% | 1.1277 | 1.137 | 1.0887
2010-07-10 | 47 | 41.4878 | 10.624 | 52.1118 | 4.724 | 0.76558 | 0.38741 | 5.877 | 11.28% | 12% | 8.109% | 1.1271 | 1.1364 | 1.0882
2010-07-10 | 48 | 40.1083 | 11.2196 | 51.328 | 4.5829 | 0.76558 | 0.38158 | 5.7301 | 11.16% | 11.88% | 8.027% | 1.1257 | 1.1348 | 1.0873
2010-07-11 | 1 | 37.6657 | 10.4238 | 48.0895 | 4.0229 | 0.76558 | 0.3575 | 5.1459 | 10.7% | 11.39% | 7.694% | 1.1198 | 1.1285 | 1.0834
2010-07-11 | 2 | 39.6302 | 10.3926 | 50.0228 | 4.3528 | 0.76558 | 0.37188 | 5.4903 | 10.98% | 11.68% | 7.891% | 1.1233 | 1.1322 | 1.0857
2010-07-11 | 3 | 38.1947 | 9.969 | 48.1637 | 4.0353 | 0.76558 | 0.35805 | 5.1589 | 10.71% | 11.4% | 7.701% | 1.12 | 1.1286 | 1.0834
2010-07-11 | 4 | 36.5138 | 9.5395 | 46.0533 | 3.6894 | 0.76558 | 0.34237 | 4.7974 | 10.42% | 11.08% | 7.49% | 1.1163 | 1.1247 | 1.081
2010-07-11 | 5 | 35.0181 | 9.347 | 44.3651 | 3.4239 | 0.76558 | 0.32982 | 4.5193 | 10.19% | 10.84% | 7.324% | 1.1134 | 1.1216 | 1.079
2010-07-11 | 6 | 34.0534 | 9.055 | 43.1085 | 3.2327 | 0.76558 | 0.32047 | 4.3187 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-07-11 | 7 | 34.2791 | 9.1129 | 43.392 | 3.2753 | 0.76558 | 0.32258 | 4.3635 | 10.06% | 10.7% | 7.23% | 1.1118 | 1.1198 | 1.0779
2010-07-11 | 8 | 34.5187 | 8.9908 | 43.5095 | 3.2931 | 0.76558 | 0.32346 | 4.3821 | 10.07% | 10.72% | 7.242% | 1.112 | 1.12 | 1.0781
2010-07-11 | 9 | 34.384 | 9.0511 | 43.4351 | 3.2818 | 0.76558 | 0.3229 | 4.3703 | 10.06% | 10.71% | 7.234% | 1.1119 | 1.1199 | 1.078
2010-07-11 | 10 | 34.7784 | 9.1775 | 43.9559 | 3.361 | 0.76558 | 0.32677 | 4.4534 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-07-11 | 11 | 35.4352 | 9.1589 | 44.5941 | 3.4593 | 0.76558 | 0.33152 | 4.5564 | 10.22% | 10.87% | 7.346% | 1.1138 | 1.122 | 1.0793
2010-07-11 | 12 | 36.0229 | 9.3917 | 45.4146 | 3.5878 | 0.76558 | 0.33762 | 4.691 | 10.33% | 10.99% | 7.427% | 1.1152 | 1.1235 | 1.0802
2010-07-11 | 13 | 36.481 | 9.7373 | 46.2183 | 3.7159 | 0.76558 | 0.34359 | 4.8251 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.125 | 1.0812
2010-07-11 | 14 | 38.4182 | 10.09 | 48.5083 | 4.0932 | 0.76558 | 0.36062 | 5.2194 | 10.76% | 11.45% | 7.736% | 1.1206 | 1.1293 | 1.0839
2010-07-11 | 15 | 39.8029 | 10.4968 | 50.2997 | 4.4011 | 0.76558 | 0.37393 | 5.5407 | 11.02% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-07-11 | 16 | 38.7451 | 10.7994 | 49.5445 | 4.27 | 0.76558 | 0.36832 | 5.4039 | 10.91% | 11.61% | 7.842% | 1.1224 | 1.1313 | 1.0851
2010-07-11 | 17 | 40.6961 | 11.926 | 52.6221 | 4.8169 | 0.76558 | 0.3912 | 5.9737 | 11.35% | 12.08% | 8.162% | 1.1281 | 1.1374 | 1.0889
2010-07-11 | 18 | 43.1273 | 13.2276 | 56.355 | 5.5246 | 0.76558 | 0.41895 | 6.7091 | 11.91% | 12.67% | 8.56% | 1.1351 | 1.145 | 1.0936
2010-07-11 | 19 | 45.8048 | 14.1519 | 59.9567 | 6.2533 | 0.76558 | 0.44573 | 7.4646 | 12.45% | 13.25% | 8.952% | 1.1422 | 1.1527 | 1.0983
2010-07-11 | 20 | 47.0316 | 14.8149 | 61.8465 | 6.6537 | 0.76558 | 0.45977 | 7.8791 | 12.74% | 13.56% | 9.16% | 1.146 | 1.1568 | 1.1008
2010-07-11 | 21 | 47.1393 | 16.1845 | 63.3238 | 6.9754 | 0.76558 | 0.47076 | 8.2117 | 12.97% | 13.8% | 9.324% | 1.149 | 1.1601 | 1.1028
2010-07-11 | 22 | 47.0954 | 16.1127 | 63.2081 | 6.9499 | 0.76558 | 0.4699 | 8.1854 | 12.95% | 13.78% | 9.311% | 1.1488 | 1.1598 | 1.1027
2010-07-11 | 23 | 47.1876 | 15.6947 | 62.8823 | 6.8785 | 0.76558 | 0.46747 | 8.1115 | 12.9% | 13.73% | 9.275% | 1.1481 | 1.1591 | 1.1022
2010-07-11 | 24 | 47.1429 | 15.3412 | 62.4841 | 6.7916 | 0.76558 | 0.46451 | 8.0217 | 12.84% | 13.66% | 9.231% | 1.1473 | 1.1582 | 1.1017
2010-07-11 | 25 | 44.5688 | 14.5414 | 59.1102 | 6.078 | 0.76558 | 0.43943 | 7.283 | 12.32% | 13.11% | 8.859% | 1.1405 | 1.1509 | 1.0972
2010-07-11 | 26 | 41.2616 | 13.799 | 55.0606 | 5.2737 | 0.76558 | 0.40933 | 6.4486 | 11.71% | 12.46% | 8.421% | 1.1327 | 1.1424 | 1.092
2010-07-11 | 27 | 40.5246 | 14.0596 | 54.5842 | 5.1828 | 0.76558 | 0.40579 | 6.3542 | 11.64% | 12.39% | 8.37% | 1.1317 | 1.1414 | 1.0913
2010-07-11 | 28 | 40.237 | 14.2294 | 54.4664 | 5.1605 | 0.76558 | 0.40491 | 6.331 | 11.62% | 12.37% | 8.357% | 1.1315 | 1.1411 | 1.0912
2010-07-11 | 29 | 39.5325 | 13.7279 | 53.2604 | 4.9345 | 0.76558 | 0.39594 | 6.096 | 11.45% | 12.18% | 8.229% | 1.1293 | 1.1387 | 1.0897
2010-07-11 | 30 | 39.2472 | 13.4174 | 52.6646 | 4.8247 | 0.76558 | 0.39152 | 5.9818 | 11.36% | 12.09% | 8.167% | 1.1281 | 1.1375 | 1.0889
2010-07-11 | 31 | 42.1007 | 13.536 | 55.6367 | 5.3847 | 0.76558 | 0.41361 | 6.5638 | 11.8% | 12.55% | 8.483% | 1.1338 | 1.1435 | 1.0927
2010-07-11 | 32 | 43.1082 | 13.2481 | 56.3563 | 5.5248 | 0.76558 | 0.41896 | 6.7094 | 11.91% | 12.67% | 8.56% | 1.1351 | 1.145 | 1.0936
2010-07-11 | 33 | 42.5496 | 13.211 | 55.7606 | 5.4087 | 0.76558 | 0.41453 | 6.5888 | 11.82% | 12.57% | 8.496% | 1.134 | 1.1438 | 1.0928
2010-07-11 | 34 | 43.5802 | 13.2495 | 56.8297 | 5.618 | 0.76558 | 0.42248 | 6.8061 | 11.98% | 12.74% | 8.611% | 1.1361 | 1.146 | 1.0942
2010-07-11 | 35 | 44.5755 | 14.0204 | 58.5959 | 5.9727 | 0.76558 | 0.43561 | 7.1739 | 12.24% | 13.03% | 8.803% | 1.1395 | 1.1498 | 1.0965
2010-07-11 | 36 | 47.1968 | 14.7475 | 61.9443 | 6.6748 | 0.76558 | 0.4605 | 7.9009 | 12.75% | 13.57% | 9.171% | 1.1462 | 1.157 | 1.101
2010-07-11 | 37 | 47.2751 | 14.6959 | 61.971 | 6.6805 | 0.76558 | 0.4607 | 7.9068 | 12.76% | 13.58% | 9.174% | 1.1462 | 1.1571 | 1.101
2010-07-11 | 38 | 47.1741 | 14.4327 | 61.6068 | 6.6023 | 0.76558 | 0.45799 | 7.8258 | 12.7% | 13.52% | 9.133% | 1.1455 | 1.1563 | 1.1005
2010-07-11 | 39 | 47.1279 | 13.9582 | 61.0862 | 6.4911 | 0.76558 | 0.45412 | 7.7108 | 12.62% | 13.43% | 9.076% | 1.1445 | 1.1551 | 1.0998
2010-07-11 | 40 | 47.0851 | 13.6074 | 60.6925 | 6.4077 | 0.76558 | 0.4512 | 7.6245 | 12.56% | 13.37% | 9.032% | 1.1437 | 1.1543 | 1.0993
2010-07-11 | 41 | 47.2854 | 13.4735 | 60.7589 | 6.4218 | 0.76558 | 0.45169 | 7.639 | 12.57% | 13.38% | 9.04% | 1.1438 | 1.1544 | 1.0994
2010-07-11 | 42 | 47.1267 | 12.9982 | 60.1249 | 6.2884 | 0.76558 | 0.44698 | 7.501 | 12.48% | 13.27% | 8.97% | 1.1425 | 1.1531 | 1.0985
2010-07-11 | 43 | 47.0838 | 12.5306 | 59.6144 | 6.1821 | 0.76558 | 0.44318 | 7.3909 | 12.4% | 13.19% | 8.914% | 1.1415 | 1.152 | 1.0979
2010-07-11 | 44 | 45.8157 | 11.8575 | 57.6732 | 5.7861 | 0.76558 | 0.42875 | 6.9804 | 12.1% | 12.88% | 8.702% | 1.1377 | 1.1478 | 1.0953
2010-07-11 | 45 | 41.1791 | 10.9793 | 52.1584 | 4.7324 | 0.76558 | 0.38775 | 5.8858 | 11.28% | 12.01% | 8.113% | 1.1272 | 1.1364 | 1.0883
2010-07-11 | 46 | 37.6581 | 10.2938 | 47.9518 | 3.9999 | 0.76558 | 0.35648 | 5.1219 | 10.68% | 11.36% | 7.68% | 1.1196 | 1.1282 | 1.0832
2010-07-11 | 47 | 37.6422 | 10.8053 | 48.4475 | 4.083 | 0.76558 | 0.36016 | 5.2087 | 10.75% | 11.44% | 7.73% | 1.1205 | 1.1292 | 1.0838
2010-07-11 | 48 | 36.7223 | 11.3367 | 48.059 | 4.0178 | 0.76558 | 0.35728 | 5.1406 | 10.7% | 11.38% | 7.691% | 1.1198 | 1.1284 | 1.0833
2010-07-12 | 1 | 34.5094 | 10.499 | 45.0084 | 3.5239 | 0.76558 | 0.3346 | 4.6241 | 10.27% | 10.93% | 7.387% | 1.1145 | 1.1227 | 1.0798
2010-07-12 | 2 | 36.8374 | 10.3029 | 47.1402 | 3.8656 | 0.76558 | 0.35045 | 4.9816 | 10.57% | 11.24% | 7.598% | 1.1182 | 1.1267 | 1.0822
2010-07-12 | 3 | 35.8868 | 9.7837 | 45.6705 | 3.6283 | 0.76558 | 0.33952 | 4.7334 | 10.36% | 11.03% | 7.452% | 1.1156 | 1.1239 | 1.0805
2010-07-12 | 4 | 33.9436 | 9.3107 | 43.2542 | 3.2546 | 0.76558 | 0.32156 | 4.3417 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-07-12 | 5 | 31.6209 | 9.061 | 40.6819 | 2.879 | 0.76558 | 0.30243 | 3.947 | 9.702% | 10.32% | 6.976% | 1.1074 | 1.1151 | 1.075
2010-07-12 | 6 | 30.5572 | 8.7957 | 39.3529 | 2.6939 | 0.76558 | 0.29255 | 3.7521 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-07-12 | 7 | 30.1356 | 8.6396 | 38.7751 | 2.6154 | 0.76558 | 0.28826 | 3.6693 | 9.463% | 10.07% | 6.804% | 1.1045 | 1.112 | 1.073
2010-07-12 | 8 | 30.0792 | 8.5426 | 38.6219 | 2.5948 | 0.76558 | 0.28712 | 3.6475 | 9.444% | 10.05% | 6.79% | 1.1043 | 1.1117 | 1.0728
2010-07-12 | 9 | 29.9449 | 8.6076 | 38.5525 | 2.5855 | 0.76558 | 0.2866 | 3.6377 | 9.436% | 10.04% | 6.784% | 1.1042 | 1.1116 | 1.0728
2010-07-12 | 10 | 30.165 | 8.7134 | 38.8785 | 2.6294 | 0.76558 | 0.28903 | 3.684 | 9.476% | 10.08% | 6.813% | 1.1047 | 1.1121 | 1.0731
2010-07-12 | 11 | 30.1602 | 8.7971 | 38.9573 | 2.64 | 0.76558 | 0.28961 | 3.6952 | 9.485% | 10.09% | 6.82% | 1.1048 | 1.1123 | 1.0732
2010-07-12 | 12 | 30.5637 | 8.8908 | 39.4544 | 2.7079 | 0.76558 | 0.29331 | 3.7667 | 9.547% | 10.16% | 6.864% | 1.1055 | 1.1131 | 1.0737
2010-07-12 | 13 | 31.909 | 9.2549 | 41.1639 | 2.9476 | 0.76558 | 0.30602 | 4.0192 | 9.764% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-07-12 | 14 | 33.7208 | 9.4194 | 43.1402 | 3.2374 | 0.76558 | 0.32071 | 4.3237 | 10.02% | 10.66% | 7.206% | 1.1114 | 1.1194 | 1.0777
2010-07-12 | 15 | 34.7493 | 9.7827 | 44.532 | 3.4497 | 0.76558 | 0.33106 | 4.5463 | 10.21% | 10.86% | 7.34% | 1.1137 | 1.1219 | 1.0792
2010-07-12 | 16 | 34.2036 | 9.973 | 44.1766 | 3.3948 | 0.76558 | 0.32841 | 4.4888 | 10.16% | 10.81% | 7.306% | 1.1131 | 1.1212 | 1.0788
2010-07-12 | 17 | 36.6543 | 11.083 | 47.7373 | 3.9642 | 0.76558 | 0.35489 | 5.0846 | 10.65% | 11.33% | 7.658% | 1.1192 | 1.1278 | 1.0829
2010-07-12 | 18 | 39.251 | 12.1853 | 51.4363 | 4.6023 | 0.76558 | 0.38238 | 5.7503 | 11.18% | 11.89% | 8.038% | 1.1259 | 1.135 | 1.0874
2010-07-12 | 19 | 42.2058 | 13.1612 | 55.3671 | 5.3326 | 0.76558 | 0.41161 | 6.5098 | 11.76% | 12.51% | 8.454% | 1.1332 | 1.143 | 1.0923
2010-07-12 | 20 | 43.4643 | 13.635 | 57.0993 | 5.6715 | 0.76558 | 0.42448 | 6.8615 | 12.02% | 12.79% | 8.64% | 1.1366 | 1.1466 | 1.0946
2010-07-12 | 21 | 46.8876 | 14.3169 | 61.2045 | 6.5163 | 0.76558 | 0.455 | 7.7369 | 12.64% | 13.45% | 9.089% | 1.1447 | 1.1554 | 1.1
2010-07-12 | 22 | 46.8563 | 14.4131 | 61.2694 | 6.5301 | 0.76558 | 0.45548 | 7.7512 | 12.65% | 13.46% | 9.096% | 1.1448 | 1.1555 | 1.1001
2010-07-12 | 23 | 45.5789 | 14.0232 | 59.602 | 6.1796 | 0.76558 | 0.44309 | 7.3882 | 12.4% | 13.19% | 8.913% | 1.1415 | 1.1519 | 1.0978
2010-07-12 | 24 | 43.7177 | 13.8929 | 57.6106 | 5.7735 | 0.76558 | 0.42828 | 6.9674 | 12.09% | 12.87% | 8.696% | 1.1376 | 1.1477 | 1.0952
2010-07-12 | 25 | 40.2362 | 13.5402 | 53.7764 | 5.0306 | 0.76558 | 0.39978 | 6.1959 | 11.52% | 12.26% | 8.284% | 1.1302 | 1.1397 | 1.0903
2010-07-12 | 26 | 38.1002 | 12.8106 | 50.9109 | 4.5087 | 0.76558 | 0.37848 | 5.6528 | 11.1% | 11.81% | 7.983% | 1.1249 | 1.134 | 1.0868
2010-07-12 | 27 | 38.0076 | 13.1776 | 51.1852 | 4.5575 | 0.76558 | 0.38052 | 5.7036 | 11.14% | 11.86% | 8.012% | 1.1254 | 1.1345 | 1.0871
2010-07-12 | 28 | 37.7903 | 13.4425 | 51.2328 | 4.5659 | 0.76558 | 0.38087 | 5.7124 | 11.15% | 11.86% | 8.017% | 1.1255 | 1.1346 | 1.0872
2010-07-12 | 29 | 37.544 | 13.1159 | 50.6599 | 4.4644 | 0.76558 | 0.37661 | 5.6066 | 11.07% | 11.78% | 7.957% | 1.1244 | 1.1335 | 1.0865
2010-07-12 | 30 | 37.0899 | 12.75 | 49.84 | 4.3211 | 0.76558 | 0.37052 | 5.4572 | 10.95% | 11.65% | 7.873% | 1.123 | 1.1319 | 1.0855
2010-07-12 | 31 | 40.1751 | 12.805 | 52.9801 | 4.8827 | 0.76558 | 0.39386 | 6.0421 | 11.4% | 12.13% | 8.2% | 1.1287 | 1.1381 | 1.0893
2010-07-12 | 32 | 41.0994 | 12.6703 | 53.7697 | 5.0293 | 0.76558 | 0.39973 | 6.1946 | 11.52% | 12.26% | 8.283% | 1.1302 | 1.1397 | 1.0903
2010-07-12 | 33 | 41.1941 | 12.8291 | 54.0232 | 5.0769 | 0.76558 | 0.40162 | 6.2441 | 11.56% | 12.3% | 8.31% | 1.1307 | 1.1402 | 1.0906
2010-07-12 | 34 | 42.6355 | 12.9868 | 55.6223 | 5.3819 | 0.76558 | 0.4135 | 6.561 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-07-12 | 35 | 43.6556 | 13.5407 | 57.1962 | 5.6907 | 0.76558 | 0.4252 | 6.8815 | 12.03% | 12.8% | 8.651% | 1.1368 | 1.1468 | 1.0947
2010-07-12 | 36 | 47.2435 | 14.8786 | 62.1222 | 6.7132 | 0.76558 | 0.46182 | 7.9406 | 12.78% | 13.6% | 9.19% | 1.1466 | 1.1574 | 1.1012
2010-07-12 | 37 | 47.149 | 14.9077 | 62.0567 | 6.699 | 0.76558 | 0.46134 | 7.9259 | 12.77% | 13.59% | 9.183% | 1.1464 | 1.1573 | 1.1011
2010-07-12 | 38 | 47.0847 | 14.7595 | 61.8442 | 6.6532 | 0.76558 | 0.45976 | 7.8786 | 12.74% | 13.55% | 9.16% | 1.146 | 1.1568 | 1.1008
2010-07-12 | 39 | 47.1614 | 14.3582 | 61.5196 | 6.5836 | 0.76558 | 0.45734 | 7.8065 | 12.69% | 13.5% | 9.124% | 1.1453 | 1.1561 | 1.1004
2010-07-12 | 40 | 47.1093 | 13.8933 | 61.0025 | 6.4734 | 0.76558 | 0.4535 | 7.6924 | 12.61% | 13.42% | 9.067% | 1.1443 | 1.155 | 1.0997
2010-07-12 | 41 | 47.207 | 13.8974 | 61.1044 | 6.495 | 0.76558 | 0.45426 | 7.7148 | 12.63% | 13.43% | 9.078% | 1.1445 | 1.1552 | 1.0998
2010-07-12 | 42 | 47.0599 | 13.3943 | 60.4542 | 6.3575 | 0.76558 | 0.44942 | 7.5725 | 12.53% | 13.33% | 9.006% | 1.1432 | 1.1538 | 1.099
2010-07-12 | 43 | 47.027 | 12.7209 | 59.7479 | 6.2098 | 0.76558 | 0.44417 | 7.4196 | 12.42% | 13.21% | 8.929% | 1.1418 | 1.1522 | 1.098
2010-07-12 | 44 | 46.7557 | 12.0966 | 58.8523 | 6.0251 | 0.76558 | 0.43751 | 7.2281 | 12.28% | 13.07% | 8.831% | 1.14 | 1.1503 | 1.0969
2010-07-12 | 45 | 42.6251 | 10.8616 | 53.4867 | 4.9765 | 0.76558 | 0.39763 | 6.1397 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.09
2010-07-12 | 46 | 38.846 | 9.7861 | 48.6321 | 4.1142 | 0.76558 | 0.36154 | 5.2413 | 10.78% | 11.47% | 7.749% | 1.1208 | 1.1295 | 1.084
2010-07-12 | 47 | 38.035 | 10.3365 | 48.3715 | 4.0702 | 0.76558 | 0.3596 | 5.1954 | 10.74% | 11.43% | 7.722% | 1.1203 | 1.129 | 1.0837
2010-07-12 | 48 | 36.8419 | 11.1008 | 47.9427 | 3.9983 | 0.76558 | 0.35641 | 5.1203 | 10.68% | 11.36% | 7.679% | 1.1196 | 1.1282 | 1.0832
2010-07-13 | 1 | 34.9559 | 10.293 | 45.2489 | 3.5616 | 0.76558 | 0.33639 | 4.6636 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-07-13 | 2 | 36.91 | 9.9663 | 46.8763 | 3.8224 | 0.76558 | 0.34848 | 4.9365 | 10.53% | 11.2% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-07-13 | 3 | 36.0166 | 9.5984 | 45.615 | 3.6195 | 0.76558 | 0.33911 | 4.7242 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0805
2010-07-13 | 4 | 34.3074 | 9.2966 | 43.604 | 3.3074 | 0.76558 | 0.32416 | 4.3971 | 10.08% | 10.73% | 7.251% | 1.1122 | 1.1202 | 1.0782
2010-07-13 | 5 | 33.7288 | 9.0696 | 42.7984 | 3.1863 | 0.76558 | 0.31817 | 4.2701 | 9.977% | 10.62% | 7.174% | 1.1108 | 1.1188 | 1.0773
2010-07-13 | 6 | 33.2673 | 8.8735 | 42.1408 | 3.0892 | 0.76558 | 0.31328 | 4.168 | 9.891% | 10.52% | 7.111% | 1.1098 | 1.1176 | 1.0766
2010-07-13 | 7 | 33.311 | 8.8651 | 42.1761 | 3.0943 | 0.76558 | 0.31354 | 4.1735 | 9.895% | 10.53% | 7.115% | 1.1098 | 1.1177 | 1.0766
2010-07-13 | 8 | 33.1212 | 8.769 | 41.8902 | 3.0525 | 0.76558 | 0.31142 | 4.1295 | 9.858% | 10.49% | 7.088% | 1.1094 | 1.1172 | 1.0763
2010-07-13 | 9 | 33.4328 | 8.9067 | 42.3395 | 3.1184 | 0.76558 | 0.31476 | 4.1987 | 9.917% | 10.55% | 7.13% | 1.1101 | 1.118 | 1.0768
2010-07-13 | 10 | 33.8159 | 9.0207 | 42.8366 | 3.192 | 0.76558 | 0.31845 | 4.276 | 9.982% | 10.62% | 7.177% | 1.1109 | 1.1188 | 1.0773
2010-07-13 | 11 | 34.7974 | 9.17 | 43.9674 | 3.3628 | 0.76558 | 0.32686 | 4.4552 | 10.13% | 10.78% | 7.286% | 1.1128 | 1.1208 | 1.0786
2010-07-13 | 12 | 35.6043 | 9.5793 | 45.1837 | 3.5514 | 0.76558 | 0.3359 | 4.6529 | 10.3% | 10.96% | 7.404% | 1.1148 | 1.123 | 1.08
2010-07-13 | 13 | 37.391 | 10.4819 | 47.8729 | 3.9867 | 0.76558 | 0.35589 | 5.1082 | 10.67% | 11.35% | 7.672% | 1.1194 | 1.1281 | 1.0831
2010-07-13 | 14 | 41.4091 | 11.7344 | 53.1436 | 4.9129 | 0.76558 | 0.39508 | 6.0735 | 11.43% | 12.16% | 8.217% | 1.129 | 1.1384 | 1.0895
2010-07-13 | 15 | 45.803 | 13.2618 | 59.0648 | 6.0687 | 0.76558 | 0.4391 | 7.2733 | 12.31% | 13.1% | 8.854% | 1.1404 | 1.1508 | 1.0971
2010-07-13 | 16 | 46.5168 | 13.9771 | 60.4939 | 6.3659 | 0.76558 | 0.44972 | 7.5812 | 12.53% | 13.33% | 9.011% | 1.1433 | 1.1539 | 1.099
2010-07-13 | 17 | 46.9795 | 15.3408 | 62.3203 | 6.7561 | 0.76558 | 0.4633 | 7.9849 | 12.81% | 13.63% | 9.212% | 1.147 | 1.1578 | 1.1015
2010-07-13 | 18 | 47.0289 | 16.0906 | 63.1195 | 6.9305 | 0.76558 | 0.46924 | 8.1653 | 12.94% | 13.76% | 9.301% | 1.1486 | 1.1596 | 1.1025
2010-07-13 | 19 | 46.8158 | 16.3568 | 63.1726 | 6.9421 | 0.76558 | 0.46963 | 8.1773 | 12.94% | 13.77% | 9.307% | 1.1487 | 1.1597 | 1.1026
2010-07-13 | 20 | 46.1979 | 15.6953 | 61.8933 | 6.6638 | 0.76558 | 0.46012 | 7.8895 | 12.75% | 13.56% | 9.165% | 1.1461 | 1.1569 | 1.1009
2010-07-13 | 21 | 46.8123 | 15.3355 | 62.1478 | 6.7187 | 0.76558 | 0.46201 | 7.9463 | 12.79% | 13.6% | 9.193% | 1.1466 | 1.1575 | 1.1012
2010-07-13 | 22 | 46.5942 | 14.7202 | 61.3144 | 6.5397 | 0.76558 | 0.45582 | 7.7611 | 12.66% | 13.47% | 9.101% | 1.1449 | 1.1556 | 1.1001
2010-07-13 | 23 | 46.7444 | 15.0651 | 61.8095 | 6.6458 | 0.76558 | 0.4595 | 7.8709 | 12.73% | 13.55% | 9.156% | 1.1459 | 1.1567 | 1.1008
2010-07-13 | 24 | 46.7559 | 14.9898 | 61.7457 | 6.6321 | 0.76558 | 0.45903 | 7.8567 | 12.72% | 13.54% | 9.149% | 1.1458 | 1.1566 | 1.1007
2010-07-13 | 25 | 46.5979 | 14.3044 | 60.9023 | 6.4521 | 0.76558 | 0.45275 | 7.6704 | 12.59% | 13.4% | 9.056% | 1.1441 | 1.1547 | 1.0996
2010-07-13 | 26 | 46.3616 | 12.9711 | 59.3327 | 6.1238 | 0.76558 | 0.44109 | 7.3305 | 12.35% | 13.15% | 8.883% | 1.141 | 1.1514 | 1.0975
2010-07-13 | 27 | 45.4154 | 13.1951 | 58.6105 | 5.9756 | 0.76558 | 0.43572 | 7.1769 | 12.25% | 13.03% | 8.804% | 1.1395 | 1.1498 | 1.0965
2010-07-13 | 28 | 44.7498 | 13.2146 | 57.9643 | 5.8446 | 0.76558 | 0.43091 | 7.0411 | 12.15% | 12.92% | 8.734% | 1.1383 | 1.1484 | 1.0957
2010-07-13 | 29 | 43.7249 | 12.5433 | 56.2682 | 5.5076 | 0.76558 | 0.4183 | 6.6915 | 11.89% | 12.65% | 8.55% | 1.135 | 1.1449 | 1.0935
2010-07-13 | 30 | 42.6245 | 12.0864 | 54.7109 | 5.2069 | 0.76558 | 0.40673 | 6.3792 | 11.66% | 12.41% | 8.383% | 1.132 | 1.1416 | 1.0915
2010-07-13 | 31 | 44.8784 | 12.2115 | 57.0899 | 5.6696 | 0.76558 | 0.42441 | 6.8596 | 12.02% | 12.78% | 8.639% | 1.1366 | 1.1466 | 1.0946
2010-07-13 | 32 | 45.0046 | 11.9759 | 56.9806 | 5.6479 | 0.76558 | 0.4236 | 6.8371 | 12% | 12.77% | 8.627% | 1.1364 | 1.1464 | 1.0944
2010-07-13 | 33 | 45.9385 | 11.9645 | 57.9029 | 5.8322 | 0.76558 | 0.43046 | 7.0283 | 12.14% | 12.91% | 8.727% | 1.1381 | 1.1483 | 1.0956
2010-07-13 | 34 | 47.282 | 12.3165 | 59.5985 | 6.1788 | 0.76558 | 0.44306 | 7.3875 | 12.4% | 13.19% | 8.912% | 1.1415 | 1.1519 | 1.0978
2010-07-13 | 35 | 47.2041 | 13.5777 | 60.7818 | 6.4266 | 0.76558 | 0.45186 | 7.644 | 12.58% | 13.38% | 9.042% | 1.1439 | 1.1545 | 1.0994
2010-07-13 | 36 | 47.0033 | 14.6226 | 61.6259 | 6.6063 | 0.76558 | 0.45813 | 7.8301 | 12.71% | 13.52% | 9.135% | 1.1456 | 1.1563 | 1.1005
2010-07-13 | 37 | 47.2794 | 13.8311 | 61.1106 | 6.4963 | 0.76558 | 0.4543 | 7.7162 | 12.63% | 13.43% | 9.079% | 1.1445 | 1.1552 | 1.0999
2010-07-13 | 38 | 47.3065 | 13.2201 | 60.5266 | 6.3728 | 0.76558 | 0.44996 | 7.5883 | 12.54% | 13.34% | 9.014% | 1.1433 | 1.1539 | 1.0991
2010-07-13 | 39 | 46.7185 | 12.7453 | 59.4638 | 6.1509 | 0.76558 | 0.44206 | 7.3586 | 12.37% | 13.17% | 8.898% | 1.1412 | 1.1516 | 1.0977
2010-07-13 | 40 | 46.4565 | 12.9648 | 59.4214 | 6.1421 | 0.76558 | 0.44175 | 7.3495 | 12.37% | 13.16% | 8.893% | 1.1411 | 1.1515 | 1.0976
2010-07-13 | 41 | 47.4812 | 13.1459 | 60.6271 | 6.3939 | 0.76558 | 0.45071 | 7.6102 | 12.55% | 13.36% | 9.025% | 1.1435 | 1.1541 | 1.0992
2010-07-13 | 42 | 47.2138 | 14.0718 | 61.2856 | 6.5336 | 0.76558 | 0.4556 | 7.7548 | 12.65% | 13.46% | 9.098% | 1.1449 | 1.1556 | 1.1001
2010-07-13 | 43 | 46.8493 | 15.4727 | 62.3219 | 6.7564 | 0.76558 | 0.46331 | 7.9853 | 12.81% | 13.63% | 9.213% | 1.147 | 1.1578 | 1.1015
2010-07-13 | 44 | 46.8726 | 13.8588 | 60.7314 | 6.416 | 0.76558 | 0.45148 | 7.633 | 12.57% | 13.37% | 9.037% | 1.1438 | 1.1544 | 1.0993
2010-07-13 | 45 | 46.7972 | 12.16 | 58.9572 | 6.0466 | 0.76558 | 0.4383 | 7.2504 | 12.3% | 13.08% | 8.842% | 1.1402 | 1.1505 | 1.097
2010-07-13 | 46 | 45.6026 | 11.0255 | 56.628 | 5.5782 | 0.76558 | 0.42098 | 6.7648 | 11.95% | 12.71% | 8.589% | 1.1357 | 1.1456 | 1.094
2010-07-13 | 47 | 44.8542 | 11.1579 | 56.0121 | 5.4576 | 0.76558 | 0.4164 | 6.6395 | 11.85% | 12.61% | 8.523% | 1.1345 | 1.1443 | 1.0932
2010-07-13 | 48 | 43.3157 | 11.5754 | 54.8912 | 5.2413 | 0.76558 | 0.40807 | 6.415 | 11.69% | 12.43% | 8.403% | 1.1323 | 1.142 | 1.0917
2010-07-14 | 1 | 40.4984 | 10.7182 | 51.2166 | 4.5631 | 0.76558 | 0.38075 | 5.7094 | 11.15% | 11.86% | 8.015% | 1.1255 | 1.1346 | 1.0871
2010-07-14 | 2 | 41.9923 | 10.6454 | 52.6378 | 4.8198 | 0.76558 | 0.39132 | 5.9767 | 11.35% | 12.08% | 8.164% | 1.1281 | 1.1374 | 1.0889
2010-07-14 | 3 | 40.3541 | 10.24 | 50.5941 | 4.4528 | 0.76558 | 0.37612 | 5.5945 | 11.06% | 11.77% | 7.95% | 1.1243 | 1.1333 | 1.0864
2010-07-14 | 4 | 38.2559 | 9.8736 | 48.1296 | 4.0296 | 0.76558 | 0.3578 | 5.1529 | 10.71% | 11.39% | 7.698% | 1.1199 | 1.1286 | 1.0834
2010-07-14 | 5 | 36.1152 | 9.5572 | 45.6723 | 3.6286 | 0.76558 | 0.33953 | 4.7337 | 10.36% | 11.03% | 7.452% | 1.1156 | 1.1239 | 1.0805
2010-07-14 | 6 | 35.2263 | 9.3724 | 44.5987 | 3.46 | 0.76558 | 0.33155 | 4.5572 | 10.22% | 10.87% | 7.347% | 1.1138 | 1.122 | 1.0793
2010-07-14 | 7 | 35.2999 | 9.3978 | 44.6977 | 3.4754 | 0.76558 | 0.33229 | 4.5733 | 10.23% | 10.89% | 7.356% | 1.114 | 1.1222 | 1.0794
2010-07-14 | 8 | 35.1462 | 9.3717 | 44.5179 | 3.4475 | 0.76558 | 0.33095 | 4.544 | 10.21% | 10.86% | 7.339% | 1.1137 | 1.1218 | 1.0792
2010-07-14 | 9 | 35.0453 | 9.4978 | 44.543 | 3.4514 | 0.76558 | 0.33114 | 4.5481 | 10.21% | 10.86% | 7.341% | 1.1137 | 1.1219 | 1.0792
2010-07-14 | 10 | 35.4639 | 9.6086 | 45.0725 | 3.5339 | 0.76558 | 0.33507 | 4.6346 | 10.28% | 10.94% | 7.393% | 1.1146 | 1.1228 | 1.0798
2010-07-14 | 11 | 35.7791 | 9.8167 | 45.5959 | 3.6165 | 0.76558 | 0.33897 | 4.721 | 10.35% | 11.02% | 7.445% | 1.1155 | 1.1238 | 1.0804
2010-07-14 | 12 | 37.1872 | 10.3034 | 47.4906 | 3.9233 | 0.76558 | 0.35305 | 5.0419 | 10.62% | 11.3% | 7.633% | 1.1188 | 1.1273 | 1.0826
2010-07-14 | 13 | 38.5651 | 11.3394 | 49.9044 | 4.3322 | 0.76558 | 0.371 | 5.4688 | 10.96% | 11.66% | 7.879% | 1.1231 | 1.132 | 1.0855
2010-07-14 | 14 | 41.9395 | 12.8587 | 54.7982 | 5.2236 | 0.76558 | 0.40738 | 6.3965 | 11.67% | 12.42% | 8.393% | 1.1322 | 1.1418 | 1.0916
2010-07-14 | 15 | 46.2498 | 14.5985 | 60.8483 | 6.4407 | 0.76558 | 0.45235 | 7.6586 | 12.59% | 13.39% | 9.05% | 1.144 | 1.1546 | 1.0995
2010-07-14 | 16 | 46.4912 | 15.1461 | 61.6373 | 6.6088 | 0.76558 | 0.45822 | 7.8326 | 12.71% | 13.52% | 9.137% | 1.1456 | 1.1563 | 1.1006
2010-07-14 | 17 | 46.7216 | 15.6259 | 62.3474 | 6.7619 | 0.76558 | 0.4635 | 7.991 | 12.82% | 13.64% | 9.215% | 1.147 | 1.1579 | 1.1015
2010-07-14 | 18 | 44.6344 | 14.8979 | 59.5323 | 6.1651 | 0.76558 | 0.44257 | 7.3733 | 12.39% | 13.18% | 8.905% | 1.1414 | 1.1518 | 1.0978
2010-07-14 | 19 | 44.9375 | 14.7124 | 59.6499 | 6.1895 | 0.76558 | 0.44344 | 7.3985 | 12.4% | 13.2% | 8.918% | 1.1416 | 1.152 | 1.0979
2010-07-14 | 20 | 45.8569 | 14.7704 | 60.6273 | 6.394 | 0.76558 | 0.45071 | 7.6103 | 12.55% | 13.36% | 9.025% | 1.1435 | 1.1541 | 1.0992
2010-07-14 | 21 | 46.8658 | 14.8513 | 61.7171 | 6.6259 | 0.76558 | 0.45881 | 7.8503 | 12.72% | 13.53% | 9.146% | 1.1457 | 1.1565 | 1.1007
2010-07-14 | 22 | 46.9839 | 15.2042 | 62.1882 | 6.7274 | 0.76558 | 0.46231 | 7.9553 | 12.79% | 13.61% | 9.198% | 1.1467 | 1.1576 | 1.1013
2010-07-14 | 23 | 45.9613 | 14.6233 | 60.5846 | 6.385 | 0.76558 | 0.45039 | 7.601 | 12.55% | 13.35% | 9.021% | 1.1435 | 1.1541 | 1.0991
2010-07-14 | 24 | 46.9764 | 16.2766 | 63.253 | 6.9598 | 0.76558 | 0.47023 | 8.1956 | 12.96% | 13.79% | 9.316% | 1.1489 | 1.1599 | 1.1027
2010-07-14 | 25 | 46.9149 | 15.1296 | 62.0444 | 6.6964 | 0.76558 | 0.46125 | 7.9232 | 12.77% | 13.59% | 9.182% | 1.1464 | 1.1572 | 1.1011
2010-07-14 | 26 | 46.9933 | 13.5545 | 60.5479 | 6.3772 | 0.76558 | 0.45012 | 7.5929 | 12.54% | 13.34% | 9.017% | 1.1434 | 1.154 | 1.0991
2010-07-14 | 27 | 46.0897 | 13.6165 | 59.7062 | 6.2012 | 0.76558 | 0.44386 | 7.4106 | 12.41% | 13.21% | 8.924% | 1.1417 | 1.1522 | 1.098
2010-07-14 | 28 | 44.7221 | 13.5577 | 58.2798 | 5.9084 | 0.76558 | 0.43326 | 7.1073 | 12.2% | 12.98% | 8.768% | 1.1389 | 1.1491 | 1.0961
2010-07-14 | 29 | 43.4738 | 12.8334 | 56.3072 | 5.5152 | 0.76558 | 0.41859 | 6.6994 | 11.9% | 12.66% | 8.555% | 1.135 | 1.1449 | 1.0935
2010-07-14 | 30 | 42.1897 | 12.5235 | 54.7132 | 5.2074 | 0.76558 | 0.40674 | 6.3797 | 11.66% | 12.41% | 8.384% | 1.132 | 1.1416 | 1.0915
2010-07-14 | 31 | 44.0915 | 12.4494 | 56.5409 | 5.5611 | 0.76558 | 0.42033 | 6.747 | 11.93% | 12.7% | 8.58% | 1.1355 | 1.1454 | 1.0939
2010-07-14 | 32 | 44.3987 | 12.1873 | 56.586 | 5.57 | 0.76558 | 0.42067 | 6.7562 | 11.94% | 12.7% | 8.585% | 1.1356 | 1.1455 | 1.0939
2010-07-14 | 33 | 44.4223 | 12.4652 | 56.8875 | 5.6295 | 0.76558 | 0.42291 | 6.818 | 11.98% | 12.75% | 8.617% | 1.1362 | 1.1462 | 1.0943
2010-07-14 | 34 | 45.9547 | 13.0186 | 58.9732 | 6.0499 | 0.76558 | 0.43841 | 7.2538 | 12.3% | 13.09% | 8.844% | 1.1403 | 1.1506 | 1.097
2010-07-14 | 35 | 46.8808 | 13.9723 | 60.8531 | 6.4417 | 0.76558 | 0.45239 | 7.6597 | 12.59% | 13.39% | 9.05% | 1.144 | 1.1546 | 1.0995
2010-07-14 | 36 | 46.8735 | 14.8859 | 61.7593 | 6.635 | 0.76558 | 0.45913 | 7.8597 | 12.73% | 13.54% | 9.15% | 1.1458 | 1.1566 | 1.1007
2010-07-14 | 37 | 46.8893 | 14.3086 | 61.1979 | 6.5149 | 0.76558 | 0.45495 | 7.7354 | 12.64% | 13.45% | 9.088% | 1.1447 | 1.1554 | 1.1
2010-07-14 | 38 | 47.0455 | 15.0426 | 62.0881 | 6.7058 | 0.76558 | 0.46157 | 7.933 | 12.78% | 13.59% | 9.187% | 1.1465 | 1.1573 | 1.1012
2010-07-14 | 39 | 47.1045 | 15.1903 | 62.2948 | 6.7505 | 0.76558 | 0.46311 | 7.9792 | 12.81% | 13.63% | 9.21% | 1.1469 | 1.1578 | 1.1014
2010-07-14 | 40 | 47.0621 | 14.7946 | 61.8567 | 6.6559 | 0.76558 | 0.45985 | 7.8813 | 12.74% | 13.56% | 9.161% | 1.146 | 1.1568 | 1.1008
2010-07-14 | 41 | 47.0812 | 14.2814 | 61.3626 | 6.55 | 0.76558 | 0.45618 | 7.7718 | 12.67% | 13.48% | 9.106% | 1.145 | 1.1557 | 1.1002
2010-07-14 | 42 | 47.1183 | 14.0284 | 61.1467 | 6.504 | 0.76558 | 0.45457 | 7.7242 | 12.63% | 13.44% | 9.083% | 1.1446 | 1.1553 | 1.0999
2010-07-14 | 43 | 46.8708 | 13.4756 | 60.3464 | 6.3349 | 0.76558 | 0.44862 | 7.5491 | 12.51% | 13.31% | 8.994% | 1.143 | 1.1535 | 1.0988
2010-07-14 | 44 | 46.9276 | 12.7177 | 59.6453 | 6.1885 | 0.76558 | 0.44341 | 7.3975 | 12.4% | 13.2% | 8.917% | 1.1416 | 1.152 | 1.0979
2010-07-14 | 45 | 45.121 | 11.4608 | 56.5818 | 5.5691 | 0.76558 | 0.42064 | 6.7554 | 11.94% | 12.7% | 8.584% | 1.1356 | 1.1455 | 1.0939
2010-07-14 | 46 | 40.3799 | 10.4963 | 50.8762 | 4.5026 | 0.76558 | 0.37822 | 5.6464 | 11.1% | 11.81% | 7.98% | 1.1248 | 1.1339 | 1.0867
2010-07-14 | 47 | 38.7576 | 10.6602 | 49.4178 | 4.2482 | 0.76558 | 0.36738 | 5.3811 | 10.89% | 11.59% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-07-14 | 48 | 36.7039 | 11.0959 | 47.7999 | 3.9745 | 0.76558 | 0.35535 | 5.0955 | 10.66% | 11.34% | 7.665% | 1.1193 | 1.1279 | 1.083
2010-07-15 | 1 | 33.4858 | 10.0586 | 43.5444 | 3.2984 | 0.76558 | 0.32371 | 4.3877 | 10.08% | 10.72% | 7.245% | 1.1121 | 1.1201 | 1.0781
2010-07-15 | 2 | 35.0081 | 9.968 | 44.9761 | 3.5188 | 0.76558 | 0.33436 | 4.6188 | 10.27% | 10.93% | 7.384% | 1.1144 | 1.1227 | 1.0797
2010-07-15 | 3 | 33.3445 | 9.5789 | 42.9234 | 3.205 | 0.76558 | 0.3191 | 4.2896 | 9.994% | 10.63% | 7.185% | 1.111 | 1.119 | 1.0774
2010-07-15 | 4 | 31.7757 | 9.2526 | 41.0283 | 2.9282 | 0.76558 | 0.30501 | 3.9988 | 9.746% | 10.37% | 7.008% | 1.108 | 1.1157 | 1.0754
2010-07-15 | 5 | 30.4414 | 8.9874 | 39.4288 | 2.7043 | 0.76558 | 0.29312 | 3.763 | 9.544% | 10.15% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-07-15 | 6 | 29.5498 | 8.804 | 38.3538 | 2.5589 | 0.76558 | 0.28513 | 3.6096 | 9.411% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-07-15 | 7 | 29.2087 | 8.7723 | 37.9809 | 2.5094 | 0.76558 | 0.28235 | 3.5573 | 9.366% | 9.965% | 6.734% | 1.1033 | 1.1107 | 1.0722
2010-07-15 | 8 | 29.2661 | 8.5811 | 37.8472 | 2.4917 | 0.76558 | 0.28136 | 3.5387 | 9.35% | 9.948% | 6.723% | 1.1031 | 1.1105 | 1.0721
2010-07-15 | 9 | 29.4104 | 8.6872 | 38.0975 | 2.5248 | 0.76558 | 0.28322 | 3.5736 | 9.38% | 9.98% | 6.744% | 1.1035 | 1.1109 | 1.0723
2010-07-15 | 10 | 28.9801 | 8.8654 | 37.8455 | 2.4915 | 0.76558 | 0.28135 | 3.5384 | 9.35% | 9.948% | 6.722% | 1.1031 | 1.1105 | 1.0721
2010-07-15 | 11 | 29.6661 | 8.9266 | 38.5928 | 2.5909 | 0.76558 | 0.2869 | 3.6434 | 9.441% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-07-15 | 12 | 30.4009 | 9.4218 | 39.8227 | 2.7586 | 0.76558 | 0.29605 | 3.8203 | 9.593% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-07-15 | 13 | 32.368 | 10.2604 | 42.6283 | 3.161 | 0.76558 | 0.3169 | 4.2435 | 9.955% | 10.59% | 7.157% | 1.1106 | 1.1185 | 1.0771
2010-07-15 | 14 | 35.8435 | 11.7841 | 47.6276 | 3.946 | 0.76558 | 0.35407 | 5.0656 | 10.64% | 11.32% | 7.647% | 1.119 | 1.1276 | 1.0828
2010-07-15 | 15 | 40.0504 | 12.9593 | 53.0097 | 4.8882 | 0.76558 | 0.39408 | 6.0478 | 11.41% | 12.14% | 8.203% | 1.1288 | 1.1382 | 1.0894
2010-07-15 | 16 | 41.5313 | 13.5856 | 55.1169 | 5.2845 | 0.76558 | 0.40975 | 6.4598 | 11.72% | 12.47% | 8.427% | 1.1328 | 1.1425 | 1.092
2010-07-15 | 17 | 43.9835 | 14.75 | 58.7335 | 6.0008 | 0.76558 | 0.43663 | 7.203 | 12.26% | 13.05% | 8.818% | 1.1398 | 1.1501 | 1.0967
2010-07-15 | 18 | 46.0503 | 15.3774 | 61.4277 | 6.5639 | 0.76558 | 0.45666 | 7.7862 | 12.68% | 13.49% | 9.114% | 1.1452 | 1.1559 | 1.1003
2010-07-15 | 19 | 46.9828 | 15.5733 | 62.5561 | 6.8073 | 0.76558 | 0.46505 | 8.0379 | 12.85% | 13.67% | 9.239% | 1.1474 | 1.1584 | 1.1018
2010-07-15 | 20 | 46.3785 | 15.245 | 61.6235 | 6.6058 | 0.76558 | 0.45812 | 7.8295 | 12.71% | 13.52% | 9.135% | 1.1455 | 1.1563 | 1.1005
2010-07-15 | 21 | 47.1399 | 15.2835 | 62.4234 | 6.7784 | 0.76558 | 0.46406 | 8.0081 | 12.83% | 13.65% | 9.224% | 1.1472 | 1.1581 | 1.1016
2010-07-15 | 22 | 47.1392 | 15.194 | 62.3333 | 6.7589 | 0.76558 | 0.46339 | 7.9878 | 12.81% | 13.63% | 9.214% | 1.147 | 1.1579 | 1.1015
2010-07-15 | 23 | 46.1684 | 14.8653 | 61.0337 | 6.48 | 0.76558 | 0.45373 | 7.6993 | 12.61% | 13.42% | 9.07% | 1.1444 | 1.155 | 1.0997
2010-07-15 | 24 | 44.9472 | 14.6078 | 59.555 | 6.1698 | 0.76558 | 0.44274 | 7.3781 | 12.39% | 13.18% | 8.908% | 1.1414 | 1.1518 | 1.0978
2010-07-15 | 25 | 42.3394 | 14.079 | 56.4183 | 5.537 | 0.76558 | 0.41942 | 6.722 | 11.91% | 12.68% | 8.567% | 1.1353 | 1.1452 | 1.0937
2010-07-15 | 26 | 40.3226 | 13.3267 | 53.6493 | 5.0068 | 0.76558 | 0.39884 | 6.1712 | 11.5% | 12.24% | 8.271% | 1.13 | 1.1395 | 1.0902
2010-07-15 | 27 | 40.8453 | 13.7777 | 54.623 | 5.1902 | 0.76558 | 0.40607 | 6.3619 | 11.65% | 12.39% | 8.374% | 1.1318 | 1.1415 | 1.0914
2010-07-15 | 28 | 40.6775 | 13.9982 | 54.6757 | 5.2002 | 0.76558 | 0.40647 | 6.3723 | 11.65% | 12.4% | 8.38% | 1.1319 | 1.1416 | 1.0915
2010-07-15 | 29 | 40.3043 | 13.6564 | 53.9607 | 5.0651 | 0.76558 | 0.40115 | 6.2319 | 11.55% | 12.29% | 8.304% | 1.1306 | 1.1401 | 1.0906
2010-07-15 | 30 | 39.1992 | 13.2878 | 52.487 | 4.7922 | 0.76558 | 0.39019 | 5.948 | 11.33% | 12.06% | 8.148% | 1.1278 | 1.1371 | 1.0887
2010-07-15 | 31 | 41.9586 | 13.394 | 55.3526 | 5.3298 | 0.76558 | 0.4115 | 6.5069 | 11.76% | 12.51% | 8.452% | 1.1332 | 1.143 | 1.0923
2010-07-15 | 32 | 42.9061 | 13.3082 | 56.2142 | 5.497 | 0.76558 | 0.4179 | 6.6805 | 11.88% | 12.64% | 8.545% | 1.1349 | 1.1447 | 1.0934
2010-07-15 | 33 | 42.3793 | 13.3716 | 55.7508 | 5.4068 | 0.76558 | 0.41446 | 6.5868 | 11.81% | 12.57% | 8.495% | 1.134 | 1.1438 | 1.0928
2010-07-15 | 34 | 43.1682 | 13.5992 | 56.7674 | 5.6057 | 0.76558 | 0.42202 | 6.7933 | 11.97% | 12.73% | 8.604% | 1.1359 | 1.1459 | 1.0941
2010-07-15 | 35 | 43.8542 | 14.041 | 57.8952 | 5.8307 | 0.76558 | 0.4304 | 7.0267 | 12.14% | 12.91% | 8.726% | 1.1381 | 1.1483 | 1.0956
2010-07-15 | 36 | 46.4519 | 14.9355 | 61.3874 | 6.5553 | 0.76558 | 0.45636 | 7.7772 | 12.67% | 13.48% | 9.109% | 1.1451 | 1.1558 | 1.1002
2010-07-15 | 37 | 46.1572 | 14.2611 | 60.4183 | 6.35 | 0.76558 | 0.44916 | 7.5647 | 12.52% | 13.32% | 9.002% | 1.1431 | 1.1537 | 1.0989
2010-07-15 | 38 | 47.0005 | 14.5728 | 61.5733 | 6.5951 | 0.76558 | 0.45774 | 7.8184 | 12.7% | 13.51% | 9.13% | 1.1454 | 1.1562 | 1.1005
2010-07-15 | 39 | 47.1209 | 14.6994 | 61.8203 | 6.6481 | 0.76558 | 0.45958 | 7.8732 | 12.74% | 13.55% | 9.157% | 1.1459 | 1.1567 | 1.1008
2010-07-15 | 40 | 47.14 | 13.7996 | 60.9395 | 6.46 | 0.76558 | 0.45303 | 7.6786 | 12.6% | 13.41% | 9.06% | 1.1442 | 1.1548 | 1.0996
2010-07-15 | 41 | 47.0815 | 13.5816 | 60.6631 | 6.4015 | 0.76558 | 0.45098 | 7.6181 | 12.56% | 13.36% | 9.029% | 1.1436 | 1.1542 | 1.0993
2010-07-15 | 42 | 47.1454 | 13.2047 | 60.35 | 6.3356 | 0.76558 | 0.44865 | 7.5499 | 12.51% | 13.31% | 8.995% | 1.143 | 1.1535 | 1.0988
2010-07-15 | 43 | 46.8301 | 12.5913 | 59.4214 | 6.1422 | 0.76558 | 0.44175 | 7.3495 | 12.37% | 13.16% | 8.893% | 1.1411 | 1.1515 | 1.0976
2010-07-15 | 44 | 44.7435 | 11.8225 | 56.566 | 5.566 | 0.76558 | 0.42052 | 6.7521 | 11.94% | 12.7% | 8.583% | 1.1355 | 1.1455 | 1.0939
2010-07-15 | 45 | 39.7181 | 10.6156 | 50.3337 | 4.4071 | 0.76558 | 0.37419 | 5.5469 | 11.02% | 11.73% | 7.924% | 1.1239 | 1.1328 | 1.0861
2010-07-15 | 46 | 35.1919 | 9.7499 | 44.9418 | 3.5135 | 0.76558 | 0.3341 | 4.6131 | 10.26% | 10.92% | 7.38% | 1.1144 | 1.1226 | 1.0797
2010-07-15 | 47 | 34.6613 | 10.0845 | 44.7458 | 3.4829 | 0.76558 | 0.33265 | 4.5811 | 10.24% | 10.89% | 7.361% | 1.1141 | 1.1223 | 1.0795
2010-07-15 | 48 | 33.5001 | 10.6743 | 44.1744 | 3.3945 | 0.76558 | 0.3284 | 4.4885 | 10.16% | 10.81% | 7.306% | 1.1131 | 1.1212 | 1.0788
2010-07-16 | 1 | 31.3593 | 9.7245 | 41.0838 | 2.9361 | 0.76558 | 0.30542 | 4.0071 | 9.754% | 10.38% | 7.013% | 1.1081 | 1.1158 | 1.0754
2010-07-16 | 2 | 32.618 | 9.559 | 42.177 | 3.0945 | 0.76558 | 0.31355 | 4.1736 | 9.895% | 10.53% | 7.115% | 1.1098 | 1.1177 | 1.0766
2010-07-16 | 3 | 31.1235 | 9.2016 | 40.3251 | 2.8287 | 0.76558 | 0.29978 | 3.8941 | 9.657% | 10.27% | 6.943% | 1.1069 | 1.1145 | 1.0746
2010-07-16 | 4 | 29.8442 | 8.8729 | 38.7171 | 2.6076 | 0.76558 | 0.28783 | 3.661 | 9.456% | 10.06% | 6.799% | 1.1044 | 1.1119 | 1.0729
2010-07-16 | 5 | 28.9413 | 8.6924 | 37.6337 | 2.4637 | 0.76558 | 0.27977 | 3.5091 | 9.324% | 9.921% | 6.704% | 1.1028 | 1.1101 | 1.0719
2010-07-16 | 6 | 27.8785 | 8.5163 | 36.3948 | 2.3042 | 0.76558 | 0.27056 | 3.3403 | 9.178% | 9.765% | 6.599% | 1.1011 | 1.1082 | 1.0707
2010-07-16 | 7 | 27.6184 | 8.3419 | 35.9603 | 2.2495 | 0.76558 | 0.26733 | 3.2824 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2010-07-16 | 8 | 27.3186 | 8.1982 | 35.5168 | 2.1943 | 0.76558 | 0.26404 | 3.2239 | 9.077% | 9.658% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-07-16 | 9 | 27.9787 | 8.4394 | 36.4181 | 2.3071 | 0.76558 | 0.27074 | 3.3434 | 9.181% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-07-16 | 10 | 27.9328 | 8.5245 | 36.4574 | 2.3121 | 0.76558 | 0.27103 | 3.3487 | 9.185% | 9.773% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-07-16 | 11 | 28.4936 | 8.6539 | 37.1474 | 2.4004 | 0.76558 | 0.27616 | 3.4422 | 9.266% | 9.859% | 6.662% | 1.1021 | 1.1094 | 1.0714
2010-07-16 | 12 | 29.3956 | 9.0075 | 38.4031 | 2.5655 | 0.76558 | 0.28549 | 3.6165 | 9.417% | 10.02% | 6.771% | 1.104 | 1.1114 | 1.0726
2010-07-16 | 13 | 31.9495 | 10.0055 | 41.9549 | 3.062 | 0.76558 | 0.3119 | 4.1394 | 9.866% | 10.5% | 7.094% | 1.1095 | 1.1173 | 1.0764
2010-07-16 | 14 | 35.1984 | 11.2952 | 46.4936 | 3.7603 | 0.76558 | 0.34564 | 4.8715 | 10.48% | 11.15% | 7.534% | 1.117 | 1.1255 | 1.0815
2010-07-16 | 15 | 39.3944 | 12.4292 | 51.8236 | 4.6719 | 0.76558 | 0.38526 | 5.8227 | 11.24% | 11.95% | 8.078% | 1.1266 | 1.1358 | 1.0879
2010-07-16 | 16 | 40.4121 | 13.1748 | 53.5869 | 4.9952 | 0.76558 | 0.39837 | 6.1591 | 11.49% | 12.23% | 8.264% | 1.1299 | 1.1393 | 1.0901
2010-07-16 | 17 | 42.9089 | 14.3435 | 57.2524 | 5.7019 | 0.76558 | 0.42562 | 6.8931 | 12.04% | 12.81% | 8.657% | 1.1369 | 1.1469 | 1.0948
2010-07-16 | 18 | 44.6471 | 15.0052 | 59.6523 | 6.19 | 0.76558 | 0.44346 | 7.399 | 12.4% | 13.2% | 8.918% | 1.1416 | 1.152 | 1.0979
2010-07-16 | 19 | 45.2945 | 14.9867 | 60.2812 | 6.3212 | 0.76558 | 0.44814 | 7.5349 | 12.5% | 13.3% | 8.987% | 1.1429 | 1.1534 | 1.0987
2010-07-16 | 20 | 45.0347 | 14.807 | 59.8416 | 6.2293 | 0.76558 | 0.44487 | 7.4398 | 12.43% | 13.23% | 8.939% | 1.142 | 1.1524 | 1.0982
2010-07-16 | 21 | 47.1031 | 15.0192 | 62.1223 | 6.7132 | 0.76558 | 0.46182 | 7.9406 | 12.78% | 13.6% | 9.19% | 1.1466 | 1.1574 | 1.1012
2010-07-16 | 22 | 47.074 | 14.7189 | 61.793 | 6.6422 | 0.76558 | 0.45938 | 7.8672 | 12.73% | 13.55% | 9.154% | 1.1459 | 1.1567 | 1.1008
2010-07-16 | 23 | 46.4417 | 14.2094 | 60.6511 | 6.399 | 0.76558 | 0.45089 | 7.6155 | 12.56% | 13.36% | 9.028% | 1.1436 | 1.1542 | 1.0992
2010-07-16 | 24 | 44.7533 | 14.002 | 58.7553 | 6.0052 | 0.76558 | 0.43679 | 7.2076 | 12.27% | 13.05% | 8.82% | 1.1398 | 1.1501 | 1.0967
2010-07-16 | 25 | 41.5207 | 13.6087 | 55.1295 | 5.2869 | 0.76558 | 0.40984 | 6.4623 | 11.72% | 12.47% | 8.428% | 1.1328 | 1.1425 | 1.092
2010-07-16 | 26 | 39.5841 | 13.0331 | 52.6171 | 4.816 | 0.76558 | 0.39116 | 5.9728 | 11.35% | 12.08% | 8.162% | 1.128 | 1.1374 | 1.0889
2010-07-16 | 27 | 39.2671 | 13.4146 | 52.6817 | 4.8278 | 0.76558 | 0.39164 | 5.9851 | 11.36% | 12.09% | 8.168% | 1.1282 | 1.1375 | 1.089
2010-07-16 | 28 | 39.8035 | 13.6405 | 53.444 | 4.9686 | 0.76558 | 0.39731 | 6.1315 | 11.47% | 12.21% | 8.249% | 1.1296 | 1.139 | 1.0899
2010-07-16 | 29 | 39.7626 | 13.4047 | 53.1673 | 4.9173 | 0.76558 | 0.39525 | 6.0781 | 11.43% | 12.16% | 8.22% | 1.1291 | 1.1385 | 1.0896
2010-07-16 | 30 | 39.4036 | 12.8538 | 52.2574 | 4.7504 | 0.76558 | 0.38849 | 5.9045 | 11.3% | 12.02% | 8.124% | 1.1274 | 1.1366 | 1.0884
2010-07-16 | 31 | 42.3098 | 13.0193 | 55.329 | 5.3253 | 0.76558 | 0.41132 | 6.5022 | 11.75% | 12.5% | 8.45% | 1.1332 | 1.1429 | 1.0923
2010-07-16 | 32 | 42.9187 | 12.888 | 55.8067 | 5.4176 | 0.76558 | 0.41487 | 6.5981 | 11.82% | 12.58% | 8.501% | 1.1341 | 1.1439 | 1.0929
2010-07-16 | 33 | 42.5268 | 13.0567 | 55.5835 | 5.3743 | 0.76558 | 0.41321 | 6.5531 | 11.79% | 12.54% | 8.477% | 1.1337 | 1.1434 | 1.0926
2010-07-16 | 34 | 43.4594 | 13.2734 | 56.7327 | 5.5989 | 0.76558 | 0.42176 | 6.7862 | 11.96% | 12.73% | 8.6% | 1.1359 | 1.1458 | 1.0941
2010-07-16 | 35 | 43.793 | 13.9898 | 57.7829 | 5.8081 | 0.76558 | 0.42956 | 7.0032 | 12.12% | 12.9% | 8.714% | 1.1379 | 1.148 | 1.0955
2010-07-16 | 36 | 46.8467 | 15.0384 | 61.885 | 6.662 | 0.76558 | 0.46006 | 7.8877 | 12.75% | 13.56% | 9.164% | 1.1461 | 1.1569 | 1.1009
2010-07-16 | 37 | 47.1661 | 14.3717 | 61.5378 | 6.5875 | 0.76558 | 0.45748 | 7.8105 | 12.69% | 13.5% | 9.126% | 1.1454 | 1.1561 | 1.1004
2010-07-16 | 38 | 47.1529 | 14.2682 | 61.4211 | 6.5625 | 0.76558 | 0.45661 | 7.7847 | 12.67% | 13.49% | 9.113% | 1.1451 | 1.1559 | 1.1003
2010-07-16 | 39 | 47.0974 | 14.5979 | 61.6953 | 6.6212 | 0.76558 | 0.45865 | 7.8455 | 12.72% | 13.53% | 9.143% | 1.1457 | 1.1565 | 1.1006
2010-07-16 | 40 | 47.081 | 13.7286 | 60.8096 | 6.4325 | 0.76558 | 0.45207 | 7.6501 | 12.58% | 13.39% | 9.045% | 1.1439 | 1.1545 | 1.0994
2010-07-16 | 41 | 47.2109 | 13.4926 | 60.7035 | 6.4101 | 0.76558 | 0.45128 | 7.6269 | 12.56% | 13.37% | 9.034% | 1.1437 | 1.1543 | 1.0993
2010-07-16 | 42 | 47.0787 | 13.2797 | 60.3584 | 6.3374 | 0.76558 | 0.44871 | 7.5517 | 12.51% | 13.31% | 8.996% | 1.143 | 1.1536 | 1.0988
2010-07-16 | 43 | 46.6516 | 12.5207 | 59.1724 | 6.0908 | 0.76558 | 0.43989 | 7.2962 | 12.33% | 13.12% | 8.866% | 1.1406 | 1.151 | 1.0973
2010-07-16 | 44 | 44.3067 | 11.9117 | 56.2184 | 5.4978 | 0.76558 | 0.41793 | 6.6814 | 11.88% | 12.65% | 8.545% | 1.1349 | 1.1448 | 1.0934
2010-07-16 | 45 | 39.6685 | 10.7453 | 50.4138 | 4.4211 | 0.76558 | 0.37478 | 5.5615 | 11.03% | 11.74% | 7.932% | 1.124 | 1.133 | 1.0862
2010-07-16 | 46 | 35.3261 | 9.703 | 45.0291 | 3.5271 | 0.76558 | 0.33475 | 4.6275 | 10.28% | 10.93% | 7.389% | 1.1145 | 1.1228 | 1.0798
2010-07-16 | 47 | 34.7512 | 10.1856 | 44.9368 | 3.5127 | 0.76558 | 0.33407 | 4.6123 | 10.26% | 10.92% | 7.38% | 1.1144 | 1.1226 | 1.0797
2010-07-16 | 48 | 33.6853 | 10.7432 | 44.4285 | 3.4337 | 0.76558 | 0.33029 | 4.5295 | 10.2% | 10.85% | 7.33% | 1.1135 | 1.1217 | 1.0791
2010-07-17 | 1 | 31.6849 | 9.7672 | 41.4522 | 2.989 | 0.76558 | 0.30816 | 4.0628 | 9.801% | 10.43% | 7.047% | 1.1087 | 1.1164 | 1.0758
2010-07-17 | 2 | 33.3671 | 9.6782 | 43.0453 | 3.2232 | 0.76558 | 0.32 | 4.3088 | 10.01% | 10.65% | 7.197% | 1.1112 | 1.1192 | 1.0776
2010-07-17 | 3 | 31.8702 | 9.1948 | 41.065 | 2.9334 | 0.76558 | 0.30528 | 4.0043 | 9.751% | 10.38% | 7.011% | 1.108 | 1.1158 | 1.0754
2010-07-17 | 4 | 30.7145 | 8.8589 | 39.5734 | 2.7242 | 0.76558 | 0.29419 | 3.784 | 9.562% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-07-17 | 5 | 29.6477 | 8.6472 | 38.2949 | 2.551 | 0.76558 | 0.28469 | 3.6013 | 9.404% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2010-07-17 | 6 | 28.809 | 8.3625 | 37.1716 | 2.4036 | 0.76558 | 0.27634 | 3.4455 | 9.269% | 9.862% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-07-17 | 7 | 28.7665 | 8.2152 | 36.9817 | 2.3791 | 0.76558 | 0.27493 | 3.4196 | 9.247% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-07-17 | 8 | 28.7189 | 8.1415 | 36.8604 | 2.3635 | 0.76558 | 0.27402 | 3.4031 | 9.232% | 9.823% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-07-17 | 9 | 28.9838 | 8.2109 | 37.1947 | 2.4066 | 0.76558 | 0.27651 | 3.4486 | 9.272% | 9.865% | 6.666% | 1.1022 | 1.1095 | 1.0714
2010-07-17 | 10 | 28.9584 | 8.2833 | 37.2417 | 2.4126 | 0.76558 | 0.27686 | 3.4551 | 9.277% | 9.871% | 6.67% | 1.1023 | 1.1095 | 1.0715
2010-07-17 | 11 | 29.4048 | 8.5557 | 37.9605 | 2.5067 | 0.76558 | 0.2822 | 3.5545 | 9.364% | 9.963% | 6.732% | 1.1033 | 1.1107 | 1.0722
2010-07-17 | 12 | 30.2551 | 8.8013 | 39.0563 | 2.6535 | 0.76558 | 0.29035 | 3.7094 | 9.498% | 10.11% | 6.829% | 1.1049 | 1.1124 | 1.0733
2010-07-17 | 13 | 32.4942 | 9.6094 | 42.1036 | 3.0837 | 0.76558 | 0.313 | 4.1623 | 9.886% | 10.52% | 7.108% | 1.1097 | 1.1175 | 1.0765
2010-07-17 | 14 | 36.1563 | 10.9609 | 47.1172 | 3.8618 | 0.76558 | 0.35027 | 4.9777 | 10.56% | 11.24% | 7.596% | 1.1181 | 1.1266 | 1.0822
2010-07-17 | 15 | 39.9763 | 12.3133 | 52.2897 | 4.7563 | 0.76558 | 0.38873 | 5.9106 | 11.3% | 12.03% | 8.127% | 1.1274 | 1.1367 | 1.0885
2010-07-17 | 16 | 41.0805 | 13.0261 | 54.1066 | 5.0926 | 0.76558 | 0.40224 | 6.2604 | 11.57% | 12.31% | 8.319% | 1.1308 | 1.1404 | 1.0907
2010-07-17 | 17 | 43.6256 | 14.269 | 57.8946 | 5.8306 | 0.76558 | 0.4304 | 7.0265 | 12.14% | 12.91% | 8.726% | 1.1381 | 1.1483 | 1.0956
2010-07-17 | 18 | 44.8878 | 14.7801 | 59.6679 | 6.1932 | 0.76558 | 0.44358 | 7.4024 | 12.41% | 13.2% | 8.92% | 1.1416 | 1.1521 | 1.0979
2010-07-17 | 19 | 44.7564 | 14.3422 | 59.0986 | 6.0756 | 0.76558 | 0.43935 | 7.2805 | 12.32% | 13.11% | 8.858% | 1.1405 | 1.1509 | 1.0972
2010-07-17 | 20 | 46.2339 | 15.0133 | 61.2472 | 6.5254 | 0.76558 | 0.45532 | 7.7463 | 12.65% | 13.46% | 9.094% | 1.1448 | 1.1555 | 1.1
2010-07-17 | 21 | 46.2769 | 14.9481 | 61.2251 | 6.5207 | 0.76558 | 0.45515 | 7.7414 | 12.64% | 13.45% | 9.091% | 1.1447 | 1.1554 | 1.1
2010-07-17 | 22 | 46.1328 | 14.9718 | 61.1046 | 6.495 | 0.76558 | 0.45426 | 7.7149 | 12.63% | 13.43% | 9.078% | 1.1445 | 1.1552 | 1.0998
2010-07-17 | 23 | 47.0328 | 14.4766 | 61.5094 | 6.5814 | 0.76558 | 0.45727 | 7.8042 | 12.69% | 13.5% | 9.123% | 1.1453 | 1.1561 | 1.1004
2010-07-17 | 24 | 45.9151 | 14.2689 | 60.184 | 6.3008 | 0.76558 | 0.44741 | 7.5138 | 12.48% | 13.28% | 8.977% | 1.1427 | 1.1532 | 1.0986
2010-07-17 | 25 | 42.816 | 13.9088 | 56.7248 | 5.5973 | 0.76558 | 0.4217 | 6.7846 | 11.96% | 12.73% | 8.6% | 1.1359 | 1.1458 | 1.0941
2010-07-17 | 26 | 39.6523 | 13.0335 | 52.6858 | 4.8286 | 0.76558 | 0.39167 | 5.9858 | 11.36% | 12.09% | 8.169% | 1.1282 | 1.1375 | 1.089
2010-07-17 | 27 | 39.3011 | 13.4618 | 52.763 | 4.8428 | 0.76558 | 0.39225 | 6.0006 | 11.37% | 12.1% | 8.177% | 1.1283 | 1.1377 | 1.0891
2010-07-17 | 28 | 39.4344 | 13.7649 | 53.1993 | 4.9232 | 0.76558 | 0.39549 | 6.0843 | 11.44% | 12.17% | 8.223% | 1.1291 | 1.1385 | 1.0896
2010-07-17 | 29 | 38.5122 | 13.4737 | 51.9858 | 4.7012 | 0.76558 | 0.38647 | 5.8532 | 11.26% | 11.98% | 8.095% | 1.1269 | 1.1361 | 1.0881
2010-07-17 | 30 | 37.9929 | 13.0145 | 51.0074 | 4.5259 | 0.76558 | 0.3792 | 5.6706 | 11.12% | 11.83% | 7.993% | 1.1251 | 1.1342 | 1.0869
2010-07-17 | 31 | 40.3171 | 13.0893 | 53.4064 | 4.9616 | 0.76558 | 0.39703 | 6.1242 | 11.47% | 12.2% | 8.245% | 1.1295 | 1.139 | 1.0899
2010-07-17 | 32 | 40.7141 | 12.9178 | 53.6319 | 5.0036 | 0.76558 | 0.39871 | 6.1679 | 11.5% | 12.24% | 8.269% | 1.1299 | 1.1394 | 1.0901
2010-07-17 | 33 | 40.2944 | 13.0777 | 53.3722 | 4.9552 | 0.76558 | 0.39678 | 6.1176 | 11.46% | 12.2% | 8.241% | 1.1295 | 1.1389 | 1.0898
2010-07-17 | 34 | 41.3458 | 12.8669 | 54.2127 | 5.1125 | 0.76558 | 0.40302 | 6.2811 | 11.59% | 12.33% | 8.33% | 1.131 | 1.1406 | 1.0909
2010-07-17 | 35 | 42.4937 | 13.2844 | 55.7781 | 5.4121 | 0.76558 | 0.41466 | 6.5923 | 11.82% | 12.58% | 8.498% | 1.134 | 1.1438 | 1.0929
2010-07-17 | 36 | 45.3248 | 14.0871 | 59.4119 | 6.1402 | 0.76558 | 0.44168 | 7.3474 | 12.37% | 13.16% | 8.892% | 1.1411 | 1.1515 | 1.0976
2010-07-17 | 37 | 47.1324 | 14.3066 | 61.439 | 6.5663 | 0.76558 | 0.45675 | 7.7887 | 12.68% | 13.49% | 9.115% | 1.1452 | 1.1559 | 1.1003
2010-07-17 | 38 | 47.1614 | 14.0883 | 61.2498 | 6.5259 | 0.76558 | 0.45534 | 7.7469 | 12.65% | 13.46% | 9.094% | 1.1448 | 1.1555 | 1.1
2010-07-17 | 39 | 47.1044 | 13.7127 | 60.8172 | 6.4341 | 0.76558 | 0.45212 | 7.6518 | 12.58% | 13.39% | 9.046% | 1.1439 | 1.1546 | 1.0995
2010-07-17 | 40 | 46.9884 | 13.5401 | 60.5285 | 6.3731 | 0.76558 | 0.44998 | 7.5887 | 12.54% | 13.34% | 9.014% | 1.1433 | 1.1539 | 1.0991
2010-07-17 | 41 | 47.1315 | 13.1111 | 60.2427 | 6.3131 | 0.76558 | 0.44785 | 7.5265 | 12.49% | 13.29% | 8.983% | 1.1428 | 1.1533 | 1.0987
2010-07-17 | 42 | 47.0562 | 12.7037 | 59.76 | 6.2123 | 0.76558 | 0.44426 | 7.4222 | 12.42% | 13.21% | 8.93% | 1.1418 | 1.1523 | 1.0981
2010-07-17 | 43 | 46.4525 | 12.226 | 58.6785 | 5.9895 | 0.76558 | 0.43622 | 7.1913 | 12.26% | 13.04% | 8.812% | 1.1397 | 1.15 | 1.0966
2010-07-17 | 44 | 45.7646 | 11.5239 | 57.2885 | 5.7091 | 0.76558 | 0.42589 | 6.9006 | 12.05% | 12.82% | 8.661% | 1.1369 | 1.147 | 1.0948
2010-07-17 | 45 | 42.63 | 10.7215 | 53.3515 | 4.9514 | 0.76558 | 0.39662 | 6.1136 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1389 | 1.0898
2010-07-17 | 46 | 39.2383 | 9.7704 | 49.0087 | 4.1781 | 0.76558 | 0.36434 | 5.308 | 10.83% | 11.52% | 7.787% | 1.1215 | 1.1302 | 1.0844
2010-07-17 | 47 | 38.606 | 10.1793 | 48.7853 | 4.1401 | 0.76558 | 0.36268 | 5.2684 | 10.8% | 11.49% | 7.765% | 1.1211 | 1.1298 | 1.0842
2010-07-17 | 48 | 37.6854 | 10.8548 | 48.5402 | 4.0986 | 0.76558 | 0.36085 | 5.225 | 10.76% | 11.45% | 7.74% | 1.1206 | 1.1293 | 1.0839
2010-07-18 | 1 | 35.7888 | 9.9054 | 45.6942 | 3.6321 | 0.76558 | 0.3397 | 4.7374 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-07-18 | 2 | 37.6183 | 9.6646 | 47.2829 | 3.889 | 0.76558 | 0.35151 | 5.0061 | 10.59% | 11.27% | 7.612% | 1.1184 | 1.127 | 1.0824
2010-07-18 | 3 | 36.2822 | 9.2296 | 45.5118 | 3.6031 | 0.76558 | 0.33834 | 4.7071 | 10.34% | 11% | 7.436% | 1.1154 | 1.1237 | 1.0803
2010-07-18 | 4 | 34.8727 | 8.9673 | 43.8399 | 3.3433 | 0.76558 | 0.32591 | 4.4348 | 10.12% | 10.76% | 7.273% | 1.1125 | 1.1206 | 1.0784
2010-07-18 | 5 | 33.7011 | 8.7671 | 42.4682 | 3.1373 | 0.76558 | 0.31571 | 4.2186 | 9.934% | 10.57% | 7.142% | 1.1103 | 1.1182 | 1.0769
2010-07-18 | 6 | 33.2842 | 8.5715 | 41.8557 | 3.0475 | 0.76558 | 0.31116 | 4.1242 | 9.853% | 10.48% | 7.085% | 1.1093 | 1.1171 | 1.0762
2010-07-18 | 7 | 33.1967 | 8.3932 | 41.5898 | 3.0089 | 0.76558 | 0.30918 | 4.0837 | 9.819% | 10.45% | 7.06% | 1.1089 | 1.1167 | 1.076
2010-07-18 | 8 | 32.2583 | 8.2434 | 40.5017 | 2.8535 | 0.76558 | 0.30109 | 3.9202 | 9.679% | 10.3% | 6.959% | 1.1072 | 1.1148 | 1.0748
2010-07-18 | 9 | 32.4074 | 8.2028 | 40.6102 | 2.8688 | 0.76558 | 0.3019 | 3.9363 | 9.693% | 10.31% | 6.969% | 1.1073 | 1.115 | 1.0749
2010-07-18 | 10 | 32.7818 | 8.3469 | 41.1286 | 2.9425 | 0.76558 | 0.30576 | 4.0139 | 9.759% | 10.38% | 7.017% | 1.1081 | 1.1159 | 1.0755
2010-07-18 | 11 | 33.47 | 8.3257 | 41.7957 | 3.0388 | 0.76558 | 0.31071 | 4.1151 | 9.846% | 10.48% | 7.079% | 1.1092 | 1.117 | 1.0762
2010-07-18 | 12 | 33.7159 | 8.6103 | 42.3261 | 3.1164 | 0.76558 | 0.31466 | 4.1966 | 9.915% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-07-18 | 13 | 34.2312 | 8.9745 | 43.2057 | 3.2473 | 0.76558 | 0.3212 | 4.334 | 10.03% | 10.67% | 7.212% | 1.1115 | 1.1195 | 1.0777
2010-07-18 | 14 | 36.0127 | 9.4141 | 45.4268 | 3.5897 | 0.76558 | 0.33771 | 4.693 | 10.33% | 10.99% | 7.428% | 1.1152 | 1.1235 | 1.0802
2010-07-18 | 15 | 37.6189 | 9.8026 | 47.4216 | 3.9119 | 0.76558 | 0.35254 | 5.03 | 10.61% | 11.29% | 7.626% | 1.1187 | 1.1272 | 1.0826
2010-07-18 | 16 | 36.5133 | 10.2648 | 46.7781 | 3.8064 | 0.76558 | 0.34775 | 4.9198 | 10.52% | 11.19% | 7.562% | 1.1175 | 1.126 | 1.0818
2010-07-18 | 17 | 38.3955 | 11.4301 | 49.8257 | 4.3186 | 0.76558 | 0.37041 | 5.4546 | 10.95% | 11.65% | 7.871% | 1.1229 | 1.1318 | 1.0854
2010-07-18 | 18 | 41.0262 | 12.6169 | 53.6431 | 5.0057 | 0.76558 | 0.39879 | 6.17 | 11.5% | 12.24% | 8.27% | 1.13 | 1.1394 | 1.0902
2010-07-18 | 19 | 43.0938 | 13.4395 | 56.5333 | 5.5596 | 0.76558 | 0.42028 | 6.7454 | 11.93% | 12.7% | 8.579% | 1.1355 | 1.1454 | 1.0938
2010-07-18 | 20 | 44.0278 | 13.6489 | 57.6767 | 5.7868 | 0.76558 | 0.42878 | 6.9811 | 12.1% | 12.88% | 8.703% | 1.1377 | 1.1478 | 1.0953
2010-07-18 | 21 | 46.741 | 13.7975 | 60.5385 | 6.3753 | 0.76558 | 0.45005 | 7.5909 | 12.54% | 13.34% | 9.016% | 1.1434 | 1.154 | 1.0991
2010-07-18 | 22 | 46.3507 | 13.4598 | 59.8105 | 6.2228 | 0.76558 | 0.44464 | 7.4331 | 12.43% | 13.22% | 8.936% | 1.1419 | 1.1524 | 1.0981
2010-07-18 | 23 | 44.1545 | 12.7126 | 56.8671 | 5.6254 | 0.76558 | 0.42276 | 6.8138 | 11.98% | 12.75% | 8.615% | 1.1361 | 1.1461 | 1.0943
2010-07-18 | 24 | 41.9003 | 12.1562 | 54.0565 | 5.0831 | 0.76558 | 0.40186 | 6.2506 | 11.56% | 12.3% | 8.314% | 1.1307 | 1.1403 | 1.0907
2010-07-18 | 25 | 38.7108 | 11.4229 | 50.1337 | 4.3721 | 0.76558 | 0.3727 | 5.5104 | 10.99% | 11.69% | 7.903% | 1.1235 | 1.1324 | 1.0858
2010-07-18 | 26 | 36.5297 | 10.6541 | 47.1838 | 3.8728 | 0.76558 | 0.35077 | 4.9891 | 10.57% | 11.25% | 7.603% | 1.1182 | 1.1268 | 1.0823
2010-07-18 | 27 | 36.1588 | 10.7759 | 46.9347 | 3.832 | 0.76558 | 0.34892 | 4.9465 | 10.54% | 11.21% | 7.578% | 1.1178 | 1.1263 | 1.082
2010-07-18 | 28 | 35.7435 | 10.8225 | 46.566 | 3.772 | 0.76558 | 0.34618 | 4.8838 | 10.49% | 11.16% | 7.541% | 1.1172 | 1.1256 | 1.0816
2010-07-18 | 29 | 35.1281 | 10.3952 | 45.5233 | 3.605 | 0.76558 | 0.33843 | 4.709 | 10.34% | 11.01% | 7.437% | 1.1154 | 1.1237 | 1.0804
2010-07-18 | 30 | 34.6248 | 10.0496 | 44.6744 | 3.4718 | 0.76558 | 0.33212 | 4.5695 | 10.23% | 10.88% | 7.354% | 1.1139 | 1.1221 | 1.0794
2010-07-18 | 31 | 37.2837 | 10.2335 | 47.5172 | 3.9277 | 0.76558 | 0.35325 | 5.0465 | 10.62% | 11.3% | 7.636% | 1.1188 | 1.1274 | 1.0827
2010-07-18 | 32 | 38.1035 | 10.0908 | 48.1943 | 4.0404 | 0.76558 | 0.35828 | 5.1643 | 10.72% | 11.4% | 7.704% | 1.12 | 1.1287 | 1.0835
2010-07-18 | 33 | 37.9756 | 10.066 | 48.0416 | 4.0148 | 0.76558 | 0.35715 | 5.1376 | 10.69% | 11.38% | 7.689% | 1.1197 | 1.1284 | 1.0833
2010-07-18 | 34 | 39.4147 | 10.1806 | 49.5953 | 4.2787 | 0.76558 | 0.3687 | 5.413 | 10.91% | 11.61% | 7.847% | 1.1225 | 1.1314 | 1.0852
2010-07-18 | 35 | 40.6652 | 11.2637 | 51.929 | 4.6909 | 0.76558 | 0.38605 | 5.8425 | 11.25% | 11.97% | 8.089% | 1.1268 | 1.136 | 1.088
2010-07-18 | 36 | 43.4228 | 12.8332 | 56.256 | 5.5052 | 0.76558 | 0.41821 | 6.689 | 11.89% | 12.65% | 8.549% | 1.1349 | 1.1448 | 1.0935
2010-07-18 | 37 | 44.7607 | 13.0113 | 57.772 | 5.8059 | 0.76558 | 0.42948 | 7.001 | 12.12% | 12.89% | 8.713% | 1.1379 | 1.148 | 1.0954
2010-07-18 | 38 | 44.3716 | 12.7365 | 57.1081 | 5.6732 | 0.76558 | 0.42455 | 6.8634 | 12.02% | 12.79% | 8.641% | 1.1366 | 1.1466 | 1.0946
2010-07-18 | 39 | 42.978 | 12.2311 | 55.2091 | 5.3022 | 0.76558 | 0.41043 | 6.4782 | 11.73% | 12.48% | 8.437% | 1.1329 | 1.1427 | 1.0921
2010-07-18 | 40 | 41.3391 | 11.6559 | 52.995 | 4.8854 | 0.76558 | 0.39397 | 6.045 | 11.41% | 12.14% | 8.201% | 1.1288 | 1.1381 | 1.0893
2010-07-18 | 41 | 42.1865 | 11.2923 | 53.4789 | 4.9751 | 0.76558 | 0.39757 | 6.1382 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.0899
2010-07-18 | 42 | 41.9033 | 10.7306 | 52.6339 | 4.8191 | 0.76558 | 0.39129 | 5.976 | 11.35% | 12.08% | 8.163% | 1.1281 | 1.1374 | 1.0889
2010-07-18 | 43 | 39.8454 | 10.4109 | 50.2563 | 4.3936 | 0.76558 | 0.37361 | 5.5327 | 11.01% | 11.71% | 7.916% | 1.1237 | 1.1327 | 1.086
2010-07-18 | 44 | 38.2204 | 10.1777 | 48.3981 | 4.0747 | 0.76558 | 0.3598 | 5.2 | 10.74% | 11.43% | 7.725% | 1.1204 | 1.1291 | 1.0837
2010-07-18 | 45 | 35.1299 | 9.449 | 44.5789 | 3.4569 | 0.76558 | 0.3314 | 4.5539 | 10.22% | 10.87% | 7.345% | 1.1138 | 1.1219 | 1.0793
2010-07-18 | 46 | 32.8055 | 8.8838 | 41.6893 | 3.0233 | 0.76558 | 0.30992 | 4.0988 | 9.832% | 10.46% | 7.069% | 1.109 | 1.1168 | 1.0761
2010-07-18 | 47 | 33.367 | 9.5156 | 42.8826 | 3.1989 | 0.76558 | 0.31879 | 4.2833 | 9.988% | 10.63% | 7.182% | 1.111 | 1.1189 | 1.0774
2010-07-18 | 48 | 32.5829 | 10.1805 | 42.7634 | 3.1811 | 0.76558 | 0.31791 | 4.2646 | 9.973% | 10.61% | 7.17% | 1.1108 | 1.1187 | 1.0772
2010-07-19 | 1 | 30.8909 | 9.4327 | 40.3236 | 2.8285 | 0.76558 | 0.29977 | 3.8938 | 9.656% | 10.27% | 6.943% | 1.1069 | 1.1145 | 1.0746
2010-07-19 | 2 | 32.8667 | 9.1 | 41.9667 | 3.0637 | 0.76558 | 0.31199 | 4.1412 | 9.868% | 10.5% | 7.095% | 1.1095 | 1.1173 | 1.0764
2010-07-19 | 3 | 31.8275 | 8.6431 | 40.4706 | 2.8491 | 0.76558 | 0.30086 | 3.9156 | 9.675% | 10.29% | 6.956% | 1.1071 | 1.1148 | 1.0748
2010-07-19 | 4 | 30.1353 | 8.3211 | 38.4564 | 2.5726 | 0.76558 | 0.28589 | 3.6241 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1114 | 1.0727
2010-07-19 | 5 | 29.1449 | 7.9677 | 37.1126 | 2.3959 | 0.76558 | 0.2759 | 3.4374 | 9.262% | 9.855% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-07-19 | 6 | 29.0007 | 7.8489 | 36.8496 | 2.3621 | 0.76558 | 0.27394 | 3.4016 | 9.231% | 9.822% | 6.637% | 1.1017 | 1.1089 | 1.0711
2010-07-19 | 7 | 29.158 | 7.7548 | 36.9128 | 2.3702 | 0.76558 | 0.27441 | 3.4102 | 9.239% | 9.83% | 6.643% | 1.1018 | 1.109 | 1.0712
2010-07-19 | 8 | 28.8467 | 7.7152 | 36.5618 | 2.3254 | 0.76558 | 0.27181 | 3.3627 | 9.197% | 9.786% | 6.613% | 1.1013 | 1.1085 | 1.0708
2010-07-19 | 9 | 28.6804 | 7.762 | 36.4424 | 2.3102 | 0.76558 | 0.27092 | 3.3467 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-07-19 | 10 | 29.2798 | 7.7059 | 36.9857 | 2.3796 | 0.76558 | 0.27496 | 3.4201 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-07-19 | 11 | 29.6936 | 7.8431 | 37.5367 | 2.451 | 0.76558 | 0.27905 | 3.4957 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-07-19 | 12 | 29.0459 | 7.9409 | 36.9868 | 2.3797 | 0.76558 | 0.27496 | 3.4203 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-07-19 | 13 | 29.6773 | 8.2498 | 37.9271 | 2.5023 | 0.76558 | 0.28195 | 3.5498 | 9.36% | 9.959% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-07-19 | 14 | 31.3051 | 8.5566 | 39.8617 | 2.7641 | 0.76558 | 0.29634 | 3.826 | 9.598% | 10.21% | 6.901% | 1.1062 | 1.1137 | 1.0741
2010-07-19 | 15 | 32.5873 | 8.5999 | 41.1871 | 2.9509 | 0.76558 | 0.30619 | 4.0227 | 9.767% | 10.39% | 7.022% | 1.1082 | 1.116 | 1.0755
2010-07-19 | 16 | 32.0341 | 8.8595 | 40.8936 | 2.909 | 0.76558 | 0.30401 | 3.9786 | 9.729% | 10.35% | 6.995% | 1.1078 | 1.1155 | 1.0752
2010-07-19 | 17 | 34.5587 | 9.9728 | 44.5315 | 3.4496 | 0.76558 | 0.33105 | 4.5462 | 10.21% | 10.86% | 7.34% | 1.1137 | 1.1219 | 1.0792
2010-07-19 | 18 | 36.9148 | 10.947 | 47.8617 | 3.9848 | 0.76558 | 0.35581 | 5.1062 | 10.67% | 11.35% | 7.671% | 1.1194 | 1.1281 | 1.0831
2010-07-19 | 19 | 38.9583 | 11.5783 | 50.5365 | 4.4427 | 0.76558 | 0.37569 | 5.584 | 11.05% | 11.76% | 7.944% | 1.1242 | 1.1332 | 1.0863
2010-07-19 | 20 | 40.5404 | 11.5813 | 52.1216 | 4.7258 | 0.76558 | 0.38748 | 5.8788 | 11.28% | 12% | 8.11% | 1.1271 | 1.1364 | 1.0883
2010-07-19 | 21 | 44.404 | 11.8628 | 56.2668 | 5.5073 | 0.76558 | 0.41829 | 6.6912 | 11.89% | 12.65% | 8.55% | 1.135 | 1.1449 | 1.0935
2010-07-19 | 22 | 43.9478 | 11.6786 | 55.6264 | 5.3826 | 0.76558 | 0.41353 | 6.5618 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-07-19 | 23 | 42.3446 | 11.2743 | 53.6188 | 5.0011 | 0.76558 | 0.39861 | 6.1653 | 11.5% | 12.23% | 8.267% | 1.1299 | 1.1394 | 1.0901
2010-07-19 | 24 | 40.7847 | 10.9802 | 51.765 | 4.6613 | 0.76558 | 0.38483 | 5.8117 | 11.23% | 11.95% | 8.072% | 1.1265 | 1.1357 | 1.0878
2010-07-19 | 25 | 38.0907 | 10.5178 | 48.6085 | 4.1102 | 0.76558 | 0.36136 | 5.2371 | 10.77% | 11.46% | 7.747% | 1.1208 | 1.1295 | 1.084
2010-07-19 | 26 | 36.2109 | 9.9331 | 46.144 | 3.704 | 0.76558 | 0.34304 | 4.8126 | 10.43% | 11.1% | 7.499% | 1.1164 | 1.1248 | 1.0811
2010-07-19 | 27 | 35.9156 | 10.3492 | 46.2648 | 3.7234 | 0.76558 | 0.34394 | 4.8329 | 10.45% | 11.11% | 7.511% | 1.1166 | 1.125 | 1.0812
2010-07-19 | 28 | 36.1574 | 10.6529 | 46.8103 | 3.8117 | 0.76558 | 0.34799 | 4.9253 | 10.52% | 11.2% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-07-19 | 29 | 35.5907 | 10.1053 | 45.696 | 3.6324 | 0.76558 | 0.33971 | 4.7377 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-07-19 | 30 | 34.8976 | 9.7572 | 44.6549 | 3.4687 | 0.76558 | 0.33197 | 4.5663 | 10.23% | 10.88% | 7.352% | 1.1139 | 1.1221 | 1.0794
2010-07-19 | 31 | 36.8708 | 9.6865 | 46.5573 | 3.7706 | 0.76558 | 0.34611 | 4.8823 | 10.49% | 11.16% | 7.54% | 1.1172 | 1.1256 | 1.0815
2010-07-19 | 32 | 37.776 | 9.5055 | 47.2815 | 3.8888 | 0.76558 | 0.3515 | 5.0059 | 10.59% | 11.27% | 7.612% | 1.1184 | 1.127 | 1.0824
2010-07-19 | 33 | 38.0337 | 9.728 | 47.7617 | 3.9682 | 0.76558 | 0.35507 | 5.0888 | 10.65% | 11.34% | 7.661% | 1.1193 | 1.1279 | 1.083
2010-07-19 | 34 | 39.4285 | 10.0264 | 49.4549 | 4.2545 | 0.76558 | 0.36765 | 5.3878 | 10.89% | 11.59% | 7.833% | 1.1223 | 1.1311 | 1.085
2010-07-19 | 35 | 40.6909 | 11.2599 | 51.9508 | 4.6948 | 0.76558 | 0.38621 | 5.8466 | 11.25% | 11.97% | 8.092% | 1.1268 | 1.136 | 1.088
2010-07-19 | 36 | 43.3165 | 13.1453 | 56.4618 | 5.5456 | 0.76558 | 0.41974 | 6.7309 | 11.92% | 12.68% | 8.571% | 1.1353 | 1.1453 | 1.0937
2010-07-19 | 37 | 46.116 | 13.5296 | 59.6456 | 6.1886 | 0.76558 | 0.44341 | 7.3976 | 12.4% | 13.2% | 8.917% | 1.1416 | 1.152 | 1.0979
2010-07-19 | 38 | 47.0358 | 13.2278 | 60.2636 | 6.3175 | 0.76558 | 0.44801 | 7.5311 | 12.5% | 13.3% | 8.985% | 1.1428 | 1.1534 | 1.0987
2010-07-19 | 39 | 46.5566 | 12.9016 | 59.4581 | 6.1497 | 0.76558 | 0.44202 | 7.3573 | 12.37% | 13.17% | 8.897% | 1.1412 | 1.1516 | 1.0977
2010-07-19 | 40 | 45.2528 | 12.6622 | 57.915 | 5.8347 | 0.76558 | 0.43055 | 7.0308 | 12.14% | 12.92% | 8.729% | 1.1382 | 1.1483 | 1.0956
2010-07-19 | 41 | 45.6629 | 12.4476 | 58.1105 | 5.8741 | 0.76558 | 0.432 | 7.0717 | 12.17% | 12.95% | 8.75% | 1.1386 | 1.1487 | 1.0959
2010-07-19 | 42 | 45.9745 | 11.9155 | 57.89 | 5.8296 | 0.76558 | 0.43036 | 7.0256 | 12.14% | 12.91% | 8.726% | 1.1381 | 1.1483 | 1.0956
2010-07-19 | 43 | 43.4591 | 11.3149 | 54.774 | 5.219 | 0.76558 | 0.4072 | 6.3917 | 11.67% | 12.42% | 8.39% | 1.1321 | 1.1418 | 1.0916
2010-07-19 | 44 | 40.9985 | 10.501 | 51.4994 | 4.6136 | 0.76558 | 0.38285 | 5.762 | 11.19% | 11.9% | 8.045% | 1.126 | 1.1351 | 1.0875
2010-07-19 | 45 | 37.0328 | 9.6826 | 46.7153 | 3.7962 | 0.76558 | 0.34729 | 4.9091 | 10.51% | 11.18% | 7.556% | 1.1174 | 1.1259 | 1.0817
2010-07-19 | 46 | 33.6559 | 8.5535 | 42.2094 | 3.0992 | 0.76558 | 0.31379 | 4.1786 | 9.9% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-07-19 | 47 | 33.6138 | 9.0141 | 42.628 | 3.161 | 0.76558 | 0.3169 | 4.2435 | 9.955% | 10.59% | 7.157% | 1.1106 | 1.1185 | 1.0771
2010-07-19 | 48 | 32.9081 | 9.6589 | 42.567 | 3.152 | 0.76558 | 0.31645 | 4.234 | 9.947% | 10.58% | 7.152% | 1.1105 | 1.1184 | 1.077
2010-07-20 | 1 | 31.1976 | 8.8158 | 40.0134 | 2.7851 | 0.76558 | 0.29746 | 3.8482 | 9.617% | 10.23% | 6.915% | 1.1064 | 1.114 | 1.0743
2010-07-20 | 2 | 32.866 | 8.533 | 41.399 | 2.9814 | 0.76558 | 0.30777 | 4.0547 | 9.794% | 10.42% | 7.042% | 1.1086 | 1.1163 | 1.0758
2010-07-20 | 3 | 32.147 | 8.1933 | 40.3403 | 2.8308 | 0.76558 | 0.29989 | 3.8963 | 9.659% | 10.28% | 6.945% | 1.1069 | 1.1145 | 1.0746
2010-07-20 | 4 | 30.9419 | 7.8411 | 38.783 | 2.6165 | 0.76558 | 0.28832 | 3.6704 | 9.464% | 10.07% | 6.805% | 1.1045 | 1.112 | 1.073
2010-07-20 | 5 | 29.9929 | 7.6169 | 37.6097 | 2.4606 | 0.76558 | 0.2796 | 3.5057 | 9.321% | 9.918% | 6.702% | 1.1028 | 1.1101 | 1.0718
2010-07-20 | 6 | 29.5636 | 7.4694 | 37.033 | 2.3857 | 0.76558 | 0.27531 | 3.4266 | 9.253% | 9.845% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-07-20 | 7 | 29.4186 | 7.3081 | 36.7267 | 2.3464 | 0.76558 | 0.27303 | 3.385 | 9.217% | 9.807% | 6.627% | 1.1015 | 1.1087 | 1.071
2010-07-20 | 8 | 29.6349 | 7.4299 | 37.0648 | 2.3898 | 0.76558 | 0.27554 | 3.4309 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-07-20 | 9 | 29.7912 | 7.6191 | 37.4104 | 2.4345 | 0.76558 | 0.27811 | 3.4782 | 9.298% | 9.893% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-07-20 | 10 | 29.7909 | 7.7107 | 37.5016 | 2.4464 | 0.76558 | 0.27879 | 3.4908 | 9.308% | 9.904% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-07-20 | 11 | 30.439 | 7.9409 | 38.3799 | 2.5624 | 0.76558 | 0.28532 | 3.6133 | 9.414% | 10.02% | 6.769% | 1.1039 | 1.1113 | 1.0726
2010-07-20 | 12 | 31.4416 | 8.4653 | 39.9069 | 2.7703 | 0.76558 | 0.29667 | 3.8326 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-07-20 | 13 | 33.4258 | 9.7438 | 43.1696 | 3.2418 | 0.76558 | 0.32093 | 4.3283 | 10.03% | 10.67% | 7.209% | 1.1114 | 1.1194 | 1.0777
2010-07-20 | 14 | 37.2595 | 11.3295 | 48.589 | 4.1069 | 0.76558 | 0.36122 | 5.2337 | 10.77% | 11.46% | 7.745% | 1.1207 | 1.1294 | 1.0839
2010-07-20 | 15 | 42.0993 | 13.4737 | 55.573 | 5.3723 | 0.76558 | 0.41314 | 6.551 | 11.79% | 12.54% | 8.476% | 1.1336 | 1.1434 | 1.0926
2010-07-20 | 16 | 42.8208 | 14.469 | 57.2898 | 5.7094 | 0.76558 | 0.4259 | 6.9009 | 12.05% | 12.82% | 8.661% | 1.137 | 1.147 | 1.0948
2010-07-20 | 17 | 42.9171 | 14.6748 | 57.5919 | 5.7698 | 0.76558 | 0.42815 | 6.9635 | 12.09% | 12.86% | 8.693% | 1.1375 | 1.1476 | 1.0952
2010-07-20 | 18 | 44.296 | 15.3253 | 59.6212 | 6.1835 | 0.76558 | 0.44323 | 7.3923 | 12.4% | 13.19% | 8.915% | 1.1415 | 1.152 | 1.0979
2010-07-20 | 19 | 46.1195 | 15.0988 | 61.2183 | 6.5192 | 0.76558 | 0.4551 | 7.7399 | 12.64% | 13.45% | 9.09% | 1.1447 | 1.1554 | 1.1
2010-07-20 | 20 | 45.1841 | 14.3498 | 59.5339 | 6.1654 | 0.76558 | 0.44258 | 7.3736 | 12.39% | 13.18% | 8.905% | 1.1414 | 1.1518 | 1.0978
2010-07-20 | 21 | 46.4496 | 13.9735 | 60.4231 | 6.351 | 0.76558 | 0.44919 | 7.5657 | 12.52% | 13.32% | 9.003% | 1.1431 | 1.1537 | 1.0989
2010-07-20 | 22 | 45.1132 | 13.5224 | 58.6356 | 5.9808 | 0.76558 | 0.4359 | 7.1823 | 12.25% | 13.03% | 8.807% | 1.1396 | 1.1499 | 1.0966
2010-07-20 | 23 | 42.8594 | 12.5215 | 55.3809 | 5.3352 | 0.76558 | 0.41171 | 6.5125 | 11.76% | 12.51% | 8.455% | 1.1333 | 1.143 | 1.0924
2010-07-20 | 24 | 40.448 | 11.9861 | 52.4341 | 4.7826 | 0.76558 | 0.3898 | 5.938 | 11.32% | 12.05% | 8.142% | 1.1277 | 1.137 | 1.0886
2010-07-20 | 25 | 37.2873 | 11.2023 | 48.4896 | 4.0901 | 0.76558 | 0.36048 | 5.2161 | 10.76% | 11.45% | 7.734% | 1.1205 | 1.1293 | 1.0838
2010-07-20 | 26 | 35.5658 | 10.3314 | 45.8972 | 3.6644 | 0.76558 | 0.34121 | 4.7712 | 10.4% | 11.06% | 7.474% | 1.116 | 1.1244 | 1.0808
2010-07-20 | 27 | 35.6379 | 10.6775 | 46.3154 | 3.7315 | 0.76558 | 0.34431 | 4.8414 | 10.45% | 11.12% | 7.516% | 1.1167 | 1.1251 | 1.0813
2010-07-20 | 28 | 35.7384 | 11.0434 | 46.7817 | 3.807 | 0.76558 | 0.34778 | 4.9204 | 10.52% | 11.19% | 7.562% | 1.1175 | 1.126 | 1.0818
2010-07-20 | 29 | 34.9575 | 10.5836 | 45.5411 | 3.6078 | 0.76558 | 0.33856 | 4.7119 | 10.35% | 11.01% | 7.439% | 1.1154 | 1.1237 | 1.0804
2010-07-20 | 30 | 34.5491 | 10.1519 | 44.701 | 3.4759 | 0.76558 | 0.33231 | 4.5738 | 10.23% | 10.89% | 7.357% | 1.114 | 1.1222 | 1.0794
2010-07-20 | 31 | 37.0626 | 10.2034 | 47.266 | 3.8863 | 0.76558 | 0.35138 | 5.0032 | 10.59% | 11.26% | 7.611% | 1.1184 | 1.1269 | 1.0824
2010-07-20 | 32 | 37.5841 | 10.2163 | 47.8003 | 3.9746 | 0.76558 | 0.35535 | 5.0956 | 10.66% | 11.34% | 7.665% | 1.1193 | 1.1279 | 1.083
2010-07-20 | 33 | 38.1901 | 10.4907 | 48.6808 | 4.1224 | 0.76558 | 0.3619 | 5.2499 | 10.78% | 11.47% | 7.754% | 1.1209 | 1.1296 | 1.0841
2010-07-20 | 34 | 40.389 | 11.1076 | 51.4966 | 4.6131 | 0.76558 | 0.38283 | 5.7615 | 11.19% | 11.9% | 8.044% | 1.126 | 1.1351 | 1.0875
2010-07-20 | 35 | 41.5962 | 12.0635 | 53.6596 | 5.0088 | 0.76558 | 0.39891 | 6.1733 | 11.5% | 12.24% | 8.272% | 1.13 | 1.1395 | 1.0902
2010-07-20 | 36 | 45.3999 | 13.8483 | 59.2482 | 6.1064 | 0.76558 | 0.44046 | 7.3124 | 12.34% | 13.13% | 8.874% | 1.1408 | 1.1512 | 1.0974
2010-07-20 | 37 | 45.5412 | 13.6639 | 59.2052 | 6.0975 | 0.76558 | 0.44014 | 7.3032 | 12.34% | 13.12% | 8.869% | 1.1407 | 1.1511 | 1.0973
2010-07-20 | 38 | 47.0022 | 14.1191 | 61.1213 | 6.4986 | 0.76558 | 0.45438 | 7.7186 | 12.63% | 13.44% | 9.08% | 1.1445 | 1.1552 | 1.0999
2010-07-20 | 39 | 46.1817 | 13.5118 | 59.6935 | 6.1985 | 0.76558 | 0.44377 | 7.4079 | 12.41% | 13.2% | 8.923% | 1.1417 | 1.1521 | 1.098
2010-07-20 | 40 | 44.7373 | 13.0658 | 57.803 | 5.8121 | 0.76558 | 0.42971 | 7.0074 | 12.12% | 12.9% | 8.716% | 1.138 | 1.1481 | 1.0955
2010-07-20 | 41 | 45.2255 | 12.8375 | 58.063 | 5.8645 | 0.76558 | 0.43165 | 7.0618 | 12.16% | 12.94% | 8.745% | 1.1385 | 1.1486 | 1.0958
2010-07-20 | 42 | 45.4547 | 12.2918 | 57.7465 | 5.8008 | 0.76558 | 0.42929 | 6.9956 | 12.11% | 12.89% | 8.71% | 1.1378 | 1.148 | 1.0954
2010-07-20 | 43 | 43.1126 | 11.7408 | 54.8534 | 5.2341 | 0.76558 | 0.40779 | 6.4075 | 11.68% | 12.43% | 8.399% | 1.1323 | 1.1419 | 1.0917
2010-07-20 | 44 | 40.2544 | 10.8821 | 51.1366 | 4.5488 | 0.76558 | 0.38016 | 5.6945 | 11.14% | 11.85% | 8.007% | 1.1253 | 1.1344 | 1.087
2010-07-20 | 45 | 35.5552 | 9.9049 | 45.4601 | 3.595 | 0.76558 | 0.33796 | 4.6985 | 10.34% | 11% | 7.431% | 1.1153 | 1.1236 | 1.0803
2010-07-20 | 46 | 32.0088 | 8.9063 | 40.9152 | 2.9121 | 0.76558 | 0.30417 | 3.9818 | 9.732% | 10.35% | 6.997% | 1.1078 | 1.1155 | 1.0752
2010-07-20 | 47 | 31.6338 | 9.2306 | 40.8644 | 2.9049 | 0.76558 | 0.30379 | 3.9742 | 9.725% | 10.35% | 6.993% | 1.1077 | 1.1154 | 1.0752
2010-07-20 | 48 | 30.815 | 9.805 | 40.6199 | 2.8702 | 0.76558 | 0.30197 | 3.9378 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2010-07-21 | 1 | 28.4754 | 9.1069 | 37.5823 | 2.457 | 0.76558 | 0.27939 | 3.5019 | 9.318% | 9.914% | 6.7% | 1.1028 | 1.1101 | 1.0718
2010-07-21 | 2 | 29.8396 | 8.8271 | 38.6667 | 2.6008 | 0.76558 | 0.28745 | 3.6538 | 9.45% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-07-21 | 3 | 28.7907 | 8.3921 | 37.1828 | 2.405 | 0.76558 | 0.27642 | 3.447 | 9.27% | 9.864% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-07-21 | 4 | 27.4964 | 8.0225 | 35.5189 | 2.1946 | 0.76558 | 0.26405 | 3.2242 | 9.077% | 9.658% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-07-21 | 5 | 26.3062 | 7.7574 | 34.0636 | 2.0184 | 0.76558 | 0.25323 | 3.0373 | 8.916% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2010-07-21 | 6 | 25.9205 | 7.553 | 33.4735 | 1.9491 | 0.76558 | 0.24885 | 2.9635 | 8.853% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-07-21 | 7 | 25.7077 | 7.5317 | 33.2394 | 1.9219 | 0.76558 | 0.24711 | 2.9346 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-07-21 | 8 | 25.4696 | 7.5307 | 33.0003 | 1.8944 | 0.76558 | 0.24533 | 2.9053 | 8.804% | 9.367% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-07-21 | 9 | 25.718 | 7.5701 | 33.2881 | 1.9276 | 0.76558 | 0.24747 | 2.9406 | 8.834% | 9.399% | 6.352% | 1.0969 | 1.1037 | 1.0678
2010-07-21 | 10 | 25.51 | 7.6706 | 33.1806 | 1.9152 | 0.76558 | 0.24667 | 2.9274 | 8.823% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-07-21 | 11 | 25.5899 | 7.8829 | 33.4728 | 1.949 | 0.76558 | 0.24884 | 2.9634 | 8.853% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-07-21 | 12 | 26.7112 | 8.4304 | 35.1417 | 2.1482 | 0.76558 | 0.26125 | 3.175 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-07-21 | 13 | 28.7027 | 9.4304 | 38.133 | 2.5295 | 0.76558 | 0.28349 | 3.5786 | 9.384% | 9.985% | 6.747% | 1.1036 | 1.1109 | 1.0724
2010-07-21 | 14 | 32.3146 | 11.0763 | 43.3908 | 3.2751 | 0.76558 | 0.32257 | 4.3633 | 10.06% | 10.7% | 7.23% | 1.1118 | 1.1198 | 1.0779
2010-07-21 | 15 | 36.6774 | 13.065 | 49.7424 | 4.3042 | 0.76558 | 0.36979 | 5.4395 | 10.94% | 11.64% | 7.863% | 1.1228 | 1.1317 | 1.0853
2010-07-21 | 16 | 38.0811 | 14.1273 | 52.2085 | 4.7415 | 0.76558 | 0.38812 | 5.8952 | 11.29% | 12.01% | 8.119% | 1.1273 | 1.1365 | 1.0884
2010-07-21 | 17 | 39.8054 | 14.6874 | 54.4928 | 5.1655 | 0.76558 | 0.40511 | 6.3362 | 11.63% | 12.37% | 8.36% | 1.1316 | 1.1412 | 1.0912
2010-07-21 | 18 | 40.0967 | 14.2249 | 54.3216 | 5.1331 | 0.76558 | 0.40383 | 6.3025 | 11.6% | 12.34% | 8.342% | 1.1313 | 1.1408 | 1.091
2010-07-21 | 19 | 39.9382 | 13.4076 | 53.3458 | 4.9503 | 0.76558 | 0.39658 | 6.1125 | 11.46% | 12.19% | 8.238% | 1.1294 | 1.1388 | 1.0898
2010-07-21 | 20 | 38.9789 | 12.8273 | 51.8062 | 4.6687 | 0.76558 | 0.38513 | 5.8194 | 11.23% | 11.95% | 8.077% | 1.1265 | 1.1357 | 1.0879
2010-07-21 | 21 | 41.0234 | 12.549 | 53.5724 | 4.9925 | 0.76558 | 0.39826 | 6.1563 | 11.49% | 12.23% | 8.262% | 1.1298 | 1.1393 | 1.0901
2010-07-21 | 22 | 40.9321 | 12.2587 | 53.1908 | 4.9216 | 0.76558 | 0.39543 | 6.0826 | 11.44% | 12.17% | 8.222% | 1.1291 | 1.1385 | 1.0896
2010-07-21 | 23 | 40.7001 | 11.2504 | 51.9505 | 4.6948 | 0.76558 | 0.38621 | 5.8466 | 11.25% | 11.97% | 8.092% | 1.1268 | 1.136 | 1.088
2010-07-21 | 24 | 40.6041 | 10.5835 | 51.1875 | 4.5579 | 0.76558 | 0.38053 | 5.704 | 11.14% | 11.86% | 8.012% | 1.1254 | 1.1345 | 1.0871
2010-07-21 | 25 | 38.2241 | 10.3099 | 48.5339 | 4.0976 | 0.76558 | 0.36081 | 5.2239 | 10.76% | 11.45% | 7.739% | 1.1206 | 1.1293 | 1.0839
2010-07-21 | 26 | 36.8019 | 9.6095 | 46.4114 | 3.747 | 0.76558 | 0.34503 | 4.8576 | 10.47% | 11.14% | 7.525% | 1.1169 | 1.1253 | 1.0814
2010-07-21 | 27 | 37.7355 | 10.1283 | 47.8638 | 3.9852 | 0.76558 | 0.35583 | 5.1066 | 10.67% | 11.35% | 7.671% | 1.1194 | 1.1281 | 1.0831
2010-07-21 | 28 | 38.7235 | 9.9795 | 48.7031 | 4.1262 | 0.76558 | 0.36206 | 5.2538 | 10.79% | 11.48% | 7.756% | 1.1209 | 1.1297 | 1.0841
2010-07-21 | 29 | 38.9666 | 10.5325 | 49.4991 | 4.2622 | 0.76558 | 0.36798 | 5.3957 | 10.9% | 11.6% | 7.838% | 1.1223 | 1.1312 | 1.085
2010-07-21 | 30 | 39.074 | 10.4924 | 49.5664 | 4.2738 | 0.76558 | 0.36848 | 5.4078 | 10.91% | 11.61% | 7.844% | 1.1225 | 1.1313 | 1.0851
2010-07-21 | 31 | 42.2482 | 11.1754 | 53.4236 | 4.9648 | 0.76558 | 0.39716 | 6.1275 | 11.47% | 12.2% | 8.247% | 1.1296 | 1.139 | 1.0899
2010-07-21 | 32 | 43.0598 | 11.7639 | 54.8237 | 5.2284 | 0.76558 | 0.40757 | 6.4016 | 11.68% | 12.42% | 8.396% | 1.1322 | 1.1419 | 1.0916
2010-07-21 | 33 | 42.9111 | 12.2145 | 55.1255 | 5.2862 | 0.76558 | 0.40981 | 6.4615 | 11.72% | 12.47% | 8.428% | 1.1328 | 1.1425 | 1.092
2010-07-21 | 34 | 42.9122 | 12.516 | 55.4282 | 5.3444 | 0.76558 | 0.41206 | 6.522 | 11.77% | 12.52% | 8.46% | 1.1334 | 1.1431 | 1.0924
2010-07-21 | 35 | 42.3254 | 12.9629 | 55.2883 | 5.3174 | 0.76558 | 0.41102 | 6.494 | 11.75% | 12.5% | 8.445% | 1.1331 | 1.1428 | 1.0922
2010-07-21 | 36 | 41.0979 | 12.6316 | 53.7295 | 5.0218 | 0.76558 | 0.39943 | 6.1868 | 11.51% | 12.25% | 8.279% | 1.1301 | 1.1396 | 1.0903
2010-07-21 | 37 | 43.0273 | 13.407 | 56.4343 | 5.5401 | 0.76558 | 0.41954 | 6.7253 | 11.92% | 12.68% | 8.568% | 1.1353 | 1.1452 | 1.0937
2010-07-21 | 38 | 46.1151 | 13.9881 | 60.1032 | 6.2839 | 0.76558 | 0.44681 | 7.4963 | 12.47% | 13.27% | 8.968% | 1.1425 | 1.153 | 1.0985
2010-07-21 | 39 | 46.4084 | 13.8165 | 60.2249 | 6.3094 | 0.76558 | 0.44772 | 7.5227 | 12.49% | 13.29% | 8.981% | 1.1427 | 1.1533 | 1.0987
2010-07-21 | 40 | 44.6219 | 13.1467 | 57.7686 | 5.8052 | 0.76558 | 0.42946 | 7.0003 | 12.12% | 12.89% | 8.713% | 1.1379 | 1.148 | 1.0954
2010-07-21 | 41 | 44.8844 | 12.6237 | 57.5081 | 5.753 | 0.76558 | 0.42752 | 6.9461 | 12.08% | 12.85% | 8.684% | 1.1374 | 1.1475 | 1.0951
2010-07-21 | 42 | 44.7952 | 12.2529 | 57.0482 | 5.6613 | 0.76558 | 0.4241 | 6.851 | 12.01% | 12.78% | 8.635% | 1.1365 | 1.1465 | 1.0945
2010-07-21 | 43 | 42.4163 | 11.7098 | 54.1261 | 5.0962 | 0.76558 | 0.40238 | 6.2642 | 11.57% | 12.31% | 8.321% | 1.1309 | 1.1404 | 1.0908
2010-07-21 | 44 | 39.9831 | 10.9247 | 50.9077 | 4.5082 | 0.76558 | 0.37845 | 5.6522 | 11.1% | 11.81% | 7.983% | 1.1249 | 1.134 | 1.0868
2010-07-21 | 45 | 35.8302 | 9.844 | 45.6742 | 3.6289 | 0.76558 | 0.33955 | 4.734 | 10.36% | 11.03% | 7.452% | 1.1156 | 1.124 | 1.0805
2010-07-21 | 46 | 32.1415 | 8.7928 | 40.9342 | 2.9148 | 0.76558 | 0.30431 | 3.9847 | 9.734% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2010-07-21 | 47 | 31.6273 | 9.1123 | 40.7396 | 2.8871 | 0.76558 | 0.30286 | 3.9556 | 9.709% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.0751
2010-07-21 | 48 | 30.8537 | 9.7282 | 40.582 | 2.8648 | 0.76558 | 0.30169 | 3.9321 | 9.689% | 10.31% | 6.967% | 1.1073 | 1.1149 | 1.0749
2010-07-22 | 1 | 28.7865 | 8.8957 | 37.6822 | 2.4701 | 0.76558 | 0.28013 | 3.5158 | 9.33% | 9.927% | 6.708% | 1.1029 | 1.1102 | 1.0719
2010-07-22 | 2 | 30.2543 | 8.6674 | 38.9217 | 2.6352 | 0.76558 | 0.28935 | 3.6902 | 9.481% | 10.09% | 6.817% | 1.1047 | 1.1122 | 1.0732
2010-07-22 | 3 | 29.2449 | 8.2948 | 37.5397 | 2.4514 | 0.76558 | 0.27907 | 3.4961 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-07-22 | 4 | 28.158 | 7.9253 | 36.0833 | 2.2649 | 0.76558 | 0.26825 | 3.2987 | 9.142% | 9.727% | 6.573% | 1.1006 | 1.1078 | 1.0704
2010-07-22 | 5 | 26.9151 | 7.7205 | 34.6356 | 2.0868 | 0.76558 | 0.25749 | 3.1099 | 8.979% | 9.553% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-07-22 | 6 | 26.453 | 7.5494 | 34.0024 | 2.0112 | 0.76558 | 0.25278 | 3.0295 | 8.91% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-07-22 | 7 | 26.434 | 7.5502 | 33.9842 | 2.009 | 0.76558 | 0.25264 | 3.0273 | 8.908% | 9.478% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-07-22 | 8 | 26.1436 | 7.4993 | 33.6429 | 1.9689 | 0.76558 | 0.25011 | 2.9846 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2010-07-22 | 9 | 26.5307 | 7.4734 | 34.0041 | 2.0114 | 0.76558 | 0.25279 | 3.0298 | 8.91% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-07-22 | 10 | 26.4561 | 7.7018 | 34.1579 | 2.0296 | 0.76558 | 0.25393 | 3.0491 | 8.927% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-07-22 | 11 | 26.9003 | 7.8404 | 34.7408 | 2.0995 | 0.76558 | 0.25827 | 3.1233 | 8.99% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-07-22 | 12 | 28.092 | 8.2028 | 36.2948 | 2.2915 | 0.76558 | 0.26982 | 3.3269 | 9.166% | 9.753% | 6.591% | 1.1009 | 1.1081 | 1.0706
2010-07-22 | 13 | 30.1304 | 9.2479 | 39.3783 | 2.6974 | 0.76558 | 0.29274 | 3.7557 | 9.538% | 10.15% | 6.858% | 1.1054 | 1.1129 | 1.0736
2010-07-22 | 14 | 33.379 | 10.8604 | 44.2394 | 3.4045 | 0.76558 | 0.32888 | 4.499 | 10.17% | 10.82% | 7.312% | 1.1132 | 1.1213 | 1.0789
2010-07-22 | 15 | 37.8308 | 12.795 | 50.6258 | 4.4584 | 0.76558 | 0.37636 | 5.6003 | 11.06% | 11.77% | 7.954% | 1.1244 | 1.1334 | 1.0864
2010-07-22 | 16 | 39.6935 | 13.9465 | 53.64 | 5.0051 | 0.76558 | 0.39877 | 6.1694 | 11.5% | 12.24% | 8.27% | 1.13 | 1.1394 | 1.0902
2010-07-22 | 17 | 41.9444 | 14.5676 | 56.512 | 5.5554 | 0.76558 | 0.42012 | 6.7411 | 11.93% | 12.69% | 8.577% | 1.1354 | 1.1454 | 1.0938
2010-07-22 | 18 | 42.8781 | 14.3888 | 57.2669 | 5.7048 | 0.76558 | 0.42573 | 6.8961 | 12.04% | 12.81% | 8.658% | 1.1369 | 1.147 | 1.0948
2010-07-22 | 19 | 43.2052 | 14.0187 | 57.2239 | 5.6963 | 0.76558 | 0.42541 | 6.8872 | 12.04% | 12.81% | 8.654% | 1.1368 | 1.1469 | 1.0947
2010-07-22 | 20 | 42.1774 | 13.4485 | 55.6259 | 5.3826 | 0.76558 | 0.41353 | 6.5617 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-07-22 | 21 | 43.0883 | 12.877 | 55.9653 | 5.4484 | 0.76558 | 0.41605 | 6.6301 | 11.85% | 12.6% | 8.518% | 1.1344 | 1.1442 | 1.0931
2010-07-22 | 22 | 42.2638 | 12.2547 | 54.5185 | 5.1704 | 0.76558 | 0.4053 | 6.3413 | 11.63% | 12.38% | 8.363% | 1.1316 | 1.1412 | 1.0913
2010-07-22 | 23 | 40.3712 | 11.3905 | 51.7617 | 4.6607 | 0.76558 | 0.3848 | 5.8111 | 11.23% | 11.95% | 8.072% | 1.1265 | 1.1357 | 1.0878
2010-07-22 | 24 | 38.5588 | 11.0921 | 49.6509 | 4.2883 | 0.76558 | 0.36911 | 5.423 | 10.92% | 11.62% | 7.853% | 1.1226 | 1.1315 | 1.0852
2010-07-22 | 25 | 36.2324 | 10.4418 | 46.6741 | 3.7895 | 0.76558 | 0.34698 | 4.9021 | 10.5% | 11.18% | 7.552% | 1.1174 | 1.1258 | 1.0817
2010-07-22 | 26 | 34.3544 | 9.7896 | 44.144 | 3.3898 | 0.76558 | 0.32817 | 4.4836 | 10.16% | 10.81% | 7.303% | 1.113 | 1.1212 | 1.0788
2010-07-22 | 27 | 34.6674 | 10.0725 | 44.7398 | 3.482 | 0.76558 | 0.3326 | 4.5801 | 10.24% | 10.89% | 7.361% | 1.114 | 1.1222 | 1.0795
2010-07-22 | 28 | 35.4551 | 10.3368 | 45.792 | 3.6477 | 0.76558 | 0.34042 | 4.7537 | 10.38% | 11.05% | 7.464% | 1.1158 | 1.1242 | 1.0807
2010-07-22 | 29 | 34.8898 | 9.909 | 44.7988 | 3.4911 | 0.76558 | 0.33304 | 4.5898 | 10.25% | 10.9% | 7.366% | 1.1141 | 1.1223 | 1.0795
2010-07-22 | 30 | 34.656 | 9.5776 | 44.2335 | 3.4036 | 0.76558 | 0.32884 | 4.498 | 10.17% | 10.82% | 7.311% | 1.1132 | 1.1213 | 1.0789
2010-07-22 | 31 | 36.6843 | 9.7234 | 46.4077 | 3.7464 | 0.76558 | 0.345 | 4.857 | 10.47% | 11.14% | 7.525% | 1.1169 | 1.1253 | 1.0814
2010-07-22 | 32 | 36.9708 | 9.7229 | 46.6937 | 3.7927 | 0.76558 | 0.34713 | 4.9054 | 10.51% | 11.18% | 7.553% | 1.1174 | 1.1258 | 1.0817
2010-07-22 | 33 | 36.3232 | 10.1424 | 46.4656 | 3.7558 | 0.76558 | 0.34543 | 4.8668 | 10.47% | 11.14% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-07-22 | 34 | 36.609 | 10.4978 | 47.1068 | 3.8601 | 0.76558 | 0.3502 | 4.9759 | 10.56% | 11.24% | 7.595% | 1.1181 | 1.1266 | 1.0822
2010-07-22 | 35 | 38.0848 | 11.31 | 49.3949 | 4.2442 | 0.76558 | 0.36721 | 5.377 | 10.89% | 11.58% | 7.827% | 1.1222 | 1.131 | 1.0849
2010-07-22 | 36 | 41.6594 | 12.9006 | 54.56 | 5.1783 | 0.76558 | 0.40561 | 6.3494 | 11.64% | 12.38% | 8.367% | 1.1317 | 1.1413 | 1.0913
2010-07-22 | 37 | 44.297 | 13.1934 | 57.4905 | 5.7494 | 0.76558 | 0.42739 | 6.9424 | 12.08% | 12.85% | 8.682% | 1.1373 | 1.1474 | 1.0951
2010-07-22 | 38 | 44.6213 | 13.0131 | 57.6344 | 5.7783 | 0.76558 | 0.42846 | 6.9723 | 12.1% | 12.87% | 8.698% | 1.1376 | 1.1477 | 1.0953
2010-07-22 | 39 | 43.5556 | 12.4107 | 55.9663 | 5.4486 | 0.76558 | 0.41606 | 6.6303 | 11.85% | 12.61% | 8.518% | 1.1344 | 1.1442 | 1.0931
2010-07-22 | 40 | 42.6618 | 12.0946 | 54.7564 | 5.2156 | 0.76558 | 0.40707 | 6.3882 | 11.67% | 12.41% | 8.388% | 1.1321 | 1.1417 | 1.0916
2010-07-22 | 41 | 43.2629 | 11.8569 | 55.1198 | 5.2851 | 0.76558 | 0.40977 | 6.4604 | 11.72% | 12.47% | 8.427% | 1.1328 | 1.1425 | 1.092
2010-07-22 | 42 | 43.0935 | 11.3678 | 54.4613 | 5.1595 | 0.76558 | 0.40487 | 6.33 | 11.62% | 12.37% | 8.357% | 1.1315 | 1.1411 | 1.0912
2010-07-22 | 43 | 40.84 | 10.8523 | 51.6923 | 4.6482 | 0.76558 | 0.38429 | 5.7981 | 11.22% | 11.93% | 8.065% | 1.1263 | 1.1355 | 1.0877
2010-07-22 | 44 | 38.4751 | 10.0438 | 48.5189 | 4.095 | 0.76558 | 0.3607 | 5.2213 | 10.76% | 11.45% | 7.737% | 1.1206 | 1.1293 | 1.0839
2010-07-22 | 45 | 34.0718 | 9.0424 | 43.1142 | 3.2335 | 0.76558 | 0.32052 | 4.3196 | 10.02% | 10.66% | 7.204% | 1.1113 | 1.1193 | 1.0776
2010-07-22 | 46 | 30.3516 | 8.0803 | 38.4319 | 2.5693 | 0.76558 | 0.28571 | 3.6206 | 9.421% | 10.02% | 6.774% | 1.104 | 1.1114 | 1.0727
2010-07-22 | 47 | 30.2266 | 8.4421 | 38.6687 | 2.6011 | 0.76558 | 0.28747 | 3.6541 | 9.45% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-07-22 | 48 | 29.4827 | 9.013 | 38.4957 | 2.5779 | 0.76558 | 0.28618 | 3.6296 | 9.429% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-07-23 | 1 | 27.6841 | 8.1267 | 35.8108 | 2.2308 | 0.76558 | 0.26622 | 3.2626 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1073 | 1.0701
2010-07-23 | 2 | 28.8578 | 7.9305 | 36.7883 | 2.3543 | 0.76558 | 0.27349 | 3.3933 | 9.224% | 9.814% | 6.632% | 1.1016 | 1.1088 | 1.071
2010-07-23 | 3 | 27.4429 | 7.5928 | 35.0357 | 2.1353 | 0.76558 | 0.26046 | 3.1613 | 9.023% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-07-23 | 4 | 26.4574 | 7.2878 | 33.7452 | 1.9809 | 0.76558 | 0.25087 | 2.9973 | 8.882% | 9.451% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-07-23 | 5 | 25.6344 | 6.9953 | 32.6297 | 1.8521 | 0.76558 | 0.24257 | 2.8602 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-07-23 | 6 | 25.2578 | 6.8884 | 32.1462 | 1.7976 | 0.76558 | 0.23898 | 2.8022 | 8.717% | 9.275% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-07-23 | 7 | 25.097 | 6.8503 | 31.9473 | 1.7754 | 0.76558 | 0.2375 | 2.7785 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-07-23 | 8 | 25.2968 | 6.8213 | 32.1181 | 1.7945 | 0.76558 | 0.23877 | 2.7988 | 8.714% | 9.272% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-07-23 | 9 | 25.1859 | 6.9872 | 32.1731 | 1.8006 | 0.76558 | 0.23918 | 2.8054 | 8.72% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-07-23 | 10 | 24.9842 | 7.1803 | 32.1644 | 1.7996 | 0.76558 | 0.23911 | 2.8043 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-07-23 | 11 | 25.5464 | 7.1607 | 32.7071 | 1.8609 | 0.76558 | 0.24315 | 2.8696 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-07-23 | 12 | 26.4916 | 7.5278 | 34.0194 | 2.0132 | 0.76558 | 0.2529 | 3.0317 | 8.912% | 9.482% | 6.407% | 1.0978 | 1.1048 | 1.0685
2010-07-23 | 13 | 28.6362 | 8.4923 | 37.1286 | 2.398 | 0.76558 | 0.27602 | 3.4396 | 9.264% | 9.857% | 6.661% | 1.1021 | 1.1093 | 1.0714
2010-07-23 | 14 | 32.0189 | 9.8419 | 41.8608 | 3.0482 | 0.76558 | 0.3112 | 4.125 | 9.854% | 10.48% | 7.085% | 1.1093 | 1.1171 | 1.0763
2010-07-23 | 15 | 36.5407 | 11.837 | 48.3777 | 4.0712 | 0.76558 | 0.35965 | 5.1964 | 10.74% | 11.43% | 7.723% | 1.1203 | 1.129 | 1.0837
2010-07-23 | 16 | 38.2593 | 12.9608 | 51.2201 | 4.5637 | 0.76558 | 0.38078 | 5.71 | 11.15% | 11.86% | 8.015% | 1.1255 | 1.1346 | 1.0871
2010-07-23 | 17 | 40.5479 | 13.4939 | 54.0418 | 5.0804 | 0.76558 | 0.40175 | 6.2477 | 11.56% | 12.3% | 8.312% | 1.1307 | 1.1403 | 1.0907
2010-07-23 | 18 | 41.8314 | 13.3969 | 55.2283 | 5.3059 | 0.76558 | 0.41057 | 6.482 | 11.74% | 12.49% | 8.439% | 1.133 | 1.1427 | 1.0922
2010-07-23 | 19 | 42.3463 | 12.9203 | 55.2666 | 5.3132 | 0.76558 | 0.41086 | 6.4897 | 11.74% | 12.49% | 8.443% | 1.133 | 1.1428 | 1.0922
2010-07-23 | 20 | 41.748 | 12.4419 | 54.19 | 5.1083 | 0.76558 | 0.40285 | 6.2767 | 11.58% | 12.32% | 8.328% | 1.131 | 1.1406 | 1.0908
2010-07-23 | 21 | 43.8373 | 12.5272 | 56.3645 | 5.5265 | 0.76558 | 0.41902 | 6.711 | 11.91% | 12.67% | 8.561% | 1.1352 | 1.1451 | 1.0936
2010-07-23 | 22 | 43.558 | 12.5805 | 56.1385 | 5.4822 | 0.76558 | 0.41734 | 6.6651 | 11.87% | 12.63% | 8.536% | 1.1347 | 1.1446 | 1.0933
2010-07-23 | 23 | 42.8111 | 12.1441 | 54.9552 | 5.2535 | 0.76558 | 0.40854 | 6.4277 | 11.7% | 12.44% | 8.41% | 1.1325 | 1.1421 | 1.0918
2010-07-23 | 24 | 41.9157 | 12.0352 | 53.9509 | 5.0633 | 0.76558 | 0.40108 | 6.2299 | 11.55% | 12.29% | 8.303% | 1.1305 | 1.1401 | 1.0905
2010-07-23 | 25 | 39.0216 | 11.6709 | 50.6925 | 4.4701 | 0.76558 | 0.37685 | 5.6126 | 11.07% | 11.78% | 7.961% | 1.1245 | 1.1335 | 1.0865
2010-07-23 | 26 | 37.6874 | 10.8156 | 48.503 | 4.0923 | 0.76558 | 0.36058 | 5.2185 | 10.76% | 11.45% | 7.736% | 1.1206 | 1.1293 | 1.0838
2010-07-23 | 27 | 37.389 | 10.7689 | 48.1579 | 4.0343 | 0.76558 | 0.35801 | 5.1579 | 10.71% | 11.4% | 7.701% | 1.12 | 1.1286 | 1.0834
2010-07-23 | 28 | 36.3513 | 10.7826 | 47.1339 | 3.8646 | 0.76558 | 0.3504 | 4.9805 | 10.57% | 11.24% | 7.598% | 1.1182 | 1.1267 | 1.0822
2010-07-23 | 29 | 35.3931 | 10.2239 | 45.617 | 3.6198 | 0.76558 | 0.33912 | 4.7245 | 10.36% | 11.02% | 7.447% | 1.1155 | 1.1238 | 1.0805
2010-07-23 | 30 | 35.1047 | 9.8823 | 44.987 | 3.5205 | 0.76558 | 0.33444 | 4.6206 | 10.27% | 10.93% | 7.385% | 1.1145 | 1.1227 | 1.0797
2010-07-23 | 31 | 36.9035 | 9.7299 | 46.6334 | 3.7829 | 0.76558 | 0.34668 | 4.8952 | 10.5% | 11.17% | 7.547% | 1.1173 | 1.1257 | 1.0816
2010-07-23 | 32 | 36.9608 | 9.7411 | 46.7018 | 3.794 | 0.76558 | 0.34719 | 4.9068 | 10.51% | 11.18% | 7.554% | 1.1174 | 1.1259 | 1.0817
2010-07-23 | 33 | 36.0591 | 9.9623 | 46.0215 | 3.6843 | 0.76558 | 0.34213 | 4.792 | 10.41% | 11.08% | 7.487% | 1.1162 | 1.1246 | 1.0809
2010-07-23 | 34 | 36.461 | 10.068 | 46.529 | 3.766 | 0.76558 | 0.3459 | 4.8775 | 10.48% | 11.15% | 7.537% | 1.1171 | 1.1255 | 1.0815
2010-07-23 | 35 | 37.4711 | 11.0493 | 48.5204 | 4.0953 | 0.76558 | 0.36071 | 5.2216 | 10.76% | 11.45% | 7.738% | 1.1206 | 1.1293 | 1.0839
2010-07-23 | 36 | 40.6186 | 12.5112 | 53.1298 | 4.9103 | 0.76558 | 0.39497 | 6.0709 | 11.43% | 12.16% | 8.216% | 1.129 | 1.1384 | 1.0895
2010-07-23 | 37 | 43.7025 | 13.0374 | 56.7399 | 5.6003 | 0.76558 | 0.42181 | 6.7877 | 11.96% | 12.73% | 8.601% | 1.1359 | 1.1458 | 1.0941
2010-07-23 | 38 | 45.0304 | 12.9165 | 57.9468 | 5.8411 | 0.76558 | 0.43078 | 7.0375 | 12.14% | 12.92% | 8.732% | 1.1382 | 1.1484 | 1.0957
2010-07-23 | 39 | 44.5041 | 12.7188 | 57.2229 | 5.6961 | 0.76558 | 0.4254 | 6.887 | 12.04% | 12.81% | 8.653% | 1.1368 | 1.1469 | 1.0947
2010-07-23 | 40 | 43.3326 | 12.2931 | 55.6257 | 5.3825 | 0.76558 | 0.41353 | 6.5616 | 11.8% | 12.55% | 8.481% | 1.1337 | 1.1435 | 1.0927
2010-07-23 | 41 | 43.7125 | 12.0091 | 55.7216 | 5.4011 | 0.76558 | 0.41424 | 6.5809 | 11.81% | 12.57% | 8.492% | 1.1339 | 1.1437 | 1.0928
2010-07-23 | 42 | 44.1799 | 11.7443 | 55.9243 | 5.4405 | 0.76558 | 0.41575 | 6.6218 | 11.84% | 12.6% | 8.513% | 1.1343 | 1.1441 | 1.0931
2010-07-23 | 43 | 42.6974 | 11.1926 | 53.89 | 5.0518 | 0.76558 | 0.40062 | 6.2181 | 11.54% | 12.28% | 8.296% | 1.1304 | 1.14 | 1.0905
2010-07-23 | 44 | 41.6167 | 10.5088 | 52.1254 | 4.7264 | 0.76558 | 0.38751 | 5.8795 | 11.28% | 12% | 8.11% | 1.1271 | 1.1364 | 1.0883
2010-07-23 | 45 | 36.5786 | 9.5815 | 46.1601 | 3.7065 | 0.76558 | 0.34316 | 4.8153 | 10.43% | 11.1% | 7.5% | 1.1165 | 1.1249 | 1.0811
2010-07-23 | 46 | 32.3347 | 8.6393 | 40.974 | 2.9205 | 0.76558 | 0.30461 | 3.9906 | 9.739% | 10.36% | 7.003% | 1.1079 | 1.1156 | 1.0753
2010-07-23 | 47 | 32.2254 | 8.9278 | 41.1533 | 2.9461 | 0.76558 | 0.30594 | 4.0176 | 9.763% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-07-23 | 48 | 31.1554 | 9.3815 | 40.5369 | 2.8585 | 0.76558 | 0.30136 | 3.9254 | 9.684% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-07-24 | 1 | 29.4628 | 8.6025 | 38.0653 | 2.5205 | 0.76558 | 0.28298 | 3.5691 | 9.376% | 9.976% | 6.742% | 1.1035 | 1.1108 | 1.0723
2010-07-24 | 2 | 31.0961 | 8.3831 | 39.4791 | 2.7113 | 0.76558 | 0.29349 | 3.7703 | 9.55% | 10.16% | 6.867% | 1.1056 | 1.1131 | 1.0737
2010-07-24 | 3 | 29.713 | 7.8103 | 37.5233 | 2.4493 | 0.76558 | 0.27895 | 3.4938 | 9.311% | 9.907% | 6.695% | 1.1027 | 1.11 | 1.0717
2010-07-24 | 4 | 29.0414 | 7.4553 | 36.4968 | 2.3171 | 0.76558 | 0.27132 | 3.354 | 9.19% | 9.778% | 6.607% | 1.1012 | 1.1084 | 1.0707
2010-07-24 | 5 | 28.0755 | 7.2019 | 35.2774 | 2.1648 | 0.76558 | 0.26226 | 3.1927 | 9.05% | 9.629% | 6.507% | 1.0995 | 1.1066 | 1.0696
2010-07-24 | 6 | 26.6627 | 7.0281 | 33.6908 | 1.9745 | 0.76558 | 0.25046 | 2.9905 | 8.876% | 9.445% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-07-24 | 7 | 26.3123 | 6.8759 | 33.1882 | 1.916 | 0.76558 | 0.24673 | 2.9283 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-07-24 | 8 | 26.4631 | 6.8256 | 33.2887 | 1.9277 | 0.76558 | 0.24747 | 2.9407 | 8.834% | 9.399% | 6.352% | 1.0969 | 1.1037 | 1.0678
2010-07-24 | 9 | 27.0144 | 6.9446 | 33.9591 | 2.0061 | 0.76558 | 0.25246 | 3.0241 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2010-07-24 | 10 | 26.872 | 7.1383 | 34.0103 | 2.0121 | 0.76558 | 0.25284 | 3.0305 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2010-07-24 | 11 | 28.2288 | 7.5145 | 35.7432 | 2.2224 | 0.76558 | 0.26572 | 3.2537 | 9.103% | 9.686% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-07-24 | 12 | 30.3348 | 7.835 | 38.1697 | 2.5344 | 0.76558 | 0.28376 | 3.5837 | 9.389% | 9.99% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-07-24 | 13 | 31.0763 | 8.8252 | 39.9015 | 2.7696 | 0.76558 | 0.29663 | 3.8318 | 9.603% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-07-24 | 14 | 34.0433 | 10.335 | 44.3783 | 3.4259 | 0.76558 | 0.32991 | 4.5214 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-07-24 | 15 | 38.5302 | 12.2816 | 50.8117 | 4.4912 | 0.76558 | 0.37774 | 5.6345 | 11.09% | 11.8% | 7.973% | 1.1247 | 1.1338 | 1.0866
2010-07-24 | 16 | 40.5194 | 13.4904 | 54.0099 | 5.0744 | 0.76558 | 0.40152 | 6.2414 | 11.56% | 12.3% | 8.309% | 1.1307 | 1.1402 | 1.0906
2010-07-24 | 17 | 42.1082 | 14.3094 | 56.4176 | 5.5369 | 0.76558 | 0.41942 | 6.7219 | 11.91% | 12.68% | 8.567% | 1.1353 | 1.1452 | 1.0937
2010-07-24 | 18 | 42.7931 | 14.3148 | 57.108 | 5.6732 | 0.76558 | 0.42455 | 6.8633 | 12.02% | 12.79% | 8.641% | 1.1366 | 1.1466 | 1.0946
2010-07-24 | 19 | 43.0478 | 14.1358 | 57.1836 | 5.6882 | 0.76558 | 0.42511 | 6.8789 | 12.03% | 12.8% | 8.649% | 1.1367 | 1.1468 | 1.0947
2010-07-24 | 20 | 42.4643 | 13.5993 | 56.0637 | 5.4676 | 0.76558 | 0.41678 | 6.65 | 11.86% | 12.62% | 8.528% | 1.1346 | 1.1444 | 1.0932
2010-07-24 | 21 | 43.8224 | 13.1982 | 57.0206 | 5.6559 | 0.76558 | 0.4239 | 6.8453 | 12.01% | 12.77% | 8.632% | 1.1364 | 1.1464 | 1.0945
2010-07-24 | 22 | 43.0115 | 12.726 | 55.7375 | 5.4042 | 0.76558 | 0.41436 | 6.5841 | 11.81% | 12.57% | 8.493% | 1.134 | 1.1438 | 1.0928
2010-07-24 | 23 | 40.9805 | 12.3166 | 53.2971 | 4.9413 | 0.76558 | 0.39622 | 6.1031 | 11.45% | 12.18% | 8.233% | 1.1293 | 1.1387 | 1.0897
2010-07-24 | 24 | 39.456 | 12.0412 | 51.4972 | 4.6132 | 0.76558 | 0.38284 | 5.7616 | 11.19% | 11.9% | 8.044% | 1.126 | 1.1351 | 1.0875
2010-07-24 | 25 | 36.8553 | 11.5346 | 48.39 | 4.0733 | 0.76558 | 0.35974 | 5.1986 | 10.74% | 11.43% | 7.724% | 1.1204 | 1.1291 | 1.0837
2010-07-24 | 26 | 35.074 | 10.9013 | 45.9754 | 3.6769 | 0.76558 | 0.34179 | 4.7843 | 10.41% | 11.07% | 7.482% | 1.1161 | 1.1245 | 1.0809
2010-07-24 | 27 | 35.7612 | 11.5092 | 47.2704 | 3.887 | 0.76558 | 0.35141 | 5.004 | 10.59% | 11.26% | 7.611% | 1.1184 | 1.1269 | 1.0824
2010-07-24 | 28 | 36.3702 | 11.6422 | 48.0124 | 4.01 | 0.76558 | 0.35693 | 5.1325 | 10.69% | 11.37% | 7.686% | 1.1197 | 1.1283 | 1.0833
2010-07-24 | 29 | 36.4034 | 10.9327 | 47.3362 | 3.8978 | 0.76558 | 0.3519 | 5.0153 | 10.6% | 11.27% | 7.618% | 1.1185 | 1.1271 | 1.0825
2010-07-24 | 30 | 35.8559 | 10.6631 | 46.519 | 3.7644 | 0.76558 | 0.34583 | 4.8758 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-07-24 | 31 | 37.7926 | 10.8513 | 48.6438 | 4.1161 | 0.76558 | 0.36162 | 5.2433 | 10.78% | 11.47% | 7.75% | 1.1208 | 1.1295 | 1.084
2010-07-24 | 32 | 38.592 | 11.0953 | 49.6873 | 4.2946 | 0.76558 | 0.36938 | 5.4296 | 10.93% | 11.63% | 7.857% | 1.1227 | 1.1316 | 1.0853
2010-07-24 | 33 | 39.1793 | 11.3391 | 50.5184 | 4.4395 | 0.76558 | 0.37556 | 5.5806 | 11.05% | 11.75% | 7.943% | 1.1242 | 1.1332 | 1.0863
2010-07-24 | 34 | 40.5687 | 11.377 | 51.9457 | 4.6939 | 0.76558 | 0.38617 | 5.8457 | 11.25% | 11.97% | 8.091% | 1.1268 | 1.136 | 1.088
2010-07-24 | 35 | 41.2268 | 11.8663 | 53.0931 | 4.9035 | 0.76558 | 0.3947 | 6.0638 | 11.42% | 12.15% | 8.212% | 1.1289 | 1.1383 | 1.0895
2010-07-24 | 36 | 43.648 | 12.8234 | 56.4714 | 5.5474 | 0.76558 | 0.41982 | 6.7328 | 11.92% | 12.69% | 8.572% | 1.1354 | 1.1453 | 1.0938
2010-07-24 | 37 | 46.0466 | 13.2616 | 59.3082 | 6.1188 | 0.76558 | 0.4409 | 7.3252 | 12.35% | 13.14% | 8.88% | 1.1409 | 1.1513 | 1.0975
2010-07-24 | 38 | 47.2075 | 13.0204 | 60.2279 | 6.31 | 0.76558 | 0.44774 | 7.5233 | 12.49% | 13.29% | 8.981% | 1.1427 | 1.1533 | 1.0987
2010-07-24 | 39 | 46.4849 | 12.7973 | 59.2821 | 6.1134 | 0.76558 | 0.44071 | 7.3197 | 12.35% | 13.14% | 8.878% | 1.1409 | 1.1512 | 1.0974
2010-07-24 | 40 | 45.4772 | 12.3407 | 57.8178 | 5.8151 | 0.76558 | 0.42982 | 7.0105 | 12.13% | 12.9% | 8.718% | 1.138 | 1.1481 | 1.0955
2010-07-24 | 41 | 46.2769 | 12.053 | 58.3299 | 5.9186 | 0.76558 | 0.43363 | 7.1178 | 12.2% | 12.98% | 8.774% | 1.139 | 1.1492 | 1.0962
2010-07-24 | 42 | 46.7021 | 11.5683 | 58.2704 | 5.9065 | 0.76558 | 0.43319 | 7.1053 | 12.19% | 12.97% | 8.767% | 1.1389 | 1.1491 | 1.0961
2010-07-24 | 43 | 44.4861 | 11.0103 | 55.4964 | 5.3575 | 0.76558 | 0.41257 | 6.5357 | 11.78% | 12.53% | 8.467% | 1.1335 | 1.1433 | 1.0925
2010-07-24 | 44 | 43.163 | 10.4245 | 53.5875 | 4.9953 | 0.76558 | 0.39838 | 6.1593 | 11.49% | 12.23% | 8.264% | 1.1299 | 1.1393 | 1.0901
2010-07-24 | 45 | 39.94 | 9.6682 | 49.6082 | 4.281 | 0.76558 | 0.36879 | 5.4153 | 10.92% | 11.61% | 7.849% | 1.1225 | 1.1314 | 1.0852
2010-07-24 | 46 | 36.4484 | 8.9634 | 45.4118 | 3.5873 | 0.76558 | 0.3376 | 4.6905 | 10.33% | 10.99% | 7.426% | 1.1152 | 1.1235 | 1.0802
2010-07-24 | 47 | 36.3555 | 9.258 | 45.6135 | 3.6193 | 0.76558 | 0.3391 | 4.724 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0805
2010-07-24 | 48 | 35.8095 | 9.7685 | 45.5779 | 3.6136 | 0.76558 | 0.33883 | 4.718 | 10.35% | 11.01% | 7.443% | 1.1155 | 1.1238 | 1.0804
2010-07-25 | 1 | 33.9793 | 9.0015 | 42.9808 | 3.2135 | 0.76558 | 0.31952 | 4.2986 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-07-25 | 2 | 35.4278 | 8.8209 | 44.2487 | 3.4059 | 0.76558 | 0.32895 | 4.5005 | 10.17% | 10.82% | 7.313% | 1.1132 | 1.1213 | 1.0789
2010-07-25 | 3 | 33.9728 | 8.4138 | 42.3866 | 3.1253 | 0.76558 | 0.31511 | 4.206 | 9.923% | 10.56% | 7.135% | 1.1102 | 1.118 | 1.0768
2010-07-25 | 4 | 32.6645 | 8.108 | 40.7724 | 2.8918 | 0.76558 | 0.30311 | 3.9605 | 9.714% | 10.34% | 6.984% | 1.1076 | 1.1153 | 1.0751
2010-07-25 | 5 | 31.858 | 7.8171 | 39.6751 | 2.7382 | 0.76558 | 0.29495 | 3.7988 | 9.575% | 10.19% | 6.884% | 1.1059 | 1.1134 | 1.0739
2010-07-25 | 6 | 31.4367 | 7.6272 | 39.0638 | 2.6545 | 0.76558 | 0.29041 | 3.7105 | 9.499% | 10.11% | 6.829% | 1.105 | 1.1124 | 1.0733
2010-07-25 | 7 | 31.1031 | 7.5413 | 38.6444 | 2.5978 | 0.76558 | 0.28729 | 3.6507 | 9.447% | 10.05% | 6.792% | 1.1043 | 1.1117 | 1.0729
2010-07-25 | 8 | 31.3022 | 7.5105 | 38.8127 | 2.6205 | 0.76558 | 0.28854 | 3.6746 | 9.468% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-07-25 | 9 | 31.4292 | 7.6892 | 39.1184 | 2.6619 | 0.76558 | 0.29081 | 3.7183 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2010-07-25 | 10 | 31.557 | 7.8908 | 39.4478 | 2.707 | 0.76558 | 0.29326 | 3.7658 | 9.546% | 10.16% | 6.864% | 1.1055 | 1.1131 | 1.0737
2010-07-25 | 11 | 31.9142 | 7.7456 | 39.6598 | 2.7361 | 0.76558 | 0.29484 | 3.7965 | 9.573% | 10.19% | 6.883% | 1.1059 | 1.1134 | 1.0739
2010-07-25 | 12 | 32.4698 | 8.0454 | 40.5152 | 2.8554 | 0.76558 | 0.3012 | 3.9222 | 9.681% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-07-25 | 13 | 33.9752 | 8.4486 | 42.4238 | 3.1308 | 0.76558 | 0.31538 | 4.2118 | 9.928% | 10.56% | 7.138% | 1.1102 | 1.1181 | 1.0769
2010-07-25 | 14 | 35.7824 | 8.9388 | 44.7212 | 3.4791 | 0.76558 | 0.33246 | 4.5771 | 10.23% | 10.89% | 7.359% | 1.114 | 1.1222 | 1.0794
2010-07-25 | 15 | 37.7883 | 9.7154 | 47.5037 | 3.9254 | 0.76558 | 0.35315 | 5.0442 | 10.62% | 11.3% | 7.635% | 1.1188 | 1.1274 | 1.0827
2010-07-25 | 16 | 36.6766 | 10.35 | 47.0266 | 3.847 | 0.76558 | 0.3496 | 4.9622 | 10.55% | 11.23% | 7.587% | 1.118 | 1.1265 | 1.0821
2010-07-25 | 17 | 38.9676 | 11.8332 | 50.8008 | 4.4893 | 0.76558 | 0.37766 | 5.6325 | 11.09% | 11.8% | 7.972% | 1.1247 | 1.1337 | 1.0866
2010-07-25 | 18 | 40.7272 | 12.8893 | 53.6165 | 5.0007 | 0.76558 | 0.39859 | 6.1649 | 11.5% | 12.23% | 8.267% | 1.1299 | 1.1394 | 1.0901
2010-07-25 | 19 | 42.4008 | 13.303 | 55.7038 | 5.3976 | 0.76558 | 0.41411 | 6.5773 | 11.81% | 12.56% | 8.49% | 1.1339 | 1.1437 | 1.0928
2010-07-25 | 20 | 42.6123 | 13.2659 | 55.8782 | 5.4315 | 0.76558 | 0.41541 | 6.6125 | 11.83% | 12.59% | 8.508% | 1.1342 | 1.144 | 1.093
2010-07-25 | 21 | 45.3927 | 13.4294 | 58.8222 | 6.0189 | 0.76558 | 0.43729 | 7.2218 | 12.28% | 13.06% | 8.827% | 1.14 | 1.1503 | 1.0968
2010-07-25 | 22 | 44.7859 | 12.9744 | 57.7603 | 5.8036 | 0.76558 | 0.4294 | 6.9985 | 12.12% | 12.89% | 8.712% | 1.1379 | 1.148 | 1.0954
2010-07-25 | 23 | 42.4742 | 12.0788 | 54.553 | 5.1769 | 0.76558 | 0.40555 | 6.3481 | 11.64% | 12.38% | 8.367% | 1.1317 | 1.1413 | 1.0913
2010-07-25 | 24 | 40.2514 | 11.4694 | 51.7208 | 4.6534 | 0.76558 | 0.3845 | 5.8034 | 11.22% | 11.94% | 8.068% | 1.1264 | 1.1356 | 1.0878
2010-07-25 | 25 | 37.0941 | 10.7842 | 47.8784 | 3.9876 | 0.76558 | 0.35593 | 5.1091 | 10.67% | 11.35% | 7.672% | 1.1195 | 1.1281 | 1.0831
2010-07-25 | 26 | 35.2018 | 10.0105 | 45.2123 | 3.5559 | 0.76558 | 0.33611 | 4.6576 | 10.3% | 10.96% | 7.407% | 1.1148 | 1.1231 | 1.08
2010-07-25 | 27 | 35.3548 | 10.133 | 45.4878 | 3.5993 | 0.76558 | 0.33816 | 4.7031 | 10.34% | 11% | 7.434% | 1.1153 | 1.1236 | 1.0803
2010-07-25 | 28 | 35.4729 | 10.2764 | 45.7494 | 3.6409 | 0.76558 | 0.34011 | 4.7466 | 10.38% | 11.04% | 7.46% | 1.1158 | 1.1241 | 1.0806
2010-07-25 | 29 | 34.6201 | 9.8752 | 44.4954 | 3.444 | 0.76558 | 0.33078 | 4.5404 | 10.2% | 10.86% | 7.337% | 1.1136 | 1.1218 | 1.0792
2010-07-25 | 30 | 33.9208 | 9.4436 | 43.3644 | 3.2712 | 0.76558 | 0.32238 | 4.3591 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-07-25 | 31 | 36.0542 | 9.3047 | 45.3589 | 3.579 | 0.76558 | 0.3372 | 4.6818 | 10.32% | 10.98% | 7.421% | 1.1151 | 1.1234 | 1.0802
2010-07-25 | 32 | 36.7454 | 9.1353 | 45.8807 | 3.6618 | 0.76558 | 0.34108 | 4.7685 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-07-25 | 33 | 36.6831 | 9.4521 | 46.1352 | 3.7025 | 0.76558 | 0.34297 | 4.8111 | 10.43% | 11.1% | 7.498% | 1.1164 | 1.1248 | 1.0811
2010-07-25 | 34 | 37.8151 | 9.8601 | 47.6752 | 3.9538 | 0.76558 | 0.35442 | 5.0739 | 10.64% | 11.32% | 7.652% | 1.1191 | 1.1277 | 1.0829
2010-07-25 | 35 | 39.3959 | 11.031 | 50.427 | 4.4234 | 0.76558 | 0.37488 | 5.5639 | 11.03% | 11.74% | 7.933% | 1.124 | 1.133 | 1.0862
2010-07-25 | 36 | 42.6686 | 12.7935 | 55.462 | 5.3509 | 0.76558 | 0.41231 | 6.5288 | 11.77% | 12.53% | 8.464% | 1.1334 | 1.1432 | 1.0925
2010-07-25 | 37 | 45.3997 | 13.2521 | 58.6518 | 5.9841 | 0.76558 | 0.43602 | 7.1857 | 12.25% | 13.04% | 8.809% | 1.1396 | 1.1499 | 1.0966
2010-07-25 | 38 | 46.8644 | 13.0317 | 59.8961 | 6.2407 | 0.76558 | 0.44527 | 7.4515 | 12.44% | 13.24% | 8.945% | 1.1421 | 1.1526 | 1.0982
2010-07-25 | 39 | 46.2597 | 12.5347 | 58.7944 | 6.0132 | 0.76558 | 0.43708 | 7.2159 | 12.27% | 13.06% | 8.824% | 1.1399 | 1.1502 | 1.0968
2010-07-25 | 40 | 45.4965 | 12.2418 | 57.7383 | 5.7991 | 0.76558 | 0.42923 | 6.9939 | 12.11% | 12.89% | 8.709% | 1.1378 | 1.148 | 1.0954
2010-07-25 | 41 | 46.4126 | 11.8831 | 58.2957 | 5.9116 | 0.76558 | 0.43338 | 7.1106 | 12.2% | 12.98% | 8.77% | 1.1389 | 1.1491 | 1.0961
2010-07-25 | 42 | 46.365 | 11.5393 | 57.9043 | 5.8325 | 0.76558 | 0.43047 | 7.0286 | 12.14% | 12.92% | 8.727% | 1.1382 | 1.1483 | 1.0956
2010-07-25 | 43 | 44.0371 | 11.153 | 55.19 | 5.2985 | 0.76558 | 0.41029 | 6.4744 | 11.73% | 12.48% | 8.435% | 1.1329 | 1.1426 | 1.0921
2010-07-25 | 44 | 43.0119 | 10.6974 | 53.7093 | 5.018 | 0.76558 | 0.39928 | 6.1829 | 11.51% | 12.25% | 8.277% | 1.1301 | 1.1396 | 1.0902
2010-07-25 | 45 | 40.1517 | 10.0197 | 50.1714 | 4.3787 | 0.76558 | 0.37298 | 5.5173 | 11% | 11.7% | 7.907% | 1.1236 | 1.1325 | 1.0859
2010-07-25 | 46 | 37.5177 | 9.344 | 46.8616 | 3.8201 | 0.76558 | 0.34838 | 4.934 | 10.53% | 11.2% | 7.57% | 1.1177 | 1.1262 | 1.0819
2010-07-25 | 47 | 37.715 | 9.8251 | 47.5401 | 3.9315 | 0.76558 | 0.35342 | 5.0505 | 10.62% | 11.3% | 7.638% | 1.1189 | 1.1274 | 1.0827
2010-07-25 | 48 | 36.6911 | 10.3815 | 47.0726 | 3.8545 | 0.76558 | 0.34994 | 4.97 | 10.56% | 11.23% | 7.591% | 1.118 | 1.1266 | 1.0822
2010-07-26 | 1 | 34.9629 | 9.643 | 44.6059 | 3.4611 | 0.76558 | 0.33161 | 4.5583 | 10.22% | 10.87% | 7.348% | 1.1138 | 1.122 | 1.0793
2010-07-26 | 2 | 37.0435 | 9.5051 | 46.5486 | 3.7692 | 0.76558 | 0.34605 | 4.8808 | 10.49% | 11.16% | 7.539% | 1.1171 | 1.1256 | 1.0815
2010-07-26 | 3 | 35.6147 | 9.1417 | 44.7564 | 3.4845 | 0.76558 | 0.33272 | 4.5828 | 10.24% | 10.89% | 7.362% | 1.1141 | 1.1223 | 1.0795
2010-07-26 | 4 | 34.3596 | 8.8021 | 43.1617 | 3.2407 | 0.76558 | 0.32087 | 4.3271 | 10.03% | 10.67% | 7.208% | 1.1114 | 1.1194 | 1.0777
2010-07-26 | 5 | 33.1161 | 8.5134 | 41.6295 | 3.0146 | 0.76558 | 0.30948 | 4.0897 | 9.824% | 10.45% | 7.063% | 1.1089 | 1.1167 | 1.076
2010-07-26 | 6 | 32.6728 | 8.3108 | 40.9836 | 2.9218 | 0.76558 | 0.30468 | 3.9921 | 9.741% | 10.36% | 7.004% | 1.1079 | 1.1156 | 1.0753
2010-07-26 | 7 | 32.7099 | 8.2798 | 40.9897 | 2.9227 | 0.76558 | 0.30472 | 3.993 | 9.741% | 10.36% | 7.004% | 1.1079 | 1.1156 | 1.0753
2010-07-26 | 8 | 32.665 | 8.1615 | 40.8266 | 2.8995 | 0.76558 | 0.30351 | 3.9686 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-07-26 | 9 | 32.4691 | 8.1843 | 40.6534 | 2.8749 | 0.76558 | 0.30222 | 3.9427 | 9.698% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-07-26 | 10 | 32.4923 | 8.1755 | 40.6678 | 2.877 | 0.76558 | 0.30233 | 3.9449 | 9.7% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-07-26 | 11 | 33.0246 | 8.144 | 41.1685 | 2.9483 | 0.76558 | 0.30605 | 4.0199 | 9.764% | 10.39% | 7.021% | 1.1082 | 1.1159 | 1.0755
2010-07-26 | 12 | 33.5813 | 8.1335 | 41.7148 | 3.027 | 0.76558 | 0.31011 | 4.1027 | 9.835% | 10.46% | 7.071% | 1.1091 | 1.1169 | 1.0761
2010-07-26 | 13 | 34.1842 | 8.621 | 42.8053 | 3.1873 | 0.76558 | 0.31822 | 4.2711 | 9.978% | 10.62% | 7.174% | 1.1108 | 1.1188 | 1.0773
2010-07-26 | 14 | 34.9728 | 8.9745 | 43.9473 | 3.3597 | 0.76558 | 0.32671 | 4.452 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-07-26 | 15 | 36.3606 | 9.2488 | 45.6094 | 3.6186 | 0.76558 | 0.33907 | 4.7233 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0804
2010-07-26 | 16 | 34.6487 | 9.5585 | 44.2072 | 3.3995 | 0.76558 | 0.32864 | 4.4938 | 10.17% | 10.82% | 7.309% | 1.1132 | 1.1213 | 1.0789
2010-07-26 | 17 | 36.2828 | 10.743 | 47.0258 | 3.8469 | 0.76558 | 0.3496 | 4.962 | 10.55% | 11.23% | 7.587% | 1.118 | 1.1265 | 1.0821
2010-07-26 | 18 | 38.1029 | 11.776 | 49.8789 | 4.3278 | 0.76558 | 0.37081 | 5.4642 | 10.95% | 11.66% | 7.877% | 1.123 | 1.1319 | 1.0855
2010-07-26 | 19 | 40.1572 | 12.5822 | 52.7394 | 4.8384 | 0.76558 | 0.39207 | 5.9961 | 11.37% | 12.1% | 8.175% | 1.1283 | 1.1376 | 1.089
2010-07-26 | 20 | 41.1752 | 12.8817 | 54.0569 | 5.0832 | 0.76558 | 0.40187 | 6.2506 | 11.56% | 12.3% | 8.314% | 1.1307 | 1.1403 | 1.0907
2010-07-26 | 21 | 43.8054 | 13.0387 | 56.8441 | 5.6209 | 0.76558 | 0.42259 | 6.8091 | 11.98% | 12.75% | 8.613% | 1.1361 | 1.1461 | 1.0942
2010-07-26 | 22 | 43.489 | 12.7882 | 56.2772 | 5.5093 | 0.76558 | 0.41837 | 6.6933 | 11.89% | 12.65% | 8.551% | 1.135 | 1.1449 | 1.0935
2010-07-26 | 23 | 42.0047 | 11.9279 | 53.9325 | 5.0598 | 0.76558 | 0.40094 | 6.2264 | 11.54% | 12.28% | 8.301% | 1.1305 | 1.14 | 1.0905
2010-07-26 | 24 | 39.9172 | 11.3732 | 51.2904 | 4.5762 | 0.76558 | 0.3813 | 5.7231 | 11.16% | 11.87% | 8.023% | 1.1256 | 1.1347 | 1.0872
2010-07-26 | 25 | 36.8501 | 10.6783 | 47.5284 | 3.9295 | 0.76558 | 0.35333 | 5.0484 | 10.62% | 11.3% | 7.637% | 1.1188 | 1.1274 | 1.0827
2010-07-26 | 26 | 35.0664 | 9.9328 | 44.9992 | 3.5224 | 0.76558 | 0.33453 | 4.6226 | 10.27% | 10.93% | 7.386% | 1.1145 | 1.1227 | 1.0797
2010-07-26 | 27 | 35.068 | 10.1513 | 45.2193 | 3.557 | 0.76558 | 0.33617 | 4.6587 | 10.3% | 10.96% | 7.408% | 1.1149 | 1.1231 | 1.08
2010-07-26 | 28 | 34.8135 | 10.2965 | 45.11 | 3.5398 | 0.76558 | 0.33535 | 4.6407 | 10.29% | 10.95% | 7.397% | 1.1147 | 1.1229 | 1.0799
2010-07-26 | 29 | 33.7671 | 9.8032 | 43.5703 | 3.3023 | 0.76558 | 0.32391 | 4.3918 | 10.08% | 10.72% | 7.247% | 1.1121 | 1.1201 | 1.0781
2010-07-26 | 30 | 32.9889 | 9.2656 | 42.2545 | 3.1059 | 0.76558 | 0.31413 | 4.1856 | 9.906% | 10.54% | 7.122% | 1.1099 | 1.1178 | 1.0767
2010-07-26 | 31 | 35.5988 | 9.2956 | 44.8944 | 3.5061 | 0.76558 | 0.33375 | 4.6054 | 10.26% | 10.91% | 7.376% | 1.1143 | 1.1225 | 1.0796
2010-07-26 | 32 | 36.1466 | 9.1278 | 45.2744 | 3.5657 | 0.76558 | 0.33658 | 4.6678 | 10.31% | 10.97% | 7.413% | 1.115 | 1.1232 | 1.0801
2010-07-26 | 33 | 35.7619 | 9.3995 | 45.1614 | 3.5479 | 0.76558 | 0.33574 | 4.6492 | 10.29% | 10.95% | 7.402% | 1.1148 | 1.123 | 1.0799
2010-07-26 | 34 | 36.6606 | 9.8077 | 46.4683 | 3.7562 | 0.76558 | 0.34545 | 4.8672 | 10.47% | 11.14% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-07-26 | 35 | 38.4264 | 11.0143 | 49.4406 | 4.2521 | 0.76558 | 0.36755 | 5.3852 | 10.89% | 11.59% | 7.832% | 1.1222 | 1.1311 | 1.085
2010-07-26 | 36 | 41.6483 | 12.8386 | 54.4869 | 5.1644 | 0.76558 | 0.40506 | 6.335 | 11.63% | 12.37% | 8.36% | 1.1316 | 1.1412 | 1.0912
2010-07-26 | 37 | 44.81 | 13.4848 | 58.2948 | 5.9115 | 0.76558 | 0.43337 | 7.1104 | 12.2% | 12.98% | 8.77% | 1.1389 | 1.1491 | 1.0961
2010-07-26 | 38 | 45.4294 | 13.4811 | 58.9105 | 6.037 | 0.76558 | 0.43795 | 7.2405 | 12.29% | 13.08% | 8.837% | 1.1401 | 1.1504 | 1.0969
2010-07-26 | 39 | 45.0987 | 13.2812 | 58.3799 | 5.9287 | 0.76558 | 0.434 | 7.1283 | 12.21% | 12.99% | 8.779% | 1.1391 | 1.1493 | 1.0962
2010-07-26 | 40 | 44.2201 | 12.8658 | 57.0859 | 5.6688 | 0.76558 | 0.42438 | 6.8588 | 12.01% | 12.78% | 8.639% | 1.1366 | 1.1466 | 1.0946
2010-07-26 | 41 | 45.1235 | 12.7885 | 57.912 | 5.8341 | 0.76558 | 0.43053 | 7.0302 | 12.14% | 12.92% | 8.728% | 1.1382 | 1.1483 | 1.0956
2010-07-26 | 42 | 44.777 | 12.1498 | 56.9268 | 5.6373 | 0.76558 | 0.4232 | 6.826 | 11.99% | 12.76% | 8.621% | 1.1362 | 1.1462 | 1.0943
2010-07-26 | 43 | 42.4914 | 11.4528 | 53.9442 | 5.062 | 0.76558 | 0.40103 | 6.2286 | 11.55% | 12.29% | 8.302% | 1.1305 | 1.1401 | 1.0905
2010-07-26 | 44 | 40.1201 | 10.7768 | 50.8968 | 4.5063 | 0.76558 | 0.37837 | 5.6502 | 11.1% | 11.81% | 7.982% | 1.1249 | 1.1339 | 1.0867
2010-07-26 | 45 | 35.7225 | 9.5484 | 45.2709 | 3.5651 | 0.76558 | 0.33655 | 4.6672 | 10.31% | 10.97% | 7.413% | 1.1149 | 1.1232 | 1.0801
2010-07-26 | 46 | 32.3309 | 8.4067 | 40.7376 | 2.8869 | 0.76558 | 0.30285 | 3.9553 | 9.709% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.075
2010-07-26 | 47 | 32.3596 | 8.8828 | 41.2425 | 2.9589 | 0.76558 | 0.3066 | 4.031 | 9.774% | 10.4% | 7.028% | 1.1083 | 1.1161 | 1.0756
2010-07-26 | 48 | 31.6528 | 9.5039 | 41.1567 | 2.9466 | 0.76558 | 0.30596 | 4.0181 | 9.763% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-07-27 | 1 | 29.9692 | 8.8568 | 38.826 | 2.6223 | 0.76558 | 0.28864 | 3.6765 | 9.469% | 10.08% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-07-27 | 2 | 31.4786 | 8.6758 | 40.1544 | 2.8048 | 0.76558 | 0.29851 | 3.8689 | 9.635% | 10.25% | 6.928% | 1.1066 | 1.1142 | 1.0744
2010-07-27 | 3 | 30.1408 | 8.4374 | 38.5782 | 2.5889 | 0.76558 | 0.28679 | 3.6413 | 9.439% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-07-27 | 4 | 29.4766 | 8.2098 | 37.6864 | 2.4706 | 0.76558 | 0.28017 | 3.5163 | 9.331% | 9.928% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-07-27 | 5 | 28.9005 | 7.9979 | 36.8983 | 2.3684 | 0.76558 | 0.27431 | 3.4082 | 9.237% | 9.828% | 6.641% | 1.1018 | 1.109 | 1.0711
2010-07-27 | 6 | 28.0365 | 7.8446 | 35.8811 | 2.2396 | 0.76558 | 0.26674 | 3.2719 | 9.119% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-07-27 | 7 | 27.9644 | 7.7735 | 35.738 | 2.2217 | 0.76558 | 0.26568 | 3.253 | 9.102% | 9.685% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-07-27 | 8 | 27.8753 | 7.7545 | 35.6298 | 2.2083 | 0.76558 | 0.26488 | 3.2388 | 9.09% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-07-27 | 9 | 27.9593 | 7.9226 | 35.8819 | 2.2397 | 0.76558 | 0.26675 | 3.272 | 9.119% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-07-27 | 10 | 28.1616 | 8.0598 | 36.2214 | 2.2823 | 0.76558 | 0.26927 | 3.3171 | 9.158% | 9.744% | 6.585% | 1.1008 | 1.108 | 1.0705
2010-07-27 | 11 | 29.1344 | 8.2772 | 37.4116 | 2.4347 | 0.76558 | 0.27812 | 3.4784 | 9.298% | 9.893% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-07-27 | 12 | 29.8802 | 8.7796 | 38.6597 | 2.5999 | 0.76558 | 0.2874 | 3.6529 | 9.449% | 10.05% | 6.794% | 1.1043 | 1.1118 | 1.0729
2010-07-27 | 13 | 32.0766 | 9.8432 | 41.9198 | 3.0568 | 0.76558 | 0.31164 | 4.1341 | 9.862% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-07-27 | 14 | 35.482 | 11.5184 | 47.0004 | 3.8427 | 0.76558 | 0.34941 | 4.9577 | 10.55% | 11.22% | 7.584% | 1.1179 | 1.1264 | 1.0821
2010-07-27 | 15 | 40.0618 | 13.6603 | 53.7221 | 5.0204 | 0.76558 | 0.39938 | 6.1854 | 11.51% | 12.25% | 8.278% | 1.1301 | 1.1396 | 1.0903
2010-07-27 | 16 | 42.0307 | 14.6626 | 56.6932 | 5.5911 | 0.76558 | 0.42146 | 6.7781 | 11.96% | 12.72% | 8.596% | 1.1358 | 1.1458 | 1.094
2010-07-27 | 17 | 44.0092 | 15.7177 | 59.7269 | 6.2055 | 0.76558 | 0.44402 | 7.4151 | 12.41% | 13.21% | 8.926% | 1.1417 | 1.1522 | 1.098
2010-07-27 | 18 | 44.4507 | 15.6929 | 60.1436 | 6.2924 | 0.76558 | 0.44712 | 7.5051 | 12.48% | 13.28% | 8.972% | 1.1426 | 1.1531 | 1.0986
2010-07-27 | 19 | 44.7978 | 15.3746 | 60.1724 | 6.2984 | 0.76558 | 0.44733 | 7.5113 | 12.48% | 13.28% | 8.975% | 1.1426 | 1.1532 | 1.0986
2010-07-27 | 20 | 44.131 | 14.8931 | 59.0241 | 6.0603 | 0.76558 | 0.43879 | 7.2647 | 12.31% | 13.1% | 8.849% | 1.1404 | 1.1507 | 1.0971
2010-07-27 | 21 | 45.8149 | 14.5966 | 60.4116 | 6.3486 | 0.76558 | 0.44911 | 7.5632 | 12.52% | 13.32% | 9.002% | 1.1431 | 1.1537 | 1.0989
2010-07-27 | 22 | 44.6776 | 14.3413 | 59.0189 | 6.0592 | 0.76558 | 0.43875 | 7.2636 | 12.31% | 13.09% | 8.849% | 1.1403 | 1.1507 | 1.0971
2010-07-27 | 23 | 42.4645 | 13.7885 | 56.253 | 5.5046 | 0.76558 | 0.41819 | 6.6884 | 11.89% | 12.65% | 8.549% | 1.1349 | 1.1448 | 1.0935
2010-07-27 | 24 | 40.3072 | 13.1748 | 53.4819 | 4.9756 | 0.76558 | 0.39759 | 6.1388 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.09
2010-07-27 | 25 | 37.4643 | 12.2413 | 49.7057 | 4.2978 | 0.76558 | 0.36952 | 5.4329 | 10.93% | 11.63% | 7.859% | 1.1227 | 1.1316 | 1.0853
2010-07-27 | 26 | 34.6919 | 11.2617 | 45.9536 | 3.6734 | 0.76558 | 0.34162 | 4.7806 | 10.4% | 11.07% | 7.48% | 1.1161 | 1.1245 | 1.0808
2010-07-27 | 27 | 35.0957 | 11.4573 | 46.5529 | 3.7699 | 0.76558 | 0.34608 | 4.8815 | 10.49% | 11.16% | 7.539% | 1.1171 | 1.1256 | 1.0815
2010-07-27 | 28 | 34.8222 | 11.527 | 46.3492 | 3.737 | 0.76558 | 0.34457 | 4.8471 | 10.46% | 11.13% | 7.519% | 1.1168 | 1.1252 | 1.0813
2010-07-27 | 29 | 34.7096 | 11.1015 | 45.8111 | 3.6507 | 0.76558 | 0.34057 | 4.7568 | 10.38% | 11.05% | 7.466% | 1.1159 | 1.1242 | 1.0807
2010-07-27 | 30 | 34.1348 | 10.8115 | 44.9463 | 3.5142 | 0.76558 | 0.33414 | 4.6139 | 10.27% | 10.92% | 7.381% | 1.1144 | 1.1226 | 1.0797
2010-07-27 | 31 | 36.2188 | 10.9384 | 47.1572 | 3.8684 | 0.76558 | 0.35057 | 4.9845 | 10.57% | 11.25% | 7.6% | 1.1182 | 1.1267 | 1.0822
2010-07-27 | 32 | 37.1665 | 11.0126 | 48.1791 | 4.0379 | 0.76558 | 0.35817 | 5.1616 | 10.71% | 11.4% | 7.703% | 1.12 | 1.1287 | 1.0835
2010-07-27 | 33 | 37.6859 | 11.3088 | 48.9946 | 4.1757 | 0.76558 | 0.36423 | 5.3055 | 10.83% | 11.52% | 7.786% | 1.1214 | 1.1302 | 1.0844
2010-07-27 | 34 | 38.2614 | 11.9741 | 50.2354 | 4.3899 | 0.76558 | 0.37346 | 5.5289 | 11.01% | 11.71% | 7.913% | 1.1237 | 1.1326 | 1.0859
2010-07-27 | 35 | 38.8652 | 13.0979 | 51.9631 | 4.6971 | 0.76558 | 0.3863 | 5.8489 | 11.26% | 11.98% | 8.093% | 1.1268 | 1.1361 | 1.0881
2010-07-27 | 36 | 42.3567 | 14.4624 | 56.8191 | 5.6159 | 0.76558 | 0.4224 | 6.8039 | 11.97% | 12.74% | 8.61% | 1.136 | 1.146 | 1.0942
2010-07-27 | 37 | 42.714 | 13.7694 | 56.4834 | 5.5498 | 0.76558 | 0.4199 | 6.7353 | 11.92% | 12.69% | 8.574% | 1.1354 | 1.1453 | 1.0938
2010-07-27 | 38 | 42.2693 | 13.3322 | 55.6015 | 5.3778 | 0.76558 | 0.41335 | 6.5568 | 11.79% | 12.55% | 8.479% | 1.1337 | 1.1435 | 1.0926
2010-07-27 | 39 | 45.5299 | 14.4161 | 59.946 | 6.2511 | 0.76558 | 0.44565 | 7.4623 | 12.45% | 13.25% | 8.95% | 1.1422 | 1.1527 | 1.0983
2010-07-27 | 40 | 44.8691 | 13.6989 | 58.568 | 5.967 | 0.76558 | 0.4354 | 7.168 | 12.24% | 13.02% | 8.8% | 1.1395 | 1.1497 | 1.0965
2010-07-27 | 41 | 45.5405 | 13.3936 | 58.934 | 6.0418 | 0.76558 | 0.43812 | 7.2455 | 12.29% | 13.08% | 8.84% | 1.1402 | 1.1505 | 1.097
2010-07-27 | 42 | 44.5788 | 12.7219 | 57.3008 | 5.7116 | 0.76558 | 0.42598 | 6.9031 | 12.05% | 12.82% | 8.662% | 1.137 | 1.147 | 1.0948
2010-07-27 | 43 | 41.8631 | 12.0373 | 53.9004 | 5.0538 | 0.76558 | 0.4007 | 6.2201 | 11.54% | 12.28% | 8.297% | 1.1305 | 1.14 | 1.0905
2010-07-27 | 44 | 39.4928 | 11.3799 | 50.8727 | 4.502 | 0.76558 | 0.37819 | 5.6458 | 11.1% | 11.81% | 7.979% | 1.1248 | 1.1339 | 1.0867
2010-07-27 | 45 | 35.3684 | 10.1989 | 45.5673 | 3.612 | 0.76558 | 0.33875 | 4.7163 | 10.35% | 11.01% | 7.442% | 1.1155 | 1.1238 | 1.0804
2010-07-27 | 46 | 31.6181 | 9.1097 | 40.7278 | 2.8855 | 0.76558 | 0.30278 | 3.9538 | 9.708% | 10.33% | 6.98% | 1.1075 | 1.1152 | 1.075
2010-07-27 | 47 | 31.0006 | 9.3122 | 40.3128 | 2.827 | 0.76558 | 0.29969 | 3.8922 | 9.655% | 10.27% | 6.942% | 1.1069 | 1.1145 | 1.0746
2010-07-27 | 48 | 30.0373 | 9.854 | 39.8913 | 2.7682 | 0.76558 | 0.29656 | 3.8303 | 9.602% | 10.22% | 6.904% | 1.1062 | 1.1138 | 1.0742
2010-07-28 | 1 | 28.1823 | 9.1251 | 37.3075 | 2.4212 | 0.76558 | 0.27735 | 3.4641 | 9.285% | 9.88% | 6.676% | 1.1024 | 1.1096 | 1.0715
2010-07-28 | 2 | 29.6621 | 8.9282 | 38.5903 | 2.5905 | 0.76558 | 0.28688 | 3.643 | 9.44% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-07-28 | 3 | 28.5419 | 8.615 | 37.1569 | 2.4017 | 0.76558 | 0.27623 | 3.4435 | 9.267% | 9.861% | 6.663% | 1.1021 | 1.1094 | 1.0714
2010-07-28 | 4 | 27.4338 | 8.2855 | 35.7192 | 2.2194 | 0.76558 | 0.26554 | 3.2505 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-07-28 | 5 | 26.585 | 7.9866 | 34.5715 | 2.0791 | 0.76558 | 0.25701 | 3.1017 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-07-28 | 6 | 25.9244 | 7.8047 | 33.7291 | 1.979 | 0.76558 | 0.25075 | 2.9953 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1043 | 1.0682
2010-07-28 | 7 | 25.2899 | 7.7568 | 33.0468 | 1.8997 | 0.76558 | 0.24567 | 2.911 | 8.809% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-07-28 | 8 | 24.7727 | 7.7125 | 32.4851 | 1.8357 | 0.76558 | 0.2415 | 2.8428 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-07-28 | 9 | 25.232 | 7.867 | 33.099 | 1.9057 | 0.76558 | 0.24606 | 2.9174 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2010-07-28 | 10 | 25.5757 | 7.8602 | 33.4359 | 1.9447 | 0.76558 | 0.24857 | 2.9589 | 8.849% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2010-07-28 | 11 | 25.9338 | 8.1728 | 34.1066 | 2.0235 | 0.76558 | 0.25355 | 3.0427 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2010-07-28 | 12 | 26.7387 | 8.6104 | 35.3491 | 2.1737 | 0.76558 | 0.26279 | 3.202 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-07-28 | 13 | 29.0996 | 9.6825 | 38.7821 | 2.6164 | 0.76558 | 0.28831 | 3.6703 | 9.464% | 10.07% | 6.804% | 1.1045 | 1.112 | 1.073
2010-07-28 | 14 | 32.2967 | 11.3538 | 43.6505 | 3.3145 | 0.76558 | 0.3245 | 4.4045 | 10.09% | 10.74% | 7.255% | 1.1122 | 1.1203 | 1.0782
2010-07-28 | 15 | 36.8252 | 13.4506 | 50.2758 | 4.397 | 0.76558 | 0.37376 | 5.5363 | 11.01% | 11.72% | 7.918% | 1.1237 | 1.1327 | 1.086
2010-07-28 | 16 | 38.4494 | 14.39 | 52.8394 | 4.8568 | 0.76558 | 0.39281 | 6.0152 | 11.38% | 12.11% | 8.185% | 1.1285 | 1.1378 | 1.0891
2010-07-28 | 17 | 39.9516 | 15.2825 | 55.2341 | 5.307 | 0.76558 | 0.41062 | 6.4832 | 11.74% | 12.49% | 8.439% | 1.133 | 1.1427 | 1.0922
2010-07-28 | 18 | 40.5831 | 15.4253 | 56.0084 | 5.4568 | 0.76558 | 0.41637 | 6.6388 | 11.85% | 12.61% | 8.522% | 1.1345 | 1.1443 | 1.0932
2010-07-28 | 19 | 40.2664 | 15.121 | 55.3874 | 5.3365 | 0.76558 | 0.41176 | 6.5138 | 11.76% | 12.51% | 8.456% | 1.1333 | 1.143 | 1.0924
2010-07-28 | 20 | 39.2281 | 14.6432 | 53.8713 | 5.0483 | 0.76558 | 0.40049 | 6.2144 | 11.54% | 12.27% | 8.294% | 1.1304 | 1.1399 | 1.0904
2010-07-28 | 21 | 40.4773 | 14.551 | 55.0283 | 5.2675 | 0.76558 | 0.40909 | 6.4422 | 11.71% | 12.46% | 8.417% | 1.1326 | 1.1423 | 1.0919
2010-07-28 | 22 | 39.0597 | 13.9812 | 53.0409 | 4.8939 | 0.76558 | 0.39431 | 6.0538 | 11.41% | 12.14% | 8.206% | 1.1288 | 1.1382 | 1.0894
2010-07-28 | 23 | 36.9076 | 13.4006 | 50.3083 | 4.4026 | 0.76558 | 0.374 | 5.5422 | 11.02% | 11.72% | 7.921% | 1.1238 | 1.1328 | 1.086
2010-07-28 | 24 | 36.3971 | 13.1381 | 49.5352 | 4.2684 | 0.76558 | 0.36825 | 5.4022 | 10.91% | 11.6% | 7.841% | 1.1224 | 1.1313 | 1.0851
2010-07-28 | 25 | 34.363 | 12.8453 | 47.2083 | 3.8768 | 0.76558 | 0.35095 | 4.9933 | 10.58% | 11.25% | 7.605% | 1.1183 | 1.1268 | 1.0823
2010-07-28 | 26 | 33.2157 | 11.6864 | 44.9021 | 3.5073 | 0.76558 | 0.33381 | 4.6066 | 10.26% | 10.92% | 7.376% | 1.1143 | 1.1225 | 1.0796
2010-07-28 | 27 | 33.965 | 11.7974 | 45.7624 | 3.6429 | 0.76558 | 0.3402 | 4.7487 | 10.38% | 11.04% | 7.461% | 1.1158 | 1.1241 | 1.0806
2010-07-28 | 28 | 33.9696 | 12.0485 | 46.0182 | 3.6838 | 0.76558 | 0.3421 | 4.7915 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-07-28 | 29 | 34.058 | 11.749 | 45.807 | 3.65 | 0.76558 | 0.34053 | 4.7562 | 10.38% | 11.05% | 7.465% | 1.1159 | 1.1242 | 1.0807
2010-07-28 | 30 | 34.2192 | 11.4708 | 45.6899 | 3.6314 | 0.76558 | 0.33966 | 4.7367 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-07-28 | 31 | 36.6061 | 11.5994 | 48.2054 | 4.0423 | 0.76558 | 0.35837 | 5.1662 | 10.72% | 11.4% | 7.706% | 1.12 | 1.1287 | 1.0835
2010-07-28 | 32 | 37.1516 | 11.5609 | 48.7124 | 4.1278 | 0.76558 | 0.36213 | 5.2555 | 10.79% | 11.48% | 7.757% | 1.1209 | 1.1297 | 1.0841
2010-07-28 | 33 | 36.6535 | 11.802 | 48.4555 | 4.0843 | 0.76558 | 0.36022 | 5.2101 | 10.75% | 11.44% | 7.731% | 1.1205 | 1.1292 | 1.0838
2010-07-28 | 34 | 36.5545 | 11.7719 | 48.3264 | 4.0626 | 0.76558 | 0.35926 | 5.1874 | 10.73% | 11.42% | 7.718% | 1.1202 | 1.1289 | 1.0836
2010-07-28 | 35 | 37.2736 | 12.5955 | 49.8691 | 4.3261 | 0.76558 | 0.37073 | 5.4624 | 10.95% | 11.65% | 7.876% | 1.123 | 1.1319 | 1.0855
2010-07-28 | 36 | 40.0321 | 13.8808 | 53.9128 | 5.0561 | 0.76558 | 0.40079 | 6.2225 | 11.54% | 12.28% | 8.299% | 1.1305 | 1.14 | 1.0905
2010-07-28 | 37 | 41.6875 | 13.8652 | 55.5527 | 5.3684 | 0.76558 | 0.41299 | 6.547 | 11.79% | 12.54% | 8.474% | 1.1336 | 1.1434 | 1.0926
2010-07-28 | 38 | 43.8494 | 14.2419 | 58.0912 | 5.8702 | 0.76558 | 0.43186 | 7.0677 | 12.17% | 12.95% | 8.748% | 1.1385 | 1.1487 | 1.0959
2010-07-28 | 39 | 42.8673 | 13.6993 | 56.5666 | 5.5661 | 0.76558 | 0.42052 | 6.7522 | 11.94% | 12.7% | 8.583% | 1.1355 | 1.1455 | 1.0939
2010-07-28 | 40 | 41.7612 | 13.1651 | 54.9263 | 5.248 | 0.76558 | 0.40833 | 6.4219 | 11.69% | 12.44% | 8.406% | 1.1324 | 1.1421 | 1.0918
2010-07-28 | 41 | 41.9918 | 12.8444 | 54.8362 | 5.2308 | 0.76558 | 0.40766 | 6.404 | 11.68% | 12.43% | 8.397% | 1.1322 | 1.1419 | 1.0917
2010-07-28 | 42 | 41.5205 | 12.3013 | 53.8218 | 5.0391 | 0.76558 | 0.40012 | 6.2048 | 11.53% | 12.27% | 8.289% | 1.1303 | 1.1398 | 1.0904
2010-07-28 | 43 | 39.6236 | 11.8778 | 51.5014 | 4.614 | 0.76558 | 0.38287 | 5.7624 | 11.19% | 11.9% | 8.045% | 1.126 | 1.1351 | 1.0875
2010-07-28 | 44 | 37.2407 | 11.1522 | 48.3929 | 4.0738 | 0.76558 | 0.35976 | 5.1991 | 10.74% | 11.43% | 7.725% | 1.1204 | 1.1291 | 1.0837
2010-07-28 | 45 | 33.4323 | 9.9023 | 43.3347 | 3.2667 | 0.76558 | 0.32216 | 4.3544 | 10.05% | 10.69% | 7.225% | 1.1117 | 1.1197 | 1.0779
2010-07-28 | 46 | 29.727 | 8.7233 | 38.4502 | 2.5718 | 0.76558 | 0.28584 | 3.6232 | 9.423% | 10.03% | 6.775% | 1.104 | 1.1114 | 1.0727
2010-07-28 | 47 | 29.67 | 8.9918 | 38.6618 | 2.6002 | 0.76558 | 0.28742 | 3.6531 | 9.449% | 10.05% | 6.794% | 1.1043 | 1.1118 | 1.0729
2010-07-28 | 48 | 28.3321 | 9.4824 | 37.8145 | 2.4874 | 0.76558 | 0.28112 | 3.5341 | 9.346% | 9.944% | 6.72% | 1.1031 | 1.1104 | 1.072
2010-07-29 | 1 | 26.6977 | 8.6568 | 35.3546 | 2.1743 | 0.76558 | 0.26283 | 3.2027 | 9.059% | 9.639% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-07-29 | 2 | 28.2493 | 8.4338 | 36.6832 | 2.3408 | 0.76558 | 0.27271 | 3.3791 | 9.212% | 9.801% | 6.623% | 1.1015 | 1.1087 | 1.0709
2010-07-29 | 3 | 27.3221 | 7.929 | 35.2511 | 2.1616 | 0.76558 | 0.26206 | 3.1893 | 9.047% | 9.626% | 6.505% | 1.0995 | 1.1065 | 1.0696
2010-07-29 | 4 | 26.2229 | 7.6616 | 33.8845 | 1.9973 | 0.76558 | 0.2519 | 3.0147 | 8.897% | 9.467% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-07-29 | 5 | 25.6435 | 7.4608 | 33.1043 | 1.9064 | 0.76558 | 0.2461 | 2.918 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-07-29 | 6 | 25.233 | 7.3855 | 32.6184 | 1.8508 | 0.76558 | 0.24249 | 2.8589 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1028 | 1.0673
2010-07-29 | 7 | 24.7986 | 7.3695 | 32.168 | 1.8 | 0.76558 | 0.23914 | 2.8048 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-07-29 | 8 | 24.7952 | 7.419 | 32.2142 | 1.8052 | 0.76558 | 0.23948 | 2.8103 | 8.724% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-07-29 | 9 | 25.0946 | 7.5568 | 32.6514 | 1.8545 | 0.76558 | 0.24273 | 2.8629 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-07-29 | 10 | 25.421 | 7.7365 | 33.1575 | 1.9125 | 0.76558 | 0.2465 | 2.9246 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-07-29 | 11 | 26.4288 | 7.9162 | 34.345 | 2.0519 | 0.76558 | 0.25532 | 3.0728 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-07-29 | 12 | 27.5164 | 8.2045 | 35.7209 | 2.2196 | 0.76558 | 0.26555 | 3.2508 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-07-29 | 13 | 30.0132 | 9.3654 | 39.3787 | 2.6975 | 0.76558 | 0.29275 | 3.7558 | 9.538% | 10.15% | 6.858% | 1.1054 | 1.1129 | 1.0736
2010-07-29 | 14 | 32.9265 | 11.0098 | 43.9363 | 3.358 | 0.76558 | 0.32663 | 4.4502 | 10.13% | 10.78% | 7.283% | 1.1127 | 1.1208 | 1.0785
2010-07-29 | 15 | 37.0184 | 13.2789 | 50.2973 | 4.4007 | 0.76558 | 0.37392 | 5.5402 | 11.01% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-07-29 | 16 | 38.7129 | 14.2555 | 52.9684 | 4.8805 | 0.76558 | 0.39377 | 6.0399 | 11.4% | 12.13% | 8.199% | 1.1287 | 1.1381 | 1.0893
2010-07-29 | 17 | 40.1607 | 14.6424 | 54.8031 | 5.2245 | 0.76558 | 0.40741 | 6.3975 | 11.67% | 12.42% | 8.393% | 1.1322 | 1.1418 | 1.0916
2010-07-29 | 18 | 41.5384 | 15.0723 | 56.6107 | 5.5748 | 0.76558 | 0.42085 | 6.7613 | 11.94% | 12.71% | 8.587% | 1.1356 | 1.1456 | 1.0939
2010-07-29 | 19 | 41.8956 | 15.0139 | 56.9095 | 5.6338 | 0.76558 | 0.42307 | 6.8225 | 11.99% | 12.76% | 8.62% | 1.1362 | 1.1462 | 1.0943
2010-07-29 | 20 | 41.1169 | 14.9001 | 56.017 | 5.4585 | 0.76558 | 0.41644 | 6.6405 | 11.85% | 12.61% | 8.523% | 1.1345 | 1.1443 | 1.0932
2010-07-29 | 21 | 43.0575 | 14.752 | 57.8095 | 5.8134 | 0.76558 | 0.42976 | 7.0088 | 12.12% | 12.9% | 8.717% | 1.138 | 1.1481 | 1.0955
2010-07-29 | 22 | 42.5235 | 14.5893 | 57.1128 | 5.6742 | 0.76558 | 0.42458 | 6.8643 | 12.02% | 12.79% | 8.642% | 1.1366 | 1.1466 | 1.0946
2010-07-29 | 23 | 40.9709 | 13.8802 | 54.8511 | 5.2337 | 0.76558 | 0.40777 | 6.407 | 11.68% | 12.43% | 8.398% | 1.1323 | 1.1419 | 1.0917
2010-07-29 | 24 | 39.5785 | 13.6217 | 53.2003 | 4.9234 | 0.76558 | 0.3955 | 6.0844 | 11.44% | 12.17% | 8.223% | 1.1291 | 1.1385 | 1.0896
2010-07-29 | 25 | 37.064 | 13.2313 | 50.2954 | 4.4004 | 0.76558 | 0.3739 | 5.5399 | 11.01% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-07-29 | 26 | 34.7063 | 12.8231 | 47.5294 | 3.9297 | 0.76558 | 0.35334 | 5.0486 | 10.62% | 11.3% | 7.637% | 1.1188 | 1.1274 | 1.0827
2010-07-29 | 27 | 34.5058 | 13.2455 | 47.7512 | 3.9665 | 0.76558 | 0.35499 | 5.087 | 10.65% | 11.34% | 7.66% | 1.1192 | 1.1278 | 1.083
2010-07-29 | 28 | 34.0604 | 13.1707 | 47.2311 | 3.8805 | 0.76558 | 0.35112 | 4.9972 | 10.58% | 11.26% | 7.607% | 1.1183 | 1.1269 | 1.0823
2010-07-29 | 29 | 33.1861 | 12.1759 | 45.3621 | 3.5795 | 0.76558 | 0.33723 | 4.6823 | 10.32% | 10.98% | 7.422% | 1.1151 | 1.1234 | 1.0802
2010-07-29 | 30 | 32.6402 | 11.3342 | 43.9745 | 3.3638 | 0.76558 | 0.32691 | 4.4563 | 10.13% | 10.78% | 7.286% | 1.1128 | 1.1209 | 1.0786
2010-07-29 | 31 | 34.7949 | 11.1019 | 45.8968 | 3.6644 | 0.76558 | 0.3412 | 4.7712 | 10.4% | 11.06% | 7.474% | 1.116 | 1.1244 | 1.0808
2010-07-29 | 32 | 34.9691 | 10.9434 | 45.9126 | 3.6669 | 0.76558 | 0.34132 | 4.7738 | 10.4% | 11.06% | 7.476% | 1.116 | 1.1244 | 1.0808
2010-07-29 | 33 | 34.7561 | 10.8572 | 45.6133 | 3.6192 | 0.76558 | 0.33909 | 4.7239 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0805
2010-07-29 | 34 | 35.4629 | 11.0357 | 46.4986 | 3.7611 | 0.76558 | 0.34568 | 4.8724 | 10.48% | 11.15% | 7.534% | 1.1171 | 1.1255 | 1.0815
2010-07-29 | 35 | 36.6968 | 11.9175 | 48.6144 | 4.1112 | 0.76558 | 0.36141 | 5.2381 | 10.77% | 11.46% | 7.747% | 1.1208 | 1.1295 | 1.084
2010-07-29 | 36 | 39.399 | 13.2778 | 52.6768 | 4.827 | 0.76558 | 0.39161 | 5.9841 | 11.36% | 12.09% | 8.168% | 1.1282 | 1.1375 | 1.0889
2010-07-29 | 37 | 41.8772 | 13.6266 | 55.5038 | 5.359 | 0.76558 | 0.41262 | 6.5372 | 11.78% | 12.53% | 8.468% | 1.1335 | 1.1433 | 1.0925
2010-07-29 | 38 | 43.3325 | 13.726 | 57.0586 | 5.6634 | 0.76558 | 0.42418 | 6.8531 | 12.01% | 12.78% | 8.636% | 1.1365 | 1.1465 | 1.0945
2010-07-29 | 39 | 42.8337 | 13.2772 | 56.1109 | 5.4768 | 0.76558 | 0.41713 | 6.6595 | 11.87% | 12.63% | 8.533% | 1.1347 | 1.1445 | 1.0933
2010-07-29 | 40 | 41.7819 | 12.8209 | 54.6029 | 5.1864 | 0.76558 | 0.40592 | 6.3579 | 11.64% | 12.39% | 8.372% | 1.1318 | 1.1414 | 1.0914
2010-07-29 | 41 | 41.9725 | 12.4812 | 54.4536 | 5.1581 | 0.76558 | 0.40482 | 6.3285 | 11.62% | 12.37% | 8.356% | 1.1315 | 1.1411 | 1.0912
2010-07-29 | 42 | 41.4251 | 12.0571 | 53.4822 | 4.9757 | 0.76558 | 0.39759 | 6.1389 | 11.48% | 12.21% | 8.253% | 1.1297 | 1.1391 | 1.09
2010-07-29 | 43 | 39.439 | 11.4265 | 50.8655 | 4.5007 | 0.76558 | 0.37814 | 5.6444 | 11.1% | 11.81% | 7.979% | 1.1248 | 1.1339 | 1.0867
2010-07-29 | 44 | 36.9953 | 10.482 | 47.4773 | 3.9211 | 0.76558 | 0.35295 | 5.0396 | 10.61% | 11.29% | 7.632% | 1.1188 | 1.1273 | 1.0826
2010-07-29 | 45 | 32.7844 | 9.3492 | 42.1336 | 3.0881 | 0.76558 | 0.31323 | 4.1669 | 9.89% | 10.52% | 7.111% | 1.1098 | 1.1176 | 1.0766
2010-07-29 | 46 | 29.8071 | 8.4794 | 38.2865 | 2.5499 | 0.76558 | 0.28463 | 3.6001 | 9.403% | 10% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-07-29 | 47 | 29.6322 | 8.8372 | 38.4694 | 2.5743 | 0.76558 | 0.28599 | 3.6259 | 9.425% | 10.03% | 6.777% | 1.1041 | 1.1115 | 1.0727
2010-07-29 | 48 | 28.7087 | 9.2056 | 37.9143 | 2.5006 | 0.76558 | 0.28186 | 3.548 | 9.358% | 9.957% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-07-30 | 1 | 26.9732 | 8.4752 | 35.4484 | 2.1859 | 0.76558 | 0.26353 | 3.215 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-07-30 | 2 | 28.4798 | 8.2995 | 36.7793 | 2.3531 | 0.76558 | 0.27342 | 3.3921 | 9.223% | 9.813% | 6.631% | 1.1016 | 1.1088 | 1.071
2010-07-30 | 3 | 27.1073 | 7.9781 | 35.0854 | 2.1414 | 0.76558 | 0.26083 | 3.1678 | 9.029% | 9.607% | 6.492% | 1.0992 | 1.1063 | 1.0694
2010-07-30 | 4 | 25.6891 | 7.5759 | 33.265 | 1.9249 | 0.76558 | 0.2473 | 2.9378 | 8.831% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-07-30 | 5 | 24.6655 | 7.2738 | 31.9394 | 1.7745 | 0.76558 | 0.23744 | 2.7776 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-07-30 | 6 | 24.6279 | 7.1426 | 31.7705 | 1.7558 | 0.76558 | 0.23619 | 2.7576 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2010-07-30 | 7 | 24.523 | 7.0521 | 31.5751 | 1.7343 | 0.76558 | 0.23473 | 2.7346 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-07-30 | 8 | 24.162 | 7.1611 | 31.3231 | 1.7067 | 0.76558 | 0.23286 | 2.7052 | 8.636% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-07-30 | 9 | 24.7608 | 7.2669 | 32.0277 | 1.7844 | 0.76558 | 0.2381 | 2.788 | 8.705% | 9.262% | 6.259% | 1.0954 | 1.1021 | 1.0668
2010-07-30 | 10 | 25.1187 | 7.3774 | 32.4961 | 1.8369 | 0.76558 | 0.24158 | 2.8441 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-07-30 | 11 | 26.2956 | 7.6191 | 33.9147 | 2.0008 | 0.76558 | 0.25213 | 3.0185 | 8.9% | 9.47% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-07-30 | 12 | 27.5551 | 8.1236 | 35.6788 | 2.2144 | 0.76558 | 0.26524 | 3.2452 | 9.096% | 9.678% | 6.54% | 1.1001 | 1.1071 | 1.07
2010-07-30 | 13 | 29.3772 | 9.2733 | 38.6505 | 2.5986 | 0.76558 | 0.28733 | 3.6515 | 9.448% | 10.05% | 6.793% | 1.1043 | 1.1118 | 1.0729
2010-07-30 | 14 | 32.6056 | 10.7911 | 43.3967 | 3.276 | 0.76558 | 0.32262 | 4.3642 | 10.06% | 10.7% | 7.231% | 1.1118 | 1.1198 | 1.0779
2010-07-30 | 15 | 37.6323 | 12.9056 | 50.5379 | 4.4429 | 0.76558 | 0.37571 | 5.5842 | 11.05% | 11.76% | 7.945% | 1.1242 | 1.1332 | 1.0863
2010-07-30 | 16 | 39.0954 | 14.1896 | 53.285 | 4.9391 | 0.76558 | 0.39613 | 6.1008 | 11.45% | 12.18% | 8.232% | 1.1293 | 1.1387 | 1.0897
2010-07-30 | 17 | 39.9551 | 14.7737 | 54.7288 | 5.2103 | 0.76558 | 0.40686 | 6.3828 | 11.66% | 12.41% | 8.385% | 1.132 | 1.1417 | 1.0915
2010-07-30 | 18 | 39.8952 | 14.629 | 54.5242 | 5.1715 | 0.76558 | 0.40534 | 6.3424 | 11.63% | 12.38% | 8.364% | 1.1316 | 1.1412 | 1.0913
2010-07-30 | 19 | 39.8669 | 14.0765 | 53.9433 | 5.0619 | 0.76558 | 0.40102 | 6.2285 | 11.55% | 12.29% | 8.302% | 1.1305 | 1.1401 | 1.0905
2010-07-30 | 20 | 38.8579 | 13.1499 | 52.0079 | 4.7051 | 0.76558 | 0.38663 | 5.8574 | 11.26% | 11.98% | 8.098% | 1.1269 | 1.1361 | 1.0881
2010-07-30 | 21 | 40.4223 | 12.683 | 53.1053 | 4.9058 | 0.76558 | 0.39479 | 6.0662 | 11.42% | 12.15% | 8.213% | 1.129 | 1.1384 | 1.0895
2010-07-30 | 22 | 39.8331 | 12.306 | 52.1391 | 4.7289 | 0.76558 | 0.38761 | 5.8821 | 11.28% | 12% | 8.111% | 1.1272 | 1.1364 | 1.0883
2010-07-30 | 23 | 37.9638 | 11.7967 | 49.7606 | 4.3073 | 0.76558 | 0.36993 | 5.4428 | 10.94% | 11.64% | 7.864% | 1.1228 | 1.1317 | 1.0854
2010-07-30 | 24 | 36.0409 | 11.5732 | 47.6141 | 3.9437 | 0.76558 | 0.35397 | 5.0633 | 10.63% | 11.31% | 7.646% | 1.119 | 1.1276 | 1.0828
2010-07-30 | 25 | 34.1855 | 11.2722 | 45.4577 | 3.5946 | 0.76558 | 0.33794 | 4.6981 | 10.34% | 11% | 7.431% | 1.1153 | 1.1236 | 1.0803
2010-07-30 | 26 | 32.0741 | 10.2854 | 42.3595 | 3.1213 | 0.76558 | 0.31491 | 4.2018 | 9.919% | 10.55% | 7.132% | 1.1101 | 1.118 | 1.0768
2010-07-30 | 27 | 32.1883 | 10.4145 | 42.6027 | 3.1573 | 0.76558 | 0.31671 | 4.2395 | 9.951% | 10.59% | 7.155% | 1.1105 | 1.1184 | 1.0771
2010-07-30 | 28 | 32.7484 | 10.436 | 43.1844 | 3.2441 | 0.76558 | 0.32104 | 4.3307 | 10.03% | 10.67% | 7.21% | 1.1115 | 1.1194 | 1.0777
2010-07-30 | 29 | 32.2467 | 10.0008 | 42.2475 | 3.1048 | 0.76558 | 0.31407 | 4.1845 | 9.905% | 10.54% | 7.121% | 1.1099 | 1.1178 | 1.0767
2010-07-30 | 30 | 32.2153 | 9.6929 | 41.9082 | 3.0552 | 0.76558 | 0.31155 | 4.1323 | 9.86% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-07-30 | 31 | 34.1552 | 9.6865 | 43.8417 | 3.3436 | 0.76558 | 0.32592 | 4.4351 | 10.12% | 10.76% | 7.273% | 1.1125 | 1.1206 | 1.0784
2010-07-30 | 32 | 34.4739 | 9.7404 | 44.2142 | 3.4006 | 0.76558 | 0.32869 | 4.4949 | 10.17% | 10.82% | 7.309% | 1.1132 | 1.1213 | 1.0789
2010-07-30 | 33 | 34.0838 | 10.1387 | 44.2225 | 3.4019 | 0.76558 | 0.32876 | 4.4962 | 10.17% | 10.82% | 7.31% | 1.1132 | 1.1213 | 1.0789
2010-07-30 | 34 | 34.8634 | 10.2981 | 45.1615 | 3.5479 | 0.76558 | 0.33574 | 4.6492 | 10.29% | 10.95% | 7.402% | 1.1148 | 1.123 | 1.0799
2010-07-30 | 35 | 35.6665 | 10.9495 | 46.616 | 3.7801 | 0.76558 | 0.34655 | 4.8922 | 10.49% | 11.17% | 7.546% | 1.1173 | 1.1257 | 1.0816
2010-07-30 | 36 | 38.6243 | 12.4245 | 51.0488 | 4.5332 | 0.76558 | 0.3795 | 5.6783 | 11.12% | 11.84% | 7.998% | 1.1252 | 1.1342 | 1.0869
2010-07-30 | 37 | 41.6537 | 13.3268 | 54.9806 | 5.2584 | 0.76558 | 0.40873 | 6.4327 | 11.7% | 12.45% | 8.412% | 1.1325 | 1.1422 | 1.0918
2010-07-30 | 38 | 42.9191 | 13.188 | 56.1071 | 5.4761 | 0.76558 | 0.41711 | 6.6588 | 11.87% | 12.63% | 8.533% | 1.1347 | 1.1445 | 1.0933
2010-07-30 | 39 | 42.1556 | 12.7311 | 54.8867 | 5.2405 | 0.76558 | 0.40803 | 6.4141 | 11.69% | 12.43% | 8.402% | 1.1323 | 1.142 | 1.0917
2010-07-30 | 40 | 41.021 | 12.2754 | 53.2963 | 4.9412 | 0.76558 | 0.39621 | 6.103 | 11.45% | 12.18% | 8.233% | 1.1293 | 1.1387 | 1.0897
2010-07-30 | 41 | 41.4479 | 11.9463 | 53.3942 | 4.9593 | 0.76558 | 0.39694 | 6.1218 | 11.47% | 12.2% | 8.244% | 1.1295 | 1.1389 | 1.0898
2010-07-30 | 42 | 41.3342 | 11.3603 | 52.6945 | 4.8302 | 0.76558 | 0.39174 | 5.9875 | 11.36% | 12.09% | 8.17% | 1.1282 | 1.1375 | 1.089
2010-07-30 | 43 | 38.9329 | 10.7168 | 49.6497 | 4.2881 | 0.76558 | 0.3691 | 5.4228 | 10.92% | 11.62% | 7.853% | 1.1226 | 1.1315 | 1.0852
2010-07-30 | 44 | 36.5174 | 10.1977 | 46.7151 | 3.7962 | 0.76558 | 0.34729 | 4.9091 | 10.51% | 11.18% | 7.556% | 1.1174 | 1.1259 | 1.0817
2010-07-30 | 45 | 32.3664 | 9.2646 | 41.631 | 3.0149 | 0.76558 | 0.30949 | 4.0899 | 9.824% | 10.45% | 7.064% | 1.1089 | 1.1167 | 1.076
2010-07-30 | 46 | 29.0191 | 8.0778 | 37.0969 | 2.3939 | 0.76558 | 0.27578 | 3.4353 | 9.26% | 9.853% | 6.658% | 1.1021 | 1.1093 | 1.0713
2010-07-30 | 47 | 29.0477 | 8.3579 | 37.4056 | 2.4339 | 0.76558 | 0.27808 | 3.4776 | 9.297% | 9.892% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-07-30 | 48 | 28.2143 | 8.8474 | 37.0617 | 2.3894 | 0.76558 | 0.27552 | 3.4305 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-07-31 | 1 | 26.3595 | 8.146 | 34.5055 | 2.0712 | 0.76558 | 0.25652 | 3.0932 | 8.965% | 9.538% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-07-31 | 2 | 27.4278 | 7.9217 | 35.3495 | 2.1737 | 0.76558 | 0.26279 | 3.2021 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-07-31 | 3 | 26.4627 | 7.5151 | 33.9778 | 2.0083 | 0.76558 | 0.2526 | 3.0265 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-07-31 | 4 | 25.5304 | 7.0525 | 32.5829 | 1.8468 | 0.76558 | 0.24223 | 2.8546 | 8.761% | 9.322% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-07-31 | 5 | 24.4092 | 6.903 | 31.3121 | 1.7055 | 0.76558 | 0.23278 | 2.7039 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-07-31 | 6 | 23.7626 | 6.7019 | 30.4645 | 1.6144 | 0.76558 | 0.22648 | 2.6065 | 8.556% | 9.103% | 6.152% | 1.0936 | 1.1002 | 1.0655
2010-07-31 | 7 | 23.1837 | 6.6388 | 29.8225 | 1.5471 | 0.76558 | 0.2217 | 2.5344 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-07-31 | 8 | 22.6933 | 6.5591 | 29.2524 | 1.4885 | 0.76558 | 0.21747 | 2.4716 | 8.449% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-07-31 | 9 | 22.8911 | 6.6427 | 29.5338 | 1.5173 | 0.76558 | 0.21956 | 2.5024 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-07-31 | 10 | 23.0991 | 6.6149 | 29.714 | 1.5359 | 0.76558 | 0.2209 | 2.5224 | 8.489% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-07-31 | 11 | 23.476 | 6.8205 | 30.2965 | 1.5967 | 0.76558 | 0.22523 | 2.5875 | 8.541% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-07-31 | 12 | 23.9826 | 7.1688 | 31.1514 | 1.6881 | 0.76558 | 0.23158 | 2.6852 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-07-31 | 13 | 25.8776 | 8.0023 | 33.8799 | 1.9967 | 0.76558 | 0.25187 | 3.0142 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-07-31 | 14 | 29.3232 | 9.3379 | 38.6611 | 2.6001 | 0.76558 | 0.28741 | 3.6531 | 9.449% | 10.05% | 6.794% | 1.1043 | 1.1118 | 1.0729
2010-07-31 | 15 | 33.7957 | 11.2166 | 45.0123 | 3.5245 | 0.76558 | 0.33463 | 4.6247 | 10.27% | 10.93% | 7.387% | 1.1145 | 1.1227 | 1.0798
2010-07-31 | 16 | 35.5764 | 12.1719 | 47.7483 | 3.966 | 0.76558 | 0.35497 | 5.0865 | 10.65% | 11.33% | 7.659% | 1.1192 | 1.1278 | 1.0829
2010-07-31 | 17 | 37.4134 | 12.6358 | 50.0492 | 4.3574 | 0.76558 | 0.37207 | 5.4951 | 10.98% | 11.68% | 7.894% | 1.1233 | 1.1323 | 1.0857
2010-07-31 | 18 | 38.4962 | 12.4604 | 50.9566 | 4.5169 | 0.76558 | 0.37882 | 5.6612 | 11.11% | 11.82% | 7.988% | 1.125 | 1.1341 | 1.0868
2010-07-31 | 19 | 39.8241 | 12.3431 | 52.1671 | 4.734 | 0.76558 | 0.38782 | 5.8874 | 11.29% | 12.01% | 8.114% | 1.1272 | 1.1365 | 1.0883
2010-07-31 | 20 | 39.5458 | 12.1531 | 51.6989 | 4.6494 | 0.76558 | 0.38434 | 5.7993 | 11.22% | 11.94% | 8.065% | 1.1263 | 1.1355 | 1.0877
2010-07-31 | 21 | 41.5199 | 12.1068 | 53.6267 | 5.0026 | 0.76558 | 0.39867 | 6.1669 | 11.5% | 12.24% | 8.268% | 1.1299 | 1.1394 | 1.0901
2010-07-31 | 22 | 40.9072 | 11.7977 | 52.7048 | 4.8321 | 0.76558 | 0.39181 | 5.9895 | 11.36% | 12.09% | 8.171% | 1.1282 | 1.1375 | 1.089
2010-07-31 | 23 | 39.2836 | 11.4209 | 50.7045 | 4.4723 | 0.76558 | 0.37694 | 5.6148 | 11.07% | 11.78% | 7.962% | 1.1245 | 1.1336 | 1.0865
2010-07-31 | 24 | 37.2631 | 11.0614 | 48.3245 | 4.0623 | 0.76558 | 0.35925 | 5.1871 | 10.73% | 11.42% | 7.718% | 1.1202 | 1.1289 | 1.0836
2010-07-31 | 25 | 34.6966 | 10.5844 | 45.281 | 3.5667 | 0.76558 | 0.33662 | 4.6689 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-07-31 | 26 | 32.7234 | 9.6241 | 42.3475 | 3.1195 | 0.76558 | 0.31482 | 4.1999 | 9.918% | 10.55% | 7.131% | 1.1101 | 1.118 | 1.0768
2010-07-31 | 27 | 32.6337 | 9.8643 | 42.498 | 3.1418 | 0.76558 | 0.31594 | 4.2233 | 9.938% | 10.57% | 7.145% | 1.1103 | 1.1182 | 1.0769
2010-07-31 | 28 | 32.9332 | 10.0294 | 42.9627 | 3.2108 | 0.76558 | 0.31939 | 4.2958 | 9.999% | 10.64% | 7.189% | 1.1111 | 1.1191 | 1.0775
2010-07-31 | 29 | 32.7632 | 9.5442 | 42.3074 | 3.1136 | 0.76558 | 0.31452 | 4.1937 | 9.913% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-07-31 | 30 | 32.2864 | 9.2817 | 41.5681 | 3.0058 | 0.76558 | 0.30902 | 4.0804 | 9.816% | 10.44% | 7.058% | 1.1088 | 1.1166 | 1.0759
2010-07-31 | 31 | 34.5027 | 9.1427 | 43.6454 | 3.3137 | 0.76558 | 0.32447 | 4.4037 | 10.09% | 10.74% | 7.255% | 1.1122 | 1.1203 | 1.0782
2010-07-31 | 32 | 35.0384 | 9.2357 | 44.2741 | 3.4098 | 0.76558 | 0.32914 | 4.5046 | 10.17% | 10.83% | 7.315% | 1.1133 | 1.1214 | 1.0789
2010-07-31 | 33 | 34.9678 | 9.4696 | 44.4374 | 3.435 | 0.76558 | 0.33035 | 4.531 | 10.2% | 10.85% | 7.331% | 1.1135 | 1.1217 | 1.0791
2010-07-31 | 34 | 35.5433 | 9.6022 | 45.1454 | 3.5454 | 0.76558 | 0.33562 | 4.6466 | 10.29% | 10.95% | 7.4% | 1.1147 | 1.123 | 1.0799
2010-07-31 | 35 | 36.189 | 10.2714 | 46.4604 | 3.7549 | 0.76558 | 0.34539 | 4.8659 | 10.47% | 11.14% | 7.53% | 1.117 | 1.1254 | 1.0814
2010-07-31 | 36 | 38.8917 | 11.2815 | 50.1733 | 4.379 | 0.76558 | 0.37299 | 5.5176 | 11% | 11.7% | 7.907% | 1.1236 | 1.1325 | 1.0859
2010-07-31 | 37 | 40.4467 | 12.0341 | 52.4808 | 4.7911 | 0.76558 | 0.39015 | 5.9468 | 11.33% | 12.06% | 8.147% | 1.1278 | 1.1371 | 1.0887
2010-07-31 | 38 | 40.9141 | 12.1377 | 53.0518 | 4.8959 | 0.76558 | 0.39439 | 6.0559 | 11.42% | 12.15% | 8.207% | 1.1289 | 1.1382 | 1.0894
2010-07-31 | 39 | 40.1891 | 11.9841 | 52.1732 | 4.7351 | 0.76558 | 0.38786 | 5.8885 | 11.29% | 12.01% | 8.115% | 1.1272 | 1.1365 | 1.0883
2010-07-31 | 40 | 39.3673 | 11.5181 | 50.8855 | 4.5042 | 0.76558 | 0.37829 | 5.6481 | 11.1% | 11.81% | 7.981% | 1.1249 | 1.1339 | 1.0867
2010-07-31 | 41 | 40.016 | 11.2081 | 51.2241 | 4.5644 | 0.76558 | 0.38081 | 5.7108 | 11.15% | 11.86% | 8.016% | 1.1255 | 1.1346 | 1.0871
2010-07-31 | 42 | 40.058 | 10.7651 | 50.823 | 4.4932 | 0.76558 | 0.37782 | 5.6366 | 11.09% | 11.8% | 7.974% | 1.1247 | 1.1338 | 1.0867
2010-07-31 | 43 | 38.5769 | 10.2296 | 48.8064 | 4.1437 | 0.76558 | 0.36283 | 5.2721 | 10.8% | 11.49% | 7.767% | 1.1211 | 1.1299 | 1.0842
2010-07-31 | 44 | 37.1836 | 9.8299 | 47.0135 | 3.8449 | 0.76558 | 0.3495 | 4.9599 | 10.55% | 11.23% | 7.585% | 1.1179 | 1.1264 | 1.0821
2010-07-31 | 45 | 33.5362 | 8.9802 | 42.5164 | 3.1445 | 0.76558 | 0.31607 | 4.2261 | 9.94% | 10.58% | 7.147% | 1.1104 | 1.1183 | 1.077
2010-07-31 | 46 | 31.1143 | 8.0511 | 39.1654 | 2.6683 | 0.76558 | 0.29116 | 3.7251 | 9.511% | 10.12% | 6.839% | 1.1051 | 1.1126 | 1.0734
2010-07-31 | 47 | 28.4601 | 8.3399 | 36.8 | 2.3558 | 0.76558 | 0.27358 | 3.3949 | 9.225% | 9.816% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-07-31 | 48 | 26.7575 | 8.9009 | 35.6584 | 2.2119 | 0.76558 | 0.26509 | 3.2425 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.07
2010-08-01 | 1 | 25.5191 | 8.0241 | 33.5432 | 1.9572 | 0.76558 | 0.24936 | 2.9722 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2010-08-01 | 2 | 24.5791 | 7.7617 | 32.3408 | 1.8194 | 0.76558 | 0.24043 | 2.8254 | 8.736% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-08-01 | 3 | 23.5063 | 7.3438 | 30.8501 | 1.6556 | 0.76558 | 0.22934 | 2.6505 | 8.592% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-08-01 | 4 | 22.8506 | 6.8943 | 29.7449 | 1.5391 | 0.76558 | 0.22113 | 2.5258 | 8.491% | 9.035% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-08-01 | 5 | 22.6955 | 6.7623 | 29.4578 | 1.5095 | 0.76558 | 0.21899 | 2.4941 | 8.467% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-08-01 | 6 | 27.2153 | 6.5884 | 33.8038 | 1.9878 | 0.76558 | 0.2513 | 3.0046 | 8.888% | 9.457% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-08-01 | 7 | 26.8781 | 6.5515 | 33.4297 | 1.944 | 0.76558 | 0.24852 | 2.9581 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-08-01 | 8 | 25.9502 | 6.534 | 32.4842 | 1.8356 | 0.76558 | 0.24149 | 2.8427 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-08-01 | 9 | 25.4843 | 6.5059 | 31.9903 | 1.7802 | 0.76558 | 0.23782 | 2.7836 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-08-01 | 10 | 25.3634 | 6.5614 | 31.9248 | 1.7729 | 0.76558 | 0.23733 | 2.7758 | 8.695% | 9.251% | 6.252% | 1.0952 | 1.1019 | 1.0667
2010-08-01 | 11 | 26.1324 | 6.6842 | 32.8166 | 1.8734 | 0.76558 | 0.24396 | 2.8829 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-08-01 | 12 | 26.4717 | 6.6967 | 33.1684 | 1.9137 | 0.76558 | 0.24658 | 2.9259 | 8.821% | 9.386% | 6.343% | 1.0967 | 1.1036 | 1.0677
2010-08-01 | 13 | 27.359 | 7.2311 | 34.5901 | 2.0813 | 0.76558 | 0.25715 | 3.104 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-08-01 | 14 | 28.8758 | 7.7838 | 36.6596 | 2.3378 | 0.76558 | 0.27253 | 3.3759 | 9.209% | 9.798% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-08-01 | 15 | 31.9787 | 8.6196 | 40.5982 | 2.8671 | 0.76558 | 0.30181 | 3.9345 | 9.691% | 10.31% | 6.968% | 1.1073 | 1.115 | 1.0749
2010-08-01 | 16 | 34.6172 | 9.4534 | 44.0706 | 3.3786 | 0.76558 | 0.32763 | 4.4718 | 10.15% | 10.8% | 7.296% | 1.1129 | 1.121 | 1.0787
2010-08-01 | 17 | 36.936 | 10.7035 | 47.6395 | 3.9479 | 0.76558 | 0.35416 | 5.0677 | 10.64% | 11.32% | 7.648% | 1.119 | 1.1276 | 1.0828
2010-08-01 | 18 | 38.7797 | 11.2992 | 50.0789 | 4.3626 | 0.76558 | 0.37229 | 5.5005 | 10.98% | 11.69% | 7.897% | 1.1234 | 1.1323 | 1.0857
2010-08-01 | 19 | 40.6886 | 11.3899 | 52.0785 | 4.7179 | 0.76558 | 0.38716 | 5.8707 | 11.27% | 11.99% | 8.105% | 1.127 | 1.1363 | 1.0882
2010-08-01 | 20 | 41.0467 | 11.3876 | 52.4343 | 4.7826 | 0.76558 | 0.3898 | 5.938 | 11.32% | 12.05% | 8.142% | 1.1277 | 1.137 | 1.0886
2010-08-01 | 21 | 40.527 | 11.352 | 51.879 | 4.6819 | 0.76558 | 0.38567 | 5.8331 | 11.24% | 11.96% | 8.084% | 1.1267 | 1.1359 | 1.088
2010-08-01 | 22 | 40.1665 | 11.0296 | 51.1962 | 4.5594 | 0.76558 | 0.3806 | 5.7056 | 11.14% | 11.86% | 8.013% | 1.1254 | 1.1345 | 1.0871
2010-08-01 | 23 | 39.2195 | 10.5465 | 49.766 | 4.3082 | 0.76558 | 0.36997 | 5.4438 | 10.94% | 11.64% | 7.865% | 1.1228 | 1.1317 | 1.0854
2010-08-01 | 24 | 38.1703 | 10.2341 | 48.4044 | 4.0757 | 0.76558 | 0.35984 | 5.2011 | 10.75% | 11.43% | 7.726% | 1.1204 | 1.1291 | 1.0837
2010-08-01 | 25 | 37.0176 | 9.9994 | 47.017 | 3.8454 | 0.76558 | 0.34953 | 4.9605 | 10.55% | 11.23% | 7.586% | 1.1179 | 1.1265 | 1.0821
2010-08-01 | 26 | 36.1395 | 9.1978 | 45.3373 | 3.5756 | 0.76558 | 0.33704 | 4.6782 | 10.32% | 10.98% | 7.419% | 1.1151 | 1.1233 | 1.0801
2010-08-01 | 27 | 35.6066 | 9.4677 | 45.0743 | 3.5342 | 0.76558 | 0.33509 | 4.6349 | 10.28% | 10.94% | 7.393% | 1.1146 | 1.1228 | 1.0798
2010-08-01 | 28 | 35.3918 | 9.6415 | 45.0333 | 3.5278 | 0.76558 | 0.33478 | 4.6282 | 10.28% | 10.93% | 7.389% | 1.1145 | 1.1228 | 1.0798
2010-08-01 | 29 | 34.0551 | 9.2039 | 43.259 | 3.2553 | 0.76558 | 0.32159 | 4.3424 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-08-01 | 30 | 34.1428 | 8.8565 | 42.9993 | 3.2163 | 0.76558 | 0.31966 | 4.3015 | 10% | 10.64% | 7.193% | 1.1112 | 1.1191 | 1.0775
2010-08-01 | 31 | 36.2236 | 8.9268 | 45.1504 | 3.5462 | 0.76558 | 0.33565 | 4.6474 | 10.29% | 10.95% | 7.401% | 1.1147 | 1.123 | 1.0799
2010-08-01 | 32 | 36.6698 | 8.7584 | 45.4282 | 3.5899 | 0.76558 | 0.33772 | 4.6932 | 10.33% | 10.99% | 7.428% | 1.1152 | 1.1235 | 1.0802
2010-08-01 | 33 | 36.5837 | 8.9732 | 45.5569 | 3.6103 | 0.76558 | 0.33868 | 4.7146 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-08-01 | 34 | 38.2646 | 9.3265 | 47.5911 | 3.9399 | 0.76558 | 0.3538 | 5.0593 | 10.63% | 11.31% | 7.644% | 1.119 | 1.1275 | 1.0828
2010-08-01 | 35 | 38.5066 | 10.0088 | 48.5154 | 4.0944 | 0.76558 | 0.36067 | 5.2207 | 10.76% | 11.45% | 7.737% | 1.1206 | 1.1293 | 1.0839
2010-08-01 | 36 | 40.934 | 11.2091 | 52.1431 | 4.7297 | 0.76558 | 0.38764 | 5.8829 | 11.28% | 12% | 8.112% | 1.1272 | 1.1364 | 1.0883
2010-08-01 | 37 | 42.7708 | 12.022 | 54.7927 | 5.2225 | 0.76558 | 0.40734 | 6.3954 | 11.67% | 12.42% | 8.392% | 1.1321 | 1.1418 | 1.0916
2010-08-01 | 38 | 43.1833 | 11.8143 | 54.9976 | 5.2616 | 0.76558 | 0.40886 | 6.4361 | 11.7% | 12.45% | 8.414% | 1.1325 | 1.1422 | 1.0919
2010-08-01 | 39 | 43.2845 | 11.4978 | 54.7823 | 5.2205 | 0.76558 | 0.40726 | 6.3934 | 11.67% | 12.42% | 8.391% | 1.1321 | 1.1418 | 1.0916
2010-08-01 | 40 | 42.1744 | 11.0794 | 53.2538 | 4.9333 | 0.76558 | 0.3959 | 6.0948 | 11.44% | 12.18% | 8.229% | 1.1292 | 1.1387 | 1.0897
2010-08-01 | 41 | 42.5431 | 10.9026 | 53.4458 | 4.9689 | 0.76558 | 0.39732 | 6.1318 | 11.47% | 12.21% | 8.249% | 1.1296 | 1.139 | 1.0899
2010-08-01 | 42 | 42.8562 | 10.4916 | 53.3478 | 4.9507 | 0.76558 | 0.39659 | 6.1129 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1388 | 1.0898
2010-08-01 | 43 | 41.4015 | 10.074 | 51.4755 | 4.6093 | 0.76558 | 0.38268 | 5.7576 | 11.19% | 11.9% | 8.042% | 1.1259 | 1.1351 | 1.0875
2010-08-01 | 44 | 39.7183 | 9.2967 | 49.015 | 4.1792 | 0.76558 | 0.36438 | 5.3092 | 10.83% | 11.52% | 7.788% | 1.1215 | 1.1303 | 1.0845
2010-08-01 | 45 | 37.0001 | 8.782 | 45.7821 | 3.6461 | 0.76558 | 0.34035 | 4.752 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0806
2010-08-01 | 46 | 34.1249 | 8.1649 | 42.2898 | 3.111 | 0.76558 | 0.31439 | 4.191 | 9.91% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-08-01 | 47 | 33.5651 | 8.6494 | 42.2145 | 3.1 | 0.76558 | 0.31383 | 4.1794 | 9.9% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-08-01 | 48 | 32.9282 | 9.1164 | 42.0446 | 3.0751 | 0.76558 | 0.31256 | 4.1532 | 9.878% | 10.51% | 7.102% | 1.1096 | 1.1174 | 1.0765
2010-08-02 | 1 | 30.8002 | 8.2828 | 39.083 | 2.6571 | 0.76558 | 0.29055 | 3.7132 | 9.501% | 10.11% | 6.831% | 1.105 | 1.1125 | 1.0733
2010-08-02 | 2 | 31.89 | 8.0177 | 39.9077 | 2.7704 | 0.76558 | 0.29668 | 3.8327 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-08-02 | 3 | 31.024 | 7.5109 | 38.5348 | 2.5831 | 0.76558 | 0.28647 | 3.6352 | 9.433% | 10.04% | 6.783% | 1.1042 | 1.1116 | 1.0728
2010-08-02 | 4 | 29.846 | 7.1819 | 37.0279 | 2.385 | 0.76558 | 0.27527 | 3.4259 | 9.252% | 9.844% | 6.652% | 1.102 | 1.1092 | 1.0713
2010-08-02 | 5 | 28.8108 | 7.0066 | 35.8174 | 2.2316 | 0.76558 | 0.26627 | 3.2635 | 9.111% | 9.695% | 6.551% | 1.1002 | 1.1074 | 1.0701
2010-08-02 | 6 | 27.7573 | 6.8588 | 34.6162 | 2.0845 | 0.76558 | 0.25734 | 3.1074 | 8.977% | 9.551% | 6.454% | 1.0986 | 1.1056 | 1.069
2010-08-02 | 7 | 27.3854 | 6.7968 | 34.1822 | 2.0325 | 0.76558 | 0.25411 | 3.0522 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2010-08-02 | 8 | 26.492 | 6.7776 | 33.2696 | 1.9254 | 0.76558 | 0.24733 | 2.9384 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-08-02 | 9 | 26.607 | 6.9837 | 33.5906 | 1.9628 | 0.76558 | 0.24972 | 2.9781 | 8.866% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2010-08-02 | 10 | 26.522 | 7.0343 | 33.5563 | 1.9588 | 0.76558 | 0.24946 | 2.9738 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-08-02 | 11 | 26.7775 | 6.9857 | 33.7632 | 1.983 | 0.76558 | 0.251 | 2.9996 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-08-02 | 12 | 27.0201 | 7.1162 | 34.1363 | 2.0271 | 0.76558 | 0.25377 | 3.0464 | 8.924% | 9.495% | 6.417% | 1.098 | 1.1049 | 1.0686
2010-08-02 | 13 | 27.9353 | 7.6003 | 35.5356 | 2.1967 | 0.76558 | 0.26418 | 3.2264 | 9.079% | 9.66% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-08-02 | 14 | 29.8481 | 7.9557 | 37.8039 | 2.486 | 0.76558 | 0.28104 | 3.5327 | 9.345% | 9.943% | 6.719% | 1.1031 | 1.1104 | 1.072
2010-08-02 | 15 | 31.1128 | 8.3083 | 39.4211 | 2.7033 | 0.76558 | 0.29306 | 3.7619 | 9.543% | 10.15% | 6.861% | 1.1055 | 1.113 | 1.0737
2010-08-02 | 16 | 31.1119 | 8.7011 | 39.813 | 2.7573 | 0.76558 | 0.29597 | 3.8189 | 9.592% | 10.21% | 6.897% | 1.1061 | 1.1137 | 1.0741
2010-08-02 | 17 | 32.7101 | 9.8358 | 42.5459 | 3.1488 | 0.76558 | 0.31629 | 4.2307 | 9.944% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-08-02 | 18 | 34.5613 | 10.8169 | 45.3783 | 3.582 | 0.76558 | 0.33735 | 4.685 | 10.32% | 10.99% | 7.423% | 1.1151 | 1.1234 | 1.0802
2010-08-02 | 19 | 37.8014 | 11.5721 | 49.3736 | 4.2406 | 0.76558 | 0.36705 | 5.3732 | 10.88% | 11.58% | 7.825% | 1.1221 | 1.131 | 1.0849
2010-08-02 | 20 | 39.5888 | 11.9004 | 51.4891 | 4.6117 | 0.76558 | 0.38278 | 5.7601 | 11.19% | 11.9% | 8.043% | 1.126 | 1.1351 | 1.0875
2010-08-02 | 21 | 43.1466 | 12.5387 | 55.6853 | 5.3941 | 0.76558 | 0.41397 | 6.5736 | 11.8% | 12.56% | 8.488% | 1.1339 | 1.1436 | 1.0927
2010-08-02 | 22 | 44.1213 | 12.7414 | 56.8627 | 5.6246 | 0.76558 | 0.42272 | 6.8129 | 11.98% | 12.75% | 8.615% | 1.1361 | 1.1461 | 1.0943
2010-08-02 | 23 | 43.5668 | 12.4012 | 55.968 | 5.449 | 0.76558 | 0.41607 | 6.6306 | 11.85% | 12.61% | 8.518% | 1.1344 | 1.1442 | 1.0931
2010-08-02 | 24 | 42.9495 | 12.0982 | 55.0477 | 5.2712 | 0.76558 | 0.40923 | 6.446 | 11.71% | 12.46% | 8.419% | 1.1326 | 1.1423 | 1.0919
2010-08-02 | 25 | 40.8776 | 11.7996 | 52.6772 | 4.827 | 0.76558 | 0.39161 | 5.9842 | 11.36% | 12.09% | 8.168% | 1.1282 | 1.1375 | 1.0889
2010-08-02 | 26 | 38.5467 | 11.1785 | 49.7253 | 4.3012 | 0.76558 | 0.36966 | 5.4364 | 10.93% | 11.63% | 7.861% | 1.1227 | 1.1316 | 1.0853
2010-08-02 | 27 | 38.1233 | 11.2408 | 49.3642 | 4.2389 | 0.76558 | 0.36698 | 5.3715 | 10.88% | 11.58% | 7.824% | 1.1221 | 1.1309 | 1.0849
2010-08-02 | 28 | 37.4974 | 11.1879 | 48.6853 | 4.1232 | 0.76558 | 0.36193 | 5.2507 | 10.78% | 11.48% | 7.754% | 1.1209 | 1.1296 | 1.0841
2010-08-02 | 29 | 36.0852 | 10.6962 | 46.7814 | 3.807 | 0.76558 | 0.34778 | 4.9203 | 10.52% | 11.19% | 7.562% | 1.1175 | 1.126 | 1.0818
2010-08-02 | 30 | 35.027 | 10.0292 | 45.0562 | 3.5314 | 0.76558 | 0.33495 | 4.6319 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-08-02 | 31 | 36.7658 | 9.7196 | 46.4854 | 3.759 | 0.76558 | 0.34558 | 4.8701 | 10.48% | 11.15% | 7.533% | 1.117 | 1.1255 | 1.0815
2010-08-02 | 32 | 36.5293 | 9.299 | 45.8283 | 3.6534 | 0.76558 | 0.34069 | 4.7597 | 10.39% | 11.05% | 7.468% | 1.1159 | 1.1242 | 1.0807
2010-08-02 | 33 | 36.0247 | 9.4054 | 45.4301 | 3.5902 | 0.76558 | 0.33773 | 4.6935 | 10.33% | 10.99% | 7.428% | 1.1152 | 1.1235 | 1.0802
2010-08-02 | 34 | 36.4184 | 9.7657 | 46.1842 | 3.7104 | 0.76558 | 0.34334 | 4.8193 | 10.44% | 11.1% | 7.503% | 1.1165 | 1.1249 | 1.0811
2010-08-02 | 35 | 37.6299 | 10.8711 | 48.5009 | 4.092 | 0.76558 | 0.36056 | 5.2181 | 10.76% | 11.45% | 7.736% | 1.1206 | 1.1293 | 1.0838
2010-08-02 | 36 | 40.566 | 12.4351 | 53.0011 | 4.8866 | 0.76558 | 0.39402 | 6.0462 | 11.41% | 12.14% | 8.202% | 1.1288 | 1.1381 | 1.0893
2010-08-02 | 37 | 42.7674 | 12.8316 | 55.599 | 5.3774 | 0.76558 | 0.41333 | 6.5563 | 11.79% | 12.55% | 8.478% | 1.1337 | 1.1435 | 1.0926
2010-08-02 | 38 | 43.2784 | 12.7028 | 55.9812 | 5.4515 | 0.76558 | 0.41617 | 6.6333 | 11.85% | 12.61% | 8.52% | 1.1344 | 1.1443 | 1.0931
2010-08-02 | 39 | 42.77 | 12.3586 | 55.1286 | 5.2868 | 0.76558 | 0.40983 | 6.4622 | 11.72% | 12.47% | 8.428% | 1.1328 | 1.1425 | 1.092
2010-08-02 | 40 | 41.5194 | 11.827 | 53.3465 | 4.9505 | 0.76558 | 0.39658 | 6.1126 | 11.46% | 12.19% | 8.239% | 1.1294 | 1.1388 | 1.0898
2010-08-02 | 41 | 41.8646 | 11.5411 | 53.4058 | 4.9615 | 0.76558 | 0.39702 | 6.1241 | 11.47% | 12.2% | 8.245% | 1.1295 | 1.139 | 1.0899
2010-08-02 | 42 | 41.8269 | 11.0513 | 52.8783 | 4.8639 | 0.76558 | 0.3931 | 6.0226 | 11.39% | 12.12% | 8.189% | 1.1285 | 1.1379 | 1.0892
2010-08-02 | 43 | 40.1016 | 10.3682 | 50.4698 | 4.431 | 0.76558 | 0.3752 | 5.5717 | 11.04% | 11.75% | 7.938% | 1.1241 | 1.1331 | 1.0862
2010-08-02 | 44 | 37.4497 | 9.6987 | 47.1484 | 3.8669 | 0.76558 | 0.35051 | 4.983 | 10.57% | 11.25% | 7.599% | 1.1182 | 1.1267 | 1.0822
2010-08-02 | 45 | 33.0942 | 8.7659 | 41.8601 | 3.0481 | 0.76558 | 0.31119 | 4.1249 | 9.854% | 10.48% | 7.085% | 1.1093 | 1.1171 | 1.0763
2010-08-02 | 46 | 29.5036 | 7.7817 | 37.2852 | 2.4183 | 0.76558 | 0.27718 | 3.461 | 9.283% | 9.877% | 6.674% | 1.1023 | 1.1096 | 1.0715
2010-08-02 | 47 | 29.6042 | 8.1748 | 37.779 | 2.4828 | 0.76558 | 0.28085 | 3.5292 | 9.342% | 9.94% | 6.717% | 1.103 | 1.1104 | 1.072
2010-08-02 | 48 | 29.1507 | 8.6737 | 37.8243 | 2.4887 | 0.76558 | 0.28119 | 3.5355 | 9.347% | 9.945% | 6.721% | 1.1031 | 1.1104 | 1.072
2010-08-03 | 1 | 27.3887 | 7.8395 | 35.2282 | 2.1588 | 0.76558 | 0.26189 | 3.1863 | 9.045% | 9.624% | 6.503% | 1.0994 | 1.1065 | 1.0696
2010-08-03 | 2 | 28.5073 | 7.6739 | 36.1813 | 2.2772 | 0.76558 | 0.26898 | 3.3118 | 9.153% | 9.739% | 6.581% | 1.1008 | 1.1079 | 1.0704
2010-08-03 | 3 | 27.1895 | 7.3416 | 34.5311 | 2.0742 | 0.76558 | 0.25671 | 3.0965 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-08-03 | 4 | 26.1708 | 7.0274 | 33.1982 | 1.9172 | 0.76558 | 0.2468 | 2.9296 | 8.824% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-08-03 | 5 | 25.4863 | 6.7768 | 32.2631 | 1.8107 | 0.76558 | 0.23985 | 2.8161 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-08-03 | 6 | 25.2762 | 6.6696 | 31.9458 | 1.7753 | 0.76558 | 0.23749 | 2.7783 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-08-03 | 7 | 24.6225 | 6.5491 | 31.1716 | 1.6903 | 0.76558 | 0.23173 | 2.6876 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2010-08-03 | 8 | 24.5237 | 6.5282 | 31.0519 | 1.6773 | 0.76558 | 0.23084 | 2.6737 | 8.61% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-08-03 | 9 | 24.8774 | 6.6043 | 31.4817 | 1.7241 | 0.76558 | 0.23404 | 2.7237 | 8.652% | 9.205% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-08-03 | 10 | 25.0888 | 6.7423 | 31.8311 | 1.7625 | 0.76558 | 0.23664 | 2.7648 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-08-03 | 11 | 25.8504 | 6.9097 | 32.7601 | 1.8669 | 0.76558 | 0.24354 | 2.876 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-08-03 | 12 | 27.0512 | 7.3992 | 34.4503 | 2.0645 | 0.76558 | 0.25611 | 3.0862 | 8.958% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-08-03 | 13 | 29.2613 | 8.4382 | 37.6994 | 2.4723 | 0.76558 | 0.28026 | 3.5182 | 9.332% | 9.929% | 6.71% | 1.1029 | 1.1102 | 1.0719
2010-08-03 | 14 | 33.2411 | 10.1225 | 43.3636 | 3.271 | 0.76558 | 0.32237 | 4.359 | 10.05% | 10.7% | 7.228% | 1.1118 | 1.1198 | 1.0779
2010-08-03 | 15 | 38.2815 | 12.321 | 50.6025 | 4.4543 | 0.76558 | 0.37619 | 5.5961 | 11.06% | 11.77% | 7.951% | 1.1243 | 1.1334 | 1.0864
2010-08-03 | 16 | 39.4302 | 13.4429 | 52.8731 | 4.863 | 0.76558 | 0.39307 | 6.0216 | 11.39% | 12.12% | 8.189% | 1.1285 | 1.1379 | 1.0892
2010-08-03 | 17 | 40.5493 | 14.0551 | 54.6044 | 5.1867 | 0.76558 | 0.40594 | 6.3582 | 11.64% | 12.39% | 8.372% | 1.1318 | 1.1414 | 1.0914
2010-08-03 | 18 | 40.7201 | 14.0378 | 54.7579 | 5.2159 | 0.76558 | 0.40708 | 6.3885 | 11.67% | 12.41% | 8.388% | 1.1321 | 1.1417 | 1.0916
2010-08-03 | 19 | 40.545 | 13.3587 | 53.9037 | 5.0544 | 0.76558 | 0.40073 | 6.2207 | 11.54% | 12.28% | 8.298% | 1.1305 | 1.14 | 1.0905
2010-08-03 | 20 | 39.7396 | 12.5363 | 52.2759 | 4.7538 | 0.76558 | 0.38863 | 5.908 | 11.3% | 12.02% | 8.126% | 1.1274 | 1.1367 | 1.0884
2010-08-03 | 21 | 41.7923 | 11.8896 | 53.6819 | 5.0129 | 0.76558 | 0.39908 | 6.1776 | 11.51% | 12.24% | 8.274% | 1.13 | 1.1395 | 1.0902
2010-08-03 | 22 | 40.4014 | 11.3905 | 51.7919 | 4.6662 | 0.76558 | 0.38503 | 5.8168 | 11.23% | 11.95% | 8.075% | 1.1265 | 1.1357 | 1.0878
2010-08-03 | 23 | 37.8131 | 10.6197 | 48.4328 | 4.0805 | 0.76558 | 0.36006 | 5.2061 | 10.75% | 11.44% | 7.729% | 1.1204 | 1.1291 | 1.0838
2010-08-03 | 24 | 35.8814 | 10.2522 | 46.1336 | 3.7023 | 0.76558 | 0.34296 | 4.8108 | 10.43% | 11.1% | 7.498% | 1.1164 | 1.1248 | 1.0811
2010-08-03 | 25 | 33.8406 | 10.0755 | 43.9161 | 3.3549 | 0.76558 | 0.32648 | 4.447 | 10.13% | 10.77% | 7.281% | 1.1127 | 1.1208 | 1.0785
2010-08-03 | 26 | 31.8012 | 9.4779 | 41.279 | 2.9641 | 0.76558 | 0.30687 | 4.0366 | 9.779% | 10.4% | 7.031% | 1.1084 | 1.1161 | 1.0756
2010-08-03 | 27 | 31.9853 | 9.7538 | 41.7391 | 3.0305 | 0.76558 | 0.31029 | 4.1064 | 9.838% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-08-03 | 28 | 32.3985 | 10.0153 | 42.4138 | 3.1293 | 0.76558 | 0.31531 | 4.2102 | 9.926% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-08-03 | 29 | 32.5734 | 9.8405 | 42.4139 | 3.1293 | 0.76558 | 0.31531 | 4.2102 | 9.926% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-08-03 | 30 | 31.9641 | 9.6737 | 41.6377 | 3.0158 | 0.76558 | 0.30954 | 4.091 | 9.825% | 10.45% | 7.064% | 1.109 | 1.1167 | 1.076
2010-08-03 | 31 | 33.9909 | 10.0024 | 43.9932 | 3.3667 | 0.76558 | 0.32705 | 4.4593 | 10.14% | 10.79% | 7.288% | 1.1128 | 1.1209 | 1.0786
2010-08-03 | 32 | 33.862 | 10.1723 | 44.0344 | 3.373 | 0.76558 | 0.32736 | 4.466 | 10.14% | 10.79% | 7.292% | 1.1129 | 1.121 | 1.0787
2010-08-03 | 33 | 33.3248 | 10.5747 | 43.8994 | 3.3524 | 0.76558 | 0.32635 | 4.4443 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-08-03 | 34 | 34.3986 | 10.5404 | 44.939 | 3.513 | 0.76558 | 0.33408 | 4.6127 | 10.26% | 10.92% | 7.38% | 1.1144 | 1.1226 | 1.0797
2010-08-03 | 35 | 35.1095 | 11.4128 | 46.5223 | 3.7649 | 0.76558 | 0.34585 | 4.8764 | 10.48% | 11.15% | 7.536% | 1.1171 | 1.1255 | 1.0815
2010-08-03 | 36 | 38.9933 | 12.6486 | 51.6419 | 4.6392 | 0.76558 | 0.38391 | 5.7887 | 11.21% | 11.93% | 8.059% | 1.1262 | 1.1354 | 1.0877
2010-08-03 | 37 | 42.2891 | 13.2924 | 55.5815 | 5.374 | 0.76558 | 0.4132 | 6.5527 | 11.79% | 12.54% | 8.477% | 1.1337 | 1.1434 | 1.0926
2010-08-03 | 38 | 42.9842 | 12.8613 | 55.8455 | 5.4251 | 0.76558 | 0.41516 | 6.6059 | 11.83% | 12.59% | 8.505% | 1.1342 | 1.144 | 1.093
2010-08-03 | 39 | 42.4794 | 12.5371 | 55.0165 | 5.2653 | 0.76558 | 0.409 | 6.4398 | 11.71% | 12.45% | 8.416% | 1.1326 | 1.1423 | 1.0919
2010-08-03 | 40 | 41.2936 | 11.8538 | 53.1474 | 4.9136 | 0.76558 | 0.3951 | 6.0743 | 11.43% | 12.16% | 8.218% | 1.129 | 1.1384 | 1.0895
2010-08-03 | 41 | 42.1046 | 11.7776 | 53.8823 | 5.0504 | 0.76558 | 0.40057 | 6.2166 | 11.54% | 12.28% | 8.295% | 1.1304 | 1.1399 | 1.0905
2010-08-03 | 42 | 41.7581 | 11.3855 | 53.1436 | 4.9129 | 0.76558 | 0.39508 | 6.0735 | 11.43% | 12.16% | 8.217% | 1.129 | 1.1384 | 1.0895
2010-08-03 | 43 | 39.4001 | 10.5534 | 49.9535 | 4.3408 | 0.76558 | 0.37136 | 5.4777 | 10.97% | 11.67% | 7.884% | 1.1232 | 1.1321 | 1.0856
2010-08-03 | 44 | 37.0863 | 9.8919 | 46.9782 | 3.8391 | 0.76558 | 0.34924 | 4.9539 | 10.55% | 11.22% | 7.582% | 1.1179 | 1.1264 | 1.082
2010-08-03 | 45 | 32.7352 | 8.9646 | 41.6997 | 3.0248 | 0.76558 | 0.31 | 4.1004 | 9.833% | 10.46% | 7.07% | 1.1091 | 1.1169 | 1.0761
2010-08-03 | 46 | 29.5169 | 7.9322 | 37.4491 | 2.4396 | 0.76558 | 0.2784 | 3.4836 | 9.302% | 9.897% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-08-03 | 47 | 28.7225 | 8.0277 | 36.7502 | 2.3494 | 0.76558 | 0.27321 | 3.3882 | 9.219% | 9.809% | 6.629% | 1.1016 | 1.1088 | 1.071
2010-08-03 | 48 | 27.7168 | 8.6001 | 36.3169 | 2.2943 | 0.76558 | 0.26998 | 3.3299 | 9.169% | 9.756% | 6.592% | 1.1009 | 1.1081 | 1.0706
2010-08-04 | 1 | 26.347 | 7.8201 | 34.1672 | 2.0307 | 0.76558 | 0.254 | 3.0503 | 8.928% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-08-04 | 2 | 27.3326 | 7.4395 | 34.7721 | 2.1033 | 0.76558 | 0.2585 | 3.1274 | 8.994% | 9.569% | 6.467% | 1.0988 | 1.1058 | 1.0691
2010-08-04 | 3 | 26.044 | 7.0615 | 33.1055 | 1.9065 | 0.76558 | 0.24611 | 2.9182 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-08-04 | 4 | 24.8069 | 6.6559 | 31.4628 | 1.722 | 0.76558 | 0.2339 | 2.7215 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-08-04 | 5 | 24.0455 | 6.4313 | 30.4768 | 1.6157 | 0.76558 | 0.22657 | 2.6079 | 8.557% | 9.105% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-08-04 | 6 | 23.3133 | 6.2235 | 29.5368 | 1.5176 | 0.76558 | 0.21958 | 2.5028 | 8.473% | 9.016% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-08-04 | 7 | 22.7473 | 6.2112 | 28.9585 | 1.4588 | 0.76558 | 0.21528 | 2.4396 | 8.425% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-08-04 | 8 | 22.5851 | 6.1392 | 28.7244 | 1.4353 | 0.76558 | 0.21354 | 2.4144 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-08-04 | 9 | 22.9637 | 6.1857 | 29.1494 | 1.4781 | 0.76558 | 0.2167 | 2.4603 | 8.44% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-08-04 | 10 | 23.49 | 6.1669 | 29.6569 | 1.53 | 0.76558 | 0.22047 | 2.516 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-08-04 | 11 | 24.5566 | 6.5189 | 31.0754 | 1.6798 | 0.76558 | 0.23102 | 2.6764 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-08-04 | 12 | 25.3211 | 6.9313 | 32.2524 | 1.8095 | 0.76558 | 0.23977 | 2.8148 | 8.728% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-08-04 | 13 | 27.1916 | 7.8184 | 35.01 | 2.1322 | 0.76558 | 0.26027 | 3.158 | 9.02% | 9.598% | 6.486% | 1.0991 | 1.1062 | 1.0694
2010-08-04 | 14 | 30.5561 | 9.3126 | 39.8688 | 2.765 | 0.76558 | 0.29639 | 3.827 | 9.599% | 10.21% | 6.902% | 1.1062 | 1.1138 | 1.0741
2010-08-04 | 15 | 35.1283 | 11.3712 | 46.4995 | 3.7612 | 0.76558 | 0.34568 | 4.8725 | 10.48% | 11.15% | 7.534% | 1.1171 | 1.1255 | 1.0815
2010-08-04 | 16 | 37.7283 | 12.4143 | 50.1426 | 4.3737 | 0.76558 | 0.37277 | 5.512 | 10.99% | 11.7% | 7.904% | 1.1235 | 1.1325 | 1.0858
2010-08-04 | 17 | 39.4894 | 13.0147 | 52.5041 | 4.7954 | 0.76558 | 0.39032 | 5.9513 | 11.33% | 12.06% | 8.15% | 1.1278 | 1.1371 | 1.0887
2010-08-04 | 18 | 40.1287 | 12.8636 | 52.9923 | 4.885 | 0.76558 | 0.39395 | 6.0445 | 11.41% | 12.14% | 8.201% | 1.1287 | 1.1381 | 1.0893
2010-08-04 | 19 | 40.0164 | 12.6132 | 52.6296 | 4.8183 | 0.76558 | 0.39126 | 5.9752 | 11.35% | 12.08% | 8.163% | 1.1281 | 1.1374 | 1.0889
2010-08-04 | 20 | 39.5999 | 12.1801 | 51.78 | 4.664 | 0.76558 | 0.38494 | 5.8145 | 11.23% | 11.95% | 8.074% | 1.1265 | 1.1357 | 1.0878
2010-08-04 | 21 | 41.9342 | 11.7895 | 53.7237 | 5.0207 | 0.76558 | 0.39939 | 6.1857 | 11.51% | 12.25% | 8.278% | 1.1301 | 1.1396 | 1.0903
2010-08-04 | 22 | 40.8484 | 11.5766 | 52.425 | 4.7809 | 0.76558 | 0.38973 | 5.9362 | 11.32% | 12.05% | 8.141% | 1.1277 | 1.137 | 1.0886
2010-08-04 | 23 | 38.5041 | 11.0419 | 49.546 | 4.2702 | 0.76558 | 0.36833 | 5.4041 | 10.91% | 11.61% | 7.842% | 1.1224 | 1.1313 | 1.0851
2010-08-04 | 24 | 36.5681 | 10.641 | 47.2091 | 3.8769 | 0.76558 | 0.35096 | 4.9934 | 10.58% | 11.25% | 7.605% | 1.1183 | 1.1268 | 1.0823
2010-08-04 | 25 | 35.3162 | 10.481 | 45.7972 | 3.6485 | 0.76558 | 0.34046 | 4.7545 | 10.38% | 11.05% | 7.464% | 1.1158 | 1.1242 | 1.0807
2010-08-04 | 26 | 35.6249 | 10.4192 | 46.044 | 3.6879 | 0.76558 | 0.3423 | 4.7958 | 10.42% | 11.08% | 7.489% | 1.1163 | 1.1246 | 1.081
2010-08-04 | 27 | 36.962 | 11.0852 | 48.0472 | 4.0158 | 0.76558 | 0.35719 | 5.1386 | 10.69% | 11.38% | 7.69% | 1.1198 | 1.1284 | 1.0833
2010-08-04 | 28 | 37.2224 | 11.2365 | 48.4589 | 4.0849 | 0.76558 | 0.36025 | 5.2107 | 10.75% | 11.44% | 7.731% | 1.1205 | 1.1292 | 1.0838
2010-08-04 | 29 | 36.9355 | 11.1372 | 48.0727 | 4.0201 | 0.76558 | 0.35738 | 5.143 | 10.7% | 11.38% | 7.692% | 1.1198 | 1.1285 | 1.0833
2010-08-04 | 30 | 35.9098 | 10.8353 | 46.7451 | 3.8011 | 0.76558 | 0.34751 | 4.9142 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.1259 | 1.0818
2010-08-04 | 31 | 37.8752 | 10.8414 | 48.7166 | 4.1285 | 0.76558 | 0.36217 | 5.2562 | 10.79% | 11.48% | 7.758% | 1.1209 | 1.1297 | 1.0841
2010-08-04 | 32 | 38.1242 | 10.9558 | 49.08 | 4.1903 | 0.76558 | 0.36487 | 5.3207 | 10.84% | 11.53% | 7.795% | 1.1216 | 1.1304 | 1.0845
2010-08-04 | 33 | 38.6044 | 11.1438 | 49.7482 | 4.3052 | 0.76558 | 0.36983 | 5.4406 | 10.94% | 11.64% | 7.863% | 1.1228 | 1.1317 | 1.0853
2010-08-04 | 34 | 39.1327 | 11.0065 | 50.1392 | 4.3731 | 0.76558 | 0.37274 | 5.5114 | 10.99% | 11.7% | 7.903% | 1.1235 | 1.1324 | 1.0858
2010-08-04 | 35 | 41.4275 | 11.6493 | 53.0768 | 4.9005 | 0.76558 | 0.39458 | 6.0607 | 11.42% | 12.15% | 8.21% | 1.1289 | 1.1383 | 1.0894
2010-08-04 | 36 | 45.3031 | 12.7396 | 58.0427 | 5.8604 | 0.76558 | 0.4315 | 7.0575 | 12.16% | 12.94% | 8.742% | 1.1384 | 1.1486 | 1.0958
2010-08-04 | 37 | 47.7418 | 12.5237 | 60.2656 | 6.3179 | 0.76558 | 0.44802 | 7.5315 | 12.5% | 13.3% | 8.985% | 1.1428 | 1.1534 | 1.0987
2010-08-04 | 38 | 48.8311 | 12.1591 | 60.9902 | 6.4707 | 0.76558 | 0.45341 | 7.6897 | 12.61% | 13.42% | 9.065% | 1.1443 | 1.1549 | 1.0997
2010-08-04 | 39 | 48.325 | 13.6405 | 61.9655 | 6.6794 | 0.76558 | 0.46066 | 7.9056 | 12.76% | 13.57% | 9.173% | 1.1462 | 1.1571 | 1.101
2010-08-04 | 40 | 46.715 | 12.9558 | 59.6708 | 6.1938 | 0.76558 | 0.4436 | 7.403 | 12.41% | 13.2% | 8.92% | 1.1416 | 1.1521 | 1.0979
2010-08-04 | 41 | 44.9046 | 12.365 | 57.2696 | 5.7054 | 0.76558 | 0.42575 | 6.8967 | 12.04% | 12.81% | 8.659% | 1.1369 | 1.147 | 1.0948
2010-08-04 | 42 | 43.6531 | 11.8777 | 55.5308 | 5.3642 | 0.76558 | 0.41282 | 6.5426 | 11.78% | 12.54% | 8.471% | 1.1336 | 1.1433 | 1.0926
2010-08-04 | 43 | 42.3141 | 11.2277 | 53.5418 | 4.9868 | 0.76558 | 0.39804 | 6.1504 | 11.49% | 12.22% | 8.259% | 1.1298 | 1.1392 | 1.09
2010-08-04 | 44 | 40.2162 | 10.3781 | 50.5943 | 4.4528 | 0.76558 | 0.37612 | 5.5945 | 11.06% | 11.77% | 7.95% | 1.1243 | 1.1333 | 1.0864
2010-08-04 | 45 | 37.6132 | 9.3431 | 46.9564 | 3.8355 | 0.76558 | 0.34908 | 4.9502 | 10.54% | 11.22% | 7.58% | 1.1178 | 1.1263 | 1.082
2010-08-04 | 46 | 35.1392 | 8.2954 | 43.4346 | 3.2818 | 0.76558 | 0.3229 | 4.3702 | 10.06% | 10.71% | 7.234% | 1.1119 | 1.1199 | 1.078
2010-08-04 | 47 | 32.8259 | 8.3946 | 41.2205 | 2.9557 | 0.76558 | 0.30644 | 4.0277 | 9.771% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2010-08-04 | 48 | 31.3988 | 8.8789 | 40.2778 | 2.8221 | 0.76558 | 0.29943 | 3.8871 | 9.651% | 10.27% | 6.939% | 1.1068 | 1.1144 | 1.0746
2010-08-05 | 1 | 29.2289 | 8.1273 | 37.3562 | 2.4275 | 0.76558 | 0.27771 | 3.4708 | 9.291% | 9.886% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-08-05 | 2 | 28.1035 | 7.7415 | 35.845 | 2.2351 | 0.76558 | 0.26648 | 3.2671 | 9.115% | 9.698% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-08-05 | 3 | 27.2536 | 7.4324 | 34.6859 | 2.0929 | 0.76558 | 0.25786 | 3.1163 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-08-05 | 4 | 26.5292 | 7.08 | 33.6092 | 1.965 | 0.76558 | 0.24986 | 2.9804 | 8.868% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2010-08-05 | 5 | 26.2971 | 6.9236 | 33.2207 | 1.9198 | 0.76558 | 0.24697 | 2.9323 | 8.827% | 9.392% | 6.346% | 1.0968 | 1.1037 | 1.0678
2010-08-05 | 6 | 26.0062 | 6.8825 | 32.8887 | 1.8816 | 0.76558 | 0.2445 | 2.8917 | 8.792% | 9.355% | 6.322% | 1.0964 | 1.1032 | 1.0675
2010-08-05 | 7 | 26.0153 | 6.744 | 32.7593 | 1.8668 | 0.76558 | 0.24354 | 2.8759 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-08-05 | 8 | 25.4516 | 6.8329 | 32.2845 | 1.8131 | 0.76558 | 0.24001 | 2.8187 | 8.731% | 9.29% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-08-05 | 9 | 25.6094 | 6.8972 | 32.5065 | 1.8381 | 0.76558 | 0.24166 | 2.8454 | 8.753% | 9.313% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-08-05 | 10 | 25.9237 | 7.0164 | 32.9401 | 1.8875 | 0.76558 | 0.24488 | 2.8979 | 8.798% | 9.361% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-08-05 | 11 | 26.5251 | 7.3289 | 33.854 | 1.9937 | 0.76558 | 0.25167 | 3.0109 | 8.894% | 9.463% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-08-05 | 12 | 27.3542 | 7.6935 | 35.0477 | 2.1368 | 0.76558 | 0.26055 | 3.1629 | 9.024% | 9.602% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-08-05 | 13 | 29.459 | 8.7383 | 38.1973 | 2.538 | 0.76558 | 0.28396 | 3.5876 | 9.392% | 9.993% | 6.753% | 1.1037 | 1.111 | 1.0724
2010-08-05 | 14 | 32.7939 | 10.3538 | 43.1477 | 3.2385 | 0.76558 | 0.32077 | 4.3249 | 10.02% | 10.66% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-08-05 | 15 | 38.5876 | 12.6614 | 51.249 | 4.5688 | 0.76558 | 0.38099 | 5.7154 | 11.15% | 11.87% | 8.018% | 1.1255 | 1.1346 | 1.0872
2010-08-05 | 16 | 43.2511 | 13.6538 | 56.9049 | 5.6329 | 0.76558 | 0.42304 | 6.8215 | 11.99% | 12.75% | 8.619% | 1.1362 | 1.1462 | 1.0943
2010-08-05 | 17 | 45.1993 | 13.8518 | 59.0511 | 6.0658 | 0.76558 | 0.43899 | 7.2704 | 12.31% | 13.1% | 8.852% | 1.1404 | 1.1507 | 1.0971
2010-08-05 | 18 | 45.8565 | 13.6774 | 59.5339 | 6.1654 | 0.76558 | 0.44258 | 7.3736 | 12.39% | 13.18% | 8.905% | 1.1414 | 1.1518 | 1.0978
2010-08-05 | 19 | 45.671 | 13.1627 | 58.8337 | 6.0213 | 0.76558 | 0.43738 | 7.2242 | 12.28% | 13.06% | 8.829% | 1.14 | 1.1503 | 1.0968
2010-08-05 | 20 | 45.1317 | 12.1756 | 57.3072 | 5.7129 | 0.76558 | 0.42603 | 6.9045 | 12.05% | 12.82% | 8.663% | 1.137 | 1.147 | 1.0948
2010-08-05 | 21 | 43.6752 | 11.595 | 55.2702 | 5.3139 | 0.76558 | 0.41089 | 6.4904 | 11.74% | 12.49% | 8.443% | 1.1331 | 1.1428 | 1.0922
2010-08-05 | 22 | 41.9221 | 11.1195 | 53.0416 | 4.894 | 0.76558 | 0.39432 | 6.0539 | 11.41% | 12.14% | 8.206% | 1.1288 | 1.1382 | 1.0894
2010-08-05 | 23 | 39.5941 | 10.4699 | 50.064 | 4.36 | 0.76558 | 0.37218 | 5.4978 | 10.98% | 11.68% | 7.896% | 1.1234 | 1.1323 | 1.0857
2010-08-05 | 24 | 37.952 | 9.9693 | 47.9213 | 3.9948 | 0.76558 | 0.35625 | 5.1166 | 10.68% | 11.36% | 7.677% | 1.1195 | 1.1282 | 1.0832
2010-08-05 | 25 | 36.616 | 9.682 | 46.298 | 3.7287 | 0.76558 | 0.34419 | 4.8385 | 10.45% | 11.12% | 7.514% | 1.1167 | 1.1251 | 1.0812
2010-08-05 | 26 | 35.7909 | 9.1225 | 44.9134 | 3.509 | 0.76558 | 0.33389 | 4.6085 | 10.26% | 10.92% | 7.378% | 1.1143 | 1.1226 | 1.0797
2010-08-05 | 27 | 34.7657 | 9.3583 | 44.1241 | 3.3868 | 0.76558 | 0.32802 | 4.4804 | 10.15% | 10.8% | 7.301% | 1.113 | 1.1211 | 1.0788
2010-08-05 | 28 | 33.9911 | 9.6785 | 43.6696 | 3.3174 | 0.76558 | 0.32464 | 4.4076 | 10.09% | 10.74% | 7.257% | 1.1123 | 1.1203 | 1.0782
2010-08-05 | 29 | 33.2311 | 9.4635 | 42.6946 | 3.1709 | 0.76558 | 0.3174 | 4.2539 | 9.963% | 10.6% | 7.164% | 1.1107 | 1.1186 | 1.0772
2010-08-05 | 30 | 33.6919 | 9.2567 | 42.9486 | 3.2087 | 0.76558 | 0.31929 | 4.2936 | 9.997% | 10.64% | 7.188% | 1.1111 | 1.119 | 1.0774
2010-08-05 | 31 | 34.4104 | 9.4952 | 43.9056 | 3.3533 | 0.76558 | 0.3264 | 4.4453 | 10.12% | 10.77% | 7.28% | 1.1127 | 1.1207 | 1.0785
2010-08-05 | 32 | 35.3538 | 9.4162 | 44.77 | 3.4866 | 0.76558 | 0.33283 | 4.5851 | 10.24% | 10.9% | 7.364% | 1.1141 | 1.1223 | 1.0795
2010-08-05 | 33 | 35.657 | 9.649 | 45.306 | 3.5706 | 0.76558 | 0.33681 | 4.673 | 10.31% | 10.97% | 7.416% | 1.115 | 1.1233 | 1.0801
2010-08-05 | 34 | 37.2093 | 9.7899 | 46.9992 | 3.8425 | 0.76558 | 0.3494 | 4.9575 | 10.55% | 11.22% | 7.584% | 1.1179 | 1.1264 | 1.0821
2010-08-05 | 35 | 40.0799 | 10.564 | 50.6438 | 4.4616 | 0.76558 | 0.37649 | 5.6036 | 11.06% | 11.77% | 7.956% | 1.1244 | 1.1334 | 1.0864
2010-08-05 | 36 | 44.1586 | 12.0524 | 56.211 | 5.4964 | 0.76558 | 0.41788 | 6.6798 | 11.88% | 12.64% | 8.544% | 1.1349 | 1.1447 | 1.0934
2010-08-05 | 37 | 48.1076 | 13.0325 | 61.1401 | 6.5026 | 0.76558 | 0.45452 | 7.7227 | 12.63% | 13.44% | 9.082% | 1.1446 | 1.1553 | 1.0999
2010-08-05 | 38 | 47.3549 | 12.8944 | 60.2493 | 6.3145 | 0.76558 | 0.4479 | 7.528 | 12.49% | 13.29% | 8.984% | 1.1428 | 1.1533 | 1.0987
2010-08-05 | 39 | 47.4371 | 12.6021 | 60.0392 | 6.2705 | 0.76558 | 0.44634 | 7.4825 | 12.46% | 13.26% | 8.961% | 1.1424 | 1.1529 | 1.0984
2010-08-05 | 40 | 46.1711 | 12.3298 | 58.5008 | 5.9533 | 0.76558 | 0.4349 | 7.1538 | 12.23% | 13.01% | 8.792% | 1.1393 | 1.1496 | 1.0964
2010-08-05 | 41 | 47.4463 | 11.9885 | 59.4348 | 6.1449 | 0.76558 | 0.44185 | 7.3523 | 12.37% | 13.16% | 8.894% | 1.1412 | 1.1516 | 1.0976
2010-08-05 | 42 | 46.6117 | 11.765 | 58.3767 | 5.9281 | 0.76558 | 0.43398 | 7.1276 | 12.21% | 12.99% | 8.779% | 1.1391 | 1.1493 | 1.0962
2010-08-05 | 43 | 43.4632 | 11.203 | 54.6661 | 5.1984 | 0.76558 | 0.40639 | 6.3704 | 11.65% | 12.4% | 8.379% | 1.1319 | 1.1415 | 1.0914
2010-08-05 | 44 | 42.8005 | 10.5067 | 53.3072 | 4.9432 | 0.76558 | 0.39629 | 6.105 | 11.45% | 12.19% | 8.234% | 1.1293 | 1.1388 | 1.0897
2010-08-05 | 45 | 39.6083 | 9.4881 | 49.0964 | 4.1931 | 0.76558 | 0.36499 | 5.3237 | 10.84% | 11.54% | 7.796% | 1.1216 | 1.1304 | 1.0846
2010-08-05 | 46 | 35.6826 | 8.4917 | 44.1743 | 3.3945 | 0.76558 | 0.3284 | 4.4885 | 10.16% | 10.81% | 7.306% | 1.1131 | 1.1212 | 1.0788
2010-08-05 | 47 | 34.5461 | 8.7435 | 43.2897 | 3.2599 | 0.76558 | 0.32182 | 4.3473 | 10.04% | 10.69% | 7.22% | 1.1116 | 1.1196 | 1.0778
2010-08-05 | 48 | 33.5517 | 9.1872 | 42.7389 | 3.1775 | 0.76558 | 0.31773 | 4.2608 | 9.969% | 10.61% | 7.168% | 1.1107 | 1.1187 | 1.0772
2010-08-06 | 1 | 31.4808 | 8.6524 | 40.1332 | 2.8018 | 0.76558 | 0.29836 | 3.8658 | 9.632% | 10.25% | 6.926% | 1.1066 | 1.1142 | 1.0744
2010-08-06 | 2 | 33.0162 | 8.3252 | 41.3414 | 2.9731 | 0.76558 | 0.30734 | 4.046 | 9.787% | 10.41% | 7.037% | 1.1085 | 1.1162 | 1.0757
2010-08-06 | 3 | 31.8627 | 7.8285 | 39.6912 | 2.7405 | 0.76558 | 0.29507 | 3.8011 | 9.577% | 10.19% | 6.886% | 1.1059 | 1.1135 | 1.0739
2010-08-06 | 4 | 30.7219 | 7.4271 | 38.149 | 2.5316 | 0.76558 | 0.2836 | 3.5808 | 9.386% | 9.987% | 6.749% | 1.1036 | 1.111 | 1.0724
2010-08-06 | 5 | 30.2138 | 7.2475 | 37.4613 | 2.4412 | 0.76558 | 0.27849 | 3.4853 | 9.304% | 9.899% | 6.689% | 1.1026 | 1.1099 | 1.0717
2010-08-06 | 6 | 30.026 | 7.1201 | 37.1461 | 2.4003 | 0.76558 | 0.27615 | 3.442 | 9.266% | 9.859% | 6.662% | 1.1021 | 1.1094 | 1.0714
2010-08-06 | 7 | 29.7191 | 6.9891 | 36.7082 | 2.344 | 0.76558 | 0.27289 | 3.3825 | 9.215% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.071
2010-08-06 | 8 | 29.6438 | 6.9928 | 36.6366 | 2.3349 | 0.76558 | 0.27236 | 3.3728 | 9.206% | 9.795% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-08-06 | 9 | 29.7275 | 7.2165 | 36.944 | 2.3742 | 0.76558 | 0.27465 | 3.4144 | 9.242% | 9.834% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-08-06 | 10 | 29.996 | 7.2917 | 37.2877 | 2.4186 | 0.76558 | 0.2772 | 3.4614 | 9.283% | 9.877% | 6.674% | 1.1023 | 1.1096 | 1.0715
2010-08-06 | 11 | 30.8076 | 7.552 | 38.3596 | 2.5597 | 0.76558 | 0.28517 | 3.6104 | 9.412% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-08-06 | 12 | 31.834 | 7.9582 | 39.7923 | 2.7544 | 0.76558 | 0.29582 | 3.8158 | 9.589% | 10.2% | 6.895% | 1.1061 | 1.1136 | 1.0741
2010-08-06 | 13 | 34.4168 | 9.1438 | 43.5607 | 3.3008 | 0.76558 | 0.32384 | 4.3902 | 10.08% | 10.72% | 7.246% | 1.1121 | 1.1201 | 1.0781
2010-08-06 | 14 | 38.3671 | 10.887 | 49.2541 | 4.2201 | 0.76558 | 0.36616 | 5.3518 | 10.87% | 11.56% | 7.812% | 1.1219 | 1.1307 | 1.0847
2010-08-06 | 15 | 43.8814 | 13.1811 | 57.0625 | 5.6642 | 0.76558 | 0.42421 | 6.854 | 12.01% | 12.78% | 8.636% | 1.1365 | 1.1465 | 1.0945
2010-08-06 | 16 | 44.996 | 14.5928 | 59.5888 | 6.1768 | 0.76558 | 0.44299 | 7.3854 | 12.39% | 13.19% | 8.911% | 1.1415 | 1.1519 | 1.0978
2010-08-06 | 17 | 45.6969 | 15.322 | 61.0189 | 6.4768 | 0.76558 | 0.45362 | 7.696 | 12.61% | 13.42% | 9.068% | 1.1443 | 1.155 | 1.0997
2010-08-06 | 18 | 45.0038 | 15.1489 | 60.1527 | 6.2943 | 0.76558 | 0.44718 | 7.507 | 12.48% | 13.28% | 8.973% | 1.1426 | 1.1531 | 1.0986
2010-08-06 | 19 | 44.6411 | 14.6176 | 59.2586 | 6.1085 | 0.76558 | 0.44054 | 7.3147 | 12.34% | 13.13% | 8.875% | 1.1408 | 1.1512 | 1.0974
2010-08-06 | 20 | 43.6227 | 13.9191 | 57.5418 | 5.7597 | 0.76558 | 0.42777 | 6.9531 | 12.08% | 12.86% | 8.688% | 1.1374 | 1.1475 | 1.0951
2010-08-06 | 21 | 44.4304 | 13.8835 | 58.3139 | 5.9153 | 0.76558 | 0.43351 | 7.1144 | 12.2% | 12.98% | 8.772% | 1.139 | 1.1492 | 1.0962
2010-08-06 | 22 | 43.1282 | 13.4285 | 56.5567 | 5.5642 | 0.76558 | 0.42045 | 6.7502 | 11.94% | 12.7% | 8.582% | 1.1355 | 1.1455 | 1.0939
2010-08-06 | 23 | 41.2662 | 12.3319 | 53.5981 | 4.9973 | 0.76558 | 0.39845 | 6.1613 | 11.5% | 12.23% | 8.265% | 1.1299 | 1.1394 | 1.0901
2010-08-06 | 24 | 39.3918 | 11.5356 | 50.9274 | 4.5117 | 0.76558 | 0.3786 | 5.6559 | 11.11% | 11.82% | 7.985% | 1.1249 | 1.134 | 1.0868
2010-08-06 | 25 | 36.1968 | 10.9193 | 47.1161 | 3.8616 | 0.76558 | 0.35027 | 4.9775 | 10.56% | 11.24% | 7.596% | 1.1181 | 1.1266 | 1.0822
2010-08-06 | 26 | 34.5986 | 10.1623 | 44.7609 | 3.4852 | 0.76558 | 0.33276 | 4.5836 | 10.24% | 10.9% | 7.363% | 1.1141 | 1.1223 | 1.0795
2010-08-06 | 27 | 34.7774 | 10.438 | 45.2154 | 3.5564 | 0.76558 | 0.33614 | 4.6581 | 10.3% | 10.96% | 7.407% | 1.1149 | 1.1231 | 1.08
2010-08-06 | 28 | 34.503 | 10.4774 | 44.9804 | 3.5195 | 0.76558 | 0.33439 | 4.6195 | 10.27% | 10.93% | 7.384% | 1.1145 | 1.1227 | 1.0797
2010-08-06 | 29 | 33.9494 | 10.0461 | 43.9956 | 3.3671 | 0.76558 | 0.32707 | 4.4597 | 10.14% | 10.79% | 7.288% | 1.1128 | 1.1209 | 1.0786
2010-08-06 | 30 | 33.5603 | 9.7148 | 43.2751 | 3.2577 | 0.76558 | 0.32171 | 4.345 | 10.04% | 10.68% | 7.219% | 1.1116 | 1.1196 | 1.0778
2010-08-06 | 31 | 35.3153 | 9.6399 | 44.9552 | 3.5156 | 0.76558 | 0.3342 | 4.6153 | 10.27% | 10.92% | 7.382% | 1.1144 | 1.1226 | 1.0797
2010-08-06 | 32 | 35.8403 | 9.5635 | 45.4038 | 3.5861 | 0.76558 | 0.33754 | 4.6892 | 10.33% | 10.99% | 7.426% | 1.1152 | 1.1235 | 1.0802
2010-08-06 | 33 | 36.1254 | 9.7631 | 45.8885 | 3.663 | 0.76558 | 0.34114 | 4.7698 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-08-06 | 34 | 37.27 | 9.8609 | 47.1308 | 3.8641 | 0.76558 | 0.35038 | 4.98 | 10.57% | 11.24% | 7.597% | 1.1181 | 1.1267 | 1.0822
2010-08-06 | 35 | 38.2991 | 10.7522 | 49.0513 | 4.1854 | 0.76558 | 0.36465 | 5.3156 | 10.84% | 11.53% | 7.792% | 1.1215 | 1.1303 | 1.0845
2010-08-06 | 36 | 41.8548 | 12.3593 | 54.2141 | 5.1128 | 0.76558 | 0.40303 | 6.2814 | 11.59% | 12.33% | 8.331% | 1.131 | 1.1406 | 1.0909
2010-08-06 | 37 | 45.5692 | 13.3448 | 58.914 | 6.0377 | 0.76558 | 0.43797 | 7.2413 | 12.29% | 13.08% | 8.837% | 1.1401 | 1.1505 | 1.0969
2010-08-06 | 38 | 46.9423 | 13.409 | 60.3514 | 6.3359 | 0.76558 | 0.44866 | 7.5501 | 12.51% | 13.31% | 8.995% | 1.143 | 1.1535 | 1.0988
2010-08-06 | 39 | 45.7172 | 13.26 | 58.9772 | 6.0507 | 0.76558 | 0.43844 | 7.2547 | 12.3% | 13.09% | 8.844% | 1.1403 | 1.1506 | 1.097
2010-08-06 | 40 | 44.5792 | 12.6789 | 57.258 | 5.7031 | 0.76558 | 0.42566 | 6.8943 | 12.04% | 12.81% | 8.657% | 1.1369 | 1.1469 | 1.0948
2010-08-06 | 41 | 44.9659 | 12.3136 | 57.2795 | 5.7073 | 0.76558 | 0.42582 | 6.8987 | 12.04% | 12.81% | 8.66% | 1.1369 | 1.147 | 1.0948
2010-08-06 | 42 | 44.6756 | 11.9686 | 56.6442 | 5.5814 | 0.76558 | 0.4211 | 6.7681 | 11.95% | 12.71% | 8.591% | 1.1357 | 1.1456 | 1.094
2010-08-06 | 43 | 42.2741 | 11.3768 | 53.6509 | 5.0071 | 0.76558 | 0.39885 | 6.1715 | 11.5% | 12.24% | 8.271% | 1.13 | 1.1395 | 1.0902
2010-08-06 | 44 | 39.8317 | 10.5461 | 50.3778 | 4.4148 | 0.76558 | 0.37451 | 5.5549 | 11.03% | 11.73% | 7.928% | 1.1239 | 1.1329 | 1.0861
2010-08-06 | 45 | 35.8359 | 9.3911 | 45.227 | 3.5582 | 0.76558 | 0.33622 | 4.66 | 10.3% | 10.96% | 7.408% | 1.1149 | 1.1231 | 1.08
2010-08-06 | 46 | 32.0988 | 8.3512 | 40.45 | 2.8462 | 0.76558 | 0.30071 | 3.9125 | 9.673% | 10.29% | 6.955% | 1.1071 | 1.1147 | 1.0747
2010-08-06 | 47 | 31.522 | 8.597 | 40.1191 | 2.7999 | 0.76558 | 0.29825 | 3.8637 | 9.631% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-08-06 | 48 | 30.5424 | 9.0908 | 39.6332 | 2.7325 | 0.76558 | 0.29464 | 3.7927 | 9.569% | 10.18% | 6.88% | 1.1058 | 1.1134 | 1.0739
2010-08-07 | 1 | 28.5437 | 8.4178 | 36.9615 | 2.3765 | 0.76558 | 0.27478 | 3.4168 | 9.244% | 9.836% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-08-07 | 2 | 29.893 | 8.1016 | 37.9946 | 2.5112 | 0.76558 | 0.28246 | 3.5592 | 9.368% | 9.967% | 6.735% | 1.1034 | 1.1107 | 1.0722
2010-08-07 | 3 | 28.353 | 7.7532 | 36.1062 | 2.2678 | 0.76558 | 0.26842 | 3.3018 | 9.145% | 9.73% | 6.575% | 1.1006 | 1.1078 | 1.0704
2010-08-07 | 4 | 27.1303 | 7.4763 | 34.6066 | 2.0833 | 0.76558 | 0.25727 | 3.1062 | 8.976% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-08-07 | 5 | 26.4393 | 7.2813 | 33.7206 | 1.978 | 0.76558 | 0.25068 | 2.9943 | 8.88% | 9.448% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-08-07 | 6 | 25.9628 | 7.0957 | 33.0585 | 1.9011 | 0.76558 | 0.24576 | 2.9124 | 8.81% | 9.374% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-08-07 | 7 | 25.7313 | 7.0177 | 32.7489 | 1.8656 | 0.76558 | 0.24346 | 2.8747 | 8.778% | 9.34% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-08-07 | 8 | 25.1149 | 7.1252 | 32.2401 | 1.8081 | 0.76558 | 0.23968 | 2.8134 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2010-08-07 | 9 | 24.9961 | 7.1634 | 32.1595 | 1.7991 | 0.76558 | 0.23908 | 2.8037 | 8.718% | 9.276% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-08-07 | 10 | 25.1976 | 7.3315 | 32.5291 | 1.8407 | 0.76558 | 0.24183 | 2.8481 | 8.756% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-08-07 | 11 | 25.842 | 7.6906 | 33.5326 | 1.956 | 0.76558 | 0.24929 | 2.9709 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-08-07 | 12 | 27.0761 | 8.1303 | 35.2064 | 2.1561 | 0.76558 | 0.26173 | 3.1834 | 9.042% | 9.621% | 6.501% | 1.0994 | 1.1065 | 1.0695
2010-08-07 | 13 | 29.429 | 9.1207 | 38.5497 | 2.5851 | 0.76558 | 0.28658 | 3.6373 | 9.435% | 10.04% | 6.784% | 1.1042 | 1.1116 | 1.0728
2010-08-07 | 14 | 33.3352 | 10.8136 | 44.1488 | 3.3906 | 0.76558 | 0.32821 | 4.4844 | 10.16% | 10.81% | 7.303% | 1.1131 | 1.1212 | 1.0788
2010-08-07 | 15 | 38.2452 | 13.1056 | 51.3507 | 4.587 | 0.76558 | 0.38175 | 5.7343 | 11.17% | 11.88% | 8.029% | 1.1257 | 1.1348 | 1.0873
2010-08-07 | 16 | 39.9818 | 14.2488 | 54.2306 | 5.1159 | 0.76558 | 0.40316 | 6.2847 | 11.59% | 12.33% | 8.332% | 1.1311 | 1.1406 | 1.0909
2010-08-07 | 17 | 41.4179 | 15.0682 | 56.4861 | 5.5503 | 0.76558 | 0.41992 | 6.7358 | 11.92% | 12.69% | 8.574% | 1.1354 | 1.1453 | 1.0938
2010-08-07 | 18 | 41.2568 | 14.9632 | 56.2199 | 5.4981 | 0.76558 | 0.41795 | 6.6817 | 11.88% | 12.65% | 8.545% | 1.1349 | 1.1448 | 1.0934
2010-08-07 | 19 | 40.9642 | 14.6143 | 55.5785 | 5.3734 | 0.76558 | 0.41318 | 6.5521 | 11.79% | 12.54% | 8.476% | 1.1336 | 1.1434 | 1.0926
2010-08-07 | 20 | 39.0119 | 14.151 | 53.1629 | 4.9165 | 0.76558 | 0.39522 | 6.0773 | 11.43% | 12.16% | 8.219% | 1.1291 | 1.1385 | 1.0896
2010-08-07 | 21 | 40.0743 | 13.5956 | 53.6699 | 5.0107 | 0.76558 | 0.39899 | 6.1752 | 11.51% | 12.24% | 8.273% | 1.13 | 1.1395 | 1.0902
2010-08-07 | 22 | 38.6069 | 13.0188 | 51.6256 | 4.6362 | 0.76558 | 0.38379 | 5.7856 | 11.21% | 11.92% | 8.058% | 1.1262 | 1.1354 | 1.0876
2010-08-07 | 23 | 36.8942 | 12.3945 | 49.2887 | 4.226 | 0.76558 | 0.36642 | 5.358 | 10.87% | 11.57% | 7.816% | 1.122 | 1.1308 | 1.0848
2010-08-07 | 24 | 34.711 | 11.8438 | 46.5548 | 3.7702 | 0.76558 | 0.34609 | 4.8819 | 10.49% | 11.16% | 7.54% | 1.1171 | 1.1256 | 1.0815
2010-08-07 | 25 | 32.6553 | 11.0285 | 43.6838 | 3.3195 | 0.76558 | 0.32475 | 4.4098 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-08-07 | 26 | 31.002 | 10.1813 | 41.1833 | 2.9504 | 0.76558 | 0.30616 | 4.0221 | 9.766% | 10.39% | 7.022% | 1.1082 | 1.116 | 1.0755
2010-08-07 | 27 | 31.0867 | 10.249 | 41.3357 | 2.9723 | 0.76558 | 0.30729 | 4.0451 | 9.786% | 10.41% | 7.036% | 1.1085 | 1.1162 | 1.0757
2010-08-07 | 28 | 31.2462 | 10.2663 | 41.5125 | 2.9977 | 0.76558 | 0.30861 | 4.0719 | 9.809% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-08-07 | 29 | 31.0182 | 9.701 | 40.7193 | 2.8843 | 0.76558 | 0.30271 | 3.9526 | 9.707% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2010-08-07 | 30 | 30.6911 | 9.1877 | 39.8787 | 2.7664 | 0.76558 | 0.29646 | 3.8285 | 9.6% | 10.21% | 6.903% | 1.1062 | 1.1138 | 1.0741
2010-08-07 | 31 | 32.8475 | 9.2038 | 42.0513 | 3.076 | 0.76558 | 0.31261 | 4.1542 | 9.879% | 10.51% | 7.103% | 1.1096 | 1.1175 | 1.0765
2010-08-07 | 32 | 32.9943 | 9.0762 | 42.0705 | 3.0789 | 0.76558 | 0.31276 | 4.1572 | 9.882% | 10.51% | 7.105% | 1.1097 | 1.1175 | 1.0765
2010-08-07 | 33 | 33.2026 | 9.2901 | 42.4927 | 3.141 | 0.76558 | 0.3159 | 4.2224 | 9.937% | 10.57% | 7.145% | 1.1103 | 1.1182 | 1.0769
2010-08-07 | 34 | 34.1547 | 9.0995 | 43.2542 | 3.2546 | 0.76558 | 0.32156 | 4.3417 | 10.04% | 10.68% | 7.217% | 1.1116 | 1.1196 | 1.0778
2010-08-07 | 35 | 35.4371 | 9.7076 | 45.1447 | 3.5453 | 0.76558 | 0.33561 | 4.6465 | 10.29% | 10.95% | 7.4% | 1.1147 | 1.123 | 1.0799
2010-08-07 | 36 | 38.3693 | 10.918 | 49.2872 | 4.2257 | 0.76558 | 0.36641 | 5.3577 | 10.87% | 11.57% | 7.816% | 1.122 | 1.1308 | 1.0848
2010-08-07 | 37 | 41.0122 | 11.8556 | 52.8679 | 4.862 | 0.76558 | 0.39303 | 6.0206 | 11.39% | 12.12% | 8.188% | 1.1285 | 1.1379 | 1.0892
2010-08-07 | 38 | 41.4993 | 12.0189 | 53.5182 | 4.9824 | 0.76558 | 0.39786 | 6.1458 | 11.48% | 12.22% | 8.257% | 1.1297 | 1.1392 | 1.09
2010-08-07 | 39 | 40.4641 | 11.961 | 52.4251 | 4.7809 | 0.76558 | 0.38973 | 5.9363 | 11.32% | 12.05% | 8.141% | 1.1277 | 1.137 | 1.0886
2010-08-07 | 40 | 39.3427 | 11.4608 | 50.8035 | 4.4898 | 0.76558 | 0.37768 | 5.633 | 11.09% | 11.8% | 7.972% | 1.1247 | 1.1338 | 1.0866
2010-08-07 | 41 | 40.1315 | 11.2465 | 51.378 | 4.5919 | 0.76558 | 0.38195 | 5.7394 | 11.17% | 11.89% | 8.032% | 1.1258 | 1.1349 | 1.0873
2010-08-07 | 42 | 40.0573 | 10.9061 | 50.9633 | 4.518 | 0.76558 | 0.37887 | 5.6625 | 11.11% | 11.82% | 7.989% | 1.125 | 1.1341 | 1.0868
2010-08-07 | 43 | 38.016 | 10.5048 | 48.5209 | 4.0954 | 0.76558 | 0.36071 | 5.2216 | 10.76% | 11.45% | 7.738% | 1.1206 | 1.1293 | 1.0839
2010-08-07 | 44 | 36.4031 | 9.9864 | 46.3896 | 3.7435 | 0.76558 | 0.34487 | 4.8539 | 10.46% | 11.13% | 7.523% | 1.1169 | 1.1253 | 1.0814
2010-08-07 | 45 | 33.0408 | 9.0888 | 42.1296 | 3.0875 | 0.76558 | 0.3132 | 4.1663 | 9.889% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-08-07 | 46 | 30.6252 | 8.2629 | 38.8881 | 2.6307 | 0.76558 | 0.2891 | 3.6854 | 9.477% | 10.08% | 6.814% | 1.1047 | 1.1121 | 1.0731
2010-08-07 | 47 | 30.493 | 8.5428 | 39.0358 | 2.6507 | 0.76558 | 0.2902 | 3.7065 | 9.495% | 10.1% | 6.827% | 1.1049 | 1.1124 | 1.0733
2010-08-07 | 48 | 29.8726 | 8.9512 | 38.8238 | 2.622 | 0.76558 | 0.28862 | 3.6762 | 9.469% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-08-08 | 1 | 27.6884 | 8.1147 | 35.8031 | 2.2299 | 0.76558 | 0.26616 | 3.2616 | 9.11% | 9.693% | 6.55% | 1.1002 | 1.1073 | 1.0701
2010-08-08 | 2 | 28.7938 | 7.708 | 36.5019 | 2.3177 | 0.76558 | 0.27136 | 3.3547 | 9.19% | 9.779% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-08-08 | 3 | 27.1257 | 7.3936 | 34.5193 | 2.0728 | 0.76558 | 0.25662 | 3.095 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-08-08 | 4 | 26.0869 | 7.0862 | 33.1731 | 1.9143 | 0.76558 | 0.24661 | 2.9265 | 8.822% | 9.386% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-08-08 | 5 | 25.0667 | 6.9295 | 31.9963 | 1.7809 | 0.76558 | 0.23786 | 2.7843 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2010-08-08 | 6 | 24.936 | 6.7681 | 31.7041 | 1.7485 | 0.76558 | 0.23569 | 2.7498 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-08-08 | 7 | 24.6473 | 6.8413 | 31.4886 | 1.7248 | 0.76558 | 0.23409 | 2.7245 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-08-08 | 8 | 24.43 | 6.7495 | 31.1795 | 1.6911 | 0.76558 | 0.23179 | 2.6885 | 8.623% | 9.174% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-08-08 | 9 | 24.2853 | 6.6998 | 30.9851 | 1.6701 | 0.76558 | 0.23035 | 2.666 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-08-08 | 10 | 24.469 | 6.7932 | 31.2623 | 1.7001 | 0.76558 | 0.23241 | 2.6981 | 8.631% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-08-08 | 11 | 24.7834 | 6.8888 | 31.6721 | 1.745 | 0.76558 | 0.23545 | 2.746 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-08-08 | 12 | 25.3862 | 7.081 | 32.4671 | 1.8337 | 0.76558 | 0.24136 | 2.8406 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1026 | 1.0671
2010-08-08 | 13 | 26.7486 | 7.6138 | 34.3624 | 2.054 | 0.76558 | 0.25545 | 3.075 | 8.949% | 9.522% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-08-08 | 14 | 28.6164 | 8.3044 | 36.9208 | 2.3712 | 0.76558 | 0.27447 | 3.4113 | 9.24% | 9.831% | 6.643% | 1.1018 | 1.109 | 1.0712
2010-08-08 | 15 | 30.6819 | 8.9592 | 39.6411 | 2.7335 | 0.76558 | 0.2947 | 3.7938 | 9.57% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-08-08 | 16 | 31.2369 | 9.5837 | 40.8206 | 2.8986 | 0.76558 | 0.30347 | 3.9677 | 9.72% | 10.34% | 6.989% | 1.1077 | 1.1153 | 1.0751
2010-08-08 | 17 | 33.8941 | 10.6965 | 44.5905 | 3.4588 | 0.76558 | 0.33149 | 4.5558 | 10.22% | 10.87% | 7.346% | 1.1138 | 1.122 | 1.0793
2010-08-08 | 18 | 36.319 | 11.8017 | 48.1207 | 4.0281 | 0.76558 | 0.35774 | 5.1514 | 10.71% | 11.39% | 7.697% | 1.1199 | 1.1285 | 1.0834
2010-08-08 | 19 | 38.2714 | 12.4702 | 50.7416 | 4.4788 | 0.76558 | 0.37722 | 5.6216 | 11.08% | 11.79% | 7.966% | 1.1246 | 1.1336 | 1.0866
2010-08-08 | 20 | 39.2622 | 13.0919 | 52.3541 | 4.768 | 0.76558 | 0.38921 | 5.9228 | 11.31% | 12.04% | 8.134% | 1.1276 | 1.1368 | 1.0885
2010-08-08 | 21 | 41.8455 | 13.3673 | 55.2129 | 5.3029 | 0.76558 | 0.41046 | 6.479 | 11.73% | 12.49% | 8.437% | 1.1329 | 1.1427 | 1.0921
2010-08-08 | 22 | 41.7571 | 13.2235 | 54.9806 | 5.2584 | 0.76558 | 0.40873 | 6.4327 | 11.7% | 12.45% | 8.412% | 1.1325 | 1.1422 | 1.0918
2010-08-08 | 23 | 40.5374 | 12.6546 | 53.192 | 4.9218 | 0.76558 | 0.39544 | 6.0829 | 11.44% | 12.17% | 8.222% | 1.1291 | 1.1385 | 1.0896
2010-08-08 | 24 | 39.7305 | 12.2409 | 51.9714 | 4.6985 | 0.76558 | 0.38636 | 5.8505 | 11.26% | 11.98% | 8.094% | 1.1269 | 1.1361 | 1.0881
2010-08-08 | 25 | 38.0329 | 11.8443 | 49.8772 | 4.3275 | 0.76558 | 0.37079 | 5.4639 | 10.95% | 11.66% | 7.876% | 1.123 | 1.1319 | 1.0855
2010-08-08 | 26 | 36.781 | 11.1273 | 47.9083 | 3.9926 | 0.76558 | 0.35616 | 5.1143 | 10.68% | 11.36% | 7.676% | 1.1195 | 1.1281 | 1.0831
2010-08-08 | 27 | 37.1537 | 11.3794 | 48.5331 | 4.0974 | 0.76558 | 0.3608 | 5.2238 | 10.76% | 11.45% | 7.739% | 1.1206 | 1.1293 | 1.0839
2010-08-08 | 28 | 37.3383 | 11.4709 | 48.8092 | 4.1442 | 0.76558 | 0.36285 | 5.2726 | 10.8% | 11.49% | 7.767% | 1.1211 | 1.1299 | 1.0842
2010-08-08 | 29 | 36.562 | 11.0242 | 47.5862 | 3.9391 | 0.76558 | 0.35376 | 5.0584 | 10.63% | 11.31% | 7.643% | 1.1189 | 1.1275 | 1.0828
2010-08-08 | 30 | 35.9307 | 10.6508 | 46.5814 | 3.7745 | 0.76558 | 0.34629 | 4.8864 | 10.49% | 11.16% | 7.542% | 1.1172 | 1.1256 | 1.0816
2010-08-08 | 31 | 37.5924 | 10.6882 | 48.2806 | 4.0549 | 0.76558 | 0.35892 | 5.1794 | 10.73% | 11.41% | 7.713% | 1.1202 | 1.1289 | 1.0836
2010-08-08 | 32 | 37.3904 | 10.5055 | 47.8959 | 3.9905 | 0.76558 | 0.35606 | 5.1122 | 10.67% | 11.36% | 7.674% | 1.1195 | 1.1281 | 1.0831
2010-08-08 | 33 | 36.3394 | 10.837 | 47.1765 | 3.8716 | 0.76558 | 0.35072 | 4.9878 | 10.57% | 11.25% | 7.602% | 1.1182 | 1.1268 | 1.0823
2010-08-08 | 34 | 36.8564 | 11.0481 | 47.9045 | 3.992 | 0.76558 | 0.35613 | 5.1137 | 10.67% | 11.36% | 7.675% | 1.1195 | 1.1281 | 1.0831
2010-08-08 | 35 | 37.9166 | 11.754 | 49.6706 | 4.2917 | 0.76558 | 0.36926 | 5.4266 | 10.93% | 11.62% | 7.855% | 1.1227 | 1.1315 | 1.0852
2010-08-08 | 36 | 40.8197 | 12.693 | 53.5127 | 4.9814 | 0.76558 | 0.39782 | 6.1448 | 11.48% | 12.22% | 8.256% | 1.1297 | 1.1392 | 1.09
2010-08-08 | 37 | 43.2723 | 13.207 | 56.4793 | 5.549 | 0.76558 | 0.41987 | 6.7344 | 11.92% | 12.69% | 8.573% | 1.1354 | 1.1453 | 1.0938
2010-08-08 | 38 | 43.7445 | 12.9629 | 56.7074 | 5.5939 | 0.76558 | 0.42157 | 6.781 | 11.96% | 12.72% | 8.598% | 1.1358 | 1.1458 | 1.0941
2010-08-08 | 39 | 42.6965 | 12.4912 | 55.1877 | 5.2981 | 0.76558 | 0.41027 | 6.4739 | 11.73% | 12.48% | 8.434% | 1.1329 | 1.1426 | 1.0921
2010-08-08 | 40 | 41.6889 | 11.998 | 53.6869 | 5.0139 | 0.76558 | 0.39912 | 6.1785 | 11.51% | 12.25% | 8.275% | 1.1301 | 1.1395 | 1.0902
2010-08-08 | 41 | 41.6641 | 11.5317 | 53.1958 | 4.9225 | 0.76558 | 0.39546 | 6.0836 | 11.44% | 12.17% | 8.223% | 1.1291 | 1.1385 | 1.0896
2010-08-08 | 42 | 41.2519 | 11.0443 | 52.2962 | 4.7575 | 0.76558 | 0.38878 | 5.9118 | 11.3% | 12.03% | 8.128% | 1.1275 | 1.1367 | 1.0885
2010-08-08 | 43 | 39.0684 | 10.4665 | 49.5349 | 4.2683 | 0.76558 | 0.36825 | 5.4022 | 10.91% | 11.6% | 7.841% | 1.1224 | 1.1313 | 1.0851
2010-08-08 | 44 | 37.2835 | 9.9675 | 47.2509 | 3.8838 | 0.76558 | 0.35127 | 5.0006 | 10.58% | 11.26% | 7.609% | 1.1184 | 1.1269 | 1.0824
2010-08-08 | 45 | 33.4326 | 9.1983 | 42.6309 | 3.1614 | 0.76558 | 0.31692 | 4.2439 | 9.955% | 10.59% | 7.158% | 1.1106 | 1.1185 | 1.0771
2010-08-08 | 46 | 30.6446 | 8.4744 | 39.119 | 2.662 | 0.76558 | 0.29082 | 3.7184 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2010-08-08 | 47 | 30.5978 | 8.8036 | 39.4014 | 2.7006 | 0.76558 | 0.29291 | 3.7591 | 9.54% | 10.15% | 6.86% | 1.1055 | 1.113 | 1.0736
2010-08-08 | 48 | 29.7508 | 9.2784 | 39.0293 | 2.6498 | 0.76558 | 0.29015 | 3.7055 | 9.494% | 10.1% | 6.826% | 1.1049 | 1.1124 | 1.0733
2010-08-09 | 1 | 27.9402 | 8.4507 | 36.3909 | 2.3037 | 0.76558 | 0.27053 | 3.3398 | 9.178% | 9.765% | 6.599% | 1.101 | 1.1082 | 1.0706
2010-08-09 | 2 | 29.014 | 8.2032 | 37.2171 | 2.4095 | 0.76558 | 0.27668 | 3.4517 | 9.275% | 9.868% | 6.668% | 1.1022 | 1.1095 | 1.0714
2010-08-09 | 3 | 27.305 | 7.7512 | 35.0562 | 2.1378 | 0.76558 | 0.26061 | 3.164 | 9.025% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-08-09 | 4 | 25.8072 | 7.3753 | 33.1825 | 1.9154 | 0.76558 | 0.24668 | 2.9276 | 8.823% | 9.387% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-08-09 | 5 | 24.8864 | 7.1667 | 32.0531 | 1.7872 | 0.76558 | 0.23829 | 2.7911 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-08-09 | 6 | 24.3394 | 6.9835 | 31.3229 | 1.7067 | 0.76558 | 0.23286 | 2.7051 | 8.636% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-08-09 | 7 | 24.4214 | 6.8905 | 31.3119 | 1.7055 | 0.76558 | 0.23278 | 2.7039 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-08-09 | 8 | 24.38 | 6.9598 | 31.3398 | 1.7085 | 0.76558 | 0.23298 | 2.7071 | 8.638% | 9.191% | 6.211% | 1.0945 | 1.1012 | 1.0662
2010-08-09 | 9 | 24.4773 | 6.9747 | 31.4521 | 1.7208 | 0.76558 | 0.23382 | 2.7202 | 8.649% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-08-09 | 10 | 24.5479 | 7.001 | 31.5489 | 1.7314 | 0.76558 | 0.23454 | 2.7315 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-08-09 | 11 | 24.7459 | 7.0552 | 31.8011 | 1.7592 | 0.76558 | 0.23641 | 2.7612 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-08-09 | 12 | 25.4624 | 7.1182 | 32.5806 | 1.8465 | 0.76558 | 0.24221 | 2.8543 | 8.761% | 9.321% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-08-09 | 13 | 26.4455 | 7.6651 | 34.1106 | 2.024 | 0.76558 | 0.25358 | 3.0432 | 8.921% | 9.492% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-08-09 | 14 | 28.4197 | 8.022 | 36.4416 | 2.3101 | 0.76558 | 0.27091 | 3.3466 | 9.183% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-08-09 | 15 | 30.3712 | 8.4758 | 38.847 | 2.6251 | 0.76558 | 0.28879 | 3.6795 | 9.472% | 10.08% | 6.81% | 1.1046 | 1.1121 | 1.0731
2010-08-09 | 16 | 30.8013 | 8.9952 | 39.7965 | 2.755 | 0.76558 | 0.29585 | 3.8164 | 9.59% | 10.2% | 6.895% | 1.1061 | 1.1136 | 1.0741
2010-08-09 | 17 | 33.2835 | 10.3092 | 43.5926 | 3.3057 | 0.76558 | 0.32407 | 4.3953 | 10.08% | 10.73% | 7.249% | 1.1121 | 1.1202 | 1.0782
2010-08-09 | 18 | 35.3648 | 11.3767 | 46.7415 | 3.8005 | 0.76558 | 0.34748 | 4.9136 | 10.51% | 11.18% | 7.558% | 1.1175 | 1.1259 | 1.0818
2010-08-09 | 19 | 36.6713 | 12.0183 | 48.6897 | 4.1239 | 0.76558 | 0.36197 | 5.2514 | 10.79% | 11.48% | 7.755% | 1.1209 | 1.1296 | 1.0841
2010-08-09 | 20 | 37.3448 | 12.0372 | 49.382 | 4.242 | 0.76558 | 0.36711 | 5.3747 | 10.88% | 11.58% | 7.826% | 1.1221 | 1.131 | 1.0849
2010-08-09 | 21 | 39.1381 | 11.8927 | 51.0308 | 4.53 | 0.76558 | 0.37937 | 5.675 | 11.12% | 11.83% | 7.996% | 1.1251 | 1.1342 | 1.0869
2010-08-09 | 22 | 38.6544 | 11.7109 | 50.3653 | 4.4126 | 0.76558 | 0.37442 | 5.5526 | 11.02% | 11.73% | 7.927% | 1.1239 | 1.1329 | 1.0861
2010-08-09 | 23 | 36.8291 | 10.9188 | 47.7479 | 3.9659 | 0.76558 | 0.35496 | 5.0865 | 10.65% | 11.33% | 7.659% | 1.1192 | 1.1278 | 1.0829
2010-08-09 | 24 | 35.2055 | 10.541 | 45.7465 | 3.6404 | 0.76558 | 0.34008 | 4.7461 | 10.37% | 11.04% | 7.459% | 1.1158 | 1.1241 | 1.0806
2010-08-09 | 25 | 32.9437 | 10.0466 | 42.9903 | 3.215 | 0.76558 | 0.3196 | 4.3001 | 10% | 10.64% | 7.192% | 1.1111 | 1.1191 | 1.0775
2010-08-09 | 26 | 31.4761 | 9.3559 | 40.8319 | 2.9002 | 0.76558 | 0.30355 | 3.9694 | 9.721% | 10.34% | 6.99% | 1.1077 | 1.1154 | 1.0751
2010-08-09 | 27 | 31.5038 | 9.3935 | 40.8973 | 2.9095 | 0.76558 | 0.30404 | 3.9792 | 9.73% | 10.35% | 6.996% | 1.1078 | 1.1155 | 1.0752
2010-08-09 | 28 | 31.3609 | 9.4554 | 40.8163 | 2.898 | 0.76558 | 0.30343 | 3.967 | 9.719% | 10.34% | 6.988% | 1.1077 | 1.1153 | 1.0751
2010-08-09 | 29 | 30.4542 | 8.9782 | 39.4324 | 2.7048 | 0.76558 | 0.29315 | 3.7636 | 9.544% | 10.16% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-08-09 | 30 | 29.9918 | 8.5179 | 38.5097 | 2.5797 | 0.76558 | 0.28629 | 3.6316 | 9.43% | 10.03% | 6.78% | 1.1041 | 1.1115 | 1.0727
2010-08-09 | 31 | 31.5313 | 8.3888 | 39.9201 | 2.7722 | 0.76558 | 0.29677 | 3.8345 | 9.605% | 10.22% | 6.906% | 1.1063 | 1.1138 | 1.0742
2010-08-09 | 32 | 31.7887 | 8.2256 | 40.0142 | 2.7852 | 0.76558 | 0.29747 | 3.8483 | 9.617% | 10.23% | 6.915% | 1.1064 | 1.114 | 1.0743
2010-08-09 | 33 | 31.2593 | 8.5825 | 39.8418 | 2.7613 | 0.76558 | 0.29619 | 3.8231 | 9.596% | 10.21% | 6.899% | 1.1061 | 1.1137 | 1.0741
2010-08-09 | 34 | 31.5331 | 8.7049 | 40.2379 | 2.8165 | 0.76558 | 0.29913 | 3.8812 | 9.646% | 10.26% | 6.935% | 1.1068 | 1.1144 | 1.0745
2010-08-09 | 35 | 33.1281 | 9.5749 | 42.703 | 3.1721 | 0.76558 | 0.31746 | 4.2552 | 9.965% | 10.6% | 7.165% | 1.1107 | 1.1186 | 1.0772
2010-08-09 | 36 | 37.0772 | 11.1312 | 48.2084 | 4.0428 | 0.76558 | 0.35839 | 5.1667 | 10.72% | 11.4% | 7.706% | 1.12 | 1.1287 | 1.0835
2010-08-09 | 37 | 40.5551 | 12.275 | 52.8301 | 4.8551 | 0.76558 | 0.39275 | 6.0134 | 11.38% | 12.11% | 8.184% | 1.1284 | 1.1378 | 1.0891
2010-08-09 | 38 | 40.3258 | 12.3457 | 52.6715 | 4.826 | 0.76558 | 0.39157 | 5.9831 | 11.36% | 12.09% | 8.167% | 1.1282 | 1.1375 | 1.0889
2010-08-09 | 39 | 41.2739 | 12.0038 | 53.2777 | 4.9377 | 0.76558 | 0.39607 | 6.0994 | 11.45% | 12.18% | 8.231% | 1.1293 | 1.1387 | 1.0897
2010-08-09 | 40 | 40.338 | 11.6007 | 51.9387 | 4.6926 | 0.76558 | 0.38612 | 5.8443 | 11.25% | 11.97% | 8.09% | 1.1268 | 1.136 | 1.088
2010-08-09 | 41 | 40.8429 | 11.2845 | 52.1275 | 4.7268 | 0.76558 | 0.38752 | 5.8799 | 11.28% | 12% | 8.11% | 1.1271 | 1.1364 | 1.0883
2010-08-09 | 42 | 40.2808 | 10.8274 | 51.1082 | 4.5438 | 0.76558 | 0.37994 | 5.6893 | 11.13% | 11.84% | 8.004% | 1.1253 | 1.1344 | 1.087
2010-08-09 | 43 | 37.8797 | 10.1993 | 48.079 | 4.0211 | 0.76558 | 0.35743 | 5.1441 | 10.7% | 11.38% | 7.693% | 1.1198 | 1.1285 | 1.0833
2010-08-09 | 44 | 35.8833 | 9.3979 | 45.2811 | 3.5667 | 0.76558 | 0.33663 | 4.6689 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-08-09 | 45 | 32.2884 | 8.5048 | 40.7932 | 2.8948 | 0.76558 | 0.30326 | 3.9636 | 9.716% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-08-09 | 46 | 28.8858 | 7.7096 | 36.5954 | 2.3296 | 0.76558 | 0.27205 | 3.3673 | 9.201% | 9.79% | 6.616% | 1.1013 | 1.1085 | 1.0708
2010-08-09 | 47 | 28.3803 | 8.0056 | 36.3859 | 2.303 | 0.76558 | 0.2705 | 3.3391 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-08-09 | 48 | 27.6907 | 8.4735 | 36.1642 | 2.2751 | 0.76558 | 0.26885 | 3.3095 | 9.151% | 9.737% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-08-10 | 1 | 25.9947 | 7.7665 | 33.7612 | 1.9828 | 0.76558 | 0.25098 | 2.9993 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-08-10 | 2 | 27.6016 | 7.5253 | 35.1269 | 2.1464 | 0.76558 | 0.26114 | 3.1731 | 9.033% | 9.611% | 6.495% | 1.0993 | 1.1063 | 1.0695
2010-08-10 | 3 | 26.4079 | 7.1803 | 33.5882 | 1.9625 | 0.76558 | 0.2497 | 2.9778 | 8.866% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2010-08-10 | 4 | 24.9992 | 6.8974 | 31.8966 | 1.7698 | 0.76558 | 0.23712 | 2.7725 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-08-10 | 5 | 24.4213 | 6.649 | 31.0703 | 1.6793 | 0.76558 | 0.23098 | 2.6758 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-08-10 | 6 | 23.82 | 6.6029 | 30.4229 | 1.61 | 0.76558 | 0.22617 | 2.6018 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-08-10 | 7 | 23.4007 | 6.5233 | 29.924 | 1.5577 | 0.76558 | 0.22246 | 2.5457 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-08-10 | 8 | 23.2716 | 6.4667 | 29.7383 | 1.5384 | 0.76558 | 0.22108 | 2.5251 | 8.491% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-08-10 | 9 | 23.5136 | 6.6083 | 30.1219 | 1.5783 | 0.76558 | 0.22393 | 2.5678 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-08-10 | 10 | 23.6699 | 6.6818 | 30.3517 | 1.6025 | 0.76558 | 0.22564 | 2.5937 | 8.546% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-08-10 | 11 | 24.3001 | 6.8815 | 31.1816 | 1.6913 | 0.76558 | 0.23181 | 2.6887 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-08-10 | 12 | 25.4205 | 7.3314 | 32.7519 | 1.866 | 0.76558 | 0.24348 | 2.875 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-08-10 | 13 | 27.5884 | 8.4886 | 36.077 | 2.2641 | 0.76558 | 0.2682 | 3.2979 | 9.141% | 9.726% | 6.573% | 1.1006 | 1.1077 | 1.0703
2010-08-10 | 14 | 31.222 | 10.1591 | 41.3811 | 2.9788 | 0.76558 | 0.30763 | 4.052 | 9.792% | 10.42% | 7.04% | 1.1085 | 1.1163 | 1.0757
2010-08-10 | 15 | 36.4493 | 12.3266 | 48.7759 | 4.1385 | 0.76558 | 0.36261 | 5.2667 | 10.8% | 11.49% | 7.764% | 1.121 | 1.1298 | 1.0842
2010-08-10 | 16 | 38.7743 | 13.3171 | 52.0914 | 4.7203 | 0.76558 | 0.38725 | 5.8731 | 11.27% | 12% | 8.106% | 1.1271 | 1.1363 | 1.0882
2010-08-10 | 17 | 40.1813 | 14.1315 | 54.3127 | 5.1314 | 0.76558 | 0.40377 | 6.3008 | 11.6% | 12.34% | 8.341% | 1.1312 | 1.1408 | 1.091
2010-08-10 | 18 | 40.4824 | 14.2189 | 54.7012 | 5.2051 | 0.76558 | 0.40666 | 6.3773 | 11.66% | 12.4% | 8.382% | 1.132 | 1.1416 | 1.0915
2010-08-10 | 19 | 40.2927 | 14.1453 | 54.438 | 5.1551 | 0.76558 | 0.4047 | 6.3254 | 11.62% | 12.36% | 8.354% | 1.1315 | 1.1411 | 1.0912
2010-08-10 | 20 | 39.5329 | 13.8046 | 53.3375 | 4.9488 | 0.76558 | 0.39652 | 6.1109 | 11.46% | 12.19% | 8.238% | 1.1294 | 1.1388 | 1.0898
2010-08-10 | 21 | 40.766 | 13.5721 | 54.3381 | 5.1362 | 0.76558 | 0.40396 | 6.3057 | 11.6% | 12.35% | 8.344% | 1.1313 | 1.1409 | 1.091
2010-08-10 | 22 | 40.2621 | 13.3207 | 53.5829 | 4.9944 | 0.76558 | 0.39834 | 6.1584 | 11.49% | 12.23% | 8.264% | 1.1299 | 1.1393 | 1.0901
2010-08-10 | 23 | 38.6823 | 12.7411 | 51.4234 | 4.6 | 0.76558 | 0.38229 | 5.7478 | 11.18% | 11.89% | 8.037% | 1.1258 | 1.135 | 1.0874
2010-08-10 | 24 | 37.071 | 12.5401 | 49.6112 | 4.2815 | 0.76558 | 0.36882 | 5.4159 | 10.92% | 11.62% | 7.849% | 1.1225 | 1.1314 | 1.0852
2010-08-10 | 25 | 34.3695 | 12.2533 | 46.6228 | 3.7812 | 0.76558 | 0.3466 | 4.8934 | 10.5% | 11.17% | 7.546% | 1.1173 | 1.1257 | 1.0816
2010-08-10 | 26 | 32.1001 | 11.7321 | 43.8322 | 3.3421 | 0.76558 | 0.32585 | 4.4335 | 10.11% | 10.76% | 7.273% | 1.1125 | 1.1206 | 1.0784
2010-08-10 | 27 | 31.9855 | 12.061 | 44.0464 | 3.3749 | 0.76558 | 0.32745 | 4.4679 | 10.14% | 10.79% | 7.293% | 1.1129 | 1.121 | 1.0787
2010-08-10 | 28 | 32.4582 | 12.2796 | 44.7378 | 3.4816 | 0.76558 | 0.33259 | 4.5798 | 10.24% | 10.89% | 7.36% | 1.114 | 1.1222 | 1.0795
2010-08-10 | 29 | 32.1999 | 11.9319 | 44.1318 | 3.388 | 0.76558 | 0.32808 | 4.4816 | 10.16% | 10.81% | 7.302% | 1.113 | 1.1211 | 1.0788
2010-08-10 | 30 | 31.3933 | 11.5145 | 42.9079 | 3.2026 | 0.76558 | 0.31898 | 4.2872 | 9.992% | 10.63% | 7.184% | 1.111 | 1.119 | 1.0774
2010-08-10 | 31 | 33.0903 | 11.7842 | 44.8745 | 3.503 | 0.76558 | 0.3336 | 4.6021 | 10.26% | 10.91% | 7.374% | 1.1143 | 1.1225 | 1.0796
2010-08-10 | 32 | 32.7483 | 11.8158 | 44.5641 | 3.4547 | 0.76558 | 0.33129 | 4.5515 | 10.21% | 10.87% | 7.343% | 1.1138 | 1.1219 | 1.0793
2010-08-10 | 33 | 31.8584 | 12.1646 | 44.0229 | 3.3713 | 0.76558 | 0.32727 | 4.4641 | 10.14% | 10.79% | 7.291% | 1.1128 | 1.1209 | 1.0786
2010-08-10 | 34 | 31.9783 | 12.3232 | 44.3014 | 3.4141 | 0.76558 | 0.32934 | 4.509 | 10.18% | 10.83% | 7.318% | 1.1133 | 1.1214 | 1.079
2010-08-10 | 35 | 33.2477 | 12.7015 | 45.9493 | 3.6728 | 0.76558 | 0.34159 | 4.7799 | 10.4% | 11.07% | 7.479% | 1.1161 | 1.1245 | 1.0808
2010-08-10 | 36 | 36.315 | 13.6191 | 49.9342 | 4.3374 | 0.76558 | 0.37122 | 5.4742 | 10.96% | 11.66% | 7.882% | 1.1231 | 1.132 | 1.0856
2010-08-10 | 37 | 39.8698 | 13.9144 | 53.7842 | 5.032 | 0.76558 | 0.39984 | 6.1975 | 11.52% | 12.26% | 8.285% | 1.1302 | 1.1397 | 1.0903
2010-08-10 | 38 | 41.6839 | 13.8295 | 55.5134 | 5.3608 | 0.76558 | 0.41269 | 6.5391 | 11.78% | 12.53% | 8.469% | 1.1335 | 1.1433 | 1.0925
2010-08-10 | 39 | 41.5718 | 13.4357 | 55.0075 | 5.2636 | 0.76558 | 0.40893 | 6.4381 | 11.7% | 12.45% | 8.415% | 1.1326 | 1.1422 | 1.0919
2010-08-10 | 40 | 39.9072 | 12.5072 | 52.4143 | 4.779 | 0.76558 | 0.38965 | 5.9342 | 11.32% | 12.05% | 8.14% | 1.1277 | 1.137 | 1.0886
2010-08-10 | 41 | 40.9293 | 12.3184 | 53.2477 | 4.9322 | 0.76558 | 0.39585 | 6.0936 | 11.44% | 12.18% | 8.228% | 1.1292 | 1.1386 | 1.0897
2010-08-10 | 42 | 40.5142 | 11.6849 | 52.1992 | 4.7398 | 0.76558 | 0.38806 | 5.8935 | 11.29% | 12.01% | 8.118% | 1.1273 | 1.1365 | 1.0883
2010-08-10 | 43 | 38.4165 | 11.0006 | 49.4171 | 4.248 | 0.76558 | 0.36737 | 5.381 | 10.89% | 11.59% | 7.829% | 1.1222 | 1.131 | 1.0849
2010-08-10 | 44 | 35.7703 | 10.2415 | 46.0119 | 3.6828 | 0.76558 | 0.34206 | 4.7904 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-08-10 | 45 | 32.0631 | 9.1582 | 41.2213 | 2.9558 | 0.76558 | 0.30644 | 4.0278 | 9.771% | 10.4% | 7.026% | 1.1083 | 1.116 | 1.0756
2010-08-10 | 46 | 28.5869 | 8.1728 | 36.7597 | 2.3506 | 0.76558 | 0.27328 | 3.3894 | 9.221% | 9.811% | 6.63% | 1.1016 | 1.1088 | 1.071
2010-08-10 | 47 | 28.1419 | 8.3824 | 36.5243 | 2.3206 | 0.76558 | 0.27153 | 3.3577 | 9.193% | 9.781% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-08-10 | 48 | 27.15 | 8.8799 | 36.0299 | 2.2582 | 0.76558 | 0.26785 | 3.2916 | 9.136% | 9.72% | 6.569% | 1.1005 | 1.1077 | 1.0703
2010-08-11 | 1 | 25.3243 | 7.9638 | 33.2881 | 1.9276 | 0.76558 | 0.24747 | 2.9406 | 8.834% | 9.399% | 6.352% | 1.0969 | 1.1037 | 1.0678
2010-08-11 | 2 | 25.8976 | 7.7585 | 33.6562 | 1.9704 | 0.76558 | 0.2502 | 2.9862 | 8.873% | 9.441% | 6.38% | 1.0974 | 1.1042 | 1.0681
2010-08-11 | 3 | 24.7928 | 7.3753 | 32.1681 | 1.8001 | 0.76558 | 0.23914 | 2.8048 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-08-11 | 4 | 23.6144 | 7.0073 | 30.6217 | 1.6311 | 0.76558 | 0.22765 | 2.6244 | 8.57% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2010-08-11 | 5 | 23.0682 | 6.8139 | 29.8821 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-08-11 | 6 | 22.4945 | 6.7117 | 29.2062 | 1.4838 | 0.76558 | 0.21712 | 2.4665 | 8.445% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-08-11 | 7 | 22.5661 | 6.4394 | 29.0056 | 1.4635 | 0.76558 | 0.21563 | 2.4447 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-08-11 | 8 | 22.435 | 6.2865 | 28.7215 | 1.435 | 0.76558 | 0.21352 | 2.4141 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-08-11 | 9 | 22.4217 | 6.4498 | 28.8715 | 1.45 | 0.76558 | 0.21463 | 2.4302 | 8.417% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-08-11 | 10 | 22.5505 | 6.6164 | 29.1668 | 1.4798 | 0.76558 | 0.21683 | 2.4622 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-08-11 | 11 | 22.879 | 6.7074 | 29.5864 | 1.5227 | 0.76558 | 0.21995 | 2.5082 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-08-11 | 12 | 23.4095 | 7.0696 | 30.4791 | 1.616 | 0.76558 | 0.22659 | 2.6082 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-08-11 | 13 | 25.5641 | 8.055 | 33.6191 | 1.9661 | 0.76558 | 0.24993 | 2.9816 | 8.869% | 9.436% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-08-11 | 14 | 29.185 | 9.7802 | 38.9652 | 2.6411 | 0.76558 | 0.28967 | 3.6964 | 9.486% | 10.09% | 6.821% | 1.1048 | 1.1123 | 1.0732
2010-08-11 | 15 | 34.1564 | 11.7171 | 45.8734 | 3.6606 | 0.76558 | 0.34103 | 4.7672 | 10.39% | 11.06% | 7.472% | 1.116 | 1.1243 | 1.0808
2010-08-11 | 16 | 36.4557 | 12.7724 | 49.2281 | 4.2156 | 0.76558 | 0.36597 | 5.3472 | 10.86% | 11.56% | 7.81% | 1.1219 | 1.1307 | 1.0847
2010-08-11 | 17 | 37.9415 | 13.426 | 51.3675 | 4.59 | 0.76558 | 0.38187 | 5.7374 | 11.17% | 11.88% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-08-11 | 18 | 38.6848 | 13.2724 | 51.9572 | 4.696 | 0.76558 | 0.38626 | 5.8478 | 11.26% | 11.98% | 8.092% | 1.1268 | 1.136 | 1.088
2010-08-11 | 19 | 38.9761 | 12.8956 | 51.8717 | 4.6805 | 0.76558 | 0.38562 | 5.8317 | 11.24% | 11.96% | 8.083% | 1.1267 | 1.1359 | 1.0879
2010-08-11 | 20 | 38.2935 | 12.4784 | 50.7719 | 4.4842 | 0.76558 | 0.37744 | 5.6272 | 11.08% | 11.79% | 7.969% | 1.1246 | 1.1337 | 1.0866
2010-08-11 | 21 | 39.3312 | 12.0893 | 51.4205 | 4.5995 | 0.76558 | 0.38227 | 5.7473 | 11.18% | 11.89% | 8.036% | 1.1258 | 1.135 | 1.0874
2010-08-11 | 22 | 38.5288 | 11.3956 | 49.9244 | 4.3357 | 0.76558 | 0.37114 | 5.4724 | 10.96% | 11.66% | 7.881% | 1.1231 | 1.132 | 1.0856
2010-08-11 | 23 | 36.1991 | 10.7686 | 46.9677 | 3.8374 | 0.76558 | 0.34916 | 4.9521 | 10.54% | 11.22% | 7.581% | 1.1179 | 1.1264 | 1.082
2010-08-11 | 24 | 34.5067 | 10.4843 | 44.9909 | 3.5212 | 0.76558 | 0.33447 | 4.6212 | 10.27% | 10.93% | 7.385% | 1.1145 | 1.1227 | 1.0797
2010-08-11 | 25 | 32.6555 | 10.0999 | 42.7554 | 3.1799 | 0.76558 | 0.31785 | 4.2634 | 9.971% | 10.61% | 7.17% | 1.1108 | 1.1187 | 1.0772
2010-08-11 | 26 | 31.1765 | 9.5763 | 40.7528 | 2.889 | 0.76558 | 0.30296 | 3.9576 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2010-08-11 | 27 | 31.2233 | 9.9912 | 41.2145 | 2.9548 | 0.76558 | 0.30639 | 4.0268 | 9.77% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2010-08-11 | 28 | 30.9693 | 10.0486 | 41.0179 | 2.9267 | 0.76558 | 0.30493 | 3.9972 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-08-11 | 29 | 30.5259 | 9.4742 | 40.0001 | 2.7833 | 0.76558 | 0.29737 | 3.8462 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-08-11 | 30 | 30.1293 | 9.086 | 39.2154 | 2.6751 | 0.76558 | 0.29153 | 3.7323 | 9.517% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-08-11 | 31 | 31.7003 | 9.0027 | 40.703 | 2.882 | 0.76558 | 0.30259 | 3.9501 | 9.705% | 10.33% | 6.978% | 1.1075 | 1.1151 | 1.075
2010-08-11 | 32 | 31.6095 | 8.8318 | 40.4413 | 2.845 | 0.76558 | 0.30065 | 3.9112 | 9.671% | 10.29% | 6.954% | 1.1071 | 1.1147 | 1.0747
2010-08-11 | 33 | 31.2295 | 8.9756 | 40.2051 | 2.8119 | 0.76558 | 0.29889 | 3.8763 | 9.641% | 10.26% | 6.932% | 1.1067 | 1.1143 | 1.0745
2010-08-11 | 34 | 31.7265 | 9.0043 | 40.7308 | 2.8859 | 0.76558 | 0.3028 | 3.9543 | 9.708% | 10.33% | 6.98% | 1.1075 | 1.1152 | 1.075
2010-08-11 | 35 | 32.7496 | 9.5337 | 42.2834 | 3.1101 | 0.76558 | 0.31434 | 4.19 | 9.909% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-08-11 | 36 | 35.5231 | 10.9706 | 46.4937 | 3.7603 | 0.76558 | 0.34564 | 4.8715 | 10.48% | 11.15% | 7.534% | 1.117 | 1.1255 | 1.0815
2010-08-11 | 37 | 39.1295 | 12.3888 | 51.5183 | 4.617 | 0.76558 | 0.38299 | 5.7656 | 11.19% | 11.91% | 8.047% | 1.126 | 1.1352 | 1.0875
2010-08-11 | 38 | 40.1899 | 12.4116 | 52.6015 | 4.8132 | 0.76558 | 0.39105 | 5.9698 | 11.35% | 12.08% | 8.16% | 1.128 | 1.1373 | 1.0889
2010-08-11 | 39 | 39.3201 | 12.1134 | 51.4335 | 4.6018 | 0.76558 | 0.38236 | 5.7497 | 11.18% | 11.89% | 8.038% | 1.1259 | 1.135 | 1.0874
2010-08-11 | 40 | 38.4361 | 11.5245 | 49.9605 | 4.342 | 0.76558 | 0.37141 | 5.479 | 10.97% | 11.67% | 7.885% | 1.1232 | 1.1321 | 1.0856
2010-08-11 | 41 | 38.8851 | 11.0872 | 49.9723 | 4.344 | 0.76558 | 0.3715 | 5.4811 | 10.97% | 11.67% | 7.886% | 1.1232 | 1.1321 | 1.0856
2010-08-11 | 42 | 38.4615 | 10.6659 | 49.1274 | 4.1984 | 0.76558 | 0.36522 | 5.3292 | 10.85% | 11.54% | 7.799% | 1.1217 | 1.1305 | 1.0846
2010-08-11 | 43 | 36.4964 | 9.9749 | 46.4713 | 3.7567 | 0.76558 | 0.34547 | 4.8677 | 10.47% | 11.15% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-08-11 | 44 | 34.4505 | 9.3433 | 43.7937 | 3.3363 | 0.76558 | 0.32557 | 4.4274 | 10.11% | 10.76% | 7.269% | 1.1125 | 1.1205 | 1.0784
2010-08-11 | 45 | 31.0196 | 8.3612 | 39.3808 | 2.6978 | 0.76558 | 0.29276 | 3.7561 | 9.538% | 10.15% | 6.858% | 1.1054 | 1.1129 | 1.0736
2010-08-11 | 46 | 27.8218 | 7.5505 | 35.3723 | 2.1765 | 0.76558 | 0.26296 | 3.2051 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-08-11 | 47 | 27.1228 | 7.7641 | 34.8869 | 2.1172 | 0.76558 | 0.25935 | 3.1421 | 9.007% | 9.583% | 6.476% | 1.099 | 1.106 | 1.0692
2010-08-11 | 48 | 25.7906 | 8.1023 | 33.8928 | 1.9983 | 0.76558 | 0.25196 | 3.0158 | 8.898% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0683
2010-08-12 | 1 | 23.9968 | 7.3591 | 31.3559 | 1.7103 | 0.76558 | 0.2331 | 2.709 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-08-12 | 2 | 24.9644 | 7.1184 | 32.0828 | 1.7905 | 0.76558 | 0.23851 | 2.7946 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1021 | 1.0668
2010-08-12 | 3 | 23.8131 | 6.6277 | 30.4408 | 1.6119 | 0.76558 | 0.2263 | 2.6038 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-08-12 | 4 | 22.7648 | 6.3951 | 29.1599 | 1.4791 | 0.76558 | 0.21678 | 2.4615 | 8.441% | 8.982% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-08-12 | 5 | 22.116 | 6.1683 | 28.2843 | 1.3916 | 0.76558 | 0.21027 | 2.3675 | 8.37% | 8.906% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-08-12 | 6 | 21.4516 | 5.9952 | 27.4468 | 1.3104 | 0.76558 | 0.20404 | 2.2801 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-08-12 | 7 | 21.2641 | 5.9244 | 27.1885 | 1.2859 | 0.76558 | 0.20212 | 2.2536 | 8.289% | 8.819% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-08-12 | 8 | 20.7087 | 5.8881 | 26.5967 | 1.2305 | 0.76558 | 0.19772 | 2.1938 | 8.248% | 8.776% | 5.931% | 1.0899 | 1.0962 | 1.063
2010-08-12 | 9 | 20.9112 | 6.0144 | 26.9256 | 1.2611 | 0.76558 | 0.20017 | 2.2269 | 8.271% | 8.8% | 5.947% | 1.0902 | 1.0965 | 1.0632
2010-08-12 | 10 | 21.1794 | 6.2202 | 27.3996 | 1.3059 | 0.76558 | 0.20369 | 2.2752 | 8.304% | 8.835% | 5.97% | 1.0906 | 1.0969 | 1.0635
2010-08-12 | 11 | 21.9677 | 6.2789 | 28.2466 | 1.3879 | 0.76558 | 0.20999 | 2.3635 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-08-12 | 12 | 22.9011 | 6.6105 | 29.5117 | 1.515 | 0.76558 | 0.21939 | 2.5 | 8.471% | 9.013% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-08-12 | 13 | 24.9786 | 7.6285 | 32.6071 | 1.8495 | 0.76558 | 0.24241 | 2.8575 | 8.763% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-08-12 | 14 | 28.5082 | 9.0321 | 37.5403 | 2.4515 | 0.76558 | 0.27908 | 3.4961 | 9.313% | 9.909% | 6.696% | 1.1027 | 1.11 | 1.0718
2010-08-12 | 15 | 33.2597 | 11.1238 | 44.3834 | 3.4267 | 0.76558 | 0.32995 | 4.5222 | 10.19% | 10.84% | 7.326% | 1.1134 | 1.1216 | 1.0791
2010-08-12 | 16 | 35.7246 | 12.3465 | 48.0711 | 4.0198 | 0.76558 | 0.35737 | 5.1427 | 10.7% | 11.38% | 7.692% | 1.1198 | 1.1284 | 1.0833
2010-08-12 | 17 | 37.9395 | 13.2543 | 51.1938 | 4.559 | 0.76558 | 0.38058 | 5.7052 | 11.14% | 11.86% | 8.013% | 1.1254 | 1.1345 | 1.0871
2010-08-12 | 18 | 38.9373 | 13.5628 | 52.5001 | 4.7946 | 0.76558 | 0.39029 | 5.9505 | 11.33% | 12.06% | 8.149% | 1.1278 | 1.1371 | 1.0887
2010-08-12 | 19 | 39.5505 | 13.5571 | 53.1076 | 4.9062 | 0.76558 | 0.39481 | 6.0666 | 11.42% | 12.15% | 8.213% | 1.129 | 1.1384 | 1.0895
2010-08-12 | 20 | 39.3549 | 13.2418 | 52.5967 | 4.8123 | 0.76558 | 0.39101 | 5.9689 | 11.35% | 12.07% | 8.159% | 1.128 | 1.1373 | 1.0888
2010-08-12 | 21 | 41.6224 | 13.0669 | 54.6893 | 5.2028 | 0.76558 | 0.40657 | 6.375 | 11.66% | 12.4% | 8.381% | 1.1319 | 1.1416 | 1.0915
2010-08-12 | 22 | 42.1035 | 12.7738 | 54.8773 | 5.2387 | 0.76558 | 0.40796 | 6.4122 | 11.68% | 12.43% | 8.401% | 1.1323 | 1.142 | 1.0917
2010-08-12 | 23 | 41.0419 | 12.3942 | 53.4361 | 4.9671 | 0.76558 | 0.39725 | 6.1299 | 11.47% | 12.21% | 8.248% | 1.1296 | 1.139 | 1.0899
2010-08-12 | 24 | 40.2934 | 11.9783 | 52.2717 | 4.753 | 0.76558 | 0.38859 | 5.9072 | 11.3% | 12.02% | 8.125% | 1.1274 | 1.1367 | 1.0884
2010-08-12 | 25 | 38.919 | 11.7073 | 50.6262 | 4.4585 | 0.76558 | 0.37636 | 5.6004 | 11.06% | 11.77% | 7.954% | 1.1244 | 1.1334 | 1.0864
2010-08-12 | 26 | 37.4131 | 11.0347 | 48.4478 | 4.083 | 0.76558 | 0.36017 | 5.2088 | 10.75% | 11.44% | 7.73% | 1.1205 | 1.1292 | 1.0838
2010-08-12 | 27 | 37.8169 | 11.5888 | 49.4057 | 4.2461 | 0.76558 | 0.36729 | 5.3789 | 10.89% | 11.58% | 7.828% | 1.1222 | 1.131 | 1.0849
2010-08-12 | 28 | 38.1349 | 11.5569 | 49.6918 | 4.2954 | 0.76558 | 0.36941 | 5.4304 | 10.93% | 11.63% | 7.857% | 1.1227 | 1.1316 | 1.0853
2010-08-12 | 29 | 38.32 | 11.0647 | 49.3848 | 4.2425 | 0.76558 | 0.36713 | 5.3752 | 10.88% | 11.58% | 7.826% | 1.1221 | 1.131 | 1.0849
2010-08-12 | 30 | 37.9361 | 10.6653 | 48.6014 | 4.109 | 0.76558 | 0.36131 | 5.2359 | 10.77% | 11.46% | 7.746% | 1.1207 | 1.1295 | 1.084
2010-08-12 | 31 | 40.13 | 10.9257 | 51.0556 | 4.5344 | 0.76558 | 0.37955 | 5.6796 | 11.12% | 11.84% | 7.998% | 1.1252 | 1.1343 | 1.0869
2010-08-12 | 32 | 40.5549 | 11.0495 | 51.6043 | 4.6324 | 0.76558 | 0.38363 | 5.7816 | 11.2% | 11.92% | 8.055% | 1.1262 | 1.1353 | 1.0876
2010-08-12 | 33 | 40.2506 | 11.1989 | 51.4495 | 4.6047 | 0.76558 | 0.38248 | 5.7527 | 11.18% | 11.9% | 8.039% | 1.1259 | 1.135 | 1.0874
2010-08-12 | 34 | 40.3316 | 11.3405 | 51.6722 | 4.6446 | 0.76558 | 0.38414 | 5.7943 | 11.21% | 11.93% | 8.063% | 1.1263 | 1.1355 | 1.0877
2010-08-12 | 35 | 40.6805 | 12.2037 | 52.8842 | 4.865 | 0.76558 | 0.39315 | 6.0238 | 11.39% | 12.12% | 8.19% | 1.1285 | 1.1379 | 1.0892
2010-08-12 | 36 | 42.3759 | 13.0523 | 55.4283 | 5.3444 | 0.76558 | 0.41206 | 6.522 | 11.77% | 12.52% | 8.46% | 1.1334 | 1.1431 | 1.0924
2010-08-12 | 37 | 44.5759 | 13.658 | 58.2339 | 5.8991 | 0.76558 | 0.43292 | 7.0976 | 12.19% | 12.97% | 8.763% | 1.1388 | 1.149 | 1.096
2010-08-12 | 38 | 43.6415 | 12.7088 | 56.3503 | 5.5237 | 0.76558 | 0.41892 | 6.7082 | 11.9% | 12.67% | 8.559% | 1.1351 | 1.145 | 1.0936
2010-08-12 | 39 | 45.6084 | 12.9689 | 58.5773 | 5.9689 | 0.76558 | 0.43547 | 7.1699 | 12.24% | 13.02% | 8.801% | 1.1395 | 1.1497 | 1.0965
2010-08-12 | 40 | 44.3889 | 12.3631 | 56.752 | 5.6027 | 0.76558 | 0.4219 | 6.7902 | 11.96% | 12.73% | 8.603% | 1.1359 | 1.1459 | 1.0941
2010-08-12 | 41 | 44.528 | 11.9612 | 56.4892 | 5.5509 | 0.76558 | 0.41995 | 6.7365 | 11.93% | 12.69% | 8.574% | 1.1354 | 1.1453 | 1.0938
2010-08-12 | 42 | 44.025 | 11.4286 | 55.4536 | 5.3493 | 0.76558 | 0.41225 | 6.5271 | 11.77% | 12.52% | 8.463% | 1.1334 | 1.1432 | 1.0925
2010-08-12 | 43 | 41.8695 | 10.8217 | 52.6912 | 4.8296 | 0.76558 | 0.39171 | 5.9869 | 11.36% | 12.09% | 8.169% | 1.1282 | 1.1375 | 1.089
2010-08-12 | 44 | 39.7159 | 10.1725 | 49.8884 | 4.3295 | 0.76558 | 0.37088 | 5.4659 | 10.96% | 11.66% | 7.878% | 1.123 | 1.132 | 1.0855
2010-08-12 | 45 | 34.8899 | 9.1497 | 44.0397 | 3.3738 | 0.76558 | 0.3274 | 4.4668 | 10.14% | 10.79% | 7.293% | 1.1129 | 1.121 | 1.0787
2010-08-12 | 46 | 31.0378 | 8.219 | 39.2568 | 2.6808 | 0.76558 | 0.29184 | 3.7382 | 9.522% | 10.13% | 6.847% | 1.1052 | 1.1127 | 1.0735
2010-08-12 | 47 | 30.1027 | 8.4136 | 38.5163 | 2.5806 | 0.76558 | 0.28634 | 3.6325 | 9.431% | 10.03% | 6.781% | 1.1041 | 1.1115 | 1.0727
2010-08-12 | 48 | 29.4719 | 8.8899 | 38.3619 | 2.56 | 0.76558 | 0.28519 | 3.6107 | 9.412% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-08-13 | 1 | 27.5529 | 8.3004 | 35.8534 | 2.2361 | 0.76558 | 0.26654 | 3.2682 | 9.116% | 9.699% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-08-13 | 2 | 28.8489 | 7.9487 | 36.7976 | 2.3554 | 0.76558 | 0.27356 | 3.3946 | 9.225% | 9.815% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-08-13 | 3 | 27.4809 | 7.5773 | 35.0582 | 2.138 | 0.76558 | 0.26063 | 3.1642 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-08-13 | 4 | 26.2042 | 7.0877 | 33.2919 | 1.928 | 0.76558 | 0.2475 | 2.9411 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1037 | 1.0678
2010-08-13 | 5 | 25.1026 | 6.842 | 31.9446 | 1.7751 | 0.76558 | 0.23748 | 2.7782 | 8.697% | 9.253% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-08-13 | 6 | 24.7186 | 6.702 | 31.4206 | 1.7174 | 0.76558 | 0.23358 | 2.7165 | 8.646% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-08-13 | 7 | 24.1546 | 6.601 | 30.7556 | 1.6454 | 0.76558 | 0.22864 | 2.6397 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-08-13 | 8 | 24.0133 | 6.643 | 30.6563 | 1.6348 | 0.76558 | 0.2279 | 2.6283 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-08-13 | 9 | 24.3993 | 6.7147 | 31.1139 | 1.684 | 0.76558 | 0.2313 | 2.6809 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-08-13 | 10 | 24.4863 | 6.784 | 31.2703 | 1.701 | 0.76558 | 0.23247 | 2.699 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-08-13 | 11 | 25.1172 | 6.9076 | 32.0249 | 1.7841 | 0.76558 | 0.23808 | 2.7877 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2010-08-13 | 12 | 26.0061 | 7.3192 | 33.3254 | 1.9319 | 0.76558 | 0.24774 | 2.9452 | 8.838% | 9.403% | 6.354% | 1.0969 | 1.1038 | 1.0679
2010-08-13 | 13 | 28.1435 | 8.2722 | 36.4157 | 2.3068 | 0.76558 | 0.27072 | 3.3431 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-08-13 | 14 | 31.3925 | 9.8229 | 41.2153 | 2.955 | 0.76558 | 0.3064 | 4.0269 | 9.77% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2010-08-13 | 15 | 36.3049 | 11.7832 | 48.0881 | 4.0226 | 0.76558 | 0.35749 | 5.1457 | 10.7% | 11.39% | 7.694% | 1.1198 | 1.1285 | 1.0833
2010-08-13 | 16 | 38.962 | 12.7325 | 51.6945 | 4.6486 | 0.76558 | 0.3843 | 5.7985 | 11.22% | 11.93% | 8.065% | 1.1263 | 1.1355 | 1.0877
2010-08-13 | 17 | 40.7722 | 13.1522 | 53.9243 | 5.0583 | 0.76558 | 0.40088 | 6.2248 | 11.54% | 12.28% | 8.3% | 1.1305 | 1.14 | 1.0905
2010-08-13 | 18 | 40.8442 | 13.0958 | 53.9399 | 5.0612 | 0.76558 | 0.401 | 6.2278 | 11.55% | 12.28% | 8.301% | 1.1305 | 1.1401 | 1.0905
2010-08-13 | 19 | 40.684 | 12.8687 | 53.5527 | 4.9888 | 0.76558 | 0.39812 | 6.1525 | 11.49% | 12.22% | 8.26% | 1.1298 | 1.1393 | 1.09
2010-08-13 | 20 | 40.2391 | 12.4715 | 52.7106 | 4.8332 | 0.76558 | 0.39186 | 5.9906 | 11.37% | 12.09% | 8.171% | 1.1282 | 1.1376 | 1.089
2010-08-13 | 21 | 41.2012 | 12.1023 | 53.3035 | 4.9425 | 0.76558 | 0.39626 | 6.1043 | 11.45% | 12.18% | 8.234% | 1.1293 | 1.1388 | 1.0897
2010-08-13 | 22 | 40.2259 | 11.7645 | 51.9904 | 4.702 | 0.76558 | 0.3865 | 5.8541 | 11.26% | 11.98% | 8.096% | 1.1269 | 1.1361 | 1.0881
2010-08-13 | 23 | 38.4577 | 11.0923 | 49.55 | 4.2709 | 0.76558 | 0.36836 | 5.4049 | 10.91% | 11.61% | 7.843% | 1.1224 | 1.1313 | 1.0851
2010-08-13 | 24 | 37.0806 | 10.7426 | 47.8232 | 3.9784 | 0.76558 | 0.35552 | 5.0995 | 10.66% | 11.35% | 7.667% | 1.1194 | 1.128 | 1.083
2010-08-13 | 25 | 34.9976 | 10.3661 | 45.3638 | 3.5798 | 0.76558 | 0.33724 | 4.6826 | 10.32% | 10.98% | 7.422% | 1.1151 | 1.1234 | 1.0802
2010-08-13 | 26 | 33.5601 | 9.8004 | 43.3604 | 3.2706 | 0.76558 | 0.32235 | 4.3585 | 10.05% | 10.7% | 7.227% | 1.1118 | 1.1198 | 1.0779
2010-08-13 | 27 | 33.7757 | 10.2114 | 43.9871 | 3.3658 | 0.76558 | 0.32701 | 4.4584 | 10.14% | 10.78% | 7.288% | 1.1128 | 1.1209 | 1.0786
2010-08-13 | 28 | 34.1206 | 10.4111 | 44.5317 | 3.4496 | 0.76558 | 0.33105 | 4.5463 | 10.21% | 10.86% | 7.34% | 1.1137 | 1.1219 | 1.0792
2010-08-13 | 29 | 33.6598 | 9.9132 | 43.573 | 3.3027 | 0.76558 | 0.32393 | 4.3922 | 10.08% | 10.73% | 7.248% | 1.1121 | 1.1201 | 1.0781
2010-08-13 | 30 | 33.4132 | 9.547 | 42.9602 | 3.2105 | 0.76558 | 0.31937 | 4.2954 | 9.999% | 10.64% | 7.189% | 1.1111 | 1.119 | 1.0775
2010-08-13 | 31 | 34.8516 | 9.4835 | 44.3351 | 3.4192 | 0.76558 | 0.32959 | 4.5144 | 10.18% | 10.83% | 7.321% | 1.1134 | 1.1215 | 1.079
2010-08-13 | 32 | 35.0375 | 9.4855 | 44.523 | 3.4483 | 0.76558 | 0.33099 | 4.5449 | 10.21% | 10.86% | 7.339% | 1.1137 | 1.1218 | 1.0792
2010-08-13 | 33 | 34.6797 | 9.9357 | 44.6154 | 3.4626 | 0.76558 | 0.33168 | 4.5599 | 10.22% | 10.87% | 7.348% | 1.1138 | 1.122 | 1.0793
2010-08-13 | 34 | 35.3264 | 10.3601 | 45.6865 | 3.6309 | 0.76558 | 0.33964 | 4.7361 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-08-13 | 35 | 36.3463 | 11.2054 | 47.5517 | 3.9334 | 0.76558 | 0.3535 | 5.0525 | 10.63% | 11.31% | 7.64% | 1.1189 | 1.1275 | 1.0827
2010-08-13 | 36 | 39.5879 | 12.4731 | 52.061 | 4.7148 | 0.76558 | 0.38703 | 5.8674 | 11.27% | 11.99% | 8.103% | 1.127 | 1.1363 | 1.0882
2010-08-13 | 37 | 42.6766 | 13.0601 | 55.7367 | 5.404 | 0.76558 | 0.41435 | 6.584 | 11.81% | 12.57% | 8.493% | 1.1339 | 1.1438 | 1.0928
2010-08-13 | 38 | 43.6242 | 13.005 | 56.6292 | 5.5785 | 0.76558 | 0.42099 | 6.7651 | 11.95% | 12.71% | 8.589% | 1.1357 | 1.1456 | 1.094
2010-08-13 | 39 | 42.8344 | 12.5179 | 55.3523 | 5.3297 | 0.76558 | 0.4115 | 6.5068 | 11.76% | 12.51% | 8.452% | 1.1332 | 1.143 | 1.0923
2010-08-13 | 40 | 41.6439 | 12.047 | 53.6909 | 5.0146 | 0.76558 | 0.39914 | 6.1793 | 11.51% | 12.25% | 8.275% | 1.1301 | 1.1395 | 1.0902
2010-08-13 | 41 | 42.0176 | 11.6586 | 53.6762 | 5.0119 | 0.76558 | 0.39904 | 6.1765 | 11.51% | 12.24% | 8.273% | 1.13 | 1.1395 | 1.0902
2010-08-13 | 42 | 41.4134 | 11.296 | 52.7094 | 4.8329 | 0.76558 | 0.39185 | 5.9904 | 11.36% | 12.09% | 8.171% | 1.1282 | 1.1376 | 1.089
2010-08-13 | 43 | 39.1733 | 10.5303 | 49.7036 | 4.2974 | 0.76558 | 0.3695 | 5.4325 | 10.93% | 11.63% | 7.859% | 1.1227 | 1.1316 | 1.0853
2010-08-13 | 44 | 37.1329 | 9.8131 | 46.946 | 3.8338 | 0.76558 | 0.349 | 4.9484 | 10.54% | 11.22% | 7.579% | 1.1178 | 1.1263 | 1.082
2010-08-13 | 45 | 33.2972 | 8.8644 | 42.1616 | 3.0922 | 0.76558 | 0.31343 | 4.1712 | 9.893% | 10.53% | 7.113% | 1.1098 | 1.1177 | 1.0766
2010-08-13 | 46 | 29.6189 | 7.7463 | 37.3653 | 2.4287 | 0.76558 | 0.27778 | 3.472 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-08-13 | 47 | 29.1748 | 8.0716 | 37.2464 | 2.4133 | 0.76558 | 0.27689 | 3.4557 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-08-13 | 48 | 28.2259 | 8.6191 | 36.845 | 2.3615 | 0.76558 | 0.27391 | 3.401 | 9.231% | 9.821% | 6.637% | 1.1017 | 1.1089 | 1.0711
2010-08-14 | 1 | 26.1698 | 7.768 | 33.9377 | 2.0036 | 0.76558 | 0.2523 | 3.0214 | 8.903% | 9.473% | 6.401% | 1.0977 | 1.1046 | 1.0684
2010-08-14 | 2 | 27.2764 | 7.3447 | 34.621 | 2.085 | 0.76558 | 0.25738 | 3.108 | 8.977% | 9.552% | 6.455% | 1.0986 | 1.1056 | 1.069
2010-08-14 | 3 | 25.8947 | 6.9064 | 32.801 | 1.8716 | 0.76558 | 0.24385 | 2.881 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-08-14 | 4 | 24.8032 | 6.6461 | 31.4494 | 1.7205 | 0.76558 | 0.2338 | 2.7199 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-08-14 | 5 | 24.3305 | 6.4045 | 30.735 | 1.6432 | 0.76558 | 0.22849 | 2.6373 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-08-14 | 6 | 23.9727 | 6.2621 | 30.2349 | 1.5902 | 0.76558 | 0.22477 | 2.5805 | 8.535% | 9.081% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-08-14 | 7 | 23.9007 | 6.1442 | 30.0449 | 1.5703 | 0.76558 | 0.22336 | 2.5592 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-08-14 | 8 | 23.5707 | 6.1443 | 29.715 | 1.536 | 0.76558 | 0.2209 | 2.5225 | 8.489% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-08-14 | 9 | 23.8573 | 6.2675 | 30.1247 | 1.5786 | 0.76558 | 0.22395 | 2.5682 | 8.525% | 9.071% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-08-14 | 10 | 23.9007 | 6.3517 | 30.2524 | 1.592 | 0.76558 | 0.2249 | 2.5825 | 8.537% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-08-14 | 11 | 24.3886 | 6.604 | 30.9927 | 1.6709 | 0.76558 | 0.2304 | 2.6669 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.0659
2010-08-14 | 12 | 25.452 | 6.9214 | 32.3734 | 1.8231 | 0.76558 | 0.24067 | 2.8293 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2010-08-14 | 13 | 27.8495 | 7.8102 | 35.6596 | 2.212 | 0.76558 | 0.2651 | 3.2427 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.07
2010-08-14 | 14 | 31.513 | 9.5044 | 41.0174 | 2.9267 | 0.76558 | 0.30493 | 3.9972 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-08-14 | 15 | 36.6984 | 11.6778 | 48.3763 | 4.071 | 0.76558 | 0.35964 | 5.1962 | 10.74% | 11.43% | 7.723% | 1.1203 | 1.129 | 1.0837
2010-08-14 | 16 | 38.8691 | 12.5945 | 51.4636 | 4.6072 | 0.76558 | 0.38259 | 5.7553 | 11.18% | 11.9% | 8.041% | 1.1259 | 1.1351 | 1.0874
2010-08-14 | 17 | 40.1332 | 12.875 | 53.0082 | 4.8879 | 0.76558 | 0.39407 | 6.0475 | 11.41% | 12.14% | 8.203% | 1.1288 | 1.1382 | 1.0894
2010-08-14 | 18 | 40.2757 | 12.8515 | 53.1271 | 4.9098 | 0.76558 | 0.39495 | 6.0704 | 11.43% | 12.16% | 8.215% | 1.129 | 1.1384 | 1.0895
2010-08-14 | 19 | 39.6416 | 12.6559 | 52.2975 | 4.7577 | 0.76558 | 0.38879 | 5.9121 | 11.3% | 12.03% | 8.128% | 1.1275 | 1.1367 | 1.0885
2010-08-14 | 20 | 38.2348 | 11.7779 | 50.0127 | 4.3511 | 0.76558 | 0.3718 | 5.4884 | 10.97% | 11.68% | 7.89% | 1.1233 | 1.1322 | 1.0857
2010-08-14 | 21 | 38.8086 | 11.1229 | 49.9315 | 4.3369 | 0.76558 | 0.3712 | 5.4737 | 10.96% | 11.66% | 7.882% | 1.1231 | 1.132 | 1.0856
2010-08-14 | 22 | 37.4008 | 10.7535 | 48.1543 | 4.0337 | 0.76558 | 0.35798 | 5.1573 | 10.71% | 11.4% | 7.7% | 1.1199 | 1.1286 | 1.0834
2010-08-14 | 23 | 35.1744 | 10.0794 | 45.2538 | 3.5624 | 0.76558 | 0.33642 | 4.6644 | 10.31% | 10.97% | 7.411% | 1.1149 | 1.1232 | 1.08
2010-08-14 | 24 | 34.0551 | 9.6704 | 43.7255 | 3.3259 | 0.76558 | 0.32506 | 4.4165 | 10.1% | 10.75% | 7.262% | 1.1124 | 1.1204 | 1.0783
2010-08-14 | 25 | 32.1279 | 9.359 | 41.4869 | 2.994 | 0.76558 | 0.30842 | 4.068 | 9.806% | 10.43% | 7.05% | 1.1087 | 1.1165 | 1.0758
2010-08-14 | 26 | 30.4764 | 8.9016 | 39.378 | 2.6974 | 0.76558 | 0.29274 | 3.7557 | 9.538% | 10.15% | 6.858% | 1.1054 | 1.1129 | 1.0736
2010-08-14 | 27 | 30.8952 | 9.0803 | 39.9755 | 2.7799 | 0.76558 | 0.29718 | 3.8426 | 9.612% | 10.23% | 6.911% | 1.1063 | 1.1139 | 1.0742
2010-08-14 | 28 | 31.0235 | 9.2464 | 40.2699 | 2.821 | 0.76558 | 0.29937 | 3.8859 | 9.65% | 10.27% | 6.938% | 1.1068 | 1.1144 | 1.0746
2010-08-14 | 29 | 30.837 | 8.7863 | 39.6233 | 2.7311 | 0.76558 | 0.29456 | 3.7912 | 9.568% | 10.18% | 6.88% | 1.1058 | 1.1133 | 1.0739
2010-08-14 | 30 | 30.7218 | 8.5524 | 39.2742 | 2.6832 | 0.76558 | 0.29197 | 3.7407 | 9.525% | 10.13% | 6.848% | 1.1053 | 1.1128 | 1.0735
2010-08-14 | 31 | 32.9061 | 8.5365 | 41.4426 | 2.9876 | 0.76558 | 0.30809 | 4.0613 | 9.8% | 10.43% | 7.046% | 1.1086 | 1.1164 | 1.0758
2010-08-14 | 32 | 33.4243 | 8.4829 | 41.9072 | 3.055 | 0.76558 | 0.31154 | 4.1321 | 9.86% | 10.49% | 7.089% | 1.1094 | 1.1172 | 1.0763
2010-08-14 | 33 | 33.4799 | 8.7832 | 42.2631 | 3.1071 | 0.76558 | 0.31419 | 4.1869 | 9.907% | 10.54% | 7.123% | 1.11 | 1.1178 | 1.0767
2010-08-14 | 34 | 34.026 | 8.7234 | 42.7494 | 3.179 | 0.76558 | 0.3178 | 4.2624 | 9.971% | 10.61% | 7.169% | 1.1107 | 1.1187 | 1.0772
2010-08-14 | 35 | 34.5856 | 9.1289 | 43.7145 | 3.3242 | 0.76558 | 0.32498 | 4.4147 | 10.1% | 10.75% | 7.261% | 1.1123 | 1.1204 | 1.0783
2010-08-14 | 36 | 36.7554 | 10.1242 | 46.8796 | 3.823 | 0.76558 | 0.34851 | 4.9371 | 10.53% | 11.21% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-08-14 | 37 | 39.7719 | 11.1979 | 50.9698 | 4.5192 | 0.76558 | 0.37892 | 5.6637 | 11.11% | 11.82% | 7.989% | 1.125 | 1.1341 | 1.0868
2010-08-14 | 38 | 41.1663 | 11.2997 | 52.466 | 4.7884 | 0.76558 | 0.39004 | 5.944 | 11.33% | 12.05% | 8.146% | 1.1278 | 1.1371 | 1.0887
2010-08-14 | 39 | 40.8506 | 11.1488 | 51.9994 | 4.7036 | 0.76558 | 0.38657 | 5.8558 | 11.26% | 11.98% | 8.097% | 1.1269 | 1.1361 | 1.0881
2010-08-14 | 40 | 39.7866 | 10.8534 | 50.64 | 4.4609 | 0.76558 | 0.37646 | 5.6029 | 11.06% | 11.77% | 7.955% | 1.1244 | 1.1334 | 1.0864
2010-08-14 | 41 | 40.2186 | 10.5489 | 50.7675 | 4.4834 | 0.76558 | 0.37741 | 5.6264 | 11.08% | 11.79% | 7.968% | 1.1246 | 1.1337 | 1.0866
2010-08-14 | 42 | 39.9028 | 10.1344 | 50.0371 | 4.3553 | 0.76558 | 0.37198 | 5.4929 | 10.98% | 11.68% | 7.893% | 1.1233 | 1.1322 | 1.0857
2010-08-14 | 43 | 38.0779 | 9.7223 | 47.8002 | 3.9746 | 0.76558 | 0.35535 | 5.0955 | 10.66% | 11.34% | 7.665% | 1.1193 | 1.1279 | 1.083
2010-08-14 | 44 | 36.3093 | 9.1316 | 45.4409 | 3.5919 | 0.76558 | 0.33781 | 4.6953 | 10.33% | 10.99% | 7.429% | 1.1152 | 1.1235 | 1.0803
2010-08-14 | 45 | 33.0346 | 8.3551 | 41.3898 | 2.98 | 0.76558 | 0.3077 | 4.0533 | 9.793% | 10.42% | 7.041% | 1.1086 | 1.1163 | 1.0757
2010-08-14 | 46 | 30.1463 | 7.7476 | 37.894 | 2.4979 | 0.76558 | 0.28171 | 3.5452 | 9.356% | 9.954% | 6.727% | 1.1032 | 1.1105 | 1.0721
2010-08-14 | 47 | 29.789 | 7.9231 | 37.7121 | 2.474 | 0.76558 | 0.28036 | 3.5199 | 9.334% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-08-14 | 48 | 28.5522 | 8.433 | 36.9852 | 2.3795 | 0.76558 | 0.27495 | 3.4201 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-08-15 | 1 | 26.5993 | 7.7076 | 34.307 | 2.0474 | 0.76558 | 0.25504 | 3.068 | 8.943% | 9.515% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-08-15 | 2 | 27.8566 | 7.1967 | 35.0533 | 2.1374 | 0.76558 | 0.26059 | 3.1636 | 9.025% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-08-15 | 3 | 26.7864 | 6.8125 | 33.5989 | 1.9637 | 0.76558 | 0.24978 | 2.9791 | 8.867% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-08-15 | 4 | 25.428 | 6.6334 | 32.0614 | 1.7881 | 0.76558 | 0.23835 | 2.7921 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-08-15 | 5 | 24.2423 | 6.429 | 30.6713 | 1.6364 | 0.76558 | 0.22801 | 2.63 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-08-15 | 6 | 23.6758 | 6.1866 | 29.8623 | 1.5513 | 0.76558 | 0.222 | 2.5388 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-08-15 | 7 | 23.4316 | 6.1312 | 29.5628 | 1.5203 | 0.76558 | 0.21977 | 2.5056 | 8.476% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-08-15 | 8 | 23.0713 | 6.051 | 29.1224 | 1.4753 | 0.76558 | 0.2165 | 2.4574 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-08-15 | 9 | 22.9995 | 6.1308 | 29.1303 | 1.4761 | 0.76558 | 0.21656 | 2.4583 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0986 | 1.0646
2010-08-15 | 10 | 23.1656 | 6.1736 | 29.3393 | 1.4974 | 0.76558 | 0.21811 | 2.4811 | 8.456% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-08-15 | 11 | 23.9836 | 6.2696 | 30.2532 | 1.5921 | 0.76558 | 0.22491 | 2.5826 | 8.537% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-08-15 | 12 | 24.5445 | 6.4686 | 31.0131 | 1.6731 | 0.76558 | 0.23055 | 2.6692 | 8.607% | 9.158% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-08-15 | 13 | 25.8937 | 6.9777 | 32.8714 | 1.8796 | 0.76558 | 0.24437 | 2.8896 | 8.791% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-08-15 | 14 | 27.6118 | 7.6169 | 35.2287 | 2.1589 | 0.76558 | 0.26189 | 3.1864 | 9.045% | 9.624% | 6.503% | 1.0994 | 1.1065 | 1.0696
2010-08-15 | 15 | 29.2414 | 8.3472 | 37.5886 | 2.4578 | 0.76558 | 0.27944 | 3.5028 | 9.319% | 9.915% | 6.7% | 1.1028 | 1.1101 | 1.0718
2010-08-15 | 16 | 29.8515 | 9.3938 | 39.2452 | 2.6792 | 0.76558 | 0.29175 | 3.7366 | 9.521% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-08-15 | 17 | 32.3879 | 10.4529 | 42.8408 | 3.1926 | 0.76558 | 0.31848 | 4.2767 | 9.983% | 10.62% | 7.178% | 1.1109 | 1.1188 | 1.0773
2010-08-15 | 18 | 35.2878 | 11.3538 | 46.6416 | 3.7843 | 0.76558 | 0.34674 | 4.8966 | 10.5% | 11.17% | 7.548% | 1.1173 | 1.1257 | 1.0816
2010-08-15 | 19 | 37.4583 | 12.117 | 49.5753 | 4.2753 | 0.76558 | 0.36855 | 5.4094 | 10.91% | 11.61% | 7.845% | 1.1225 | 1.1313 | 1.0851
2010-08-15 | 20 | 37.9457 | 12.3365 | 50.2822 | 4.3981 | 0.76558 | 0.3738 | 5.5375 | 11.01% | 11.72% | 7.918% | 1.1238 | 1.1327 | 1.086
2010-08-15 | 21 | 39.842 | 12.4132 | 52.2552 | 4.75 | 0.76558 | 0.38847 | 5.904 | 11.3% | 12.02% | 8.124% | 1.1274 | 1.1366 | 1.0884
2010-08-15 | 22 | 38.7212 | 11.8723 | 50.5935 | 4.4527 | 0.76558 | 0.37612 | 5.5944 | 11.06% | 11.77% | 7.95% | 1.1243 | 1.1333 | 1.0864
2010-08-15 | 23 | 36.9397 | 10.8726 | 47.8123 | 3.9766 | 0.76558 | 0.35544 | 5.0976 | 10.66% | 11.34% | 7.666% | 1.1193 | 1.128 | 1.083
2010-08-15 | 24 | 35.2456 | 10.2235 | 45.4691 | 3.5964 | 0.76558 | 0.33802 | 4.7 | 10.34% | 11% | 7.432% | 1.1153 | 1.1236 | 1.0803
2010-08-15 | 25 | 32.876 | 9.6073 | 42.4833 | 3.1396 | 0.76558 | 0.31583 | 4.221 | 9.936% | 10.57% | 7.144% | 1.1103 | 1.1182 | 1.0769
2010-08-15 | 26 | 31.4232 | 9.0244 | 40.4475 | 2.8459 | 0.76558 | 0.30069 | 3.9122 | 9.672% | 10.29% | 6.954% | 1.1071 | 1.1147 | 1.0747
2010-08-15 | 27 | 31.8693 | 9.0654 | 40.9347 | 2.9149 | 0.76558 | 0.30431 | 3.9848 | 9.734% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2010-08-15 | 28 | 32.3436 | 9.1328 | 41.4763 | 2.9925 | 0.76558 | 0.30834 | 4.0664 | 9.804% | 10.43% | 7.049% | 1.1087 | 1.1165 | 1.0758
2010-08-15 | 29 | 31.3816 | 9.0925 | 40.4741 | 2.8496 | 0.76558 | 0.30089 | 3.9161 | 9.676% | 10.29% | 6.957% | 1.1071 | 1.1148 | 1.0748
2010-08-15 | 30 | 30.6347 | 8.4002 | 39.0349 | 2.6506 | 0.76558 | 0.29019 | 3.7063 | 9.495% | 10.1% | 6.827% | 1.1049 | 1.1124 | 1.0733
2010-08-15 | 31 | 31.9996 | 8.1486 | 40.1482 | 2.8039 | 0.76558 | 0.29847 | 3.868 | 9.634% | 10.25% | 6.927% | 1.1066 | 1.1142 | 1.0744
2010-08-15 | 32 | 32.2716 | 7.9384 | 40.2099 | 2.8126 | 0.76558 | 0.29893 | 3.8771 | 9.642% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-08-15 | 33 | 31.9558 | 8.2618 | 40.2176 | 2.8136 | 0.76558 | 0.29898 | 3.8782 | 9.643% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-08-15 | 34 | 32.6176 | 8.5513 | 41.1688 | 2.9483 | 0.76558 | 0.30605 | 4.0199 | 9.765% | 10.39% | 7.021% | 1.1082 | 1.1159 | 1.0755
2010-08-15 | 35 | 33.3497 | 9.5975 | 42.9472 | 3.2085 | 0.76558 | 0.31927 | 4.2934 | 9.997% | 10.64% | 7.188% | 1.1111 | 1.119 | 1.0774
2010-08-15 | 36 | 36.3397 | 10.9785 | 47.3182 | 3.8949 | 0.76558 | 0.35177 | 5.0122 | 10.59% | 11.27% | 7.616% | 1.1185 | 1.127 | 1.0824
2010-08-15 | 37 | 39.1539 | 11.4859 | 50.6398 | 4.4609 | 0.76558 | 0.37646 | 5.6029 | 11.06% | 11.77% | 7.955% | 1.1244 | 1.1334 | 1.0864
2010-08-15 | 38 | 39.8024 | 11.5702 | 51.3726 | 4.5909 | 0.76558 | 0.38191 | 5.7384 | 11.17% | 11.89% | 8.031% | 1.1257 | 1.1349 | 1.0873
2010-08-15 | 39 | 38.4937 | 11.1482 | 49.6419 | 4.2868 | 0.76558 | 0.36904 | 5.4214 | 10.92% | 11.62% | 7.852% | 1.1226 | 1.1315 | 1.0852
2010-08-15 | 40 | 37.3302 | 10.6871 | 48.0173 | 4.0108 | 0.76558 | 0.35697 | 5.1333 | 10.69% | 11.37% | 7.687% | 1.1197 | 1.1283 | 1.0833
2010-08-15 | 41 | 38.0051 | 10.3107 | 48.3159 | 4.0608 | 0.76558 | 0.35919 | 5.1856 | 10.73% | 11.42% | 7.717% | 1.1202 | 1.1289 | 1.0836
2010-08-15 | 42 | 38.1044 | 9.9196 | 48.024 | 4.0119 | 0.76558 | 0.35702 | 5.1345 | 10.69% | 11.38% | 7.687% | 1.1197 | 1.1284 | 1.0833
2010-08-15 | 43 | 35.8921 | 9.4524 | 45.3445 | 3.5767 | 0.76558 | 0.3371 | 4.6794 | 10.32% | 10.98% | 7.42% | 1.1151 | 1.1233 | 1.0801
2010-08-15 | 44 | 33.7519 | 8.9812 | 42.733 | 3.1766 | 0.76558 | 0.31768 | 4.2599 | 9.969% | 10.61% | 7.167% | 1.1107 | 1.1186 | 1.0772
2010-08-15 | 45 | 30.7204 | 8.3431 | 39.0635 | 2.6545 | 0.76558 | 0.2904 | 3.7105 | 9.499% | 10.11% | 6.829% | 1.105 | 1.1124 | 1.0733
2010-08-15 | 46 | 27.92 | 7.6582 | 35.5782 | 2.2019 | 0.76558 | 0.26449 | 3.232 | 9.084% | 9.666% | 6.532% | 1.0999 | 1.107 | 1.0699
2010-08-15 | 47 | 27.6052 | 7.834 | 35.4392 | 2.1848 | 0.76558 | 0.26346 | 3.2138 | 9.068% | 9.649% | 6.52% | 1.0997 | 1.1068 | 1.0698
2010-08-15 | 48 | 27.045 | 8.321 | 35.366 | 2.1757 | 0.76558 | 0.26292 | 3.2042 | 9.06% | 9.64% | 6.514% | 1.0996 | 1.1067 | 1.0697
2010-08-16 | 1 | 25.3206 | 7.5468 | 32.8674 | 1.8792 | 0.76558 | 0.24434 | 2.8891 | 8.79% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-08-16 | 2 | 26.2684 | 7.0676 | 33.336 | 1.9331 | 0.76558 | 0.24782 | 2.9465 | 8.839% | 9.405% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-08-16 | 3 | 24.9449 | 6.5924 | 31.5373 | 1.7301 | 0.76558 | 0.23445 | 2.7302 | 8.657% | 9.211% | 6.224% | 1.0948 | 1.1015 | 1.0664
2010-08-16 | 4 | 23.6529 | 6.1489 | 29.8018 | 1.545 | 0.76558 | 0.22155 | 2.5321 | 8.496% | 9.04% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-08-16 | 5 | 22.5458 | 5.9986 | 28.5444 | 1.4173 | 0.76558 | 0.2122 | 2.3951 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-08-16 | 6 | 22.1583 | 5.7237 | 27.882 | 1.3523 | 0.76558 | 0.20728 | 2.3252 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-08-16 | 7 | 21.9 | 5.5468 | 27.4468 | 1.3104 | 0.76558 | 0.20404 | 2.2801 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-08-16 | 8 | 21.656 | 5.5946 | 27.2506 | 1.2918 | 0.76558 | 0.20258 | 2.2599 | 8.293% | 8.824% | 5.963% | 1.0904 | 1.0968 | 1.0634
2010-08-16 | 9 | 21.842 | 5.7242 | 27.5661 | 1.3219 | 0.76558 | 0.20493 | 2.2924 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-08-16 | 10 | 21.9994 | 5.78 | 27.7794 | 1.3424 | 0.76558 | 0.20652 | 2.3145 | 8.332% | 8.865% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-08-16 | 11 | 22.2577 | 5.7965 | 28.0542 | 1.3691 | 0.76558 | 0.20856 | 2.3432 | 8.352% | 8.887% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-08-16 | 12 | 22.5147 | 5.9285 | 28.4432 | 1.4073 | 0.76558 | 0.21145 | 2.3843 | 8.383% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2010-08-16 | 13 | 23.3627 | 6.2559 | 29.6187 | 1.526 | 0.76558 | 0.22019 | 2.5118 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2010-08-16 | 14 | 24.7126 | 6.5437 | 31.2563 | 1.6995 | 0.76558 | 0.23236 | 2.6974 | 8.63% | 9.182% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-08-16 | 15 | 26.1078 | 7.0102 | 33.118 | 1.9079 | 0.76558 | 0.2462 | 2.9197 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-08-16 | 16 | 27.2278 | 7.835 | 35.0629 | 2.1386 | 0.76558 | 0.26066 | 3.1648 | 9.026% | 9.604% | 6.49% | 1.0992 | 1.1062 | 1.0694
2010-08-16 | 17 | 29.497 | 8.9507 | 38.4477 | 2.5714 | 0.76558 | 0.28582 | 3.6228 | 9.423% | 10.03% | 6.775% | 1.104 | 1.1114 | 1.0727
2010-08-16 | 18 | 31.4788 | 9.8019 | 41.2807 | 2.9643 | 0.76558 | 0.30689 | 4.0368 | 9.779% | 10.4% | 7.031% | 1.1084 | 1.1161 | 1.0756
2010-08-16 | 19 | 33.662 | 10.3891 | 44.0511 | 3.3756 | 0.76558 | 0.32748 | 4.4686 | 10.14% | 10.79% | 7.294% | 1.1129 | 1.121 | 1.0787
2010-08-16 | 20 | 34.5796 | 10.5831 | 45.1626 | 3.5481 | 0.76558 | 0.33574 | 4.6494 | 10.29% | 10.95% | 7.402% | 1.1148 | 1.123 | 1.0799
2010-08-16 | 21 | 36.9663 | 10.7799 | 47.7463 | 3.9656 | 0.76558 | 0.35495 | 5.0862 | 10.65% | 11.33% | 7.659% | 1.1192 | 1.1278 | 1.0829
2010-08-16 | 22 | 36.5917 | 10.8491 | 47.4407 | 3.915 | 0.76558 | 0.35268 | 5.0333 | 10.61% | 11.29% | 7.628% | 1.1187 | 1.1273 | 1.0826
2010-08-16 | 23 | 35.4275 | 10.521 | 45.9485 | 3.6726 | 0.76558 | 0.34159 | 4.7798 | 10.4% | 11.07% | 7.479% | 1.1161 | 1.1245 | 1.0808
2010-08-16 | 24 | 34.3796 | 10.2688 | 44.6485 | 3.4677 | 0.76558 | 0.33192 | 4.5652 | 10.22% | 10.88% | 7.352% | 1.1139 | 1.1221 | 1.0794
2010-08-16 | 25 | 33.0428 | 9.9886 | 43.0315 | 3.2211 | 0.76558 | 0.3199 | 4.3066 | 10.01% | 10.65% | 7.196% | 1.1112 | 1.1192 | 1.0775
2010-08-16 | 26 | 32.239 | 9.1645 | 41.4036 | 2.982 | 0.76558 | 0.3078 | 4.0554 | 9.795% | 10.42% | 7.042% | 1.1086 | 1.1163 | 1.0758
2010-08-16 | 27 | 31.7663 | 9.2485 | 41.0149 | 2.9263 | 0.76558 | 0.30491 | 3.9968 | 9.745% | 10.37% | 7.006% | 1.108 | 1.1157 | 1.0753
2010-08-16 | 28 | 30.5608 | 9.2439 | 39.8047 | 2.7562 | 0.76558 | 0.29591 | 3.8176 | 9.591% | 10.2% | 6.896% | 1.1061 | 1.1136 | 1.0741
2010-08-16 | 29 | 29.8711 | 9.014 | 38.8852 | 2.6303 | 0.76558 | 0.28908 | 3.6849 | 9.476% | 10.08% | 6.814% | 1.1047 | 1.1121 | 1.0731
2010-08-16 | 30 | 29.3115 | 8.7368 | 38.0482 | 2.5183 | 0.76558 | 0.28286 | 3.5667 | 9.374% | 9.974% | 6.74% | 1.1034 | 1.1108 | 1.0723
2010-08-16 | 31 | 28.9372 | 8.4127 | 37.3499 | 2.4267 | 0.76558 | 0.27766 | 3.4699 | 9.29% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-08-16 | 32 | 29.0814 | 8.5533 | 37.6347 | 2.4638 | 0.76558 | 0.27978 | 3.5092 | 9.324% | 9.921% | 6.704% | 1.1028 | 1.1101 | 1.0719
2010-08-16 | 33 | 29.526 | 9.1179 | 38.6439 | 2.5977 | 0.76558 | 0.28728 | 3.6506 | 9.447% | 10.05% | 6.792% | 1.1043 | 1.1117 | 1.0729
2010-08-16 | 34 | 30.8623 | 9.5719 | 40.4341 | 2.844 | 0.76558 | 0.30059 | 3.9102 | 9.67% | 10.29% | 6.953% | 1.1071 | 1.1147 | 1.0747
2010-08-16 | 35 | 32.0986 | 10.1035 | 42.2021 | 3.0982 | 0.76558 | 0.31374 | 4.1775 | 9.899% | 10.53% | 7.117% | 1.1099 | 1.1177 | 1.0766
2010-08-16 | 36 | 34.7276 | 11.1538 | 45.8814 | 3.6619 | 0.76558 | 0.34109 | 4.7686 | 10.39% | 11.06% | 7.473% | 1.116 | 1.1243 | 1.0808
2010-08-16 | 37 | 37.3997 | 11.8835 | 49.2832 | 4.2251 | 0.76558 | 0.36638 | 5.357 | 10.87% | 11.57% | 7.815% | 1.122 | 1.1308 | 1.0848
2010-08-16 | 38 | 38.721 | 11.7385 | 50.4595 | 4.4291 | 0.76558 | 0.37512 | 5.5698 | 11.04% | 11.74% | 7.937% | 1.1241 | 1.1331 | 1.0862
2010-08-16 | 39 | 38.5914 | 11.2656 | 49.8569 | 4.324 | 0.76558 | 0.37064 | 5.4602 | 10.95% | 11.65% | 7.874% | 1.123 | 1.1319 | 1.0855
2010-08-16 | 40 | 37.6432 | 11.0897 | 48.7329 | 4.1312 | 0.76558 | 0.36229 | 5.2591 | 10.79% | 11.48% | 7.759% | 1.121 | 1.1297 | 1.0841
2010-08-16 | 41 | 37.989 | 10.7438 | 48.7328 | 4.1312 | 0.76558 | 0.36229 | 5.2591 | 10.79% | 11.48% | 7.759% | 1.121 | 1.1297 | 1.0841
2010-08-16 | 42 | 37.6299 | 10.0891 | 47.719 | 3.9611 | 0.76558 | 0.35475 | 5.0814 | 10.65% | 11.33% | 7.656% | 1.1192 | 1.1278 | 1.0829
2010-08-16 | 43 | 35.417 | 9.4792 | 44.8962 | 3.5063 | 0.76558 | 0.33376 | 4.6057 | 10.26% | 10.92% | 7.376% | 1.1143 | 1.1225 | 1.0796
2010-08-16 | 44 | 33.1193 | 8.6563 | 41.7756 | 3.0358 | 0.76558 | 0.31056 | 4.112 | 9.843% | 10.47% | 7.077% | 1.1092 | 1.117 | 1.0762
2010-08-16 | 45 | 29.6131 | 7.7425 | 37.3555 | 2.4274 | 0.76558 | 0.27771 | 3.4707 | 9.291% | 9.886% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-08-16 | 46 | 26.4968 | 6.8691 | 33.3658 | 1.9366 | 0.76558 | 0.24805 | 2.9502 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-08-16 | 47 | 26.4847 | 7.0531 | 33.5377 | 1.9566 | 0.76558 | 0.24932 | 2.9715 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-08-16 | 48 | 25.8379 | 7.6176 | 33.4556 | 1.947 | 0.76558 | 0.24871 | 2.9613 | 8.851% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2010-08-17 | 1 | 24.3569 | 6.8318 | 31.1888 | 1.6921 | 0.76558 | 0.23186 | 2.6896 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-08-17 | 2 | 25.5347 | 6.5255 | 32.0602 | 1.788 | 0.76558 | 0.23834 | 2.7919 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-08-17 | 3 | 23.7355 | 6.1424 | 29.8779 | 1.5529 | 0.76558 | 0.22212 | 2.5406 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-08-17 | 4 | 23.1726 | 5.8293 | 29.0018 | 1.4631 | 0.76558 | 0.2156 | 2.4443 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-08-17 | 5 | 22.5116 | 5.6566 | 28.1683 | 1.3802 | 0.76558 | 0.20941 | 2.3552 | 8.361% | 8.896% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-08-17 | 6 | 22.2397 | 5.6449 | 27.8845 | 1.3526 | 0.76558 | 0.2073 | 2.3255 | 8.34% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-08-17 | 7 | 22.2665 | 5.5367 | 27.8031 | 1.3447 | 0.76558 | 0.20669 | 2.317 | 8.333% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-08-17 | 8 | 22.267 | 5.4792 | 27.7462 | 1.3392 | 0.76558 | 0.20627 | 2.311 | 8.329% | 8.862% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-08-17 | 9 | 22.4827 | 5.6491 | 28.1318 | 1.3767 | 0.76558 | 0.20914 | 2.3514 | 8.358% | 8.893% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-08-17 | 10 | 22.5674 | 5.6229 | 28.1903 | 1.3824 | 0.76558 | 0.20957 | 2.3575 | 8.363% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-08-17 | 11 | 23.0134 | 5.8297 | 28.8431 | 1.4472 | 0.76558 | 0.21442 | 2.4272 | 8.415% | 8.954% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-08-17 | 12 | 23.9177 | 6.2795 | 30.1973 | 1.5862 | 0.76558 | 0.22449 | 2.5763 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-08-17 | 13 | 25.9998 | 7.1863 | 33.1861 | 1.9158 | 0.76558 | 0.24671 | 2.9281 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-08-17 | 14 | 29.7784 | 8.7215 | 38.4999 | 2.5784 | 0.76558 | 0.28621 | 3.6302 | 9.429% | 10.03% | 6.78% | 1.1041 | 1.1115 | 1.0727
2010-08-17 | 15 | 35.2521 | 10.9568 | 46.2089 | 3.7144 | 0.76558 | 0.34352 | 4.8235 | 10.44% | 11.11% | 7.505% | 1.1166 | 1.1249 | 1.0811
2010-08-17 | 16 | 37.5117 | 11.773 | 49.2847 | 4.2253 | 0.76558 | 0.36639 | 5.3573 | 10.87% | 11.57% | 7.816% | 1.122 | 1.1308 | 1.0848
2010-08-17 | 17 | 39.294 | 12.4646 | 51.7586 | 4.6601 | 0.76558 | 0.38478 | 5.8105 | 11.23% | 11.94% | 8.072% | 1.1265 | 1.1356 | 1.0878
2010-08-17 | 18 | 39.6687 | 12.3671 | 52.0357 | 4.7102 | 0.76558 | 0.38684 | 5.8626 | 11.27% | 11.99% | 8.101% | 1.127 | 1.1362 | 1.0881
2010-08-17 | 19 | 39.2667 | 11.9942 | 51.2608 | 4.5709 | 0.76558 | 0.38108 | 5.7176 | 11.15% | 11.87% | 8.02% | 1.1255 | 1.1347 | 1.0872
2010-08-17 | 20 | 37.8866 | 11.6784 | 49.565 | 4.2735 | 0.76558 | 0.36847 | 5.4076 | 10.91% | 11.61% | 7.844% | 1.1225 | 1.1313 | 1.0851
2010-08-17 | 21 | 38.5908 | 11.2528 | 49.8436 | 4.3217 | 0.76558 | 0.37054 | 5.4578 | 10.95% | 11.65% | 7.873% | 1.123 | 1.1319 | 1.0855
2010-08-17 | 22 | 36.551 | 10.8206 | 47.3716 | 3.9036 | 0.76558 | 0.35217 | 5.0214 | 10.6% | 11.28% | 7.621% | 1.1186 | 1.1271 | 1.0825
2010-08-17 | 23 | 34.6833 | 10.1251 | 44.8084 | 3.4926 | 0.76558 | 0.33311 | 4.5913 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-08-17 | 24 | 33.4042 | 10.0327 | 43.4368 | 3.2821 | 0.76558 | 0.32291 | 4.3706 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-08-17 | 25 | 31.247 | 9.7978 | 41.0448 | 2.9306 | 0.76558 | 0.30513 | 4.0013 | 9.749% | 10.37% | 7.009% | 1.108 | 1.1157 | 1.0754
2010-08-17 | 26 | 29.3649 | 9.027 | 38.392 | 2.564 | 0.76558 | 0.28541 | 3.615 | 9.416% | 10.02% | 6.77% | 1.1039 | 1.1113 | 1.0726
2010-08-17 | 27 | 30.0855 | 9.388 | 39.4735 | 2.7105 | 0.76558 | 0.29345 | 3.7695 | 9.549% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-08-17 | 28 | 29.8699 | 9.532 | 39.4019 | 2.7007 | 0.76558 | 0.29292 | 3.7592 | 9.541% | 10.15% | 6.86% | 1.1055 | 1.113 | 1.0736
2010-08-17 | 29 | 29.6979 | 9.1421 | 38.8399 | 2.6242 | 0.76558 | 0.28874 | 3.6785 | 9.471% | 10.08% | 6.81% | 1.1046 | 1.1121 | 1.0731
2010-08-17 | 30 | 29.3417 | 8.8304 | 38.1721 | 2.5347 | 0.76558 | 0.28378 | 3.5841 | 9.389% | 9.99% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-08-17 | 31 | 31.18 | 8.9898 | 40.1698 | 2.8069 | 0.76558 | 0.29863 | 3.8712 | 9.637% | 10.25% | 6.929% | 1.1066 | 1.1143 | 1.0744
2010-08-17 | 32 | 31.5977 | 9.1184 | 40.7161 | 2.8838 | 0.76558 | 0.30269 | 3.9521 | 9.706% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2010-08-17 | 33 | 31.1527 | 9.4291 | 40.5817 | 2.8648 | 0.76558 | 0.30169 | 3.9321 | 9.689% | 10.31% | 6.967% | 1.1073 | 1.1149 | 1.0749
2010-08-17 | 34 | 31.3686 | 9.7278 | 41.0964 | 2.9379 | 0.76558 | 0.30552 | 4.009 | 9.755% | 10.38% | 7.014% | 1.1081 | 1.1158 | 1.0754
2010-08-17 | 35 | 32.5748 | 10.3425 | 42.9173 | 3.204 | 0.76558 | 0.31905 | 4.2887 | 9.993% | 10.63% | 7.185% | 1.111 | 1.119 | 1.0774
2010-08-17 | 36 | 35.3329 | 11.4789 | 46.8118 | 3.8119 | 0.76558 | 0.348 | 4.9255 | 10.52% | 11.2% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-08-17 | 37 | 38.8815 | 12.4329 | 51.3144 | 4.5805 | 0.76558 | 0.38148 | 5.7276 | 11.16% | 11.88% | 8.025% | 1.1256 | 1.1348 | 1.0873
2010-08-17 | 38 | 40.3171 | 12.4562 | 52.7733 | 4.8447 | 0.76558 | 0.39232 | 6.0026 | 11.37% | 12.1% | 8.178% | 1.1283 | 1.1377 | 1.0891
2010-08-17 | 39 | 39.5411 | 11.9089 | 51.45 | 4.6047 | 0.76558 | 0.38249 | 5.7528 | 11.18% | 11.9% | 8.039% | 1.1259 | 1.135 | 1.0874
2010-08-17 | 40 | 38.5073 | 11.5125 | 50.0198 | 4.3523 | 0.76558 | 0.37185 | 5.4897 | 10.98% | 11.68% | 7.891% | 1.1233 | 1.1322 | 1.0857
2010-08-17 | 41 | 38.5787 | 11.2085 | 49.7872 | 4.3119 | 0.76558 | 0.37012 | 5.4476 | 10.94% | 11.64% | 7.867% | 1.1229 | 1.1318 | 1.0854
2010-08-17 | 42 | 37.946 | 10.649 | 48.595 | 4.1079 | 0.76558 | 0.36126 | 5.2347 | 10.77% | 11.46% | 7.745% | 1.1207 | 1.1295 | 1.084
2010-08-17 | 43 | 35.3598 | 10.1218 | 45.4816 | 3.5984 | 0.76558 | 0.33812 | 4.7021 | 10.34% | 11% | 7.433% | 1.1153 | 1.1236 | 1.0803
2010-08-17 | 44 | 32.9623 | 9.4982 | 42.4605 | 3.1362 | 0.76558 | 0.31566 | 4.2174 | 9.933% | 10.57% | 7.142% | 1.1103 | 1.1182 | 1.0769
2010-08-17 | 45 | 29.5279 | 8.5936 | 38.1215 | 2.528 | 0.76558 | 0.2834 | 3.577 | 9.383% | 9.984% | 6.746% | 1.1035 | 1.1109 | 1.0723
2010-08-17 | 46 | 26.756 | 7.6903 | 34.4463 | 2.064 | 0.76558 | 0.25608 | 3.0857 | 8.958% | 9.531% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-08-17 | 47 | 25.9371 | 7.6942 | 33.6313 | 1.9675 | 0.76558 | 0.25002 | 2.9831 | 8.87% | 9.438% | 6.378% | 1.0973 | 1.1042 | 1.0681
2010-08-17 | 48 | 27.0292 | 8.1902 | 35.2193 | 2.1577 | 0.76558 | 0.26182 | 3.1851 | 9.044% | 9.622% | 6.502% | 1.0994 | 1.1065 | 1.0695
2010-08-18 | 1 | 24.9312 | 7.3153 | 32.2465 | 1.8088 | 0.76558 | 0.23972 | 2.8141 | 8.727% | 9.285% | 6.275% | 1.0956 | 1.1024 | 1.0669
2010-08-18 | 2 | 23.5671 | 6.7709 | 30.338 | 1.6011 | 0.76558 | 0.22554 | 2.5922 | 8.544% | 9.091% | 6.143% | 1.0934 | 1.1 | 1.0655
2010-08-18 | 3 | 22.5515 | 6.4182 | 28.9697 | 1.4599 | 0.76558 | 0.21536 | 2.4408 | 8.425% | 8.965% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-08-18 | 4 | 21.7061 | 6.1757 | 27.8818 | 1.3523 | 0.76558 | 0.20728 | 2.3252 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-08-18 | 5 | 20.8142 | 6.178 | 26.9921 | 1.2674 | 0.76558 | 0.20066 | 2.2336 | 8.275% | 8.805% | 5.95% | 1.0902 | 1.0965 | 1.0633
2010-08-18 | 6 | 20.2353 | 6.0628 | 26.2981 | 1.203 | 0.76558 | 0.1955 | 2.1641 | 8.229% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-08-18 | 7 | 20.0115 | 6.0232 | 26.0346 | 1.1791 | 0.76558 | 0.19354 | 2.1382 | 8.213% | 8.738% | 5.905% | 1.0895 | 1.0958 | 1.0628
2010-08-18 | 8 | 19.7632 | 5.9213 | 25.6845 | 1.1476 | 0.76558 | 0.19094 | 2.1041 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-08-18 | 9 | 20.2005 | 5.8273 | 26.0278 | 1.1784 | 0.76558 | 0.19349 | 2.1375 | 8.212% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-08-18 | 10 | 20.517 | 5.9091 | 26.4261 | 1.2148 | 0.76558 | 0.19645 | 2.1768 | 8.237% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-08-18 | 11 | 20.9755 | 6.0339 | 27.0094 | 1.269 | 0.76558 | 0.20079 | 2.2354 | 8.276% | 8.806% | 5.951% | 1.0902 | 1.0966 | 1.0633
2010-08-18 | 12 | 21.9168 | 6.5569 | 28.4737 | 1.4103 | 0.76558 | 0.21168 | 2.3876 | 8.385% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-08-18 | 13 | 23.9704 | 7.5074 | 31.4777 | 1.7236 | 0.76558 | 0.23401 | 2.7232 | 8.651% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-08-18 | 14 | 27.6051 | 8.9615 | 36.5666 | 2.326 | 0.76558 | 0.27184 | 3.3634 | 9.198% | 9.787% | 6.613% | 1.1013 | 1.1085 | 1.0708
2010-08-18 | 15 | 32.4303 | 10.9146 | 43.3449 | 3.2682 | 0.76558 | 0.32223 | 4.356 | 10.05% | 10.69% | 7.226% | 1.1117 | 1.1197 | 1.0779
2010-08-18 | 16 | 34.5919 | 12.1214 | 46.7133 | 3.7959 | 0.76558 | 0.34727 | 4.9088 | 10.51% | 11.18% | 7.555% | 1.1174 | 1.1259 | 1.0817
2010-08-18 | 17 | 35.8423 | 12.6899 | 48.5322 | 4.0973 | 0.76558 | 0.36079 | 5.2236 | 10.76% | 11.45% | 7.739% | 1.1206 | 1.1293 | 1.0839
2010-08-18 | 18 | 36.3947 | 12.6383 | 49.033 | 4.1823 | 0.76558 | 0.36452 | 5.3124 | 10.83% | 11.53% | 7.79% | 1.1215 | 1.1303 | 1.0845
2010-08-18 | 19 | 36.4116 | 12.1436 | 48.5551 | 4.1011 | 0.76558 | 0.36096 | 5.2277 | 10.77% | 11.46% | 7.741% | 1.1207 | 1.1294 | 1.0839
2010-08-18 | 20 | 35.0036 | 11.7484 | 46.752 | 3.8022 | 0.76558 | 0.34756 | 4.9153 | 10.51% | 11.19% | 7.559% | 1.1175 | 1.126 | 1.0818
2010-08-18 | 21 | 34.938 | 11.3855 | 46.3235 | 3.7328 | 0.76558 | 0.34437 | 4.8428 | 10.45% | 11.12% | 7.517% | 1.1167 | 1.1252 | 1.0813
2010-08-18 | 22 | 33.868 | 10.9938 | 44.8618 | 3.501 | 0.76558 | 0.33351 | 4.6001 | 10.25% | 10.91% | 7.373% | 1.1143 | 1.1225 | 1.0796
2010-08-18 | 23 | 32.1165 | 10.4211 | 42.5376 | 3.1476 | 0.76558 | 0.31623 | 4.2294 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-08-18 | 24 | 30.4871 | 10.017 | 40.5042 | 2.8539 | 0.76558 | 0.30111 | 3.9206 | 9.679% | 10.3% | 6.959% | 1.1072 | 1.1148 | 1.0748
2010-08-18 | 25 | 29.0727 | 9.8779 | 38.9507 | 2.6392 | 0.76558 | 0.28956 | 3.6943 | 9.485% | 10.09% | 6.819% | 1.1048 | 1.1122 | 1.0732
2010-08-18 | 26 | 28.1263 | 9.6541 | 37.7804 | 2.483 | 0.76558 | 0.28086 | 3.5294 | 9.342% | 9.94% | 6.717% | 1.103 | 1.1104 | 1.072
2010-08-18 | 27 | 28.9657 | 9.8845 | 38.8502 | 2.6256 | 0.76558 | 0.28882 | 3.6799 | 9.472% | 10.08% | 6.81% | 1.1046 | 1.1121 | 1.0731
2010-08-18 | 28 | 29.2097 | 10.3504 | 39.5601 | 2.7224 | 0.76558 | 0.29409 | 3.7821 | 9.56% | 10.17% | 6.874% | 1.1057 | 1.1132 | 1.0738
2010-08-18 | 29 | 28.994 | 10.1114 | 39.1053 | 2.6602 | 0.76558 | 0.29071 | 3.7164 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-08-18 | 30 | 29.0519 | 9.6547 | 38.7066 | 2.6062 | 0.76558 | 0.28775 | 3.6595 | 9.454% | 10.06% | 6.798% | 1.1044 | 1.1118 | 1.0729
2010-08-18 | 31 | 30.7312 | 9.747 | 40.4782 | 2.8502 | 0.76558 | 0.30092 | 3.9167 | 9.676% | 10.3% | 6.957% | 1.1071 | 1.1148 | 1.0748
2010-08-18 | 32 | 32.2171 | 9.5708 | 41.7879 | 3.0376 | 0.76558 | 0.31066 | 4.1139 | 9.845% | 10.47% | 7.078% | 1.1092 | 1.117 | 1.0762
2010-08-18 | 33 | 31.5574 | 9.5137 | 41.0711 | 2.9343 | 0.76558 | 0.30533 | 4.0052 | 9.752% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-08-18 | 34 | 32.1035 | 9.6393 | 41.7428 | 3.0311 | 0.76558 | 0.31032 | 4.107 | 9.839% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-08-18 | 35 | 33.5982 | 10.0806 | 43.6787 | 3.3188 | 0.76558 | 0.32471 | 4.409 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-08-18 | 36 | 36.2392 | 11.3385 | 47.5778 | 3.9377 | 0.76558 | 0.3537 | 5.057 | 10.63% | 11.31% | 7.642% | 1.1189 | 1.1275 | 1.0827
2010-08-18 | 37 | 40.2623 | 12.78 | 53.0423 | 4.8942 | 0.76558 | 0.39432 | 6.0541 | 11.41% | 12.14% | 8.206% | 1.1288 | 1.1382 | 1.0894
2010-08-18 | 38 | 41.9119 | 13.0295 | 54.9413 | 5.2509 | 0.76558 | 0.40844 | 6.4249 | 11.69% | 12.44% | 8.408% | 1.1324 | 1.1421 | 1.0918
2010-08-18 | 39 | 41.9843 | 12.8404 | 54.8247 | 5.2286 | 0.76558 | 0.40757 | 6.4018 | 11.68% | 12.42% | 8.396% | 1.1322 | 1.1419 | 1.0917
2010-08-18 | 40 | 42.6888 | 12.3278 | 55.0166 | 5.2653 | 0.76558 | 0.409 | 6.4399 | 11.71% | 12.45% | 8.416% | 1.1326 | 1.1423 | 1.0919
2010-08-18 | 41 | 43.7802 | 11.9021 | 55.6824 | 5.3935 | 0.76558 | 0.41395 | 6.573 | 11.8% | 12.56% | 8.487% | 1.1338 | 1.1436 | 1.0927
2010-08-18 | 42 | 43.4645 | 11.5743 | 55.0388 | 5.2695 | 0.76558 | 0.40917 | 6.4443 | 11.71% | 12.46% | 8.418% | 1.1326 | 1.1423 | 1.0919
2010-08-18 | 43 | 41.5822 | 10.8666 | 52.4488 | 4.7853 | 0.76558 | 0.38991 | 5.9408 | 11.33% | 12.05% | 8.144% | 1.1277 | 1.137 | 1.0887
2010-08-18 | 44 | 39.3289 | 10.2985 | 49.6274 | 4.2843 | 0.76558 | 0.36894 | 5.4188 | 10.92% | 11.62% | 7.851% | 1.1226 | 1.1314 | 1.0852
2010-08-18 | 45 | 35.7359 | 9.2501 | 44.986 | 3.5204 | 0.76558 | 0.33443 | 4.6204 | 10.27% | 10.93% | 7.385% | 1.1145 | 1.1227 | 1.0797
2010-08-18 | 46 | 32.4623 | 8.2503 | 40.7126 | 2.8833 | 0.76558 | 0.30266 | 3.9516 | 9.706% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2010-08-18 | 47 | 30.5939 | 8.3085 | 38.9025 | 2.6326 | 0.76558 | 0.28921 | 3.6874 | 9.479% | 10.09% | 6.815% | 1.1047 | 1.1122 | 1.0731
2010-08-18 | 48 | 31.0376 | 8.9337 | 39.9714 | 2.7793 | 0.76558 | 0.29715 | 3.842 | 9.612% | 10.23% | 6.911% | 1.1063 | 1.1139 | 1.0742
2010-08-19 | 1 | 29.5734 | 8.1925 | 37.7658 | 2.481 | 0.76558 | 0.28076 | 3.5274 | 9.34% | 9.938% | 6.716% | 1.103 | 1.1103 | 1.072
2010-08-19 | 2 | 28.0788 | 7.6184 | 35.6972 | 2.2167 | 0.76558 | 0.26538 | 3.2476 | 9.098% | 9.68% | 6.541% | 1.1001 | 1.1072 | 1.07
2010-08-19 | 3 | 26.3266 | 7.2585 | 33.5852 | 1.9621 | 0.76558 | 0.24968 | 2.9774 | 8.865% | 9.433% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-08-19 | 4 | 25.3787 | 7.0813 | 32.4599 | 1.8329 | 0.76558 | 0.24131 | 2.8398 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-08-19 | 5 | 24.8325 | 6.9439 | 31.7764 | 1.7565 | 0.76558 | 0.23623 | 2.7583 | 8.68% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2010-08-19 | 6 | 24.6165 | 6.7476 | 31.3642 | 1.7112 | 0.76558 | 0.23316 | 2.7099 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-08-19 | 7 | 24.4159 | 6.6617 | 31.0776 | 1.6801 | 0.76558 | 0.23103 | 2.6767 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-08-19 | 8 | 23.9701 | 6.7049 | 30.6749 | 1.6368 | 0.76558 | 0.22804 | 2.6304 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-08-19 | 9 | 24.746 | 6.8215 | 31.5675 | 1.7335 | 0.76558 | 0.23468 | 2.7337 | 8.66% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-08-19 | 10 | 24.1857 | 6.958 | 31.1437 | 1.6872 | 0.76558 | 0.23153 | 2.6843 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-08-19 | 11 | 24.4005 | 7.1046 | 31.5051 | 1.7266 | 0.76558 | 0.23421 | 2.7264 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0663
2010-08-19 | 12 | 25.348 | 7.4238 | 32.7718 | 1.8682 | 0.76558 | 0.24363 | 2.8775 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.103 | 1.0674
2010-08-19 | 13 | 27.392 | 8.6757 | 36.0677 | 2.2629 | 0.76558 | 0.26813 | 3.2966 | 9.14% | 9.725% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-08-19 | 14 | 31.1247 | 10.3014 | 41.4261 | 2.9853 | 0.76558 | 0.30797 | 4.0588 | 9.798% | 10.42% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-08-19 | 15 | 36.4017 | 12.6553 | 49.057 | 4.1864 | 0.76558 | 0.3647 | 5.3166 | 10.84% | 11.53% | 7.792% | 1.1215 | 1.1303 | 1.0845
2010-08-19 | 16 | 38.6152 | 13.7032 | 52.3184 | 4.7615 | 0.76558 | 0.38894 | 5.916 | 11.31% | 12.03% | 8.13% | 1.1275 | 1.1368 | 1.0885
2010-08-19 | 17 | 40.0358 | 14.6757 | 54.7115 | 5.207 | 0.76558 | 0.40673 | 6.3794 | 11.66% | 12.41% | 8.384% | 1.132 | 1.1416 | 1.0915
2010-08-19 | 18 | 40.2331 | 14.8402 | 55.0733 | 5.2761 | 0.76558 | 0.40942 | 6.4511 | 11.71% | 12.46% | 8.422% | 1.1327 | 1.1424 | 1.092
2010-08-19 | 19 | 39.9763 | 14.0931 | 54.0694 | 5.0855 | 0.76558 | 0.40196 | 6.2531 | 11.56% | 12.31% | 8.315% | 1.1308 | 1.1403 | 1.0907
2010-08-19 | 20 | 38.5106 | 13.2788 | 51.7893 | 4.6657 | 0.76558 | 0.38501 | 5.8163 | 11.23% | 11.95% | 8.075% | 1.1265 | 1.1357 | 1.0878
2010-08-19 | 21 | 38.741 | 12.5115 | 51.2525 | 4.5695 | 0.76558 | 0.38102 | 5.7161 | 11.15% | 11.87% | 8.019% | 1.1255 | 1.1346 | 1.0872
2010-08-19 | 22 | 36.9856 | 11.9364 | 48.922 | 4.1634 | 0.76558 | 0.36369 | 5.2926 | 10.82% | 11.51% | 7.778% | 1.1213 | 1.1301 | 1.0843
2010-08-19 | 23 | 35.1027 | 10.972 | 46.0746 | 3.6928 | 0.76558 | 0.34252 | 4.8009 | 10.42% | 11.09% | 7.492% | 1.1163 | 1.1247 | 1.081
2010-08-19 | 24 | 33.6865 | 10.4419 | 44.1284 | 3.3874 | 0.76558 | 0.32806 | 4.4811 | 10.15% | 10.8% | 7.301% | 1.113 | 1.1211 | 1.0788
2010-08-19 | 25 | 31.4102 | 10.1482 | 41.5584 | 3.0044 | 0.76558 | 0.30895 | 4.0789 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-08-19 | 26 | 29.8718 | 9.3729 | 39.2447 | 2.6792 | 0.76558 | 0.29175 | 3.7365 | 9.521% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-08-19 | 27 | 30.2165 | 9.6286 | 39.8452 | 2.7618 | 0.76558 | 0.29621 | 3.8236 | 9.596% | 10.21% | 6.9% | 1.1061 | 1.1137 | 1.0741
2010-08-19 | 28 | 30.2353 | 9.7492 | 39.9845 | 2.7811 | 0.76558 | 0.29725 | 3.8439 | 9.614% | 10.23% | 6.912% | 1.1064 | 1.1139 | 1.0743
2010-08-19 | 29 | 29.3228 | 9.1335 | 38.4563 | 2.5726 | 0.76558 | 0.28589 | 3.624 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1114 | 1.0727
2010-08-19 | 30 | 28.8217 | 8.9344 | 37.7561 | 2.4798 | 0.76558 | 0.28068 | 3.526 | 9.339% | 9.937% | 6.715% | 1.103 | 1.1103 | 1.072
2010-08-19 | 31 | 30.4093 | 8.9924 | 39.4017 | 2.7006 | 0.76558 | 0.29292 | 3.7591 | 9.541% | 10.15% | 6.86% | 1.1055 | 1.113 | 1.0736
2010-08-19 | 32 | 30.9634 | 8.9379 | 39.9014 | 2.7696 | 0.76558 | 0.29663 | 3.8318 | 9.603% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-08-19 | 33 | 30.9393 | 9.1316 | 40.0709 | 2.7931 | 0.76558 | 0.29789 | 3.8566 | 9.624% | 10.24% | 6.92% | 1.1065 | 1.1141 | 1.0743
2010-08-19 | 34 | 31.7232 | 9.1938 | 40.9171 | 2.9123 | 0.76558 | 0.30418 | 3.9821 | 9.732% | 10.36% | 6.997% | 1.1078 | 1.1155 | 1.0752
2010-08-19 | 35 | 32.6504 | 9.6962 | 42.3466 | 3.1194 | 0.76558 | 0.31481 | 4.1998 | 9.918% | 10.55% | 7.131% | 1.1101 | 1.118 | 1.0768
2010-08-19 | 36 | 35.5876 | 10.8097 | 46.3973 | 3.7447 | 0.76558 | 0.34492 | 4.8552 | 10.46% | 11.13% | 7.524% | 1.1169 | 1.1253 | 1.0814
2010-08-19 | 37 | 39.2204 | 12.1578 | 51.3781 | 4.5919 | 0.76558 | 0.38195 | 5.7394 | 11.17% | 11.89% | 8.032% | 1.1258 | 1.1349 | 1.0873
2010-08-19 | 38 | 41.3506 | 12.4587 | 53.8093 | 5.0367 | 0.76558 | 0.40002 | 6.2023 | 11.53% | 12.26% | 8.288% | 1.1303 | 1.1398 | 1.0904
2010-08-19 | 39 | 41.0072 | 12.22 | 53.2272 | 4.9284 | 0.76558 | 0.3957 | 6.0896 | 11.44% | 12.17% | 8.226% | 1.1292 | 1.1386 | 1.0896
2010-08-19 | 40 | 39.9365 | 11.8063 | 51.7428 | 4.6573 | 0.76558 | 0.38466 | 5.8075 | 11.22% | 11.94% | 8.07% | 1.1264 | 1.1356 | 1.0878
2010-08-19 | 41 | 40.1943 | 11.4514 | 51.6457 | 4.6398 | 0.76558 | 0.38394 | 5.7894 | 11.21% | 11.93% | 8.06% | 1.1262 | 1.1354 | 1.0877
2010-08-19 | 42 | 40.0583 | 11.1869 | 51.2452 | 4.5682 | 0.76558 | 0.38096 | 5.7147 | 11.15% | 11.87% | 8.018% | 1.1255 | 1.1346 | 1.0872
2010-08-19 | 43 | 37.9244 | 10.6749 | 48.5993 | 4.1086 | 0.76558 | 0.36129 | 5.2355 | 10.77% | 11.46% | 7.746% | 1.1207 | 1.1295 | 1.084
2010-08-19 | 44 | 35.5703 | 10.0564 | 45.6267 | 3.6214 | 0.76558 | 0.33919 | 4.7261 | 10.36% | 11.02% | 7.448% | 1.1156 | 1.1239 | 1.0805
2010-08-19 | 45 | 32.0838 | 9.0323 | 41.1161 | 2.9408 | 0.76558 | 0.30566 | 4.012 | 9.758% | 10.38% | 7.016% | 1.1081 | 1.1158 | 1.0755
2010-08-19 | 46 | 28.6376 | 7.9081 | 36.5457 | 2.3233 | 0.76558 | 0.27169 | 3.3606 | 9.196% | 9.784% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-08-19 | 47 | 27.7401 | 8.1393 | 35.8794 | 2.2394 | 0.76558 | 0.26673 | 3.2717 | 9.119% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-08-19 | 48 | 28.8262 | 8.6889 | 37.5151 | 2.4482 | 0.76558 | 0.27889 | 3.4927 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.11 | 1.0717
2010-08-20 | 1 | 26.7165 | 7.9629 | 34.6794 | 2.0921 | 0.76558 | 0.25781 | 3.1155 | 8.984% | 9.559% | 6.459% | 1.0987 | 1.1057 | 1.0691
2010-08-20 | 2 | 25.3862 | 7.3059 | 32.6921 | 1.8592 | 0.76558 | 0.24304 | 2.8678 | 8.772% | 9.334% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-08-20 | 3 | 24.3968 | 6.9848 | 31.3816 | 1.7131 | 0.76558 | 0.23329 | 2.712 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-08-20 | 4 | 23.9639 | 6.714 | 30.6779 | 1.6371 | 0.76558 | 0.22806 | 2.6308 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-08-20 | 5 | 23.4178 | 6.592 | 30.0097 | 1.5666 | 0.76558 | 0.2231 | 2.5553 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-08-20 | 6 | 23.0586 | 6.483 | 29.5416 | 1.5181 | 0.76558 | 0.21962 | 2.5033 | 8.474% | 9.016% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-08-20 | 7 | 22.784 | 6.3984 | 29.1824 | 1.4814 | 0.76558 | 0.21695 | 2.4639 | 8.443% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-08-20 | 8 | 22.7123 | 6.399 | 29.1113 | 1.4742 | 0.76558 | 0.21642 | 2.4562 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-08-20 | 9 | 22.9158 | 6.5979 | 29.5137 | 1.5152 | 0.76558 | 0.21941 | 2.5002 | 8.471% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-08-20 | 10 | 23.1591 | 6.7425 | 29.9016 | 1.5553 | 0.76558 | 0.22229 | 2.5432 | 8.505% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-08-20 | 11 | 24.1083 | 6.9767 | 31.0849 | 1.6809 | 0.76558 | 0.23109 | 2.6775 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2010-08-20 | 12 | 25.5029 | 7.5024 | 33.0053 | 1.895 | 0.76558 | 0.24537 | 2.9059 | 8.804% | 9.368% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-08-20 | 13 | 27.8575 | 8.8483 | 36.7057 | 2.3437 | 0.76558 | 0.27287 | 3.3822 | 9.214% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.071
2010-08-20 | 14 | 31.692 | 10.453 | 42.145 | 3.0898 | 0.76558 | 0.31331 | 4.1687 | 9.891% | 10.52% | 7.112% | 1.1098 | 1.1176 | 1.0766
2010-08-20 | 15 | 36.9242 | 12.8625 | 49.7868 | 4.3118 | 0.76558 | 0.37012 | 5.4475 | 10.94% | 11.64% | 7.867% | 1.1229 | 1.1318 | 1.0854
2010-08-20 | 16 | 38.8021 | 13.7636 | 52.5657 | 4.8066 | 0.76558 | 0.39078 | 5.963 | 11.34% | 12.07% | 8.156% | 1.128 | 1.1373 | 1.0888
2010-08-20 | 17 | 39.72 | 14.2668 | 53.9869 | 5.07 | 0.76558 | 0.40134 | 6.237 | 11.55% | 12.29% | 8.306% | 1.1306 | 1.1401 | 1.0906
2010-08-20 | 18 | 39.7348 | 14.1422 | 53.877 | 5.0494 | 0.76558 | 0.40053 | 6.2155 | 11.54% | 12.27% | 8.295% | 1.1304 | 1.1399 | 1.0905
2010-08-20 | 19 | 39.4919 | 14.1328 | 53.6247 | 5.0022 | 0.76558 | 0.39865 | 6.1665 | 11.5% | 12.24% | 8.268% | 1.1299 | 1.1394 | 1.0901
2010-08-20 | 20 | 37.983 | 13.7659 | 51.749 | 4.6584 | 0.76558 | 0.38471 | 5.8087 | 11.22% | 11.94% | 8.071% | 1.1264 | 1.1356 | 1.0878
2010-08-20 | 21 | 38.5156 | 13.1419 | 51.6575 | 4.642 | 0.76558 | 0.38403 | 5.7916 | 11.21% | 11.93% | 8.061% | 1.1263 | 1.1354 | 1.0877
2010-08-20 | 22 | 37.3802 | 12.8298 | 50.21 | 4.3855 | 0.76558 | 0.37327 | 5.5243 | 11% | 11.71% | 7.911% | 1.1236 | 1.1326 | 1.0859
2010-08-20 | 23 | 35.6132 | 12.211 | 47.8242 | 3.9786 | 0.76558 | 0.35553 | 5.0997 | 10.66% | 11.35% | 7.667% | 1.1194 | 1.128 | 1.083
2010-08-20 | 24 | 34.2043 | 11.7875 | 45.9918 | 3.6796 | 0.76558 | 0.34191 | 4.787 | 10.41% | 11.07% | 7.484% | 1.1162 | 1.1245 | 1.0809
2010-08-20 | 25 | 31.8071 | 11.0351 | 42.8422 | 3.1929 | 0.76558 | 0.31849 | 4.2769 | 9.983% | 10.62% | 7.178% | 1.1109 | 1.1188 | 1.0773
2010-08-20 | 26 | 30.1243 | 9.8515 | 39.9758 | 2.7799 | 0.76558 | 0.29718 | 3.8427 | 9.612% | 10.23% | 6.911% | 1.1063 | 1.1139 | 1.0742
2010-08-20 | 27 | 30.2273 | 9.8491 | 40.0764 | 2.7939 | 0.76558 | 0.29793 | 3.8574 | 9.625% | 10.24% | 6.92% | 1.1065 | 1.1141 | 1.0744
2010-08-20 | 28 | 30.399 | 9.7774 | 40.1764 | 2.8079 | 0.76558 | 0.29868 | 3.8721 | 9.638% | 10.25% | 6.93% | 1.1067 | 1.1143 | 1.0745
2010-08-20 | 29 | 30.0689 | 9.1531 | 39.2221 | 2.6761 | 0.76558 | 0.29158 | 3.7332 | 9.518% | 10.13% | 6.844% | 1.1052 | 1.1127 | 1.0735
2010-08-20 | 30 | 29.7229 | 8.5703 | 38.2932 | 2.5508 | 0.76558 | 0.28468 | 3.6011 | 9.404% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-08-20 | 31 | 31.3459 | 8.5463 | 39.8922 | 2.7683 | 0.76558 | 0.29656 | 3.8304 | 9.602% | 10.22% | 6.904% | 1.1062 | 1.1138 | 1.0742
2010-08-20 | 32 | 31.5775 | 8.5283 | 40.1059 | 2.798 | 0.76558 | 0.29815 | 3.8617 | 9.629% | 10.25% | 6.923% | 1.1065 | 1.1141 | 1.0744
2010-08-20 | 33 | 31.4473 | 9.1026 | 40.5499 | 2.8603 | 0.76558 | 0.30145 | 3.9273 | 9.685% | 10.31% | 6.964% | 1.1072 | 1.1149 | 1.0748
2010-08-20 | 34 | 32.0926 | 9.4596 | 41.5522 | 3.0035 | 0.76558 | 0.3089 | 4.078 | 9.814% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-08-20 | 35 | 33.1576 | 10.2807 | 43.4383 | 3.2823 | 0.76558 | 0.32293 | 4.3708 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-08-20 | 36 | 35.4828 | 11.5079 | 46.9907 | 3.8411 | 0.76558 | 0.34933 | 4.956 | 10.55% | 11.22% | 7.583% | 1.1179 | 1.1264 | 1.0821
2010-08-20 | 37 | 38.7303 | 12.5197 | 51.25 | 4.569 | 0.76558 | 0.381 | 5.7156 | 11.15% | 11.87% | 8.019% | 1.1255 | 1.1346 | 1.0872
2010-08-20 | 38 | 40.8113 | 12.8923 | 53.7035 | 5.017 | 0.76558 | 0.39924 | 6.1818 | 11.51% | 12.25% | 8.276% | 1.1301 | 1.1396 | 1.0902
2010-08-20 | 39 | 40.5408 | 12.5672 | 53.1081 | 4.9063 | 0.76558 | 0.39481 | 6.0667 | 11.42% | 12.15% | 8.213% | 1.129 | 1.1384 | 1.0895
2010-08-20 | 40 | 39.3607 | 11.9846 | 51.3453 | 4.586 | 0.76558 | 0.38171 | 5.7333 | 11.17% | 11.88% | 8.028% | 1.1257 | 1.1348 | 1.0873
2010-08-20 | 41 | 39.4477 | 11.6653 | 51.1131 | 4.5446 | 0.76558 | 0.37998 | 5.6902 | 11.13% | 11.85% | 8.004% | 1.1253 | 1.1344 | 1.087
2010-08-20 | 42 | 38.6295 | 11.1984 | 49.8279 | 4.319 | 0.76558 | 0.37043 | 5.455 | 10.95% | 11.65% | 7.871% | 1.1229 | 1.1318 | 1.0854
2010-08-20 | 43 | 36.3889 | 10.6814 | 47.0704 | 3.8542 | 0.76558 | 0.34993 | 4.9697 | 10.56% | 11.23% | 7.591% | 1.118 | 1.1266 | 1.0821
2010-08-20 | 44 | 34.3353 | 9.9871 | 44.3224 | 3.4173 | 0.76558 | 0.3295 | 4.5124 | 10.18% | 10.83% | 7.32% | 1.1133 | 1.1215 | 1.079
2010-08-20 | 45 | 30.9717 | 9.1834 | 40.1552 | 2.8049 | 0.76558 | 0.29852 | 3.869 | 9.635% | 10.25% | 6.928% | 1.1066 | 1.1142 | 1.0744
2010-08-20 | 46 | 27.8231 | 8.0761 | 35.8992 | 2.2418 | 0.76558 | 0.26688 | 3.2743 | 9.121% | 9.705% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-08-20 | 47 | 27.2735 | 8.0163 | 35.2898 | 2.1664 | 0.76558 | 0.26235 | 3.1943 | 9.052% | 9.631% | 6.508% | 1.0995 | 1.1066 | 1.0696
2010-08-20 | 48 | 28.4452 | 8.5043 | 36.9495 | 2.3749 | 0.76558 | 0.27469 | 3.4152 | 9.243% | 9.834% | 6.646% | 1.1018 | 1.1091 | 1.0712
2010-08-21 | 1 | 26.354 | 7.5825 | 33.9365 | 2.0034 | 0.76558 | 0.25229 | 3.0213 | 8.903% | 9.472% | 6.401% | 1.0977 | 1.1046 | 1.0684
2010-08-21 | 2 | 24.854 | 6.9524 | 31.8065 | 1.7598 | 0.76558 | 0.23645 | 2.7618 | 8.683% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-08-21 | 3 | 23.618 | 6.5572 | 30.1752 | 1.5839 | 0.76558 | 0.22433 | 2.5738 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2010-08-21 | 4 | 23.058 | 6.2837 | 29.3418 | 1.4976 | 0.76558 | 0.21813 | 2.4813 | 8.457% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-08-21 | 5 | 22.7277 | 6.1688 | 28.8965 | 1.4525 | 0.76558 | 0.21482 | 2.4329 | 8.419% | 8.958% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-08-21 | 6 | 22.4121 | 6.0468 | 28.4589 | 1.4089 | 0.76558 | 0.21157 | 2.386 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-08-21 | 7 | 21.8663 | 5.9784 | 27.8446 | 1.3487 | 0.76558 | 0.207 | 2.3213 | 8.337% | 8.87% | 5.994% | 1.0909 | 1.0973 | 1.0638
2010-08-21 | 8 | 21.4926 | 5.8857 | 27.3784 | 1.3039 | 0.76558 | 0.20353 | 2.273 | 8.302% | 8.834% | 5.969% | 1.0905 | 1.0969 | 1.0635
2010-08-21 | 9 | 21.5789 | 5.9957 | 27.5746 | 1.3227 | 0.76558 | 0.20499 | 2.2932 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-08-21 | 10 | 21.9951 | 6.1266 | 28.1217 | 1.3757 | 0.76558 | 0.20906 | 2.3503 | 8.358% | 8.893% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-08-21 | 11 | 22.729 | 6.323 | 29.052 | 1.4682 | 0.76558 | 0.21598 | 2.4498 | 8.432% | 8.972% | 6.063% | 1.0921 | 1.0986 | 1.0645
2010-08-21 | 12 | 23.8744 | 6.6445 | 30.5189 | 1.6202 | 0.76558 | 0.22688 | 2.6127 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-08-21 | 13 | 26.2748 | 7.6351 | 33.9099 | 2.0003 | 0.76558 | 0.25209 | 3.0179 | 8.9% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-08-21 | 14 | 29.7521 | 9.2377 | 38.9898 | 2.6445 | 0.76558 | 0.28985 | 3.6999 | 9.489% | 10.1% | 6.823% | 1.1048 | 1.1123 | 1.0732
2010-08-21 | 15 | 34.5046 | 11.6933 | 46.198 | 3.7126 | 0.76558 | 0.34344 | 4.8216 | 10.44% | 11.1% | 7.504% | 1.1165 | 1.1249 | 1.0811
2010-08-21 | 16 | 36.1975 | 12.5951 | 48.7927 | 4.1414 | 0.76558 | 0.36273 | 5.2697 | 10.8% | 11.49% | 7.765% | 1.1211 | 1.1298 | 1.0842
2010-08-21 | 17 | 37.3275 | 12.8703 | 50.1978 | 4.3833 | 0.76558 | 0.37318 | 5.5221 | 11% | 11.7% | 7.909% | 1.1236 | 1.1326 | 1.0859
2010-08-21 | 18 | 37.8858 | 12.5577 | 50.4435 | 4.4263 | 0.76558 | 0.375 | 5.5669 | 11.04% | 11.74% | 7.935% | 1.124 | 1.133 | 1.0862
2010-08-21 | 19 | 37.8562 | 12.3641 | 50.2203 | 4.3873 | 0.76558 | 0.37334 | 5.5262 | 11% | 11.71% | 7.912% | 1.1236 | 1.1326 | 1.0859
2010-08-21 | 20 | 36.4483 | 11.9331 | 48.3814 | 4.0718 | 0.76558 | 0.35967 | 5.1971 | 10.74% | 11.43% | 7.723% | 1.1203 | 1.129 | 1.0837
2010-08-21 | 21 | 37.1213 | 11.441 | 48.5623 | 4.1023 | 0.76558 | 0.36102 | 5.2289 | 10.77% | 11.46% | 7.742% | 1.1207 | 1.1294 | 1.0839
2010-08-21 | 22 | 36.0439 | 11.1377 | 47.1816 | 3.8724 | 0.76558 | 0.35075 | 4.9887 | 10.57% | 11.25% | 7.602% | 1.1182 | 1.1268 | 1.0823
2010-08-21 | 23 | 34.2882 | 10.5323 | 44.8205 | 3.4945 | 0.76558 | 0.3332 | 4.5933 | 10.25% | 10.9% | 7.368% | 1.1142 | 1.1224 | 1.0795
2010-08-21 | 24 | 32.9822 | 10.1664 | 43.1486 | 3.2387 | 0.76558 | 0.32077 | 4.325 | 10.02% | 10.67% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-08-21 | 25 | 31.0996 | 9.6525 | 40.7521 | 2.8889 | 0.76558 | 0.30296 | 3.9574 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2010-08-21 | 26 | 29.6334 | 9.1413 | 38.7748 | 2.6154 | 0.76558 | 0.28826 | 3.6692 | 9.463% | 10.07% | 6.804% | 1.1045 | 1.112 | 1.073
2010-08-21 | 27 | 29.8913 | 9.4639 | 39.3551 | 2.6942 | 0.76558 | 0.29257 | 3.7524 | 9.535% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-08-21 | 28 | 30.7512 | 9.4669 | 40.2181 | 2.8137 | 0.76558 | 0.29899 | 3.8783 | 9.643% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-08-21 | 29 | 30.7508 | 9.1943 | 39.9451 | 2.7756 | 0.76558 | 0.29696 | 3.8382 | 9.609% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-08-21 | 30 | 30.5062 | 9.0663 | 39.5724 | 2.7241 | 0.76558 | 0.29419 | 3.7838 | 9.562% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-08-21 | 31 | 32.2144 | 9.1835 | 41.3978 | 2.9812 | 0.76558 | 0.30776 | 4.0545 | 9.794% | 10.42% | 7.042% | 1.1086 | 1.1163 | 1.0758
2010-08-21 | 32 | 32.7168 | 9.3112 | 42.028 | 3.0726 | 0.76558 | 0.31244 | 4.1507 | 9.876% | 10.51% | 7.101% | 1.1096 | 1.1174 | 1.0764
2010-08-21 | 33 | 32.6306 | 9.4974 | 42.128 | 3.0873 | 0.76558 | 0.31318 | 4.166 | 9.889% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-08-21 | 34 | 32.8531 | 9.5894 | 42.4424 | 3.1335 | 0.76558 | 0.31552 | 4.2146 | 9.93% | 10.57% | 7.14% | 1.1103 | 1.1181 | 1.0769
2010-08-21 | 35 | 33.356 | 9.9601 | 43.3161 | 3.2639 | 0.76558 | 0.32202 | 4.3515 | 10.05% | 10.69% | 7.223% | 1.1117 | 1.1197 | 1.0779
2010-08-21 | 36 | 35.1226 | 10.9741 | 46.0966 | 3.6964 | 0.76558 | 0.34269 | 4.8046 | 10.42% | 11.09% | 7.494% | 1.1164 | 1.1247 | 1.081
2010-08-21 | 37 | 37.2749 | 11.6651 | 48.94 | 4.1664 | 0.76558 | 0.36383 | 5.2958 | 10.82% | 11.51% | 7.78% | 1.1213 | 1.1301 | 1.0844
2010-08-21 | 38 | 38.8387 | 11.9233 | 50.762 | 4.4824 | 0.76558 | 0.37737 | 5.6254 | 11.08% | 11.79% | 7.968% | 1.1246 | 1.1337 | 1.0866
2010-08-21 | 39 | 38.9677 | 11.6353 | 50.603 | 4.4544 | 0.76558 | 0.37619 | 5.5962 | 11.06% | 11.77% | 7.951% | 1.1243 | 1.1334 | 1.0864
2010-08-21 | 40 | 38.3465 | 11.1591 | 49.5055 | 4.2633 | 0.76558 | 0.36803 | 5.3969 | 10.9% | 11.6% | 7.838% | 1.1224 | 1.1312 | 1.085
2010-08-21 | 41 | 38.934 | 11.0121 | 49.9461 | 4.3395 | 0.76558 | 0.37131 | 5.4764 | 10.96% | 11.67% | 7.884% | 1.1231 | 1.1321 | 1.0856
2010-08-21 | 42 | 38.7028 | 10.5684 | 49.2712 | 4.223 | 0.76558 | 0.36629 | 5.3549 | 10.87% | 11.56% | 7.814% | 1.1219 | 1.1308 | 1.0848
2010-08-21 | 43 | 36.4575 | 10.0307 | 46.4882 | 3.7594 | 0.76558 | 0.3456 | 4.8706 | 10.48% | 11.15% | 7.533% | 1.117 | 1.1255 | 1.0815
2010-08-21 | 44 | 34.6901 | 9.461 | 44.1511 | 3.3909 | 0.76558 | 0.32822 | 4.4847 | 10.16% | 10.81% | 7.303% | 1.1131 | 1.1212 | 1.0788
2010-08-21 | 45 | 32.1152 | 8.6224 | 40.7376 | 2.8869 | 0.76558 | 0.30285 | 3.9553 | 9.709% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.075
2010-08-21 | 46 | 29.2415 | 7.8584 | 37.0999 | 2.3943 | 0.76558 | 0.27581 | 3.4357 | 9.261% | 9.853% | 6.658% | 1.1021 | 1.1093 | 1.0713
2010-08-21 | 47 | 28.6505 | 8.0084 | 36.6589 | 2.3377 | 0.76558 | 0.27253 | 3.3758 | 9.209% | 9.798% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-08-21 | 48 | 29.3656 | 8.5591 | 37.9247 | 2.502 | 0.76558 | 0.28194 | 3.5495 | 9.359% | 9.958% | 6.729% | 1.1033 | 1.1106 | 1.0721
2010-08-22 | 1 | 27.9412 | 7.6118 | 35.5531 | 2.1988 | 0.76558 | 0.26431 | 3.2287 | 9.081% | 9.663% | 6.529% | 1.0999 | 1.107 | 1.0699
2010-08-22 | 2 | 26.2588 | 7.0208 | 33.2797 | 1.9266 | 0.76558 | 0.24741 | 2.9396 | 8.833% | 9.398% | 6.351% | 1.0969 | 1.1037 | 1.0678
2010-08-22 | 3 | 25.1513 | 6.6519 | 31.8032 | 1.7594 | 0.76558 | 0.23643 | 2.7615 | 8.683% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-08-22 | 4 | 24.3586 | 6.3142 | 30.6728 | 1.6366 | 0.76558 | 0.22803 | 2.6302 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-08-22 | 5 | 23.7532 | 6.1752 | 29.9285 | 1.5581 | 0.76558 | 0.22249 | 2.5462 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-08-22 | 6 | 23.2343 | 6.0685 | 29.3028 | 1.4937 | 0.76558 | 0.21784 | 2.4771 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-08-22 | 7 | 22.8441 | 5.9441 | 28.7881 | 1.4417 | 0.76558 | 0.21401 | 2.4212 | 8.411% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-08-22 | 8 | 22.64 | 5.8818 | 28.5218 | 1.4151 | 0.76558 | 0.21203 | 2.3927 | 8.389% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-08-22 | 9 | 22.7547 | 6.0736 | 28.8283 | 1.4457 | 0.76558 | 0.21431 | 2.4256 | 8.414% | 8.952% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-08-22 | 10 | 22.9514 | 6.1722 | 29.1236 | 1.4755 | 0.76558 | 0.21651 | 2.4575 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-08-22 | 11 | 23.2387 | 6.2157 | 29.4544 | 1.5092 | 0.76558 | 0.21897 | 2.4937 | 8.466% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-08-22 | 12 | 23.7828 | 6.5758 | 30.3585 | 1.6032 | 0.76558 | 0.22569 | 2.5945 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2010-08-22 | 13 | 25.0008 | 7.031 | 32.0318 | 1.7848 | 0.76558 | 0.23813 | 2.7885 | 8.706% | 9.263% | 6.259% | 1.0954 | 1.1021 | 1.0668
2010-08-22 | 14 | 26.7809 | 7.6344 | 34.4153 | 2.0603 | 0.76558 | 0.25585 | 3.0818 | 8.955% | 9.528% | 6.438% | 1.0984 | 1.1053 | 1.0688
2010-08-22 | 15 | 28.8454 | 8.3778 | 37.2232 | 2.4103 | 0.76558 | 0.27672 | 3.4526 | 9.275% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2010-08-22 | 16 | 29.823 | 9.1957 | 39.0187 | 2.6484 | 0.76558 | 0.29007 | 3.704 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-08-22 | 17 | 32.232 | 10.3162 | 42.5482 | 3.1492 | 0.76558 | 0.31631 | 4.2311 | 9.944% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-08-22 | 18 | 34.3703 | 11.327 | 45.6973 | 3.6326 | 0.76558 | 0.33972 | 4.7379 | 10.37% | 11.03% | 7.455% | 1.1157 | 1.124 | 1.0806
2010-08-22 | 19 | 35.775 | 12.0095 | 47.7845 | 3.972 | 0.76558 | 0.35524 | 5.0928 | 10.66% | 11.34% | 7.663% | 1.1193 | 1.1279 | 1.083
2010-08-22 | 20 | 35.4001 | 12.2315 | 47.6316 | 3.9466 | 0.76558 | 0.3541 | 5.0663 | 10.64% | 11.32% | 7.648% | 1.119 | 1.1276 | 1.0828
2010-08-22 | 21 | 36.5202 | 12.0188 | 48.539 | 4.0984 | 0.76558 | 0.36084 | 5.2248 | 10.76% | 11.45% | 7.739% | 1.1206 | 1.1293 | 1.0839
2010-08-22 | 22 | 36.0015 | 11.5115 | 47.5131 | 3.927 | 0.76558 | 0.35322 | 5.0458 | 10.62% | 11.3% | 7.636% | 1.1188 | 1.1274 | 1.0827
2010-08-22 | 23 | 34.3607 | 10.7739 | 45.1346 | 3.5437 | 0.76558 | 0.33554 | 4.6448 | 10.29% | 10.95% | 7.399% | 1.1147 | 1.123 | 1.0799
2010-08-22 | 24 | 32.6922 | 10.1961 | 42.8883 | 3.1997 | 0.76558 | 0.31884 | 4.2841 | 9.989% | 10.63% | 7.182% | 1.111 | 1.1189 | 1.0774
2010-08-22 | 25 | 30.5803 | 9.5868 | 40.1671 | 2.8066 | 0.76558 | 0.29861 | 3.8708 | 9.637% | 10.25% | 6.929% | 1.1066 | 1.1142 | 1.0744
2010-08-22 | 26 | 28.9276 | 8.8747 | 37.8023 | 2.4858 | 0.76558 | 0.28103 | 3.5324 | 9.344% | 9.943% | 6.719% | 1.1031 | 1.1104 | 1.072
2010-08-22 | 27 | 28.6524 | 8.9173 | 37.5697 | 2.4553 | 0.76558 | 0.2793 | 3.5002 | 9.317% | 9.913% | 6.699% | 1.1027 | 1.11 | 1.0718
2010-08-22 | 28 | 28.5938 | 8.8222 | 37.416 | 2.4353 | 0.76558 | 0.27816 | 3.479 | 9.298% | 9.893% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-08-22 | 29 | 28.1177 | 8.2646 | 36.3823 | 2.3026 | 0.76558 | 0.27047 | 3.3386 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-08-22 | 30 | 27.8451 | 7.7961 | 35.6412 | 2.2097 | 0.76558 | 0.26496 | 3.2403 | 9.091% | 9.673% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-08-22 | 31 | 29.1522 | 7.6016 | 36.7537 | 2.3498 | 0.76558 | 0.27323 | 3.3886 | 9.22% | 9.81% | 6.629% | 1.1016 | 1.1088 | 1.071
2010-08-22 | 32 | 29.1974 | 7.5285 | 36.7259 | 2.3463 | 0.76558 | 0.27302 | 3.3849 | 9.217% | 9.806% | 6.627% | 1.1015 | 1.1087 | 1.071
2010-08-22 | 33 | 29.0861 | 7.9068 | 36.9929 | 2.3805 | 0.76558 | 0.27501 | 3.4211 | 9.248% | 9.84% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-08-22 | 34 | 29.6776 | 8.0331 | 37.7107 | 2.4738 | 0.76558 | 0.28035 | 3.5197 | 9.333% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-08-22 | 35 | 30.8191 | 8.9216 | 39.7406 | 2.7473 | 0.76558 | 0.29544 | 3.8083 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-08-22 | 36 | 33.7575 | 10.3548 | 44.1124 | 3.385 | 0.76558 | 0.32794 | 4.4785 | 10.15% | 10.8% | 7.3% | 1.113 | 1.1211 | 1.0787
2010-08-22 | 37 | 36.4205 | 11.3479 | 47.7684 | 3.9693 | 0.76558 | 0.35512 | 5.09 | 10.66% | 11.34% | 7.661% | 1.1193 | 1.1279 | 1.083
2010-08-22 | 38 | 38.1074 | 11.7095 | 49.8169 | 4.3171 | 0.76558 | 0.37034 | 5.453 | 10.95% | 11.65% | 7.87% | 1.1229 | 1.1318 | 1.0854
2010-08-22 | 39 | 37.7633 | 11.3932 | 49.1565 | 4.2034 | 0.76558 | 0.36544 | 5.3344 | 10.85% | 11.55% | 7.802% | 1.1217 | 1.1305 | 1.0846
2010-08-22 | 40 | 36.5993 | 10.6926 | 47.2919 | 3.8905 | 0.76558 | 0.35157 | 5.0077 | 10.59% | 11.27% | 7.613% | 1.1184 | 1.127 | 1.0824
2010-08-22 | 41 | 36.8446 | 10.4165 | 47.261 | 3.8854 | 0.76558 | 0.35134 | 5.0024 | 10.58% | 11.26% | 7.61% | 1.1184 | 1.1269 | 1.0824
2010-08-22 | 42 | 36.3258 | 9.9924 | 46.3182 | 3.732 | 0.76558 | 0.34434 | 4.8419 | 10.45% | 11.12% | 7.516% | 1.1167 | 1.1251 | 1.0813
2010-08-22 | 43 | 34.256 | 9.4294 | 43.6854 | 3.3198 | 0.76558 | 0.32476 | 4.4101 | 10.1% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-08-22 | 44 | 32.5587 | 9.0041 | 41.5629 | 3.005 | 0.76558 | 0.30898 | 4.0796 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-08-22 | 45 | 29.7717 | 8.5036 | 38.2753 | 2.5484 | 0.76558 | 0.28454 | 3.5985 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-08-22 | 46 | 27.2273 | 8.0087 | 35.2361 | 2.1598 | 0.76558 | 0.26195 | 3.1873 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-08-22 | 47 | 27.497 | 8.3408 | 35.8378 | 2.2342 | 0.76558 | 0.26642 | 3.2662 | 9.114% | 9.697% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-08-22 | 48 | 28.7609 | 8.931 | 37.692 | 2.4713 | 0.76558 | 0.28021 | 3.5171 | 9.331% | 9.928% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-08-23 | 1 | 26.8042 | 8.1338 | 34.9381 | 2.1234 | 0.76558 | 0.25973 | 3.1487 | 9.012% | 9.589% | 6.48% | 1.099 | 1.1061 | 1.0693
2010-08-23 | 2 | 24.9505 | 7.4317 | 32.3822 | 1.8241 | 0.76558 | 0.24073 | 2.8304 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-08-23 | 3 | 23.7005 | 6.9631 | 30.6636 | 1.6356 | 0.76558 | 0.22796 | 2.6292 | 8.574% | 9.123% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-08-23 | 4 | 22.6583 | 6.3457 | 29.004 | 1.4634 | 0.76558 | 0.21562 | 2.4446 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-08-23 | 5 | 21.6276 | 6.0941 | 27.7217 | 1.3368 | 0.76558 | 0.20609 | 2.3085 | 8.327% | 8.86% | 5.987% | 1.0908 | 1.0972 | 1.0637
2010-08-23 | 6 | 20.8894 | 5.7972 | 26.6865 | 1.2388 | 0.76558 | 0.19839 | 2.2028 | 8.254% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-08-23 | 7 | 20.6447 | 5.6917 | 26.3364 | 1.2066 | 0.76558 | 0.19579 | 2.1679 | 8.232% | 8.758% | 5.919% | 1.0897 | 1.096 | 1.0629
2010-08-23 | 8 | 20.3996 | 5.6241 | 26.0236 | 1.1781 | 0.76558 | 0.19346 | 2.1371 | 8.212% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-08-23 | 9 | 20.4906 | 5.6711 | 26.1617 | 1.1906 | 0.76558 | 0.19449 | 2.1507 | 8.221% | 8.747% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-08-23 | 10 | 20.5645 | 5.6492 | 26.2137 | 1.1953 | 0.76558 | 0.19488 | 2.1558 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-08-23 | 11 | 20.9654 | 5.8284 | 26.7938 | 1.2488 | 0.76558 | 0.19919 | 2.2136 | 8.262% | 8.79% | 5.94% | 1.0901 | 1.0964 | 1.0632
2010-08-23 | 12 | 21.5663 | 5.979 | 27.5453 | 1.3199 | 0.76558 | 0.20478 | 2.2902 | 8.314% | 8.846% | 5.978% | 1.0907 | 1.0971 | 1.0636
2010-08-23 | 13 | 22.3559 | 6.3027 | 28.6586 | 1.4287 | 0.76558 | 0.21305 | 2.4073 | 8.4% | 8.938% | 6.04% | 1.0917 | 1.0981 | 1.0643
2010-08-23 | 14 | 23.9206 | 6.6463 | 30.5669 | 1.6253 | 0.76558 | 0.22724 | 2.6181 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-08-23 | 15 | 25.6436 | 6.9337 | 32.5773 | 1.8461 | 0.76558 | 0.24218 | 2.8539 | 8.76% | 9.321% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-08-23 | 16 | 26.7767 | 7.7089 | 34.4856 | 2.0688 | 0.76558 | 0.25637 | 3.0907 | 8.962% | 9.536% | 6.444% | 1.0984 | 1.1054 | 1.0689
2010-08-23 | 17 | 28.3953 | 8.9409 | 37.3362 | 2.4249 | 0.76558 | 0.27756 | 3.468 | 9.289% | 9.883% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-08-23 | 18 | 30.2276 | 9.5163 | 39.7439 | 2.7477 | 0.76558 | 0.29546 | 3.8088 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-08-23 | 19 | 31.7006 | 9.9155 | 41.6161 | 3.0127 | 0.76558 | 0.30938 | 4.0877 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-08-23 | 20 | 31.7678 | 10.0637 | 41.8315 | 3.044 | 0.76558 | 0.31098 | 4.1205 | 9.85% | 10.48% | 7.082% | 1.1093 | 1.1171 | 1.0762
2010-08-23 | 21 | 33.6722 | 9.9629 | 43.6351 | 3.3121 | 0.76558 | 0.32439 | 4.4021 | 10.09% | 10.73% | 7.254% | 1.1122 | 1.1202 | 1.0782
2010-08-23 | 22 | 33.5107 | 9.7232 | 43.2339 | 3.2515 | 0.76558 | 0.32141 | 4.3385 | 10.03% | 10.68% | 7.215% | 1.1115 | 1.1195 | 1.0778
2010-08-23 | 23 | 32.2005 | 9.2294 | 41.4299 | 2.9858 | 0.76558 | 0.30799 | 4.0594 | 9.798% | 10.43% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-08-23 | 24 | 30.9634 | 9.0344 | 39.9978 | 2.783 | 0.76558 | 0.29735 | 3.8459 | 9.615% | 10.23% | 6.913% | 1.1064 | 1.114 | 1.0743
2010-08-23 | 25 | 29.0921 | 8.8084 | 37.9004 | 2.4988 | 0.76558 | 0.28176 | 3.5461 | 9.356% | 9.955% | 6.727% | 1.1032 | 1.1106 | 1.0721
2010-08-23 | 26 | 27.8981 | 8.4189 | 36.317 | 2.2943 | 0.76558 | 0.26999 | 3.3299 | 9.169% | 9.756% | 6.592% | 1.1009 | 1.1081 | 1.0706
2010-08-23 | 27 | 27.8416 | 8.5142 | 36.3558 | 2.2992 | 0.76558 | 0.27027 | 3.3351 | 9.173% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-08-23 | 28 | 27.7969 | 8.4738 | 36.2708 | 2.2885 | 0.76558 | 0.26964 | 3.3237 | 9.164% | 9.75% | 6.589% | 1.1009 | 1.108 | 1.0705
2010-08-23 | 29 | 27.0086 | 8.147 | 35.1556 | 2.1499 | 0.76558 | 0.26135 | 3.1769 | 9.037% | 9.615% | 6.497% | 1.0993 | 1.1064 | 1.0695
2010-08-23 | 30 | 26.2632 | 7.7302 | 33.9934 | 2.0101 | 0.76558 | 0.25271 | 3.0284 | 8.909% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-08-23 | 31 | 27.1737 | 7.6795 | 34.8532 | 2.1131 | 0.76558 | 0.2591 | 3.1378 | 9.003% | 9.579% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-08-23 | 32 | 27.4253 | 7.6447 | 35.07 | 2.1395 | 0.76558 | 0.26071 | 3.1658 | 9.027% | 9.605% | 6.49% | 1.0992 | 1.1063 | 1.0694
2010-08-23 | 33 | 27.2028 | 7.9332 | 35.136 | 2.1475 | 0.76558 | 0.26121 | 3.1743 | 9.034% | 9.613% | 6.496% | 1.0993 | 1.1063 | 1.0695
2010-08-23 | 34 | 27.7861 | 7.9354 | 35.7215 | 2.2197 | 0.76558 | 0.26556 | 3.2508 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-08-23 | 35 | 29.0172 | 8.8619 | 37.8791 | 2.4959 | 0.76558 | 0.2816 | 3.5431 | 9.354% | 9.952% | 6.725% | 1.1032 | 1.1105 | 1.0721
2010-08-23 | 36 | 32.1855 | 10.1203 | 42.3057 | 3.1134 | 0.76558 | 0.31451 | 4.1935 | 9.912% | 10.55% | 7.127% | 1.11 | 1.1179 | 1.0767
2010-08-23 | 37 | 35.0509 | 11.3306 | 46.3814 | 3.7422 | 0.76558 | 0.34481 | 4.8525 | 10.46% | 11.13% | 7.522% | 1.1168 | 1.1253 | 1.0813
2010-08-23 | 38 | 37.1959 | 11.6196 | 48.8155 | 4.1452 | 0.76558 | 0.3629 | 5.2737 | 10.8% | 11.49% | 7.768% | 1.1211 | 1.1299 | 1.0842
2010-08-23 | 39 | 37.0582 | 11.4339 | 48.492 | 4.0905 | 0.76558 | 0.3605 | 5.2166 | 10.76% | 11.45% | 7.735% | 1.1205 | 1.1293 | 1.0838
2010-08-23 | 40 | 36.1266 | 11.0736 | 47.2002 | 3.8755 | 0.76558 | 0.35089 | 4.9919 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-08-23 | 41 | 36.2413 | 10.6527 | 46.894 | 3.8253 | 0.76558 | 0.34862 | 4.9395 | 10.53% | 11.21% | 7.574% | 1.1177 | 1.1262 | 1.0819
2010-08-23 | 42 | 35.8979 | 10.1169 | 46.0147 | 3.6832 | 0.76558 | 0.34208 | 4.7909 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-08-23 | 43 | 34.3795 | 9.5488 | 43.9283 | 3.3568 | 0.76558 | 0.32657 | 4.4489 | 10.13% | 10.78% | 7.282% | 1.1127 | 1.1208 | 1.0785
2010-08-23 | 44 | 32.1746 | 8.8417 | 41.0163 | 2.9265 | 0.76558 | 0.30492 | 3.997 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-08-23 | 45 | 28.8592 | 7.7945 | 36.6537 | 2.3371 | 0.76558 | 0.27249 | 3.3751 | 9.208% | 9.797% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-08-23 | 46 | 26.3426 | 6.9912 | 33.3338 | 1.9329 | 0.76558 | 0.24781 | 2.9463 | 8.839% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-08-23 | 47 | 26.0096 | 7.262 | 33.2716 | 1.9257 | 0.76558 | 0.24734 | 2.9386 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-08-23 | 48 | 26.7457 | 7.7726 | 34.5183 | 2.0727 | 0.76558 | 0.25661 | 3.0949 | 8.966% | 9.54% | 6.446% | 1.0985 | 1.1055 | 1.0689
2010-08-24 | 1 | 24.6878 | 7.079 | 31.7668 | 1.7554 | 0.76558 | 0.23616 | 2.7572 | 8.679% | 9.235% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-08-24 | 2 | 23.1772 | 6.5315 | 29.7087 | 1.5353 | 0.76558 | 0.22086 | 2.5218 | 8.488% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-08-24 | 3 | 22.4684 | 6.1267 | 28.595 | 1.4224 | 0.76558 | 0.21258 | 2.4005 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-08-24 | 4 | 22.1354 | 5.9123 | 28.0477 | 1.3684 | 0.76558 | 0.20851 | 2.3425 | 8.352% | 8.887% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-08-24 | 5 | 21.6425 | 5.8524 | 27.4948 | 1.315 | 0.76558 | 0.2044 | 2.285 | 8.311% | 8.843% | 5.975% | 1.0906 | 1.097 | 1.0636
2010-08-24 | 6 | 21.381 | 5.6815 | 27.0625 | 1.274 | 0.76558 | 0.20119 | 2.2408 | 8.28% | 8.81% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-08-24 | 7 | 21.3056 | 5.68 | 26.9856 | 1.2668 | 0.76558 | 0.20061 | 2.233 | 8.275% | 8.804% | 5.949% | 1.0902 | 1.0965 | 1.0633
2010-08-24 | 8 | 21.2468 | 5.6746 | 26.9214 | 1.2608 | 0.76558 | 0.20014 | 2.2265 | 8.27% | 8.8% | 5.946% | 1.0902 | 1.0965 | 1.0632
2010-08-24 | 9 | 21.371 | 5.7456 | 27.1165 | 1.2791 | 0.76558 | 0.20159 | 2.2463 | 8.284% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-08-24 | 10 | 21.5399 | 5.9202 | 27.4601 | 1.3117 | 0.76558 | 0.20414 | 2.2814 | 8.308% | 8.84% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-08-24 | 11 | 22.0111 | 6.2304 | 28.2415 | 1.3874 | 0.76558 | 0.20995 | 2.363 | 8.367% | 8.902% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-08-24 | 12 | 22.9286 | 6.6297 | 29.5583 | 1.5198 | 0.76558 | 0.21974 | 2.5051 | 8.475% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-08-24 | 13 | 25.2103 | 7.7388 | 32.949 | 1.8885 | 0.76558 | 0.24495 | 2.899 | 8.799% | 9.362% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-08-24 | 14 | 28.9138 | 9.2358 | 38.1496 | 2.5317 | 0.76558 | 0.28361 | 3.5809 | 9.386% | 9.987% | 6.749% | 1.1036 | 1.111 | 1.0724
2010-08-24 | 15 | 33.7234 | 11.4074 | 45.1308 | 3.5431 | 0.76558 | 0.33551 | 4.6442 | 10.29% | 10.95% | 7.399% | 1.1147 | 1.123 | 1.0799
2010-08-24 | 16 | 36.1175 | 12.5222 | 48.6397 | 4.1154 | 0.76558 | 0.36159 | 5.2426 | 10.78% | 11.47% | 7.75% | 1.1208 | 1.1295 | 1.084
2010-08-24 | 17 | 37.6534 | 12.9218 | 50.5752 | 4.4495 | 0.76558 | 0.37598 | 5.591 | 11.05% | 11.76% | 7.948% | 1.1243 | 1.1333 | 1.0863
2010-08-24 | 18 | 37.9944 | 12.5656 | 50.56 | 4.4468 | 0.76558 | 0.37587 | 5.5883 | 11.05% | 11.76% | 7.947% | 1.1243 | 1.1333 | 1.0863
2010-08-24 | 19 | 37.5762 | 12.2635 | 49.8397 | 4.321 | 0.76558 | 0.37051 | 5.4571 | 10.95% | 11.65% | 7.873% | 1.123 | 1.1319 | 1.0855
2010-08-24 | 20 | 36.1952 | 11.7311 | 47.9263 | 3.9956 | 0.76558 | 0.35629 | 5.1175 | 10.68% | 11.36% | 7.677% | 1.1195 | 1.1282 | 1.0832
2010-08-24 | 21 | 36.2932 | 11.0728 | 47.366 | 3.9027 | 0.76558 | 0.35212 | 5.0204 | 10.6% | 11.28% | 7.621% | 1.1186 | 1.1271 | 1.0825
2010-08-24 | 22 | 34.8553 | 10.5197 | 45.375 | 3.5815 | 0.76558 | 0.33732 | 4.6844 | 10.32% | 10.98% | 7.423% | 1.1151 | 1.1234 | 1.0802
2010-08-24 | 23 | 33.1707 | 9.9432 | 43.1139 | 3.2335 | 0.76558 | 0.32051 | 4.3196 | 10.02% | 10.66% | 7.204% | 1.1113 | 1.1193 | 1.0776
2010-08-24 | 24 | 31.7911 | 9.5622 | 41.3533 | 2.9748 | 0.76558 | 0.30743 | 4.0478 | 9.788% | 10.41% | 7.038% | 1.1085 | 1.1163 | 1.0757
2010-08-24 | 25 | 29.7041 | 9.3137 | 39.0178 | 2.6483 | 0.76558 | 0.29006 | 3.7039 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-08-24 | 26 | 28.3944 | 8.7677 | 37.1621 | 2.4023 | 0.76558 | 0.27627 | 3.4442 | 9.268% | 9.861% | 6.664% | 1.1021 | 1.1094 | 1.0714
2010-08-24 | 27 | 28.6828 | 9.0521 | 37.7349 | 2.477 | 0.76558 | 0.28053 | 3.5231 | 9.336% | 9.934% | 6.713% | 1.103 | 1.1103 | 1.072
2010-08-24 | 28 | 28.5672 | 8.9402 | 37.5074 | 2.4472 | 0.76558 | 0.27883 | 3.4916 | 9.309% | 9.905% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-08-24 | 29 | 27.9083 | 8.4983 | 36.4065 | 2.3057 | 0.76558 | 0.27065 | 3.3419 | 9.179% | 9.767% | 6.6% | 1.1011 | 1.1082 | 1.0707
2010-08-24 | 30 | 27.1755 | 8.2184 | 35.3939 | 2.1792 | 0.76558 | 0.26312 | 3.2079 | 9.063% | 9.643% | 6.517% | 1.0997 | 1.1067 | 1.0697
2010-08-24 | 31 | 28.2426 | 8.1103 | 36.3529 | 2.2989 | 0.76558 | 0.27025 | 3.3347 | 9.173% | 9.76% | 6.595% | 1.101 | 1.1082 | 1.0706
2010-08-24 | 32 | 28.2911 | 8.246 | 36.5371 | 2.3222 | 0.76558 | 0.27162 | 3.3594 | 9.195% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2010-08-24 | 33 | 28.2268 | 8.4861 | 36.7129 | 2.3446 | 0.76558 | 0.27293 | 3.3831 | 9.215% | 9.805% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-08-24 | 34 | 28.6854 | 8.3969 | 37.0823 | 2.392 | 0.76558 | 0.27567 | 3.4333 | 9.259% | 9.851% | 6.657% | 1.102 | 1.1093 | 1.0713
2010-08-24 | 35 | 30.0916 | 9.0722 | 39.1638 | 2.6681 | 0.76558 | 0.29115 | 3.7248 | 9.511% | 10.12% | 6.838% | 1.1051 | 1.1126 | 1.0734
2010-08-24 | 36 | 33.3367 | 10.1336 | 43.4703 | 3.2872 | 0.76558 | 0.32316 | 4.3759 | 10.07% | 10.71% | 7.238% | 1.1119 | 1.12 | 1.078
2010-08-24 | 37 | 37.0544 | 11.5351 | 48.5895 | 4.107 | 0.76558 | 0.36122 | 5.2337 | 10.77% | 11.46% | 7.745% | 1.1207 | 1.1294 | 1.0839
2010-08-24 | 38 | 38.7288 | 11.9201 | 50.6489 | 4.4625 | 0.76558 | 0.37653 | 5.6046 | 11.07% | 11.77% | 7.956% | 1.1244 | 1.1334 | 1.0864
2010-08-24 | 39 | 38.7064 | 11.5272 | 50.2336 | 4.3896 | 0.76558 | 0.37344 | 5.5286 | 11.01% | 11.71% | 7.913% | 1.1237 | 1.1326 | 1.0859
2010-08-24 | 40 | 37.764 | 10.9075 | 48.6714 | 4.1208 | 0.76558 | 0.36183 | 5.2482 | 10.78% | 11.47% | 7.753% | 1.1209 | 1.1296 | 1.084
2010-08-24 | 41 | 38.0122 | 10.7143 | 48.7265 | 4.1301 | 0.76558 | 0.36224 | 5.258 | 10.79% | 11.48% | 7.759% | 1.121 | 1.1297 | 1.0841
2010-08-24 | 42 | 37.2945 | 10.1892 | 47.4837 | 3.9222 | 0.76558 | 0.353 | 5.0407 | 10.62% | 11.3% | 7.633% | 1.1188 | 1.1273 | 1.0826
2010-08-24 | 43 | 35.0393 | 9.6522 | 44.6915 | 3.4744 | 0.76558 | 0.33224 | 4.5723 | 10.23% | 10.89% | 7.356% | 1.114 | 1.1222 | 1.0794
2010-08-24 | 44 | 32.8269 | 8.905 | 41.7319 | 3.0295 | 0.76558 | 0.31024 | 4.1053 | 9.837% | 10.47% | 7.073% | 1.1091 | 1.1169 | 1.0761
2010-08-24 | 45 | 29.291 | 8.0351 | 37.3261 | 2.4236 | 0.76558 | 0.27749 | 3.4667 | 9.287% | 9.882% | 6.678% | 1.1024 | 1.1097 | 1.0716
2010-08-24 | 46 | 25.8838 | 7.0106 | 32.8945 | 1.8823 | 0.76558 | 0.24454 | 2.8924 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2010-08-24 | 47 | 24.7755 | 7.1198 | 31.8953 | 1.7697 | 0.76558 | 0.23711 | 2.7723 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-08-24 | 48 | 25.5918 | 7.474 | 33.0658 | 1.9019 | 0.76558 | 0.24582 | 2.9133 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-08-25 | 1 | 23.9376 | 6.7851 | 30.7227 | 1.6419 | 0.76558 | 0.2284 | 2.6359 | 8.58% | 9.129% | 6.169% | 1.0938 | 1.1005 | 1.0657
2010-08-25 | 2 | 22.3159 | 6.2763 | 28.5922 | 1.4221 | 0.76558 | 0.21256 | 2.4002 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-08-25 | 3 | 21.3943 | 6.0387 | 27.4329 | 1.3091 | 0.76558 | 0.20394 | 2.2786 | 8.306% | 8.838% | 5.972% | 1.0906 | 1.0969 | 1.0635
2010-08-25 | 4 | 20.5925 | 5.7915 | 26.384 | 1.2109 | 0.76558 | 0.19614 | 2.1726 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-08-25 | 5 | 19.9087 | 5.6936 | 25.6022 | 1.1402 | 0.76558 | 0.19033 | 2.0961 | 8.187% | 8.711% | 5.887% | 1.0892 | 1.0954 | 1.0625
2010-08-25 | 6 | 19.1162 | 5.5663 | 24.6824 | 1.0598 | 0.76558 | 0.18349 | 2.0088 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-08-25 | 7 | 18.8914 | 5.4586 | 24.35 | 1.0314 | 0.76558 | 0.18102 | 1.978 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-08-25 | 8 | 18.6221 | 5.408 | 24.0301 | 1.0045 | 0.76558 | 0.17864 | 1.9487 | 8.109% | 8.628% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-08-25 | 9 | 19.0586 | 5.4475 | 24.5061 | 1.0447 | 0.76558 | 0.18218 | 1.9924 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-08-25 | 10 | 19.279 | 5.5169 | 24.7958 | 1.0695 | 0.76558 | 0.18434 | 2.0194 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-08-25 | 11 | 19.7451 | 5.6869 | 25.432 | 1.1251 | 0.76558 | 0.18906 | 2.0798 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-08-25 | 12 | 20.7021 | 6.0566 | 26.7588 | 1.2456 | 0.76558 | 0.19893 | 2.2101 | 8.259% | 8.788% | 5.938% | 1.09 | 1.0963 | 1.0631
2010-08-25 | 13 | 22.7496 | 6.9411 | 29.6907 | 1.5335 | 0.76558 | 0.22072 | 2.5198 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-08-25 | 14 | 25.709 | 8.358 | 34.067 | 2.0188 | 0.76558 | 0.25326 | 3.0377 | 8.917% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2010-08-25 | 15 | 30.0527 | 10.3259 | 40.3785 | 2.8362 | 0.76558 | 0.30018 | 3.902 | 9.663% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-08-25 | 16 | 32.0085 | 11.1618 | 43.1703 | 3.2419 | 0.76558 | 0.32093 | 4.3285 | 10.03% | 10.67% | 7.209% | 1.1114 | 1.1194 | 1.0777
2010-08-25 | 17 | 33.7185 | 11.327 | 45.0455 | 3.5297 | 0.76558 | 0.33487 | 4.6302 | 10.28% | 10.94% | 7.39% | 1.1146 | 1.1228 | 1.0798
2010-08-25 | 18 | 34.8237 | 11.0375 | 45.8612 | 3.6587 | 0.76558 | 0.34094 | 4.7652 | 10.39% | 11.06% | 7.471% | 1.116 | 1.1243 | 1.0807
2010-08-25 | 19 | 35.3168 | 11.1324 | 46.4492 | 3.7531 | 0.76558 | 0.34531 | 4.864 | 10.47% | 11.14% | 7.529% | 1.117 | 1.1254 | 1.0814
2010-08-25 | 20 | 35.1492 | 10.7615 | 45.9108 | 3.6666 | 0.76558 | 0.34131 | 4.7735 | 10.4% | 11.06% | 7.476% | 1.116 | 1.1244 | 1.0808
2010-08-25 | 21 | 36.6927 | 10.422 | 47.1147 | 3.8614 | 0.76558 | 0.35026 | 4.9773 | 10.56% | 11.24% | 7.596% | 1.1181 | 1.1266 | 1.0822
2010-08-25 | 22 | 36.5082 | 10.4975 | 47.0057 | 3.8436 | 0.76558 | 0.34945 | 4.9586 | 10.55% | 11.22% | 7.585% | 1.1179 | 1.1264 | 1.0821
2010-08-25 | 23 | 34.6713 | 10.34 | 45.0113 | 3.5243 | 0.76558 | 0.33462 | 4.6245 | 10.27% | 10.93% | 7.387% | 1.1145 | 1.1227 | 1.0798
2010-08-25 | 24 | 32.9198 | 10.1831 | 43.1028 | 3.2318 | 0.76558 | 0.32043 | 4.3178 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-08-25 | 25 | 31.4403 | 9.5758 | 41.0161 | 2.9265 | 0.76558 | 0.30492 | 3.997 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-08-25 | 26 | 30.5778 | 8.7988 | 39.3766 | 2.6972 | 0.76558 | 0.29273 | 3.7555 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-08-25 | 27 | 30.6831 | 9.0234 | 39.7065 | 2.7426 | 0.76558 | 0.29518 | 3.8033 | 9.579% | 10.19% | 6.887% | 1.1059 | 1.1135 | 1.074
2010-08-25 | 28 | 30.7966 | 8.6667 | 39.4634 | 2.7091 | 0.76558 | 0.29338 | 3.768 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-08-25 | 29 | 29.9358 | 8.3192 | 38.255 | 2.5457 | 0.76558 | 0.28439 | 3.5957 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-08-25 | 30 | 29.5611 | 7.9572 | 37.5183 | 2.4486 | 0.76558 | 0.27892 | 3.4931 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.11 | 1.0717
2010-08-25 | 31 | 30.9974 | 8.0584 | 39.0559 | 2.6534 | 0.76558 | 0.29035 | 3.7094 | 9.498% | 10.11% | 6.829% | 1.1049 | 1.1124 | 1.0733
2010-08-25 | 32 | 31.3288 | 8.2645 | 39.5933 | 2.727 | 0.76558 | 0.29434 | 3.7869 | 9.564% | 10.18% | 6.877% | 1.1058 | 1.1133 | 1.0738
2010-08-25 | 33 | 31.6564 | 8.6435 | 40.2999 | 2.8252 | 0.76558 | 0.29959 | 3.8903 | 9.653% | 10.27% | 6.941% | 1.1068 | 1.1145 | 1.0746
2010-08-25 | 34 | 32.1306 | 9.0238 | 41.1544 | 2.9462 | 0.76558 | 0.30595 | 4.0178 | 9.763% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-08-25 | 35 | 32.8039 | 10.1 | 42.9038 | 3.202 | 0.76558 | 0.31895 | 4.2866 | 9.991% | 10.63% | 7.184% | 1.111 | 1.119 | 1.0774
2010-08-25 | 36 | 34.8708 | 11.0206 | 45.8914 | 3.6635 | 0.76558 | 0.34116 | 4.7702 | 10.39% | 11.06% | 7.474% | 1.116 | 1.1244 | 1.0808
2010-08-25 | 37 | 37.4827 | 11.8011 | 49.2838 | 4.2252 | 0.76558 | 0.36638 | 5.3571 | 10.87% | 11.57% | 7.815% | 1.122 | 1.1308 | 1.0848
2010-08-25 | 38 | 39.049 | 11.888 | 50.9371 | 4.5134 | 0.76558 | 0.37867 | 5.6576 | 11.11% | 11.82% | 7.986% | 1.1249 | 1.134 | 1.0868
2010-08-25 | 39 | 38.2436 | 11.5769 | 49.8205 | 4.3177 | 0.76558 | 0.37037 | 5.4536 | 10.95% | 11.65% | 7.871% | 1.1229 | 1.1318 | 1.0854
2010-08-25 | 40 | 36.9637 | 10.9871 | 47.9508 | 3.9997 | 0.76558 | 0.35647 | 5.1217 | 10.68% | 11.36% | 7.68% | 1.1196 | 1.1282 | 1.0832
2010-08-25 | 41 | 37.0361 | 10.4773 | 47.5135 | 3.9271 | 0.76558 | 0.35322 | 5.0459 | 10.62% | 11.3% | 7.636% | 1.1188 | 1.1274 | 1.0827
2010-08-25 | 42 | 36.3329 | 10.0314 | 46.3643 | 3.7394 | 0.76558 | 0.34468 | 4.8497 | 10.46% | 11.13% | 7.521% | 1.1168 | 1.1252 | 1.0813
2010-08-25 | 43 | 34.5093 | 9.5409 | 44.0502 | 3.3754 | 0.76558 | 0.32747 | 4.4685 | 10.14% | 10.79% | 7.294% | 1.1129 | 1.121 | 1.0787
2010-08-25 | 44 | 32.539 | 8.8778 | 41.4168 | 2.9839 | 0.76558 | 0.3079 | 4.0574 | 9.797% | 10.42% | 7.044% | 1.1086 | 1.1164 | 1.0758
2010-08-25 | 45 | 29.1083 | 7.8914 | 36.9997 | 2.3814 | 0.76558 | 0.27506 | 3.422 | 9.249% | 9.841% | 6.65% | 1.1019 | 1.1091 | 1.0712
2010-08-25 | 46 | 25.8477 | 7.0084 | 32.8561 | 1.8779 | 0.76558 | 0.24426 | 2.8877 | 8.789% | 9.351% | 6.319% | 1.0964 | 1.1032 | 1.0675
2010-08-25 | 47 | 25.313 | 7.1473 | 32.4603 | 1.8329 | 0.76558 | 0.24131 | 2.8398 | 8.749% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-08-25 | 48 | 26.2705 | 7.6026 | 33.8732 | 1.9959 | 0.76558 | 0.25182 | 3.0133 | 8.896% | 9.465% | 6.396% | 1.0976 | 1.1045 | 1.0683
2010-08-26 | 1 | 24.3176 | 6.7011 | 31.0186 | 1.6737 | 0.76558 | 0.2306 | 2.6699 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-08-26 | 2 | 22.6079 | 6.1729 | 28.7808 | 1.4409 | 0.76558 | 0.21396 | 2.4205 | 8.41% | 8.948% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-08-26 | 3 | 21.7038 | 5.8752 | 27.579 | 1.3231 | 0.76558 | 0.20503 | 2.2937 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-08-26 | 4 | 20.8405 | 5.6829 | 26.5233 | 1.2237 | 0.76558 | 0.19718 | 2.1865 | 8.244% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2010-08-26 | 5 | 20.3087 | 5.5399 | 25.8486 | 1.1623 | 0.76558 | 0.19216 | 2.12 | 8.202% | 8.727% | 5.897% | 1.0893 | 1.0956 | 1.0627
2010-08-26 | 6 | 19.9341 | 5.2719 | 25.2061 | 1.1052 | 0.76558 | 0.18738 | 2.0582 | 8.165% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-08-26 | 7 | 19.6042 | 5.303 | 24.9072 | 1.0792 | 0.76558 | 0.18516 | 2.0299 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2010-08-26 | 8 | 19.504 | 5.1557 | 24.6597 | 1.0578 | 0.76558 | 0.18332 | 2.0067 | 8.138% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-08-26 | 9 | 19.9065 | 5.3482 | 25.2547 | 1.1095 | 0.76558 | 0.18775 | 2.0628 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-08-26 | 10 | 20.0793 | 5.5472 | 25.6265 | 1.1424 | 0.76558 | 0.19051 | 2.0985 | 8.189% | 8.713% | 5.888% | 1.0892 | 1.0954 | 1.0626
2010-08-26 | 11 | 20.6254 | 5.5835 | 26.2089 | 1.1949 | 0.76558 | 0.19484 | 2.1553 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-08-26 | 12 | 21.4577 | 5.9482 | 27.4059 | 1.3065 | 0.76558 | 0.20374 | 2.2759 | 8.304% | 8.836% | 5.971% | 1.0906 | 1.0969 | 1.0635
2010-08-26 | 13 | 23.2283 | 6.9288 | 30.1571 | 1.582 | 0.76558 | 0.22419 | 2.5718 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-08-26 | 14 | 26.3569 | 8.6359 | 34.9928 | 2.1301 | 0.76558 | 0.26014 | 3.1558 | 9.018% | 9.596% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-08-26 | 15 | 30.8104 | 10.6248 | 41.4352 | 2.9866 | 0.76558 | 0.30803 | 4.0602 | 9.799% | 10.43% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-08-26 | 16 | 33.2255 | 11.2999 | 44.5254 | 3.4487 | 0.76558 | 0.33101 | 4.5453 | 10.21% | 10.86% | 7.34% | 1.1137 | 1.1219 | 1.0792
2010-08-26 | 17 | 34.5591 | 11.6199 | 46.179 | 3.7096 | 0.76558 | 0.3433 | 4.8185 | 10.43% | 11.1% | 7.502% | 1.1165 | 1.1249 | 1.0811
2010-08-26 | 18 | 34.886 | 11.3304 | 46.2164 | 3.7156 | 0.76558 | 0.34358 | 4.8247 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.125 | 1.0812
2010-08-26 | 19 | 34.4643 | 11.0341 | 45.4984 | 3.601 | 0.76558 | 0.33824 | 4.7049 | 10.34% | 11% | 7.435% | 1.1153 | 1.1236 | 1.0803
2010-08-26 | 20 | 33.1811 | 10.546 | 43.7272 | 3.3261 | 0.76558 | 0.32507 | 4.4168 | 10.1% | 10.75% | 7.262% | 1.1124 | 1.1204 | 1.0783
2010-08-26 | 21 | 33.3031 | 9.9675 | 43.2706 | 3.257 | 0.76558 | 0.32168 | 4.3443 | 10.04% | 10.68% | 7.219% | 1.1116 | 1.1196 | 1.0778
2010-08-26 | 22 | 31.9383 | 9.7384 | 41.6766 | 3.0215 | 0.76558 | 0.30983 | 4.0969 | 9.83% | 10.46% | 7.068% | 1.109 | 1.1168 | 1.0761
2010-08-26 | 23 | 30.5253 | 9.3782 | 39.9035 | 2.7699 | 0.76558 | 0.29665 | 3.8321 | 9.603% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-08-26 | 24 | 29.7439 | 9.1146 | 38.8585 | 2.6267 | 0.76558 | 0.28888 | 3.6811 | 9.473% | 10.08% | 6.811% | 1.1046 | 1.1121 | 1.0731
2010-08-26 | 25 | 28.3258 | 8.7355 | 37.0613 | 2.3893 | 0.76558 | 0.27552 | 3.4304 | 9.256% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-08-26 | 26 | 26.6333 | 8.4613 | 35.0946 | 2.1425 | 0.76558 | 0.2609 | 3.1689 | 9.03% | 9.608% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-08-26 | 27 | 26.6921 | 8.757 | 35.4491 | 2.186 | 0.76558 | 0.26353 | 3.2151 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-08-26 | 28 | 27.1308 | 8.8372 | 35.9679 | 2.2504 | 0.76558 | 0.26739 | 3.2834 | 9.129% | 9.713% | 6.564% | 1.1005 | 1.1076 | 1.0702
2010-08-26 | 29 | 26.7001 | 8.4414 | 35.1416 | 2.1482 | 0.76558 | 0.26125 | 3.175 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-08-26 | 30 | 26.557 | 8.1117 | 34.6687 | 2.0908 | 0.76558 | 0.25773 | 3.1141 | 8.982% | 9.557% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-08-26 | 31 | 28.2203 | 8.1595 | 36.3798 | 2.3023 | 0.76558 | 0.27045 | 3.3383 | 9.176% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-08-26 | 32 | 28.2643 | 8.0316 | 36.2958 | 2.2917 | 0.76558 | 0.26983 | 3.3271 | 9.166% | 9.753% | 6.591% | 1.1009 | 1.1081 | 1.0706
2010-08-26 | 33 | 27.7538 | 8.3911 | 36.1449 | 2.2726 | 0.76558 | 0.26871 | 3.3069 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-08-26 | 34 | 28.1702 | 8.4962 | 36.6664 | 2.3387 | 0.76558 | 0.27258 | 3.3768 | 9.21% | 9.799% | 6.622% | 1.1014 | 1.1086 | 1.0709
2010-08-26 | 35 | 28.9166 | 9.055 | 37.9716 | 2.5081 | 0.76558 | 0.28229 | 3.556 | 9.365% | 9.964% | 6.733% | 1.1033 | 1.1107 | 1.0722
2010-08-26 | 36 | 31.2628 | 9.939 | 41.2018 | 2.953 | 0.76558 | 0.3063 | 4.0249 | 9.769% | 10.39% | 7.024% | 1.1083 | 1.116 | 1.0755
2010-08-26 | 37 | 34.6526 | 11.1199 | 45.7725 | 3.6446 | 0.76558 | 0.34028 | 4.7504 | 10.38% | 11.04% | 7.462% | 1.1158 | 1.1241 | 1.0806
2010-08-26 | 38 | 37.2373 | 11.6704 | 48.9077 | 4.1609 | 0.76558 | 0.36359 | 5.2901 | 10.82% | 11.51% | 7.777% | 1.1213 | 1.1301 | 1.0843
2010-08-26 | 39 | 37.2651 | 11.4425 | 48.7076 | 4.1269 | 0.76558 | 0.3621 | 5.2546 | 10.79% | 11.48% | 7.757% | 1.1209 | 1.1297 | 1.0841
2010-08-26 | 40 | 36.9633 | 11.1169 | 48.0802 | 4.0213 | 0.76558 | 0.35743 | 5.1443 | 10.7% | 11.38% | 7.693% | 1.1198 | 1.1285 | 1.0833
2010-08-26 | 41 | 36.994 | 10.629 | 47.623 | 3.9452 | 0.76558 | 0.35404 | 5.0648 | 10.64% | 11.32% | 7.647% | 1.119 | 1.1276 | 1.0828
2010-08-26 | 42 | 36.2322 | 10.2187 | 46.4509 | 3.7534 | 0.76558 | 0.34532 | 4.8643 | 10.47% | 11.14% | 7.529% | 1.117 | 1.1254 | 1.0814
2010-08-26 | 43 | 33.9607 | 9.5097 | 43.4704 | 3.2872 | 0.76558 | 0.32316 | 4.3759 | 10.07% | 10.71% | 7.238% | 1.1119 | 1.12 | 1.078
2010-08-26 | 44 | 31.7922 | 8.8618 | 40.654 | 2.875 | 0.76558 | 0.30223 | 3.9428 | 9.699% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-08-26 | 45 | 28.5312 | 8.0726 | 36.6038 | 2.3307 | 0.76558 | 0.27212 | 3.3684 | 9.202% | 9.791% | 6.616% | 1.1013 | 1.1085 | 1.0709
2010-08-26 | 46 | 25.8037 | 7.1891 | 32.9928 | 1.8935 | 0.76558 | 0.24527 | 2.9044 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-08-26 | 47 | 25.3737 | 7.2477 | 32.6214 | 1.8511 | 0.76558 | 0.24251 | 2.8592 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1029 | 1.0673
2010-08-26 | 48 | 26.0077 | 7.5714 | 33.5791 | 1.9614 | 0.76558 | 0.24963 | 2.9766 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-08-27 | 1 | 24.3847 | 6.7065 | 31.0912 | 1.6815 | 0.76558 | 0.23114 | 2.6783 | 8.614% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-08-27 | 2 | 22.7012 | 6.1807 | 28.8819 | 1.4511 | 0.76558 | 0.21471 | 2.4314 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-08-27 | 3 | 21.7532 | 5.7977 | 27.5509 | 1.3204 | 0.76558 | 0.20482 | 2.2908 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2010-08-27 | 4 | 20.8488 | 5.4796 | 26.3284 | 1.2058 | 0.76558 | 0.19573 | 2.1671 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2010-08-27 | 5 | 20.1176 | 5.3138 | 25.4314 | 1.1251 | 0.76558 | 0.18906 | 2.0797 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-08-27 | 6 | 19.8881 | 5.2105 | 25.0986 | 1.0958 | 0.76558 | 0.18659 | 2.048 | 8.16% | 8.682% | 5.867% | 1.0888 | 1.0951 | 1.0623
2010-08-27 | 7 | 20.1016 | 5.1941 | 25.2956 | 1.1131 | 0.76558 | 0.18805 | 2.0667 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-08-27 | 8 | 19.974 | 5.18 | 25.154 | 1.1007 | 0.76558 | 0.187 | 2.0532 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2010-08-27 | 9 | 20.3906 | 5.3878 | 25.7784 | 1.156 | 0.76558 | 0.19164 | 2.1132 | 8.198% | 8.722% | 5.894% | 1.0893 | 1.0956 | 1.0626
2010-08-27 | 10 | 20.7341 | 5.4448 | 26.1789 | 1.1922 | 0.76558 | 0.19462 | 2.1524 | 8.222% | 8.748% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-08-27 | 11 | 21.1942 | 5.7173 | 26.9114 | 1.2598 | 0.76558 | 0.20006 | 2.2255 | 8.27% | 8.799% | 5.946% | 1.0902 | 1.0965 | 1.0632
2010-08-27 | 12 | 22.1133 | 6.0882 | 28.2015 | 1.3835 | 0.76558 | 0.20965 | 2.3587 | 8.364% | 8.899% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-08-27 | 13 | 24.497 | 7.0345 | 31.5314 | 1.7295 | 0.76558 | 0.23441 | 2.7295 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2010-08-27 | 14 | 27.9314 | 8.5715 | 36.5029 | 2.3179 | 0.76558 | 0.27137 | 3.3548 | 9.191% | 9.779% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-08-27 | 15 | 32.8159 | 10.6325 | 43.4484 | 3.2838 | 0.76558 | 0.323 | 4.3724 | 10.06% | 10.71% | 7.236% | 1.1119 | 1.1199 | 1.078
2010-08-27 | 16 | 35.1002 | 11.6346 | 46.7347 | 3.7994 | 0.76558 | 0.34743 | 4.9124 | 10.51% | 11.18% | 7.558% | 1.1175 | 1.1259 | 1.0818
2010-08-27 | 17 | 37.1111 | 12.0151 | 49.1262 | 4.1982 | 0.76558 | 0.36521 | 5.329 | 10.85% | 11.54% | 7.799% | 1.1217 | 1.1305 | 1.0846
2010-08-27 | 18 | 37.4538 | 12.3955 | 49.8493 | 4.3227 | 0.76558 | 0.37059 | 5.4588 | 10.95% | 11.65% | 7.874% | 1.123 | 1.1319 | 1.0855
2010-08-27 | 19 | 37.009 | 12.0361 | 49.0451 | 4.1843 | 0.76558 | 0.36461 | 5.3145 | 10.84% | 11.53% | 7.791% | 1.1215 | 1.1303 | 1.0845
2010-08-27 | 20 | 36.4057 | 11.0218 | 47.4275 | 3.9129 | 0.76558 | 0.35258 | 5.031 | 10.61% | 11.29% | 7.627% | 1.1187 | 1.1272 | 1.0826
2010-08-27 | 21 | 37.4549 | 10.2501 | 47.7051 | 3.9588 | 0.76558 | 0.35465 | 5.079 | 10.65% | 11.33% | 7.655% | 1.1192 | 1.1278 | 1.0829
2010-08-27 | 22 | 36.8109 | 10.0006 | 46.8115 | 3.8119 | 0.76558 | 0.348 | 4.9255 | 10.52% | 11.2% | 7.565% | 1.1176 | 1.1261 | 1.0818
2010-08-27 | 23 | 36.1378 | 9.681 | 45.8188 | 3.6519 | 0.76558 | 0.34062 | 4.7581 | 10.38% | 11.05% | 7.467% | 1.1159 | 1.1242 | 1.0807
2010-08-27 | 24 | 35.905 | 9.6156 | 45.5206 | 3.6045 | 0.76558 | 0.33841 | 4.7085 | 10.34% | 11.01% | 7.437% | 1.1154 | 1.1237 | 1.0803
2010-08-27 | 25 | 33.981 | 9.5028 | 43.4839 | 3.2892 | 0.76558 | 0.32326 | 4.378 | 10.07% | 10.71% | 7.239% | 1.112 | 1.12 | 1.078
2010-08-27 | 26 | 32.0709 | 8.8143 | 40.8852 | 2.9078 | 0.76558 | 0.30395 | 3.9773 | 9.728% | 10.35% | 6.994% | 1.1078 | 1.1155 | 1.0752
2010-08-27 | 27 | 31.8404 | 9.1015 | 40.942 | 2.9159 | 0.76558 | 0.30437 | 3.9858 | 9.735% | 10.36% | 7% | 1.1079 | 1.1156 | 1.0753
2010-08-27 | 28 | 32.2571 | 9.1129 | 41.37 | 2.9772 | 0.76558 | 0.30755 | 4.0503 | 9.79% | 10.42% | 7.039% | 1.1085 | 1.1163 | 1.0757
2010-08-27 | 29 | 33.0046 | 8.96 | 41.9646 | 3.0634 | 0.76558 | 0.31197 | 4.1409 | 9.868% | 10.5% | 7.095% | 1.1095 | 1.1173 | 1.0764
2010-08-27 | 30 | 32.861 | 8.6714 | 41.5323 | 3.0006 | 0.76558 | 0.30876 | 4.0749 | 9.811% | 10.44% | 7.054% | 1.1088 | 1.1166 | 1.0759
2010-08-27 | 31 | 34.714 | 8.6329 | 43.3469 | 3.2685 | 0.76558 | 0.32225 | 4.3563 | 10.05% | 10.69% | 7.226% | 1.1117 | 1.1197 | 1.0779
2010-08-27 | 32 | 34.7135 | 8.5127 | 43.2263 | 3.2503 | 0.76558 | 0.32135 | 4.3373 | 10.03% | 10.68% | 7.214% | 1.1115 | 1.1195 | 1.0778
2010-08-27 | 33 | 34.3404 | 8.8817 | 43.2221 | 3.2497 | 0.76558 | 0.32132 | 4.3366 | 10.03% | 10.68% | 7.214% | 1.1115 | 1.1195 | 1.0777
2010-08-27 | 34 | 34.0644 | 8.9203 | 42.9847 | 3.2141 | 0.76558 | 0.31955 | 4.2992 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-08-27 | 35 | 33.8063 | 9.5419 | 43.3482 | 3.2687 | 0.76558 | 0.32226 | 4.3566 | 10.05% | 10.69% | 7.226% | 1.1117 | 1.1197 | 1.0779
2010-08-27 | 36 | 35.8183 | 10.5761 | 46.3944 | 3.7443 | 0.76558 | 0.3449 | 4.8547 | 10.46% | 11.13% | 7.524% | 1.1169 | 1.1253 | 1.0814
2010-08-27 | 37 | 39.0482 | 11.6414 | 50.6896 | 4.4696 | 0.76558 | 0.37683 | 5.6121 | 11.07% | 11.78% | 7.96% | 1.1245 | 1.1335 | 1.0865
2010-08-27 | 38 | 42.9105 | 12.1623 | 55.0728 | 5.2761 | 0.76558 | 0.40942 | 6.4511 | 11.71% | 12.46% | 8.422% | 1.1327 | 1.1424 | 1.092
2010-08-27 | 39 | 43.2998 | 11.7189 | 55.0187 | 5.2657 | 0.76558 | 0.40902 | 6.4403 | 11.71% | 12.45% | 8.416% | 1.1326 | 1.1423 | 1.0919
2010-08-27 | 40 | 42.3922 | 11.1876 | 53.5798 | 4.9939 | 0.76558 | 0.39832 | 6.1578 | 11.49% | 12.23% | 8.263% | 1.1299 | 1.1393 | 1.0901
2010-08-27 | 41 | 42.8091 | 11.0241 | 53.8332 | 5.0412 | 0.76558 | 0.4002 | 6.207 | 11.53% | 12.27% | 8.29% | 1.1303 | 1.1398 | 1.0904
2010-08-27 | 42 | 42.8923 | 10.5211 | 53.4134 | 4.9629 | 0.76558 | 0.39708 | 6.1256 | 11.47% | 12.2% | 8.246% | 1.1295 | 1.139 | 1.0899
2010-08-27 | 43 | 40.986 | 9.9343 | 50.9203 | 4.5104 | 0.76558 | 0.37855 | 5.6545 | 11.1% | 11.82% | 7.984% | 1.1249 | 1.134 | 1.0868
2010-08-27 | 44 | 38.3631 | 9.1925 | 47.5556 | 3.934 | 0.76558 | 0.35353 | 5.0531 | 10.63% | 11.31% | 7.64% | 1.1189 | 1.1275 | 1.0827
2010-08-27 | 45 | 33.5007 | 8.3561 | 41.8569 | 3.0477 | 0.76558 | 0.31117 | 4.1244 | 9.854% | 10.48% | 7.085% | 1.1093 | 1.1171 | 1.0762
2010-08-27 | 46 | 29.7959 | 7.4124 | 37.2083 | 2.4083 | 0.76558 | 0.27661 | 3.4505 | 9.273% | 9.867% | 6.668% | 1.1022 | 1.1095 | 1.0714
2010-08-27 | 47 | 28.6931 | 7.3961 | 36.0891 | 2.2656 | 0.76558 | 0.26829 | 3.2995 | 9.143% | 9.728% | 6.574% | 1.1006 | 1.1078 | 1.0704
2010-08-27 | 48 | 29.6277 | 7.8034 | 37.431 | 2.4372 | 0.76558 | 0.27827 | 3.4811 | 9.3% | 9.895% | 6.687% | 1.1025 | 1.1098 | 1.0717
2010-08-28 | 1 | 27.3163 | 7.0725 | 34.3888 | 2.0572 | 0.76558 | 0.25565 | 3.0784 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2010-08-28 | 2 | 25.3181 | 6.5565 | 31.8746 | 1.7674 | 0.76558 | 0.23696 | 2.7699 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-08-28 | 3 | 23.9134 | 6.1104 | 30.0238 | 1.5681 | 0.76558 | 0.2232 | 2.5568 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-08-28 | 4 | 23.0777 | 5.8541 | 28.9318 | 1.4561 | 0.76558 | 0.21508 | 2.4367 | 8.422% | 8.961% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-08-28 | 5 | 22.2009 | 5.787 | 27.9879 | 1.3626 | 0.76558 | 0.20807 | 2.3363 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2010-08-28 | 6 | 21.9438 | 5.5954 | 27.5393 | 1.3193 | 0.76558 | 0.20473 | 2.2896 | 8.314% | 8.846% | 5.978% | 1.0907 | 1.097 | 1.0636
2010-08-28 | 7 | 21.7854 | 5.3984 | 27.1838 | 1.2854 | 0.76558 | 0.20209 | 2.2531 | 8.288% | 8.819% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-08-28 | 8 | 21.6414 | 5.3712 | 27.0126 | 1.2693 | 0.76558 | 0.20081 | 2.2357 | 8.277% | 8.806% | 5.951% | 1.0902 | 1.0966 | 1.0633
2010-08-28 | 9 | 21.9245 | 5.5541 | 27.4786 | 1.3135 | 0.76558 | 0.20428 | 2.2833 | 8.31% | 8.841% | 5.975% | 1.0906 | 1.097 | 1.0635
2010-08-28 | 10 | 21.9836 | 5.6892 | 27.6728 | 1.3321 | 0.76558 | 0.20572 | 2.3034 | 8.324% | 8.856% | 5.985% | 1.0908 | 1.0972 | 1.0637
2010-08-28 | 11 | 22.43 | 5.8656 | 28.2956 | 1.3927 | 0.76558 | 0.21035 | 2.3687 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-08-28 | 12 | 22.9339 | 6.2775 | 29.2114 | 1.4844 | 0.76558 | 0.21716 | 2.4671 | 8.446% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0647
2010-08-28 | 13 | 24.9319 | 7.1385 | 32.0703 | 1.7891 | 0.76558 | 0.23841 | 2.7931 | 8.709% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-08-28 | 14 | 27.9338 | 8.78 | 36.7138 | 2.3447 | 0.76558 | 0.27293 | 3.3832 | 9.215% | 9.805% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-08-28 | 15 | 32.5893 | 10.8555 | 43.4448 | 3.2833 | 0.76558 | 0.32297 | 4.3718 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-08-28 | 16 | 35.3879 | 11.8107 | 47.1986 | 3.8752 | 0.76558 | 0.35088 | 4.9917 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-08-28 | 17 | 36.5779 | 12.029 | 48.6068 | 4.1099 | 0.76558 | 0.36135 | 5.2368 | 10.77% | 11.46% | 7.746% | 1.1207 | 1.1295 | 1.084
2010-08-28 | 18 | 37.2398 | 11.7649 | 49.0047 | 4.1774 | 0.76558 | 0.36431 | 5.3073 | 10.83% | 11.52% | 7.787% | 1.1215 | 1.1302 | 1.0844
2010-08-28 | 19 | 37.6246 | 11.2202 | 48.8449 | 4.1502 | 0.76558 | 0.36312 | 5.2789 | 10.81% | 11.5% | 7.771% | 1.1212 | 1.1299 | 1.0843
2010-08-28 | 20 | 36.8492 | 10.6132 | 47.4624 | 3.9186 | 0.76558 | 0.35284 | 5.037 | 10.61% | 11.29% | 7.631% | 1.1187 | 1.1273 | 1.0826
2010-08-28 | 21 | 37.8551 | 10.1005 | 47.9555 | 4.0005 | 0.76558 | 0.35651 | 5.1226 | 10.68% | 11.37% | 7.68% | 1.1196 | 1.1282 | 1.0832
2010-08-28 | 22 | 37.2679 | 9.8027 | 47.0706 | 3.8542 | 0.76558 | 0.34993 | 4.9697 | 10.56% | 11.23% | 7.591% | 1.118 | 1.1266 | 1.0821
2010-08-28 | 23 | 36.3087 | 9.4779 | 45.7866 | 3.6468 | 0.76558 | 0.34038 | 4.7528 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0807
2010-08-28 | 24 | 35.8623 | 9.278 | 45.1403 | 3.5446 | 0.76558 | 0.33558 | 4.6457 | 10.29% | 10.95% | 7.4% | 1.1147 | 1.123 | 1.0799
2010-08-28 | 25 | 34.9599 | 9.5105 | 44.4704 | 3.4401 | 0.76558 | 0.3306 | 4.5363 | 10.2% | 10.85% | 7.334% | 1.1136 | 1.1218 | 1.0791
2010-08-28 | 26 | 33.6649 | 9.1641 | 42.829 | 3.1909 | 0.76558 | 0.3184 | 4.2749 | 9.981% | 10.62% | 7.176% | 1.1109 | 1.1188 | 1.0773
2010-08-28 | 27 | 33.7221 | 9.5137 | 43.2358 | 3.2518 | 0.76558 | 0.32142 | 4.3388 | 10.04% | 10.68% | 7.215% | 1.1115 | 1.1195 | 1.0778
2010-08-28 | 28 | 34.2267 | 9.3748 | 43.6015 | 3.307 | 0.76558 | 0.32414 | 4.3967 | 10.08% | 10.73% | 7.25% | 1.1121 | 1.1202 | 1.0782
2010-08-28 | 29 | 33.9821 | 8.988 | 42.9701 | 3.2119 | 0.76558 | 0.31945 | 4.297 | 10% | 10.64% | 7.19% | 1.1111 | 1.1191 | 1.0775
2010-08-28 | 30 | 34.1391 | 8.5977 | 42.7368 | 3.1772 | 0.76558 | 0.31771 | 4.2604 | 9.969% | 10.61% | 7.168% | 1.1107 | 1.1187 | 1.0772
2010-08-28 | 31 | 35.3766 | 8.7062 | 44.0828 | 3.3804 | 0.76558 | 0.32772 | 4.4737 | 10.15% | 10.8% | 7.297% | 1.1129 | 1.1211 | 1.0787
2010-08-28 | 32 | 35.6773 | 8.5366 | 44.2139 | 3.4006 | 0.76558 | 0.32869 | 4.4949 | 10.17% | 10.82% | 7.309% | 1.1132 | 1.1213 | 1.0789
2010-08-28 | 33 | 35.0462 | 8.7624 | 43.8086 | 3.3385 | 0.76558 | 0.32568 | 4.4298 | 10.11% | 10.76% | 7.27% | 1.1125 | 1.1206 | 1.0784
2010-08-28 | 34 | 35.1459 | 8.6739 | 43.8198 | 3.3402 | 0.76558 | 0.32576 | 4.4316 | 10.11% | 10.76% | 7.271% | 1.1125 | 1.1206 | 1.0784
2010-08-28 | 35 | 34.959 | 8.8217 | 43.7808 | 3.3343 | 0.76558 | 0.32547 | 4.4253 | 10.11% | 10.75% | 7.268% | 1.1124 | 1.1205 | 1.0784
2010-08-28 | 36 | 36.3096 | 9.8208 | 46.1304 | 3.7018 | 0.76558 | 0.34294 | 4.8103 | 10.43% | 11.09% | 7.497% | 1.1164 | 1.1248 | 1.0811
2010-08-28 | 37 | 37.7723 | 10.8181 | 48.5904 | 4.1071 | 0.76558 | 0.36123 | 5.2339 | 10.77% | 11.46% | 7.745% | 1.1207 | 1.1294 | 1.0839
2010-08-28 | 38 | 38.8773 | 11.4227 | 50.3 | 4.4012 | 0.76558 | 0.37394 | 5.5407 | 11.02% | 11.72% | 7.92% | 1.1238 | 1.1328 | 1.086
2010-08-28 | 39 | 38.3176 | 11.0828 | 49.4004 | 4.2452 | 0.76558 | 0.36725 | 5.378 | 10.89% | 11.58% | 7.827% | 1.1222 | 1.131 | 1.0849
2010-08-28 | 40 | 37.6125 | 10.6907 | 48.3032 | 4.0587 | 0.76558 | 0.35909 | 5.1834 | 10.73% | 11.42% | 7.716% | 1.1202 | 1.1289 | 1.0836
2010-08-28 | 41 | 38.001 | 10.3488 | 48.3498 | 4.0665 | 0.76558 | 0.35944 | 5.1916 | 10.74% | 11.42% | 7.72% | 1.1203 | 1.129 | 1.0837
2010-08-28 | 42 | 37.4866 | 9.9629 | 47.4495 | 3.9165 | 0.76558 | 0.35275 | 5.0348 | 10.61% | 11.29% | 7.629% | 1.1187 | 1.1273 | 1.0826
2010-08-28 | 43 | 35.5184 | 9.5822 | 45.1005 | 3.5383 | 0.76558 | 0.33528 | 4.6392 | 10.29% | 10.94% | 7.396% | 1.1147 | 1.1229 | 1.0799
2010-08-28 | 44 | 33.9089 | 8.9709 | 42.8798 | 3.1985 | 0.76558 | 0.31877 | 4.2828 | 9.988% | 10.63% | 7.181% | 1.111 | 1.1189 | 1.0774
2010-08-28 | 45 | 31.0513 | 8.2631 | 39.3143 | 2.6887 | 0.76558 | 0.29227 | 3.7465 | 9.53% | 10.14% | 6.852% | 1.1053 | 1.1128 | 1.0736
2010-08-28 | 46 | 28.5088 | 7.4966 | 36.0053 | 2.2551 | 0.76558 | 0.26767 | 3.2884 | 9.133% | 9.717% | 6.567% | 1.1005 | 1.1076 | 1.0703
2010-08-28 | 47 | 27.7769 | 7.4757 | 35.2526 | 2.1618 | 0.76558 | 0.26207 | 3.1895 | 9.047% | 9.626% | 6.505% | 1.0995 | 1.1065 | 1.0696
2010-08-28 | 48 | 28.5268 | 7.7583 | 36.2851 | 2.2903 | 0.76558 | 0.26975 | 3.3256 | 9.165% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0705
2010-08-29 | 1 | 26.7035 | 7.105 | 33.8085 | 1.9883 | 0.76558 | 0.25134 | 3.0052 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-08-29 | 2 | 25.3515 | 6.6645 | 32.016 | 1.7831 | 0.76558 | 0.23801 | 2.7867 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-08-29 | 3 | 24.201 | 6.1478 | 30.3489 | 1.6022 | 0.76558 | 0.22562 | 2.5934 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-08-29 | 4 | 23.4687 | 5.8042 | 29.2729 | 1.4906 | 0.76558 | 0.21762 | 2.4738 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-08-29 | 5 | 22.7649 | 5.6657 | 28.4306 | 1.4061 | 0.76558 | 0.21136 | 2.383 | 8.382% | 8.918% | 6.027% | 1.0915 | 1.0979 | 1.0641
2010-08-29 | 6 | 22.1051 | 5.5164 | 27.6215 | 1.3272 | 0.76558 | 0.20534 | 2.2981 | 8.32% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2010-08-29 | 7 | 21.8168 | 5.4073 | 27.2241 | 1.2893 | 0.76558 | 0.20239 | 2.2572 | 8.291% | 8.822% | 5.961% | 1.0904 | 1.0968 | 1.0634
2010-08-29 | 8 | 21.4422 | 5.381 | 26.8231 | 1.2516 | 0.76558 | 0.19941 | 2.2166 | 8.264% | 8.792% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-08-29 | 9 | 21.8882 | 5.4563 | 27.3445 | 1.3007 | 0.76558 | 0.20328 | 2.2696 | 8.3% | 8.831% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-08-29 | 10 | 22.348 | 5.5825 | 27.9304 | 1.357 | 0.76558 | 0.20764 | 2.3302 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-08-29 | 11 | 22.5921 | 5.6755 | 28.2676 | 1.39 | 0.76558 | 0.21014 | 2.3657 | 8.369% | 8.905% | 6.017% | 1.0913 | 1.0978 | 1.064
2010-08-29 | 12 | 23.6558 | 5.836 | 29.4918 | 1.513 | 0.76558 | 0.21925 | 2.4978 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-08-29 | 13 | 24.9195 | 6.2977 | 31.2172 | 1.6952 | 0.76558 | 0.23207 | 2.6929 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-08-29 | 14 | 26.952 | 6.9972 | 33.9492 | 2.0049 | 0.76558 | 0.25238 | 3.0229 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2010-08-29 | 15 | 28.7181 | 7.8204 | 36.5385 | 2.3224 | 0.76558 | 0.27163 | 3.3596 | 9.195% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2010-08-29 | 16 | 29.5367 | 8.8432 | 38.3799 | 2.5624 | 0.76558 | 0.28532 | 3.6133 | 9.414% | 10.02% | 6.769% | 1.1039 | 1.1113 | 1.0726
2010-08-29 | 17 | 31.0234 | 9.7158 | 40.7393 | 2.8871 | 0.76558 | 0.30286 | 3.9555 | 9.709% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.075
2010-08-29 | 18 | 32.2578 | 10.262 | 42.5198 | 3.145 | 0.76558 | 0.3161 | 4.2266 | 9.94% | 10.58% | 7.147% | 1.1104 | 1.1183 | 1.077
2010-08-29 | 19 | 33.1996 | 10.3703 | 43.57 | 3.3022 | 0.76558 | 0.3239 | 4.3917 | 10.08% | 10.72% | 7.247% | 1.1121 | 1.1201 | 1.0781
2010-08-29 | 20 | 32.8967 | 10.1715 | 43.0682 | 3.2266 | 0.76558 | 0.32017 | 4.3124 | 10.01% | 10.65% | 7.199% | 1.1113 | 1.1192 | 1.0776
2010-08-29 | 21 | 35.1094 | 10.0236 | 45.133 | 3.5434 | 0.76558 | 0.33552 | 4.6445 | 10.29% | 10.95% | 7.399% | 1.1147 | 1.123 | 1.0799
2010-08-29 | 22 | 34.7804 | 9.9032 | 44.6836 | 3.4732 | 0.76558 | 0.33218 | 4.571 | 10.23% | 10.88% | 7.355% | 1.114 | 1.1221 | 1.0794
2010-08-29 | 23 | 32.9066 | 9.449 | 42.3556 | 3.1207 | 0.76558 | 0.31488 | 4.2012 | 9.919% | 10.55% | 7.132% | 1.1101 | 1.118 | 1.0768
2010-08-29 | 24 | 31.9705 | 9.1695 | 41.14 | 2.9442 | 0.76558 | 0.30584 | 4.0156 | 9.761% | 10.39% | 7.018% | 1.1082 | 1.1159 | 1.0755
2010-08-29 | 25 | 30.1164 | 8.9094 | 39.0258 | 2.6493 | 0.76558 | 0.29012 | 3.705 | 9.494% | 10.1% | 6.826% | 1.1049 | 1.1124 | 1.0733
2010-08-29 | 26 | 28.7743 | 8.3933 | 37.1677 | 2.4031 | 0.76558 | 0.27631 | 3.445 | 9.269% | 9.862% | 6.664% | 1.1022 | 1.1094 | 1.0714
2010-08-29 | 27 | 28.6949 | 8.3849 | 37.0798 | 2.3917 | 0.76558 | 0.27566 | 3.4329 | 9.258% | 9.851% | 6.657% | 1.102 | 1.1093 | 1.0713
2010-08-29 | 28 | 28.8888 | 8.4184 | 37.3073 | 2.4211 | 0.76558 | 0.27735 | 3.4641 | 9.285% | 9.88% | 6.676% | 1.1024 | 1.1096 | 1.0715
2010-08-29 | 29 | 28.4147 | 7.9993 | 36.414 | 2.3066 | 0.76558 | 0.27071 | 3.3429 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-08-29 | 30 | 27.9631 | 7.4815 | 35.4446 | 2.1854 | 0.76558 | 0.2635 | 3.2145 | 9.069% | 9.649% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-08-29 | 31 | 28.6966 | 7.4537 | 36.1502 | 2.2733 | 0.76558 | 0.26875 | 3.3076 | 9.15% | 9.735% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-08-29 | 32 | 29.0565 | 7.4657 | 36.5222 | 2.3203 | 0.76558 | 0.27151 | 3.3574 | 9.193% | 9.781% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-08-29 | 33 | 28.8552 | 7.8838 | 36.739 | 2.348 | 0.76558 | 0.27312 | 3.3867 | 9.218% | 9.808% | 6.628% | 1.1015 | 1.1087 | 1.071
2010-08-29 | 34 | 29.9333 | 7.9749 | 37.9082 | 2.4998 | 0.76558 | 0.28181 | 3.5472 | 9.357% | 9.956% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-08-29 | 35 | 30.678 | 8.7845 | 39.4625 | 2.709 | 0.76558 | 0.29337 | 3.7679 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-08-29 | 36 | 33.1915 | 10.1112 | 43.3027 | 3.2619 | 0.76558 | 0.32192 | 4.3494 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2010-08-29 | 37 | 36.0758 | 10.9352 | 47.011 | 3.8444 | 0.76558 | 0.34949 | 4.9595 | 10.55% | 11.22% | 7.585% | 1.1179 | 1.1264 | 1.0821
2010-08-29 | 38 | 37.3392 | 11.2819 | 48.6211 | 4.1123 | 0.76558 | 0.36146 | 5.2393 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-08-29 | 39 | 36.708 | 10.9484 | 47.6564 | 3.9507 | 0.76558 | 0.35428 | 5.0706 | 10.64% | 11.32% | 7.65% | 1.1191 | 1.1277 | 1.0828
2010-08-29 | 40 | 35.516 | 10.4454 | 45.9614 | 3.6747 | 0.76558 | 0.34168 | 4.782 | 10.4% | 11.07% | 7.481% | 1.1161 | 1.1245 | 1.0809
2010-08-29 | 41 | 35.6321 | 9.7604 | 45.3925 | 3.5843 | 0.76558 | 0.33745 | 4.6873 | 10.33% | 10.99% | 7.425% | 1.1152 | 1.1234 | 1.0802
2010-08-29 | 42 | 35.1713 | 9.2975 | 44.4688 | 3.4399 | 0.76558 | 0.33059 | 4.5361 | 10.2% | 10.85% | 7.334% | 1.1136 | 1.1217 | 1.0791
2010-08-29 | 43 | 32.7447 | 8.7701 | 41.5148 | 2.9981 | 0.76558 | 0.30863 | 4.0723 | 9.809% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-08-29 | 44 | 31.0206 | 8.3714 | 39.392 | 2.6993 | 0.76558 | 0.29284 | 3.7577 | 9.539% | 10.15% | 6.859% | 1.1055 | 1.113 | 1.0736
2010-08-29 | 45 | 28.6499 | 7.8983 | 36.5482 | 2.3236 | 0.76558 | 0.2717 | 3.3609 | 9.196% | 9.784% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-08-29 | 46 | 26.3938 | 7.3078 | 33.7015 | 1.9758 | 0.76558 | 0.25054 | 2.9919 | 8.878% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-08-29 | 47 | 26.3532 | 7.3902 | 33.7434 | 1.9807 | 0.76558 | 0.25085 | 2.9971 | 8.882% | 9.45% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-08-29 | 48 | 27.4743 | 7.8417 | 35.316 | 2.1696 | 0.76558 | 0.26254 | 3.1977 | 9.055% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-08-30 | 1 | 25.4487 | 7.0616 | 32.5103 | 1.8386 | 0.76558 | 0.24169 | 2.8458 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-08-30 | 2 | 24.0421 | 6.4595 | 30.5016 | 1.6184 | 0.76558 | 0.22675 | 2.6107 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-08-30 | 3 | 22.8758 | 6.0752 | 28.951 | 1.458 | 0.76558 | 0.21523 | 2.4388 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-08-30 | 4 | 21.7867 | 5.7649 | 27.5517 | 1.3205 | 0.76558 | 0.20482 | 2.2909 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2010-08-30 | 5 | 20.9796 | 5.5611 | 26.5407 | 1.2253 | 0.76558 | 0.19731 | 2.1882 | 8.245% | 8.772% | 5.928% | 1.0899 | 1.0962 | 1.063
2010-08-30 | 6 | 20.7065 | 5.3893 | 26.0958 | 1.1846 | 0.76558 | 0.194 | 2.1442 | 8.217% | 8.742% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-08-30 | 7 | 20.5922 | 5.351 | 25.9432 | 1.1708 | 0.76558 | 0.19286 | 2.1292 | 8.207% | 8.733% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-08-30 | 8 | 20.2334 | 5.276 | 25.5094 | 1.132 | 0.76558 | 0.18964 | 2.0872 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-08-30 | 9 | 20.2047 | 5.3552 | 25.5599 | 1.1365 | 0.76558 | 0.19002 | 2.0921 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-08-30 | 10 | 20.3463 | 5.5767 | 25.923 | 1.169 | 0.76558 | 0.19271 | 2.1273 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-08-30 | 11 | 20.4767 | 5.6408 | 26.1175 | 1.1866 | 0.76558 | 0.19416 | 2.1463 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-08-30 | 12 | 20.8373 | 5.7533 | 26.5906 | 1.23 | 0.76558 | 0.19768 | 2.1932 | 8.248% | 8.776% | 5.93% | 1.0899 | 1.0962 | 1.063
2010-08-30 | 13 | 22.0432 | 6.1693 | 28.2124 | 1.3846 | 0.76558 | 0.20973 | 2.3599 | 8.365% | 8.9% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-08-30 | 14 | 23.7094 | 6.6472 | 30.3566 | 1.603 | 0.76558 | 0.22567 | 2.5943 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2010-08-30 | 15 | 25.1769 | 6.8825 | 32.0593 | 1.7879 | 0.76558 | 0.23833 | 2.7918 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-08-30 | 16 | 25.648 | 7.5588 | 33.2068 | 1.9182 | 0.76558 | 0.24686 | 2.9306 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0678
2010-08-30 | 17 | 27.3559 | 8.6873 | 36.0433 | 2.2599 | 0.76558 | 0.26795 | 3.2934 | 9.137% | 9.722% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-08-30 | 18 | 29.757 | 9.6863 | 39.4433 | 2.7063 | 0.76558 | 0.29323 | 3.7651 | 9.546% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-08-30 | 19 | 31.4951 | 10.245 | 41.7401 | 3.0307 | 0.76558 | 0.3103 | 4.1066 | 9.838% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-08-30 | 20 | 32.4713 | 10.5511 | 43.0224 | 3.2198 | 0.76558 | 0.31983 | 4.3052 | 10.01% | 10.65% | 7.195% | 1.1112 | 1.1192 | 1.0775
2010-08-30 | 21 | 34.9008 | 10.6024 | 45.5032 | 3.6018 | 0.76558 | 0.33828 | 4.7056 | 10.34% | 11% | 7.435% | 1.1153 | 1.1236 | 1.0803
2010-08-30 | 22 | 34.8734 | 10.6902 | 45.5636 | 3.6114 | 0.76558 | 0.33873 | 4.7157 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-08-30 | 23 | 33.3904 | 10.4136 | 43.804 | 3.3378 | 0.76558 | 0.32564 | 4.429 | 10.11% | 10.76% | 7.27% | 1.1125 | 1.1206 | 1.0784
2010-08-30 | 24 | 32.212 | 9.3478 | 41.5599 | 3.0046 | 0.76558 | 0.30896 | 4.0791 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-08-30 | 25 | 30.9752 | 9.5097 | 40.4849 | 2.8512 | 0.76558 | 0.30097 | 3.9177 | 9.677% | 10.3% | 6.958% | 1.1071 | 1.1148 | 1.0748
2010-08-30 | 26 | 29.4958 | 9.8647 | 39.3605 | 2.695 | 0.76558 | 0.29261 | 3.7532 | 9.535% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-08-30 | 27 | 30.1132 | 10.0312 | 40.1444 | 2.8034 | 0.76558 | 0.29844 | 3.8674 | 9.634% | 10.25% | 6.927% | 1.1066 | 1.1142 | 1.0744
2010-08-30 | 28 | 30.7745 | 9.7976 | 40.5721 | 2.8635 | 0.76558 | 0.30162 | 3.9306 | 9.688% | 10.31% | 6.966% | 1.1073 | 1.1149 | 1.0749
2010-08-30 | 29 | 31.1765 | 9.4232 | 40.5997 | 2.8673 | 0.76558 | 0.30182 | 3.9347 | 9.692% | 10.31% | 6.968% | 1.1073 | 1.115 | 1.0749
2010-08-30 | 30 | 31.8802 | 9.2769 | 41.1571 | 2.9466 | 0.76558 | 0.30597 | 4.0182 | 9.763% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-08-30 | 31 | 33.6179 | 9.2606 | 42.8785 | 3.1983 | 0.76558 | 0.31876 | 4.2826 | 9.988% | 10.63% | 7.181% | 1.111 | 1.1189 | 1.0774
2010-08-30 | 32 | 33.8498 | 8.9669 | 42.8168 | 3.1891 | 0.76558 | 0.31831 | 4.2729 | 9.98% | 10.62% | 7.175% | 1.1109 | 1.1188 | 1.0773
2010-08-30 | 33 | 33.7191 | 9.0704 | 42.7895 | 3.185 | 0.76558 | 0.3181 | 4.2687 | 9.976% | 10.61% | 7.173% | 1.1108 | 1.1187 | 1.0773
2010-08-30 | 34 | 34.1941 | 9.0504 | 43.2445 | 3.2531 | 0.76558 | 0.32148 | 4.3402 | 10.04% | 10.68% | 7.216% | 1.1116 | 1.1196 | 1.0778
2010-08-30 | 35 | 34.5586 | 9.9124 | 44.4711 | 3.4402 | 0.76558 | 0.3306 | 4.5364 | 10.2% | 10.85% | 7.334% | 1.1136 | 1.1218 | 1.0791
2010-08-30 | 36 | 36.0352 | 10.7868 | 46.822 | 3.8136 | 0.76558 | 0.34808 | 4.9273 | 10.52% | 11.2% | 7.566% | 1.1176 | 1.1261 | 1.0819
2010-08-30 | 37 | 37.9737 | 11.3228 | 49.2965 | 4.2273 | 0.76558 | 0.36648 | 5.3594 | 10.87% | 11.57% | 7.817% | 1.122 | 1.1308 | 1.0848
2010-08-30 | 38 | 38.3457 | 11.815 | 50.1607 | 4.3769 | 0.76558 | 0.3729 | 5.5153 | 11% | 11.7% | 7.906% | 1.1235 | 1.1325 | 1.0858
2010-08-30 | 39 | 37.5557 | 11.3151 | 48.8709 | 4.1547 | 0.76558 | 0.36331 | 5.2835 | 10.81% | 11.5% | 7.773% | 1.1212 | 1.13 | 1.0843
2010-08-30 | 40 | 36.7798 | 11.0516 | 47.8314 | 3.9798 | 0.76558 | 0.35558 | 5.101 | 10.66% | 11.35% | 7.668% | 1.1194 | 1.128 | 1.083
2010-08-30 | 41 | 37.0242 | 10.7258 | 47.75 | 3.9663 | 0.76558 | 0.35498 | 5.0868 | 10.65% | 11.33% | 7.66% | 1.1192 | 1.1278 | 1.0829
2010-08-30 | 42 | 36.3807 | 10.2391 | 46.6198 | 3.7807 | 0.76558 | 0.34658 | 4.8929 | 10.5% | 11.17% | 7.546% | 1.1173 | 1.1257 | 1.0816
2010-08-30 | 43 | 34.2376 | 9.3269 | 43.5645 | 3.3014 | 0.76558 | 0.32386 | 4.3909 | 10.08% | 10.72% | 7.247% | 1.1121 | 1.1201 | 1.0781
2010-08-30 | 44 | 31.8404 | 8.6651 | 40.5055 | 2.8541 | 0.76558 | 0.30112 | 3.9208 | 9.68% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-08-30 | 45 | 28.6937 | 7.75 | 36.4437 | 2.3104 | 0.76558 | 0.27093 | 3.3469 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-08-30 | 46 | 26.0808 | 7.0573 | 33.1381 | 1.9103 | 0.76558 | 0.24635 | 2.9222 | 8.818% | 9.383% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-08-30 | 47 | 25.7069 | 6.9893 | 32.6962 | 1.8596 | 0.76558 | 0.24307 | 2.8683 | 8.773% | 9.334% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-08-30 | 48 | 26.7867 | 7.4163 | 34.203 | 2.035 | 0.76558 | 0.25427 | 3.0548 | 8.932% | 9.503% | 6.422% | 1.0981 | 1.105 | 1.0686
2010-08-31 | 1 | 24.9882 | 6.764 | 31.7523 | 1.7538 | 0.76558 | 0.23605 | 2.7554 | 8.678% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-08-31 | 2 | 23.4946 | 6.1826 | 29.6771 | 1.5321 | 0.76558 | 0.22062 | 2.5183 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-08-31 | 3 | 22.1302 | 5.8372 | 27.9674 | 1.3606 | 0.76558 | 0.20791 | 2.3341 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-08-31 | 4 | 21.4261 | 5.6353 | 27.0614 | 1.2739 | 0.76558 | 0.20118 | 2.2407 | 8.28% | 8.81% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-08-31 | 5 | 20.8801 | 5.4978 | 26.3778 | 1.2104 | 0.76558 | 0.1961 | 2.172 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-08-31 | 6 | 20.6647 | 5.2617 | 25.9263 | 1.1693 | 0.76558 | 0.19274 | 2.1276 | 8.206% | 8.732% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-08-31 | 7 | 20.6357 | 5.2386 | 25.8743 | 1.1646 | 0.76558 | 0.19235 | 2.1225 | 8.203% | 8.728% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-08-31 | 8 | 20.5025 | 5.2593 | 25.7618 | 1.1545 | 0.76558 | 0.19152 | 2.1116 | 8.197% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-08-31 | 9 | 20.8761 | 5.4114 | 26.2875 | 1.2021 | 0.76558 | 0.19542 | 2.1631 | 8.229% | 8.755% | 5.916% | 1.0897 | 1.096 | 1.0629
2010-08-31 | 10 | 21.8971 | 5.6121 | 27.5092 | 1.3164 | 0.76558 | 0.20451 | 2.2865 | 8.312% | 8.844% | 5.976% | 1.0907 | 1.097 | 1.0636
2010-08-31 | 11 | 22.7319 | 5.6925 | 28.4245 | 1.4055 | 0.76558 | 0.21131 | 2.3824 | 8.381% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-08-31 | 12 | 23.8686 | 6.1764 | 30.045 | 1.5703 | 0.76558 | 0.22336 | 2.5592 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-08-31 | 13 | 26.4555 | 7.1249 | 33.5804 | 1.9616 | 0.76558 | 0.24964 | 2.9768 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-08-31 | 14 | 30.6506 | 8.7503 | 39.4009 | 2.7005 | 0.76558 | 0.29291 | 3.759 | 9.54% | 10.15% | 6.86% | 1.1055 | 1.113 | 1.0736
2010-08-31 | 15 | 35.5947 | 10.9376 | 46.5323 | 3.7665 | 0.76558 | 0.34593 | 4.878 | 10.48% | 11.15% | 7.537% | 1.1171 | 1.1255 | 1.0815
2010-08-31 | 16 | 36.8127 | 11.8126 | 48.6253 | 4.113 | 0.76558 | 0.36149 | 5.2401 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-08-31 | 17 | 38.0332 | 12.0199 | 50.053 | 4.3581 | 0.76558 | 0.3721 | 5.4958 | 10.98% | 11.68% | 7.895% | 1.1233 | 1.1323 | 1.0857
2010-08-31 | 18 | 37.9038 | 11.7426 | 49.6464 | 4.2876 | 0.76558 | 0.36908 | 5.4222 | 10.92% | 11.62% | 7.853% | 1.1226 | 1.1315 | 1.0852
2010-08-31 | 19 | 35.7341 | 11.2017 | 46.9359 | 3.8322 | 0.76558 | 0.34893 | 4.9467 | 10.54% | 11.21% | 7.578% | 1.1178 | 1.1263 | 1.082
2010-08-31 | 20 | 34.1981 | 10.5438 | 44.7418 | 3.4823 | 0.76558 | 0.33262 | 4.5805 | 10.24% | 10.89% | 7.361% | 1.1141 | 1.1222 | 1.0795
2010-08-31 | 21 | 35.2902 | 9.9583 | 45.2484 | 3.5616 | 0.76558 | 0.33638 | 4.6635 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-08-31 | 22 | 34.5158 | 9.7481 | 44.2639 | 3.4083 | 0.76558 | 0.32906 | 4.5029 | 10.17% | 10.82% | 7.314% | 1.1132 | 1.1214 | 1.0789
2010-08-31 | 23 | 32.1737 | 9.3453 | 41.519 | 2.9987 | 0.76558 | 0.30866 | 4.0729 | 9.81% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-08-31 | 24 | 31.427 | 9.4479 | 40.8749 | 2.9064 | 0.76558 | 0.30387 | 3.9758 | 9.727% | 10.35% | 6.994% | 1.1077 | 1.1154 | 1.0752
2010-08-31 | 25 | 30.349 | 9.1659 | 39.5149 | 2.7162 | 0.76558 | 0.29376 | 3.7755 | 9.555% | 10.17% | 6.87% | 1.1056 | 1.1132 | 1.0738
2010-08-31 | 26 | 29.517 | 8.7395 | 38.2565 | 2.5459 | 0.76558 | 0.2844 | 3.5959 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-08-31 | 27 | 29.4161 | 8.8339 | 38.2501 | 2.5451 | 0.76558 | 0.28436 | 3.595 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-08-31 | 28 | 29.2302 | 8.8112 | 38.0414 | 2.5174 | 0.76558 | 0.2828 | 3.5658 | 9.373% | 9.973% | 6.739% | 1.1034 | 1.1108 | 1.0723
2010-08-31 | 29 | 29.1582 | 8.4742 | 37.6325 | 2.4635 | 0.76558 | 0.27976 | 3.5089 | 9.324% | 9.921% | 6.704% | 1.1028 | 1.1101 | 1.0719
2010-08-31 | 30 | 28.8143 | 8.2342 | 37.0485 | 2.3877 | 0.76558 | 0.27542 | 3.4287 | 9.255% | 9.847% | 6.654% | 1.102 | 1.1092 | 1.0713
2010-08-31 | 31 | 29.6048 | 8.1034 | 37.7082 | 2.4735 | 0.76558 | 0.28033 | 3.5194 | 9.333% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-08-31 | 32 | 29.3144 | 8.1365 | 37.4509 | 2.4398 | 0.76558 | 0.27841 | 3.4838 | 9.302% | 9.898% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-08-31 | 33 | 29.0521 | 8.6346 | 37.6867 | 2.4707 | 0.76558 | 0.28017 | 3.5164 | 9.331% | 9.928% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-08-31 | 34 | 29.426 | 8.7537 | 38.1797 | 2.5357 | 0.76558 | 0.28383 | 3.5851 | 9.39% | 9.991% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-08-31 | 35 | 29.9426 | 9.3675 | 39.31 | 2.6881 | 0.76558 | 0.29224 | 3.7459 | 9.529% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0736
2010-08-31 | 36 | 32.9436 | 10.5878 | 43.5314 | 3.2964 | 0.76558 | 0.32362 | 4.3856 | 10.07% | 10.72% | 7.244% | 1.112 | 1.1201 | 1.0781
2010-08-31 | 37 | 37.1345 | 11.7555 | 48.89 | 4.1579 | 0.76558 | 0.36345 | 5.2869 | 10.81% | 11.51% | 7.775% | 1.1213 | 1.13 | 1.0843
2010-08-31 | 38 | 39.7932 | 12.3074 | 52.1005 | 4.7219 | 0.76558 | 0.38732 | 5.8748 | 11.28% | 12% | 8.107% | 1.1271 | 1.1363 | 1.0882
2010-08-31 | 39 | 39.9775 | 11.949 | 51.9265 | 4.6904 | 0.76558 | 0.38603 | 5.842 | 11.25% | 11.97% | 8.089% | 1.1268 | 1.136 | 1.088
2010-08-31 | 40 | 39.1889 | 11.5463 | 50.7352 | 4.4777 | 0.76558 | 0.37717 | 5.6204 | 11.08% | 11.79% | 7.965% | 1.1246 | 1.1336 | 1.0865
2010-08-31 | 41 | 38.7002 | 11.1116 | 49.8118 | 4.3162 | 0.76558 | 0.37031 | 5.4521 | 10.95% | 11.65% | 7.87% | 1.1229 | 1.1318 | 1.0854
2010-08-31 | 42 | 37.7259 | 10.5351 | 48.261 | 4.0516 | 0.76558 | 0.35878 | 5.176 | 10.72% | 11.41% | 7.711% | 1.1201 | 1.1288 | 1.0836
2010-08-31 | 43 | 35.67 | 9.8663 | 45.5363 | 3.607 | 0.76558 | 0.33852 | 4.7111 | 10.35% | 11.01% | 7.439% | 1.1154 | 1.1237 | 1.0804
2010-08-31 | 44 | 33.8598 | 9.2009 | 43.0608 | 3.2255 | 0.76558 | 0.32012 | 4.3112 | 10.01% | 10.65% | 7.199% | 1.1113 | 1.1192 | 1.0776
2010-08-31 | 45 | 30.9692 | 8.2204 | 39.1897 | 2.6716 | 0.76558 | 0.29134 | 3.7286 | 9.514% | 10.12% | 6.841% | 1.1051 | 1.1126 | 1.0734
2010-08-31 | 46 | 27.5809 | 7.223 | 34.8039 | 2.1071 | 0.76558 | 0.25874 | 3.1314 | 8.997% | 9.573% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-08-31 | 47 | 26.6786 | 7.138 | 33.8167 | 1.9893 | 0.76558 | 0.2514 | 3.0063 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-08-31 | 48 | 26.6507 | 7.4544 | 34.1051 | 2.0234 | 0.76558 | 0.25354 | 3.0425 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2010-09-01 | 1 | 25.1419 | 6.8239 | 31.9658 | 1.7775 | 0.76558 | 0.23764 | 2.7807 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-09-01 | 2 | 23.5198 | 6.2465 | 29.7663 | 1.5413 | 0.76558 | 0.22129 | 2.5282 | 8.493% | 9.037% | 6.107% | 1.0928 | 1.0993 | 1.065
2010-09-01 | 3 | 22.4672 | 5.941 | 28.4081 | 1.4038 | 0.76558 | 0.21119 | 2.3806 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-09-01 | 4 | 21.9651 | 5.7234 | 27.6885 | 1.3336 | 0.76558 | 0.20584 | 2.305 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-09-01 | 5 | 21.3605 | 5.5213 | 26.8819 | 1.2571 | 0.76558 | 0.19984 | 2.2225 | 8.268% | 8.797% | 5.944% | 1.0901 | 1.0965 | 1.0632
2010-09-01 | 6 | 21.0023 | 5.4669 | 26.4692 | 1.2188 | 0.76558 | 0.19678 | 2.1811 | 8.24% | 8.768% | 5.925% | 1.0898 | 1.0961 | 1.063
2010-09-01 | 7 | 20.4547 | 5.3465 | 25.8012 | 1.158 | 0.76558 | 0.19181 | 2.1154 | 8.199% | 8.724% | 5.895% | 1.0893 | 1.0956 | 1.0626
2010-09-01 | 8 | 19.8647 | 5.2789 | 25.1436 | 1.0997 | 0.76558 | 0.18692 | 2.0522 | 8.162% | 8.684% | 5.869% | 1.0889 | 1.0951 | 1.0623
2010-09-01 | 9 | 20.0664 | 5.4225 | 25.4889 | 1.1302 | 0.76558 | 0.18949 | 2.0852 | 8.181% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-09-01 | 10 | 20.4545 | 5.577 | 26.0315 | 1.1788 | 0.76558 | 0.19352 | 2.1379 | 8.213% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-09-01 | 11 | 21.0876 | 5.681 | 26.7687 | 1.2465 | 0.76558 | 0.199 | 2.2111 | 8.26% | 8.789% | 5.939% | 1.09 | 1.0964 | 1.0631
2010-09-01 | 12 | 21.7791 | 6.1892 | 27.9683 | 1.3607 | 0.76558 | 0.20792 | 2.3342 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-09-01 | 13 | 23.9345 | 7.1029 | 31.0374 | 1.6757 | 0.76558 | 0.23074 | 2.672 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-09-01 | 14 | 27.1385 | 8.7193 | 35.8578 | 2.2367 | 0.76558 | 0.26657 | 3.2688 | 9.116% | 9.699% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-09-01 | 15 | 31.5067 | 10.805 | 42.3117 | 3.1143 | 0.76558 | 0.31455 | 4.1944 | 9.913% | 10.55% | 7.128% | 1.11 | 1.1179 | 1.0767
2010-09-01 | 16 | 33.7043 | 11.9146 | 45.6189 | 3.6201 | 0.76558 | 0.33914 | 4.7248 | 10.36% | 11.02% | 7.447% | 1.1155 | 1.1238 | 1.0805
2010-09-01 | 17 | 35.4697 | 12.4005 | 47.8703 | 3.9863 | 0.76558 | 0.35587 | 5.1077 | 10.67% | 11.35% | 7.672% | 1.1194 | 1.1281 | 1.0831
2010-09-01 | 18 | 36.3182 | 12.308 | 48.6262 | 4.1132 | 0.76558 | 0.36149 | 5.2402 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-09-01 | 19 | 36.4752 | 11.8962 | 48.3714 | 4.0702 | 0.76558 | 0.3596 | 5.1953 | 10.74% | 11.43% | 7.722% | 1.1203 | 1.129 | 1.0837
2010-09-01 | 20 | 35.3689 | 11.408 | 46.7769 | 3.8062 | 0.76558 | 0.34774 | 4.9196 | 10.52% | 11.19% | 7.562% | 1.1175 | 1.126 | 1.0818
2010-09-01 | 21 | 36.4754 | 10.7325 | 47.208 | 3.8767 | 0.76558 | 0.35095 | 4.9933 | 10.58% | 11.25% | 7.605% | 1.1183 | 1.1268 | 1.0823
2010-09-01 | 22 | 36.4891 | 10.4752 | 46.9643 | 3.8368 | 0.76558 | 0.34914 | 4.9515 | 10.54% | 11.22% | 7.581% | 1.1179 | 1.1264 | 1.082
2010-09-01 | 23 | 36.5457 | 10.6562 | 47.2018 | 3.8757 | 0.76558 | 0.3509 | 4.9922 | 10.58% | 11.25% | 7.604% | 1.1183 | 1.1268 | 1.0823
2010-09-01 | 24 | 36.5755 | 10.8242 | 47.3997 | 3.9083 | 0.76558 | 0.35238 | 5.0262 | 10.6% | 11.28% | 7.624% | 1.1186 | 1.1272 | 1.0825
2010-09-01 | 25 | 35.2684 | 10.6494 | 45.9178 | 3.6677 | 0.76558 | 0.34136 | 4.7747 | 10.4% | 11.06% | 7.476% | 1.1161 | 1.1244 | 1.0808
2010-09-01 | 26 | 33.026 | 10.1635 | 43.1894 | 3.2448 | 0.76558 | 0.32108 | 4.3315 | 10.03% | 10.67% | 7.211% | 1.1115 | 1.1195 | 1.0777
2010-09-01 | 27 | 34.1192 | 10.1153 | 44.2345 | 3.4037 | 0.76558 | 0.32884 | 4.4982 | 10.17% | 10.82% | 7.311% | 1.1132 | 1.1213 | 1.0789
2010-09-01 | 28 | 34.6509 | 10.7009 | 45.3518 | 3.5779 | 0.76558 | 0.33715 | 4.6806 | 10.32% | 10.98% | 7.421% | 1.1151 | 1.1234 | 1.0802
2010-09-01 | 29 | 34.3762 | 10.5194 | 44.8957 | 3.5063 | 0.76558 | 0.33376 | 4.6056 | 10.26% | 10.91% | 7.376% | 1.1143 | 1.1225 | 1.0796
2010-09-01 | 30 | 34.4343 | 10.105 | 44.5393 | 3.4508 | 0.76558 | 0.33111 | 4.5475 | 10.21% | 10.86% | 7.341% | 1.1137 | 1.1219 | 1.0792
2010-09-01 | 31 | 36.6198 | 10.2557 | 46.8755 | 3.8223 | 0.76558 | 0.34848 | 4.9364 | 10.53% | 11.2% | 7.572% | 1.1177 | 1.1262 | 1.0819
2010-09-01 | 32 | 37.9975 | 10.6313 | 48.6288 | 4.1136 | 0.76558 | 0.36151 | 5.2407 | 10.78% | 11.47% | 7.749% | 1.1208 | 1.1295 | 1.084
2010-09-01 | 33 | 37.7538 | 11.1474 | 48.9013 | 4.1598 | 0.76558 | 0.36354 | 5.2889 | 10.82% | 11.51% | 7.776% | 1.1213 | 1.13 | 1.0843
2010-09-01 | 34 | 37.5241 | 10.8023 | 48.3264 | 4.0626 | 0.76558 | 0.35926 | 5.1874 | 10.73% | 11.42% | 7.718% | 1.1202 | 1.1289 | 1.0836
2010-09-01 | 35 | 37.08 | 11.1702 | 48.2502 | 4.0498 | 0.76558 | 0.3587 | 5.1741 | 10.72% | 11.41% | 7.71% | 1.1201 | 1.1288 | 1.0835
2010-09-01 | 36 | 38.1696 | 12.2881 | 50.4577 | 4.4288 | 0.76558 | 0.37511 | 5.5695 | 11.04% | 11.74% | 7.936% | 1.1241 | 1.1331 | 1.0862
2010-09-01 | 37 | 41.2581 | 12.9609 | 54.219 | 5.1137 | 0.76558 | 0.40307 | 6.2824 | 11.59% | 12.33% | 8.331% | 1.1311 | 1.1406 | 1.0909
2010-09-01 | 38 | 42.1584 | 12.5419 | 54.7003 | 5.2049 | 0.76558 | 0.40665 | 6.3771 | 11.66% | 12.4% | 8.382% | 1.132 | 1.1416 | 1.0915
2010-09-01 | 39 | 44.5606 | 12.8252 | 57.3858 | 5.7285 | 0.76558 | 0.42661 | 6.9207 | 12.06% | 12.83% | 8.671% | 1.1371 | 1.1472 | 1.0949
2010-09-01 | 40 | 45.1607 | 12.9325 | 58.0932 | 5.8706 | 0.76558 | 0.43187 | 7.0681 | 12.17% | 12.95% | 8.748% | 1.1385 | 1.1487 | 1.0959
2010-09-01 | 41 | 45.4191 | 12.2837 | 57.7028 | 5.792 | 0.76558 | 0.42897 | 6.9865 | 12.11% | 12.88% | 8.706% | 1.1378 | 1.1479 | 1.0954
2010-09-01 | 42 | 44.4591 | 11.7216 | 56.1807 | 5.4905 | 0.76558 | 0.41765 | 6.6737 | 11.88% | 12.64% | 8.541% | 1.1348 | 1.1447 | 1.0934
2010-09-01 | 43 | 42.2897 | 10.8632 | 53.153 | 4.9146 | 0.76558 | 0.39515 | 6.0753 | 11.43% | 12.16% | 8.218% | 1.129 | 1.1385 | 1.0895
2010-09-01 | 44 | 40.3816 | 10.0525 | 50.4341 | 4.4247 | 0.76558 | 0.37493 | 5.5652 | 11.03% | 11.74% | 7.934% | 1.124 | 1.133 | 1.0862
2010-09-01 | 45 | 36.6038 | 8.9427 | 45.5465 | 3.6087 | 0.76558 | 0.3386 | 4.7128 | 10.35% | 11.01% | 7.44% | 1.1154 | 1.1237 | 1.0804
2010-09-01 | 46 | 33.1274 | 7.8914 | 41.0188 | 2.9269 | 0.76558 | 0.30494 | 3.9974 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-09-01 | 47 | 32.5115 | 7.7023 | 40.2138 | 2.8131 | 0.76558 | 0.29895 | 3.8776 | 9.643% | 10.26% | 6.933% | 1.1067 | 1.1143 | 1.0745
2010-09-01 | 48 | 33.4726 | 8.1218 | 41.5944 | 3.0096 | 0.76558 | 0.30922 | 4.0844 | 9.82% | 10.45% | 7.06% | 1.1089 | 1.1167 | 1.076
2010-09-02 | 1 | 31.5492 | 7.3792 | 38.9284 | 2.6361 | 0.76558 | 0.2894 | 3.6911 | 9.482% | 10.09% | 6.817% | 1.1048 | 1.1122 | 1.0732
2010-09-02 | 2 | 29.8098 | 6.8464 | 36.6561 | 2.3374 | 0.76558 | 0.27251 | 3.3755 | 9.208% | 9.798% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-09-02 | 3 | 28.6616 | 6.4924 | 35.1539 | 2.1497 | 0.76558 | 0.26134 | 3.1766 | 9.036% | 9.615% | 6.497% | 1.0993 | 1.1064 | 1.0695
2010-09-02 | 4 | 27.7156 | 6.2978 | 34.0134 | 2.0125 | 0.76558 | 0.25286 | 3.0309 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2010-09-02 | 5 | 27.0697 | 6.0865 | 33.1562 | 1.9123 | 0.76558 | 0.24649 | 2.9244 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-09-02 | 6 | 26.7934 | 6.0903 | 32.8837 | 1.881 | 0.76558 | 0.24446 | 2.8911 | 8.792% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-09-02 | 7 | 26.5475 | 6.1019 | 32.6494 | 1.8543 | 0.76558 | 0.24272 | 2.8626 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-09-02 | 8 | 26.1721 | 6.1439 | 32.316 | 1.8166 | 0.76558 | 0.24024 | 2.8225 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2010-09-02 | 9 | 26.6782 | 6.1454 | 32.8236 | 1.8742 | 0.76558 | 0.24401 | 2.8838 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-09-02 | 10 | 26.7649 | 6.2946 | 33.0595 | 1.9012 | 0.76558 | 0.24577 | 2.9125 | 8.81% | 9.374% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-09-02 | 11 | 27.198 | 6.5364 | 33.7344 | 1.9796 | 0.76558 | 0.25079 | 2.996 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1044 | 1.0682
2010-09-02 | 12 | 26.7369 | 6.826 | 33.5629 | 1.9595 | 0.76558 | 0.24951 | 2.9746 | 8.863% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-09-02 | 13 | 27.7145 | 7.8756 | 35.5901 | 2.2034 | 0.76558 | 0.26458 | 3.2336 | 9.086% | 9.667% | 6.533% | 1.0999 | 1.107 | 1.0699
2010-09-02 | 14 | 31.4201 | 9.5682 | 40.9883 | 2.9225 | 0.76558 | 0.30471 | 3.9928 | 9.741% | 10.36% | 7.004% | 1.1079 | 1.1156 | 1.0753
2010-09-02 | 15 | 36.8071 | 11.8469 | 48.654 | 4.1179 | 0.76558 | 0.3617 | 5.2451 | 10.78% | 11.47% | 7.751% | 1.1208 | 1.1296 | 1.084
2010-09-02 | 16 | 39.5204 | 12.7855 | 52.3059 | 4.7592 | 0.76558 | 0.38885 | 5.9137 | 11.31% | 12.03% | 8.129% | 1.1275 | 1.1367 | 1.0885
2010-09-02 | 17 | 40.0354 | 13.1366 | 53.172 | 4.9181 | 0.76558 | 0.39529 | 6.079 | 11.43% | 12.16% | 8.22% | 1.1291 | 1.1385 | 1.0896
2010-09-02 | 18 | 36.0853 | 11.8294 | 47.9147 | 3.9937 | 0.76558 | 0.3562 | 5.1154 | 10.68% | 11.36% | 7.676% | 1.1195 | 1.1282 | 1.0831
2010-09-02 | 19 | 38.6129 | 12.9785 | 51.5913 | 4.6301 | 0.76558 | 0.38354 | 5.7792 | 11.2% | 11.92% | 8.054% | 1.1261 | 1.1353 | 1.0876
2010-09-02 | 20 | 40.8701 | 13.5467 | 54.4168 | 5.1511 | 0.76558 | 0.40454 | 6.3212 | 11.62% | 12.36% | 8.352% | 1.1314 | 1.141 | 1.0911
2010-09-02 | 21 | 41.2286 | 12.6618 | 53.8903 | 5.0519 | 0.76558 | 0.40063 | 6.2181 | 11.54% | 12.28% | 8.296% | 1.1304 | 1.14 | 1.0905
2010-09-02 | 22 | 39.9044 | 12.2942 | 52.1987 | 4.7397 | 0.76558 | 0.38805 | 5.8934 | 11.29% | 12.01% | 8.118% | 1.1273 | 1.1365 | 1.0883
2010-09-02 | 23 | 37.3978 | 11.2852 | 48.683 | 4.1228 | 0.76558 | 0.36192 | 5.2503 | 10.78% | 11.47% | 7.754% | 1.1209 | 1.1296 | 1.0841
2010-09-02 | 24 | 35.5419 | 10.6267 | 46.1686 | 3.7079 | 0.76558 | 0.34322 | 4.8167 | 10.43% | 11.1% | 7.501% | 1.1165 | 1.1249 | 1.0811
2010-09-02 | 25 | 33.5328 | 10.368 | 43.9008 | 3.3526 | 0.76558 | 0.32636 | 4.4445 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-09-02 | 26 | 31.8502 | 9.6246 | 41.4748 | 2.9923 | 0.76558 | 0.30833 | 4.0662 | 9.804% | 10.43% | 7.049% | 1.1087 | 1.1165 | 1.0758
2010-09-02 | 27 | 31.8232 | 9.5277 | 41.3509 | 2.9744 | 0.76558 | 0.30741 | 4.0474 | 9.788% | 10.41% | 7.038% | 1.1085 | 1.1163 | 1.0757
2010-09-02 | 28 | 31.4802 | 9.51 | 40.9902 | 2.9228 | 0.76558 | 0.30473 | 3.9931 | 9.742% | 10.36% | 7.004% | 1.1079 | 1.1156 | 1.0753
2010-09-02 | 29 | 30.6739 | 8.9982 | 39.6722 | 2.7378 | 0.76558 | 0.29493 | 3.7983 | 9.574% | 10.19% | 6.884% | 1.1059 | 1.1134 | 1.0739
2010-09-02 | 30 | 29.7981 | 8.7727 | 38.5707 | 2.5879 | 0.76558 | 0.28674 | 3.6402 | 9.438% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-09-02 | 31 | 31.4236 | 8.8638 | 40.2873 | 2.8234 | 0.76558 | 0.2995 | 3.8885 | 9.652% | 10.27% | 6.94% | 1.1068 | 1.1144 | 1.0746
2010-09-02 | 32 | 32.4415 | 8.7942 | 41.2357 | 2.9579 | 0.76558 | 0.30655 | 4.03 | 9.773% | 10.4% | 7.027% | 1.1083 | 1.1161 | 1.0756
2010-09-02 | 33 | 33.3168 | 9.1151 | 42.4319 | 3.132 | 0.76558 | 0.31544 | 4.213 | 9.929% | 10.56% | 7.139% | 1.1102 | 1.1181 | 1.0769
2010-09-02 | 34 | 35.872 | 9.4183 | 45.2903 | 3.5682 | 0.76558 | 0.33669 | 4.6704 | 10.31% | 10.97% | 7.414% | 1.115 | 1.1232 | 1.0801
2010-09-02 | 35 | 38.0592 | 10.4631 | 48.5222 | 4.0956 | 0.76558 | 0.36072 | 5.2219 | 10.76% | 11.45% | 7.738% | 1.1206 | 1.1293 | 1.0839
2010-09-02 | 36 | 40.1699 | 11.5294 | 51.6993 | 4.6495 | 0.76558 | 0.38434 | 5.7994 | 11.22% | 11.94% | 8.065% | 1.1263 | 1.1355 | 1.0877
2010-09-02 | 37 | 41.577 | 11.9137 | 53.4907 | 4.9773 | 0.76558 | 0.39766 | 6.1405 | 11.48% | 12.21% | 8.254% | 1.1297 | 1.1391 | 1.09
2010-09-02 | 38 | 40.9008 | 11.1846 | 52.0854 | 4.7192 | 0.76558 | 0.38721 | 5.872 | 11.27% | 12% | 8.106% | 1.1271 | 1.1363 | 1.0882
2010-09-02 | 39 | 41.8458 | 11.5192 | 53.365 | 4.9539 | 0.76558 | 0.39672 | 6.1162 | 11.46% | 12.19% | 8.241% | 1.1294 | 1.1389 | 1.0898
2010-09-02 | 40 | 46.1546 | 13.223 | 59.3776 | 6.1331 | 0.76558 | 0.44142 | 7.3401 | 12.36% | 13.15% | 8.888% | 1.1411 | 1.1514 | 1.0976
2010-09-02 | 41 | 45.6512 | 12.2478 | 57.899 | 5.8315 | 0.76558 | 0.43043 | 7.0275 | 12.14% | 12.91% | 8.727% | 1.1381 | 1.1483 | 1.0956
2010-09-02 | 42 | 44.7047 | 11.5793 | 56.284 | 5.5107 | 0.76558 | 0.41842 | 6.6947 | 11.89% | 12.66% | 8.552% | 1.135 | 1.1449 | 1.0935
2010-09-02 | 43 | 42.5216 | 10.9173 | 53.4389 | 4.9676 | 0.76558 | 0.39727 | 6.1305 | 11.47% | 12.21% | 8.248% | 1.1296 | 1.139 | 1.0899
2010-09-02 | 44 | 40.3515 | 10.0921 | 50.4436 | 4.4264 | 0.76558 | 0.375 | 5.5669 | 11.04% | 11.74% | 7.935% | 1.124 | 1.133 | 1.0862
2010-09-02 | 45 | 36.5743 | 8.9611 | 45.5353 | 3.6069 | 0.76558 | 0.33852 | 4.711 | 10.35% | 11.01% | 7.439% | 1.1154 | 1.1237 | 1.0804
2010-09-02 | 46 | 33.1985 | 7.8646 | 41.0631 | 2.9332 | 0.76558 | 0.30527 | 4.004 | 9.751% | 10.37% | 7.011% | 1.108 | 1.1158 | 1.0754
2010-09-02 | 47 | 32.5262 | 7.8575 | 40.3837 | 2.8369 | 0.76558 | 0.30022 | 3.9027 | 9.664% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-09-02 | 48 | 33.1759 | 8.2005 | 41.3764 | 2.9781 | 0.76558 | 0.3076 | 4.0513 | 9.791% | 10.42% | 7.04% | 1.1085 | 1.1163 | 1.0757
2010-09-03 | 1 | 31.022 | 7.3506 | 38.3726 | 2.5614 | 0.76558 | 0.28527 | 3.6122 | 9.414% | 10.02% | 6.768% | 1.1039 | 1.1113 | 1.0726
2010-09-03 | 2 | 29.4276 | 6.882 | 36.3096 | 2.2934 | 0.76558 | 0.26993 | 3.3289 | 9.168% | 9.755% | 6.592% | 1.1009 | 1.1081 | 1.0706
2010-09-03 | 3 | 28.5794 | 6.6421 | 35.2216 | 2.158 | 0.76558 | 0.26184 | 3.1854 | 9.044% | 9.623% | 6.503% | 1.0994 | 1.1065 | 1.0695
2010-09-03 | 4 | 28.0907 | 6.3973 | 34.488 | 2.0691 | 0.76558 | 0.25639 | 3.091 | 8.963% | 9.536% | 6.444% | 1.0984 | 1.1054 | 1.0689
2010-09-03 | 5 | 27.4437 | 6.1535 | 33.5972 | 1.9635 | 0.76558 | 0.24977 | 2.9789 | 8.866% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-09-03 | 6 | 27.1273 | 6.0651 | 33.1924 | 1.9165 | 0.76558 | 0.24676 | 2.9288 | 8.824% | 9.389% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-09-03 | 7 | 26.8546 | 6.0262 | 32.8808 | 1.8807 | 0.76558 | 0.24444 | 2.8907 | 8.792% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-09-03 | 8 | 26.653 | 5.9416 | 32.5946 | 1.8481 | 0.76558 | 0.24231 | 2.856 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-09-03 | 9 | 26.6968 | 6.0838 | 32.7805 | 1.8692 | 0.76558 | 0.24369 | 2.8785 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-09-03 | 10 | 27.2284 | 6.3865 | 33.6148 | 1.9656 | 0.76558 | 0.2499 | 2.9811 | 8.868% | 9.436% | 6.376% | 1.0973 | 1.1042 | 1.0681
2010-09-03 | 11 | 28.1621 | 6.4403 | 34.6024 | 2.0828 | 0.76558 | 0.25724 | 3.1056 | 8.975% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-09-03 | 12 | 28.9227 | 6.926 | 35.8487 | 2.2355 | 0.76558 | 0.2665 | 3.2676 | 9.115% | 9.698% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-09-03 | 13 | 31.3071 | 7.9873 | 39.2944 | 2.6859 | 0.76558 | 0.29212 | 3.7436 | 9.527% | 10.14% | 6.85% | 1.1053 | 1.1128 | 1.0735
2010-09-03 | 14 | 34.9991 | 9.7346 | 44.7338 | 3.481 | 0.76558 | 0.33256 | 4.5791 | 10.24% | 10.89% | 7.36% | 1.114 | 1.1222 | 1.0794
2010-09-03 | 15 | 40.3574 | 11.8673 | 52.2247 | 4.7445 | 0.76558 | 0.38824 | 5.8983 | 11.29% | 12.02% | 8.12% | 1.1273 | 1.1366 | 1.0884
2010-09-03 | 16 | 40.2417 | 12.2464 | 52.4881 | 4.7924 | 0.76558 | 0.3902 | 5.9482 | 11.33% | 12.06% | 8.148% | 1.1278 | 1.1371 | 1.0887
2010-09-03 | 17 | 40.2826 | 12.4136 | 52.6962 | 4.8305 | 0.76558 | 0.39175 | 5.9878 | 11.36% | 12.09% | 8.17% | 1.1282 | 1.1375 | 1.089
2010-09-03 | 18 | 40.4535 | 13.1861 | 53.6397 | 5.005 | 0.76558 | 0.39876 | 6.1694 | 11.5% | 12.24% | 8.27% | 1.13 | 1.1394 | 1.0902
2010-09-03 | 19 | 36.6065 | 11.9285 | 48.535 | 4.0977 | 0.76558 | 0.36081 | 5.2241 | 10.76% | 11.45% | 7.739% | 1.1206 | 1.1293 | 1.0839
2010-09-03 | 20 | 37.454 | 12.0364 | 49.4903 | 4.2606 | 0.76558 | 0.36792 | 5.3941 | 10.9% | 11.6% | 7.837% | 1.1223 | 1.1312 | 1.085
2010-09-03 | 21 | 39.596 | 12.6797 | 52.2756 | 4.7537 | 0.76558 | 0.38862 | 5.9079 | 11.3% | 12.02% | 8.126% | 1.1274 | 1.1367 | 1.0884
2010-09-03 | 22 | 37.6995 | 11.645 | 49.3445 | 4.2356 | 0.76558 | 0.36683 | 5.368 | 10.88% | 11.57% | 7.822% | 1.1221 | 1.1309 | 1.0849
2010-09-03 | 23 | 35.3285 | 10.9164 | 46.2449 | 3.7202 | 0.76558 | 0.34379 | 4.8295 | 10.44% | 11.11% | 7.509% | 1.1166 | 1.125 | 1.0812
2010-09-03 | 24 | 34.1807 | 10.6715 | 44.8522 | 3.4995 | 0.76558 | 0.33344 | 4.5985 | 10.25% | 10.91% | 7.372% | 1.1142 | 1.1224 | 1.0796
2010-09-03 | 25 | 31.9822 | 10.4056 | 42.3878 | 3.1255 | 0.76558 | 0.31512 | 4.2062 | 9.923% | 10.56% | 7.135% | 1.1102 | 1.118 | 1.0768
2010-09-03 | 26 | 30.3569 | 9.7539 | 40.1109 | 2.7987 | 0.76558 | 0.29819 | 3.8625 | 9.63% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-09-03 | 27 | 30.4008 | 9.8575 | 40.2583 | 2.8193 | 0.76558 | 0.29929 | 3.8842 | 9.648% | 10.27% | 6.937% | 1.1068 | 1.1144 | 1.0745
2010-09-03 | 28 | 30.1581 | 9.8358 | 39.9939 | 2.7824 | 0.76558 | 0.29732 | 3.8453 | 9.615% | 10.23% | 6.913% | 1.1064 | 1.114 | 1.0743
2010-09-03 | 29 | 29.6706 | 9.4297 | 39.1003 | 2.6595 | 0.76558 | 0.29068 | 3.7157 | 9.503% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-09-03 | 30 | 29.4683 | 8.9758 | 38.4441 | 2.571 | 0.76558 | 0.2858 | 3.6223 | 9.422% | 10.03% | 6.775% | 1.104 | 1.1114 | 1.0727
2010-09-03 | 31 | 30.7772 | 8.8004 | 39.5775 | 2.7248 | 0.76558 | 0.29422 | 3.7846 | 9.562% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-09-03 | 32 | 31.0799 | 8.5698 | 39.6497 | 2.7347 | 0.76558 | 0.29476 | 3.7951 | 9.571% | 10.18% | 6.882% | 1.1058 | 1.1134 | 1.0739
2010-09-03 | 33 | 30.7795 | 8.8768 | 39.6563 | 2.7356 | 0.76558 | 0.29481 | 3.796 | 9.572% | 10.18% | 6.882% | 1.1059 | 1.1134 | 1.0739
2010-09-03 | 34 | 31.7133 | 8.8093 | 40.5226 | 2.8565 | 0.76558 | 0.30125 | 3.9233 | 9.682% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-09-03 | 35 | 33.8106 | 9.3408 | 43.1514 | 3.2391 | 0.76558 | 0.32079 | 4.3255 | 10.02% | 10.67% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-09-03 | 36 | 37.4436 | 10.2563 | 47.6999 | 3.9579 | 0.76558 | 0.35461 | 5.0781 | 10.65% | 11.33% | 7.654% | 1.1191 | 1.1277 | 1.0829
2010-09-03 | 37 | 41.1785 | 11.679 | 52.8575 | 4.8601 | 0.76558 | 0.39295 | 6.0187 | 11.39% | 12.12% | 8.187% | 1.1285 | 1.1379 | 1.0892
2010-09-03 | 38 | 44.1331 | 12.5021 | 56.6352 | 5.5797 | 0.76558 | 0.42103 | 6.7663 | 11.95% | 12.71% | 8.59% | 1.1357 | 1.1456 | 1.094
2010-09-03 | 39 | 43.7876 | 12.2886 | 56.0761 | 5.47 | 0.76558 | 0.41688 | 6.6525 | 11.86% | 12.62% | 8.53% | 1.1346 | 1.1445 | 1.0933
2010-09-03 | 40 | 44.9096 | 12.3868 | 57.2964 | 5.7107 | 0.76558 | 0.42595 | 6.9022 | 12.05% | 12.82% | 8.661% | 1.137 | 1.147 | 1.0948
2010-09-03 | 41 | 45.3407 | 12.01 | 57.3507 | 5.7215 | 0.76558 | 0.42635 | 6.9135 | 12.05% | 12.83% | 8.667% | 1.1371 | 1.1471 | 1.0949
2010-09-03 | 42 | 44.5087 | 11.5225 | 56.0311 | 5.4613 | 0.76558 | 0.41654 | 6.6434 | 11.86% | 12.62% | 8.525% | 1.1345 | 1.1444 | 1.0932
2010-09-03 | 43 | 42.5521 | 10.9446 | 53.4968 | 4.9784 | 0.76558 | 0.3977 | 6.1417 | 11.48% | 12.22% | 8.254% | 1.1297 | 1.1391 | 1.09
2010-09-03 | 44 | 40.8723 | 10.2292 | 51.1015 | 4.5426 | 0.76558 | 0.37989 | 5.688 | 11.13% | 11.84% | 8.003% | 1.1253 | 1.1343 | 1.087
2010-09-03 | 45 | 36.9079 | 9.2114 | 46.1193 | 3.7 | 0.76558 | 0.34286 | 4.8084 | 10.43% | 11.09% | 7.496% | 1.1164 | 1.1248 | 1.081
2010-09-03 | 46 | 33.5759 | 8.5705 | 42.1464 | 3.09 | 0.76558 | 0.31332 | 4.1689 | 9.891% | 10.52% | 7.112% | 1.1098 | 1.1176 | 1.0766
2010-09-03 | 47 | 32.8004 | 8.8105 | 41.6109 | 3.012 | 0.76558 | 0.30934 | 4.0869 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-09-03 | 48 | 34.0526 | 9.7152 | 43.7677 | 3.3323 | 0.76558 | 0.32537 | 4.4232 | 10.11% | 10.75% | 7.266% | 1.1124 | 1.1205 | 1.0784
2010-09-04 | 1 | 32.0007 | 9.45 | 41.4507 | 2.9888 | 0.76558 | 0.30815 | 4.0625 | 9.801% | 10.43% | 7.047% | 1.1087 | 1.1164 | 1.0758
2010-09-04 | 2 | 30.4785 | 9.2614 | 39.7399 | 2.7472 | 0.76558 | 0.29543 | 3.8082 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-09-04 | 3 | 29.3858 | 8.9701 | 38.3559 | 2.5592 | 0.76558 | 0.28514 | 3.6099 | 9.412% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-09-04 | 4 | 29.0831 | 8.8073 | 37.8904 | 2.4974 | 0.76558 | 0.28168 | 3.5447 | 9.355% | 9.954% | 6.726% | 1.1032 | 1.1105 | 1.0721
2010-09-04 | 5 | 28.481 | 8.695 | 37.1759 | 2.4041 | 0.76558 | 0.27637 | 3.4461 | 9.27% | 9.863% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-09-04 | 6 | 28.2213 | 8.5309 | 36.7521 | 2.3496 | 0.76558 | 0.27322 | 3.3884 | 9.22% | 9.81% | 6.629% | 1.1016 | 1.1088 | 1.071
2010-09-04 | 7 | 27.9365 | 8.6534 | 36.5898 | 2.3289 | 0.76558 | 0.27201 | 3.3665 | 9.201% | 9.79% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-09-04 | 8 | 27.6197 | 8.6528 | 36.2725 | 2.2887 | 0.76558 | 0.26965 | 3.3239 | 9.164% | 9.75% | 6.589% | 1.1009 | 1.108 | 1.0705
2010-09-04 | 9 | 27.8502 | 8.7653 | 36.6155 | 2.3322 | 0.76558 | 0.2722 | 3.37 | 9.204% | 9.793% | 6.617% | 1.1014 | 1.1086 | 1.0709
2010-09-04 | 10 | 28.2216 | 9.0559 | 37.2775 | 2.4173 | 0.76558 | 0.27713 | 3.46 | 9.282% | 9.876% | 6.674% | 1.1023 | 1.1096 | 1.0715
2010-09-04 | 11 | 29.1834 | 9.3438 | 38.5272 | 2.5821 | 0.76558 | 0.28642 | 3.6341 | 9.432% | 10.04% | 6.782% | 1.1041 | 1.1116 | 1.0728
2010-09-04 | 12 | 30.162 | 9.7506 | 39.9126 | 2.7711 | 0.76558 | 0.29672 | 3.8334 | 9.605% | 10.22% | 6.906% | 1.1062 | 1.1138 | 1.0742
2010-09-04 | 13 | 32.5025 | 10.9477 | 43.4502 | 3.2841 | 0.76558 | 0.32301 | 4.3727 | 10.06% | 10.71% | 7.236% | 1.1119 | 1.1199 | 1.078
2010-09-04 | 14 | 36.7523 | 12.638 | 49.3903 | 4.2434 | 0.76558 | 0.36717 | 5.3762 | 10.89% | 11.58% | 7.826% | 1.1221 | 1.131 | 1.0849
2010-09-04 | 15 | 41.5377 | 14.5281 | 56.0658 | 5.468 | 0.76558 | 0.4168 | 6.6504 | 11.86% | 12.62% | 8.529% | 1.1346 | 1.1444 | 1.0932
2010-09-04 | 16 | 40.2426 | 14.567 | 54.8097 | 5.2258 | 0.76558 | 0.40746 | 6.3988 | 11.67% | 12.42% | 8.394% | 1.1322 | 1.1418 | 1.0916
2010-09-04 | 17 | 37.7136 | 13.8673 | 51.5809 | 4.6282 | 0.76558 | 0.38346 | 5.7772 | 11.2% | 11.92% | 8.053% | 1.1261 | 1.1353 | 1.0876
2010-09-04 | 18 | 37.585 | 13.3539 | 50.9389 | 4.5137 | 0.76558 | 0.37869 | 5.658 | 11.11% | 11.82% | 7.986% | 1.125 | 1.134 | 1.0868
2010-09-04 | 19 | 41.1599 | 14.7623 | 55.9222 | 5.4401 | 0.76558 | 0.41573 | 6.6214 | 11.84% | 12.6% | 8.513% | 1.1343 | 1.1441 | 1.0931
2010-09-04 | 20 | 42.6253 | 14.257 | 56.8822 | 5.6284 | 0.76558 | 0.42287 | 6.8169 | 11.98% | 12.75% | 8.617% | 1.1362 | 1.1461 | 1.0943
2010-09-04 | 21 | 41.7207 | 12.9029 | 54.6236 | 5.1903 | 0.76558 | 0.40608 | 6.362 | 11.65% | 12.39% | 8.374% | 1.1318 | 1.1415 | 1.0914
2010-09-04 | 22 | 40.1714 | 12.0337 | 52.2051 | 4.7409 | 0.76558 | 0.3881 | 5.8946 | 11.29% | 12.01% | 8.118% | 1.1273 | 1.1365 | 1.0884
2010-09-04 | 23 | 37.7856 | 11.1175 | 48.9031 | 4.1601 | 0.76558 | 0.36355 | 5.2893 | 10.82% | 11.51% | 7.777% | 1.1213 | 1.13 | 1.0843
2010-09-04 | 24 | 35.6743 | 10.5458 | 46.2201 | 3.7162 | 0.76558 | 0.34361 | 4.8254 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.125 | 1.0812
2010-09-04 | 25 | 33.1309 | 10.1176 | 43.2485 | 3.2537 | 0.76558 | 0.32151 | 4.3408 | 10.04% | 10.68% | 7.216% | 1.1116 | 1.1196 | 1.0778
2010-09-04 | 26 | 31.0903 | 9.4164 | 40.5066 | 2.8542 | 0.76558 | 0.30113 | 3.9209 | 9.68% | 10.3% | 6.96% | 1.1072 | 1.1148 | 1.0748
2010-09-04 | 27 | 30.8179 | 9.4417 | 40.2596 | 2.8195 | 0.76558 | 0.29929 | 3.8844 | 9.648% | 10.27% | 6.937% | 1.1068 | 1.1144 | 1.0745
2010-09-04 | 28 | 30.6332 | 9.3872 | 40.0205 | 2.7861 | 0.76558 | 0.29752 | 3.8492 | 9.618% | 10.23% | 6.915% | 1.1064 | 1.114 | 1.0743
2010-09-04 | 29 | 29.838 | 8.9121 | 38.7501 | 2.612 | 0.76558 | 0.28807 | 3.6657 | 9.46% | 10.07% | 6.802% | 1.1045 | 1.1119 | 1.073
2010-09-04 | 30 | 29.0172 | 8.5505 | 37.5678 | 2.4551 | 0.76558 | 0.27928 | 3.4999 | 9.316% | 9.913% | 6.698% | 1.1027 | 1.11 | 1.0718
2010-09-04 | 31 | 30.6838 | 8.5044 | 39.1882 | 2.6714 | 0.76558 | 0.29133 | 3.7283 | 9.514% | 10.12% | 6.841% | 1.1051 | 1.1126 | 1.0734
2010-09-04 | 32 | 30.8289 | 8.5001 | 39.329 | 2.6907 | 0.76558 | 0.29238 | 3.7486 | 9.531% | 10.14% | 6.853% | 1.1054 | 1.1129 | 1.0736
2010-09-04 | 33 | 30.7846 | 8.6498 | 39.4344 | 2.7051 | 0.76558 | 0.29316 | 3.7639 | 9.545% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-09-04 | 34 | 30.8789 | 8.6445 | 39.5235 | 2.7173 | 0.76558 | 0.29382 | 3.7767 | 9.556% | 10.17% | 6.871% | 1.1057 | 1.1132 | 1.0738
2010-09-04 | 35 | 31.3385 | 8.891 | 40.2295 | 2.8153 | 0.76558 | 0.29907 | 3.8799 | 9.645% | 10.26% | 6.934% | 1.1067 | 1.1144 | 1.0745
2010-09-04 | 36 | 32.8466 | 9.5059 | 42.3525 | 3.1203 | 0.76558 | 0.31485 | 4.2007 | 9.918% | 10.55% | 7.131% | 1.1101 | 1.118 | 1.0768
2010-09-04 | 37 | 35.0436 | 10.5712 | 45.6148 | 3.6195 | 0.76558 | 0.33911 | 4.7242 | 10.36% | 11.02% | 7.446% | 1.1155 | 1.1238 | 1.0805
2010-09-04 | 38 | 37.8848 | 11.6081 | 49.4929 | 4.2611 | 0.76558 | 0.36794 | 5.3946 | 10.9% | 11.6% | 7.837% | 1.1223 | 1.1312 | 1.085
2010-09-04 | 39 | 38.4807 | 11.6399 | 50.1206 | 4.3699 | 0.76558 | 0.3726 | 5.508 | 10.99% | 11.69% | 7.902% | 1.1235 | 1.1324 | 1.0858
2010-09-04 | 40 | 38.5747 | 11.2631 | 49.8377 | 4.3207 | 0.76558 | 0.3705 | 5.4567 | 10.95% | 11.65% | 7.872% | 1.123 | 1.1319 | 1.0855
2010-09-04 | 41 | 39.4716 | 10.9963 | 50.4679 | 4.4306 | 0.76558 | 0.37518 | 5.5714 | 11.04% | 11.75% | 7.937% | 1.1241 | 1.1331 | 1.0862
2010-09-04 | 42 | 39.4385 | 10.7583 | 50.1968 | 4.3832 | 0.76558 | 0.37317 | 5.5219 | 11% | 11.7% | 7.909% | 1.1236 | 1.1326 | 1.0859
2010-09-04 | 43 | 38.0359 | 10.3307 | 48.3666 | 4.0694 | 0.76558 | 0.35956 | 5.1945 | 10.74% | 11.43% | 7.722% | 1.1203 | 1.129 | 1.0837
2010-09-04 | 44 | 37.5568 | 9.7245 | 47.2813 | 3.8888 | 0.76558 | 0.3515 | 5.0059 | 10.59% | 11.26% | 7.612% | 1.1184 | 1.127 | 1.0824
2010-09-04 | 45 | 34.5112 | 8.9302 | 43.4414 | 3.2828 | 0.76558 | 0.32295 | 4.3713 | 10.06% | 10.71% | 7.235% | 1.1119 | 1.1199 | 1.078
2010-09-04 | 46 | 31.7391 | 8.1013 | 39.8404 | 2.7611 | 0.76558 | 0.29618 | 3.8229 | 9.595% | 10.21% | 6.899% | 1.1061 | 1.1137 | 1.0741
2010-09-04 | 47 | 31.5382 | 8.0089 | 39.5471 | 2.7206 | 0.76558 | 0.294 | 3.7802 | 9.559% | 10.17% | 6.873% | 1.1057 | 1.1132 | 1.0738
2010-09-04 | 48 | 33.0068 | 8.6799 | 41.6866 | 3.0229 | 0.76558 | 0.3099 | 4.0984 | 9.831% | 10.46% | 7.069% | 1.109 | 1.1168 | 1.0761
2010-09-05 | 1 | 31.1832 | 8.2485 | 39.4318 | 2.7047 | 0.76558 | 0.29314 | 3.7635 | 9.544% | 10.16% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-09-05 | 2 | 29.6318 | 7.7853 | 37.4171 | 2.4354 | 0.76558 | 0.27816 | 3.4792 | 9.298% | 9.893% | 6.686% | 1.1025 | 1.1098 | 1.0716
2010-09-05 | 3 | 28.5404 | 7.5172 | 36.0576 | 2.2617 | 0.76558 | 0.26806 | 3.2953 | 9.139% | 9.724% | 6.571% | 1.1006 | 1.1077 | 1.0703
2010-09-05 | 4 | 27.5043 | 7.4196 | 34.9239 | 2.1217 | 0.76558 | 0.25963 | 3.1469 | 9.011% | 9.587% | 6.479% | 1.099 | 1.106 | 1.0693
2010-09-05 | 5 | 26.9435 | 7.2512 | 34.1947 | 2.034 | 0.76558 | 0.25421 | 3.0538 | 8.931% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-09-05 | 6 | 26.9713 | 7.3235 | 34.2949 | 2.0459 | 0.76558 | 0.25495 | 3.0665 | 8.941% | 9.514% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-09-05 | 7 | 26.7437 | 7.6063 | 34.35 | 2.0525 | 0.76558 | 0.25536 | 3.0735 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-09-05 | 8 | 26.5276 | 7.796 | 34.3236 | 2.0494 | 0.76558 | 0.25517 | 3.0701 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-09-05 | 9 | 26.7438 | 8.006 | 34.7498 | 2.1006 | 0.76558 | 0.25833 | 3.1245 | 8.991% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-09-05 | 10 | 26.6861 | 8.1353 | 34.8214 | 2.1092 | 0.76558 | 0.25887 | 3.1337 | 8.999% | 9.575% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-09-05 | 11 | 27.3767 | 8.4696 | 35.8462 | 2.2352 | 0.76558 | 0.26649 | 3.2673 | 9.115% | 9.698% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-09-05 | 12 | 28.2229 | 9.0754 | 37.2982 | 2.42 | 0.76558 | 0.27728 | 3.4628 | 9.284% | 9.878% | 6.675% | 1.1023 | 1.1096 | 1.0715
2010-09-05 | 13 | 29.9325 | 9.6698 | 39.6023 | 2.7282 | 0.76558 | 0.29441 | 3.7882 | 9.566% | 10.18% | 6.878% | 1.1058 | 1.1133 | 1.0739
2010-09-05 | 14 | 32.0724 | 10.3541 | 42.4265 | 3.1312 | 0.76558 | 0.3154 | 4.2122 | 9.928% | 10.56% | 7.138% | 1.1102 | 1.1181 | 1.0769
2010-09-05 | 15 | 34.0986 | 11.2622 | 45.3608 | 3.5793 | 0.76558 | 0.33722 | 4.6821 | 10.32% | 10.98% | 7.421% | 1.1151 | 1.1234 | 1.0802
2010-09-05 | 16 | 34.0826 | 12.3886 | 46.4712 | 3.7567 | 0.76558 | 0.34547 | 4.8677 | 10.47% | 11.15% | 7.531% | 1.117 | 1.1254 | 1.0814
2010-09-05 | 17 | 35.6029 | 13.193 | 48.796 | 4.1419 | 0.76558 | 0.36276 | 5.2703 | 10.8% | 11.49% | 7.766% | 1.1211 | 1.1298 | 1.0842
2010-09-05 | 18 | 36.6504 | 13.011 | 49.6614 | 4.2902 | 0.76558 | 0.36919 | 5.4249 | 10.92% | 11.62% | 7.854% | 1.1226 | 1.1315 | 1.0852
2010-09-05 | 19 | 37.2388 | 12.0788 | 49.3176 | 4.231 | 0.76558 | 0.36663 | 5.3632 | 10.87% | 11.57% | 7.819% | 1.122 | 1.1308 | 1.0848
2010-09-05 | 20 | 36.8068 | 11.6927 | 48.4994 | 4.0917 | 0.76558 | 0.36055 | 5.2179 | 10.76% | 11.45% | 7.735% | 1.1206 | 1.1293 | 1.0838
2010-09-05 | 21 | 38.2017 | 11.5245 | 49.7262 | 4.3014 | 0.76558 | 0.36967 | 5.4366 | 10.93% | 11.63% | 7.861% | 1.1228 | 1.1316 | 1.0853
2010-09-05 | 22 | 37.0683 | 11.0327 | 48.101 | 4.0248 | 0.76558 | 0.35759 | 5.1479 | 10.7% | 11.39% | 7.695% | 1.1199 | 1.1285 | 1.0834
2010-09-05 | 23 | 35.4724 | 10.502 | 45.9744 | 3.6768 | 0.76558 | 0.34178 | 4.7841 | 10.41% | 11.07% | 7.482% | 1.1161 | 1.1245 | 1.0809
2010-09-05 | 24 | 33.621 | 9.9854 | 43.6064 | 3.3078 | 0.76558 | 0.32418 | 4.3975 | 10.08% | 10.73% | 7.251% | 1.1122 | 1.1202 | 1.0782
2010-09-05 | 25 | 30.8922 | 9.662 | 40.5542 | 2.8609 | 0.76558 | 0.30148 | 3.928 | 9.686% | 10.31% | 6.964% | 1.1072 | 1.1149 | 1.0749
2010-09-05 | 26 | 29.5149 | 8.9902 | 38.5051 | 2.5791 | 0.76558 | 0.28625 | 3.6309 | 9.43% | 10.03% | 6.78% | 1.1041 | 1.1115 | 1.0727
2010-09-05 | 27 | 29.384 | 8.9569 | 38.341 | 2.5572 | 0.76558 | 0.28503 | 3.6078 | 9.41% | 10.01% | 6.766% | 1.1039 | 1.1113 | 1.0726
2010-09-05 | 28 | 29.3257 | 8.6285 | 37.9542 | 2.5058 | 0.76558 | 0.28216 | 3.5536 | 9.363% | 9.962% | 6.732% | 1.1033 | 1.1106 | 1.0722
2010-09-05 | 29 | 28.4094 | 8.0914 | 36.5008 | 2.3176 | 0.76558 | 0.27135 | 3.3545 | 9.19% | 9.778% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-09-05 | 30 | 27.7606 | 7.6984 | 35.459 | 2.1872 | 0.76558 | 0.26361 | 3.2164 | 9.071% | 9.651% | 6.522% | 1.0998 | 1.1068 | 1.0698
2010-09-05 | 31 | 28.8972 | 7.5747 | 36.472 | 2.3139 | 0.76558 | 0.27114 | 3.3507 | 9.187% | 9.775% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-09-05 | 32 | 28.738 | 7.4529 | 36.1909 | 2.2784 | 0.76558 | 0.26905 | 3.313 | 9.154% | 9.74% | 6.582% | 1.1008 | 1.1079 | 1.0705
2010-09-05 | 33 | 28.336 | 7.7031 | 36.0391 | 2.2593 | 0.76558 | 0.26792 | 3.2928 | 9.137% | 9.722% | 6.569% | 1.1006 | 1.1077 | 1.0703
2010-09-05 | 34 | 29.3566 | 7.9577 | 37.3143 | 2.4221 | 0.76558 | 0.2774 | 3.465 | 9.286% | 9.88% | 6.677% | 1.1024 | 1.1096 | 1.0715
2010-09-05 | 35 | 30.1896 | 8.5389 | 38.7284 | 2.6091 | 0.76558 | 0.28791 | 3.6626 | 9.457% | 10.06% | 6.8% | 1.1044 | 1.1119 | 1.073
2010-09-05 | 36 | 32.4721 | 9.6846 | 42.1566 | 3.0915 | 0.76558 | 0.3134 | 4.1705 | 9.893% | 10.53% | 7.113% | 1.1098 | 1.1176 | 1.0766
2010-09-05 | 37 | 35.1587 | 10.9315 | 46.0902 | 3.6953 | 0.76558 | 0.34264 | 4.8035 | 10.42% | 11.09% | 7.493% | 1.1163 | 1.1247 | 1.081
2010-09-05 | 38 | 37.7703 | 11.7314 | 49.5017 | 4.2626 | 0.76558 | 0.368 | 5.3962 | 10.9% | 11.6% | 7.838% | 1.1223 | 1.1312 | 1.085
2010-09-05 | 39 | 38.0734 | 11.6958 | 49.7692 | 4.3088 | 0.76558 | 0.36999 | 5.4444 | 10.94% | 11.64% | 7.865% | 1.1228 | 1.1317 | 1.0854
2010-09-05 | 40 | 37.5127 | 11.2181 | 48.7308 | 4.1309 | 0.76558 | 0.36227 | 5.2587 | 10.79% | 11.48% | 7.759% | 1.121 | 1.1297 | 1.0841
2010-09-05 | 41 | 37.7295 | 10.7512 | 48.4807 | 4.0886 | 0.76558 | 0.36041 | 5.2146 | 10.76% | 11.44% | 7.734% | 1.1205 | 1.1292 | 1.0838
2010-09-05 | 42 | 37.7137 | 10.2867 | 48.0004 | 4.008 | 0.76558 | 0.35684 | 5.1304 | 10.69% | 11.37% | 7.685% | 1.1197 | 1.1283 | 1.0832
2010-09-05 | 43 | 35.7439 | 9.8124 | 45.5564 | 3.6102 | 0.76558 | 0.33867 | 4.7145 | 10.35% | 11.01% | 7.441% | 1.1154 | 1.1237 | 1.0804
2010-09-05 | 44 | 34.0799 | 9.4367 | 43.5166 | 3.2942 | 0.76558 | 0.32351 | 4.3832 | 10.07% | 10.72% | 7.242% | 1.112 | 1.12 | 1.0781
2010-09-05 | 45 | 31.2636 | 8.683 | 39.9466 | 2.7758 | 0.76558 | 0.29697 | 3.8384 | 9.609% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-09-05 | 46 | 29.0218 | 8.0113 | 37.0331 | 2.3857 | 0.76558 | 0.27531 | 3.4266 | 9.253% | 9.845% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-09-05 | 47 | 29.311 | 8.2062 | 37.5171 | 2.4485 | 0.76558 | 0.27891 | 3.4929 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.11 | 1.0717
2010-09-05 | 48 | 30.9502 | 8.5981 | 39.5482 | 2.7208 | 0.76558 | 0.29401 | 3.7803 | 9.559% | 10.17% | 6.873% | 1.1057 | 1.1132 | 1.0738
2010-09-06 | 1 | 28.897 | 7.9377 | 36.8347 | 2.3602 | 0.76558 | 0.27383 | 3.3996 | 9.229% | 9.82% | 6.636% | 1.1017 | 1.1089 | 1.0711
2010-09-06 | 2 | 27.4162 | 7.6417 | 35.0579 | 2.138 | 0.76558 | 0.26062 | 3.1642 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-09-06 | 3 | 26.2245 | 7.2924 | 33.5169 | 1.9542 | 0.76558 | 0.24917 | 2.9689 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-09-06 | 4 | 25.6206 | 6.9576 | 32.5781 | 1.8462 | 0.76558 | 0.24219 | 2.854 | 8.76% | 9.321% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-09-06 | 5 | 25.2904 | 6.8245 | 32.1149 | 1.7941 | 0.76558 | 0.23875 | 2.7984 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-09-06 | 6 | 25.2483 | 6.7626 | 32.0108 | 1.7825 | 0.76558 | 0.23797 | 2.786 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-09-06 | 7 | 24.7024 | 6.795 | 31.4974 | 1.7258 | 0.76558 | 0.23416 | 2.7255 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2010-09-06 | 8 | 24.327 | 6.8688 | 31.1958 | 1.6929 | 0.76558 | 0.23191 | 2.6904 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-09-06 | 9 | 24.6304 | 7.0739 | 31.7043 | 1.7485 | 0.76558 | 0.23569 | 2.7498 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-09-06 | 10 | 25.4063 | 7.6248 | 33.0311 | 1.8979 | 0.76558 | 0.24556 | 2.9091 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-09-06 | 11 | 26.0367 | 7.9826 | 34.0193 | 2.0132 | 0.76558 | 0.2529 | 3.0317 | 8.912% | 9.482% | 6.407% | 1.0978 | 1.1048 | 1.0685
2010-09-06 | 12 | 26.224 | 8.3831 | 34.6071 | 2.0834 | 0.76558 | 0.25727 | 3.1062 | 8.976% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-09-06 | 13 | 27.373 | 8.7913 | 36.1643 | 2.2751 | 0.76558 | 0.26885 | 3.3095 | 9.151% | 9.737% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-09-06 | 14 | 28.8376 | 9.1948 | 38.0323 | 2.5162 | 0.76558 | 0.28274 | 3.5645 | 9.372% | 9.972% | 6.739% | 1.1034 | 1.1108 | 1.0723
2010-09-06 | 15 | 30.8633 | 9.9361 | 40.7994 | 2.8956 | 0.76558 | 0.30331 | 3.9645 | 9.717% | 10.34% | 6.987% | 1.1076 | 1.1153 | 1.0751
2010-09-06 | 16 | 31.2063 | 10.7402 | 41.9465 | 3.0607 | 0.76558 | 0.31184 | 4.1382 | 9.865% | 10.5% | 7.093% | 1.1095 | 1.1173 | 1.0763
2010-09-06 | 17 | 33.0175 | 11.7904 | 44.8079 | 3.4926 | 0.76558 | 0.33311 | 4.5912 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-09-06 | 18 | 34.4836 | 12.0111 | 46.4947 | 3.7605 | 0.76558 | 0.34565 | 4.8717 | 10.48% | 11.15% | 7.534% | 1.117 | 1.1255 | 1.0815
2010-09-06 | 19 | 35.1702 | 11.5528 | 46.723 | 3.7975 | 0.76558 | 0.34734 | 4.9104 | 10.51% | 11.18% | 7.556% | 1.1174 | 1.1259 | 1.0817
2010-09-06 | 20 | 35.0433 | 11.169 | 46.2123 | 3.7149 | 0.76558 | 0.34355 | 4.824 | 10.44% | 11.11% | 7.506% | 1.1166 | 1.1249 | 1.0811
2010-09-06 | 21 | 36.7681 | 10.9316 | 47.6997 | 3.9579 | 0.76558 | 0.35461 | 5.0781 | 10.65% | 11.33% | 7.654% | 1.1191 | 1.1277 | 1.0829
2010-09-06 | 22 | 36.9269 | 10.7248 | 47.6517 | 3.95 | 0.76558 | 0.35425 | 5.0698 | 10.64% | 11.32% | 7.65% | 1.1191 | 1.1277 | 1.0828
2010-09-06 | 23 | 35.5763 | 10.2788 | 45.8551 | 3.6577 | 0.76558 | 0.34089 | 4.7642 | 10.39% | 11.05% | 7.47% | 1.1159 | 1.1243 | 1.0807
2010-09-06 | 24 | 34.8283 | 10.0223 | 44.8506 | 3.4992 | 0.76558 | 0.33342 | 4.5982 | 10.25% | 10.91% | 7.371% | 1.1142 | 1.1224 | 1.0796
2010-09-06 | 25 | 33.3201 | 9.7052 | 43.0253 | 3.2202 | 0.76558 | 0.31986 | 4.3056 | 10.01% | 10.65% | 7.195% | 1.1112 | 1.1192 | 1.0775
2010-09-06 | 26 | 32.6017 | 9.2112 | 41.8129 | 3.0413 | 0.76558 | 0.31084 | 4.1177 | 9.848% | 10.48% | 7.081% | 1.1092 | 1.117 | 1.0762
2010-09-06 | 27 | 32.9457 | 9.3354 | 42.2811 | 3.1098 | 0.76558 | 0.31432 | 4.1897 | 9.909% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-09-06 | 28 | 32.8018 | 9.5274 | 42.3292 | 3.1168 | 0.76558 | 0.31468 | 4.1971 | 9.915% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-09-06 | 29 | 31.998 | 9.376 | 41.3739 | 2.9778 | 0.76558 | 0.30758 | 4.0509 | 9.791% | 10.42% | 7.04% | 1.1085 | 1.1163 | 1.0757
2010-09-06 | 30 | 31.3952 | 9.2603 | 40.6554 | 2.8752 | 0.76558 | 0.30224 | 3.943 | 9.699% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-09-06 | 31 | 31.97 | 9.3221 | 41.2921 | 2.966 | 0.76558 | 0.30697 | 4.0385 | 9.78% | 10.41% | 7.032% | 1.1084 | 1.1162 | 1.0756
2010-09-06 | 32 | 31.7981 | 9.2948 | 41.0929 | 2.9374 | 0.76558 | 0.30549 | 4.0085 | 9.755% | 10.38% | 7.014% | 1.1081 | 1.1158 | 1.0754
2010-09-06 | 33 | 31.3531 | 9.7475 | 41.1007 | 2.9385 | 0.76558 | 0.30555 | 4.0097 | 9.756% | 10.38% | 7.014% | 1.1081 | 1.1158 | 1.0754
2010-09-06 | 34 | 31.009 | 9.9539 | 40.9629 | 2.9189 | 0.76558 | 0.30452 | 3.989 | 9.738% | 10.36% | 7.002% | 1.1079 | 1.1156 | 1.0753
2010-09-06 | 35 | 30.9778 | 10.6391 | 41.6169 | 3.0128 | 0.76558 | 0.30939 | 4.0878 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-09-06 | 36 | 32.7009 | 11.4069 | 44.1078 | 3.3843 | 0.76558 | 0.3279 | 4.4778 | 10.15% | 10.8% | 7.299% | 1.113 | 1.1211 | 1.0787
2010-09-06 | 37 | 35.2155 | 11.8401 | 47.0556 | 3.8517 | 0.76558 | 0.34982 | 4.9671 | 10.56% | 11.23% | 7.59% | 1.118 | 1.1265 | 1.0821
2010-09-06 | 38 | 37.9711 | 12.3042 | 50.2753 | 4.3969 | 0.76558 | 0.37375 | 5.5362 | 11.01% | 11.72% | 7.917% | 1.1237 | 1.1327 | 1.086
2010-09-06 | 39 | 37.786 | 11.8992 | 49.6853 | 4.2943 | 0.76558 | 0.36937 | 5.4292 | 10.93% | 11.63% | 7.857% | 1.1227 | 1.1316 | 1.0853
2010-09-06 | 40 | 37.1238 | 11.6704 | 48.7942 | 4.1416 | 0.76558 | 0.36274 | 5.2699 | 10.8% | 11.49% | 7.765% | 1.1211 | 1.1298 | 1.0842
2010-09-06 | 41 | 37.4548 | 11.315 | 48.7698 | 4.1375 | 0.76558 | 0.36256 | 5.2656 | 10.8% | 11.49% | 7.763% | 1.121 | 1.1298 | 1.0842
2010-09-06 | 42 | 37.225 | 10.6693 | 47.8943 | 3.9903 | 0.76558 | 0.35605 | 5.1119 | 10.67% | 11.36% | 7.674% | 1.1195 | 1.1281 | 1.0831
2010-09-06 | 43 | 34.5965 | 9.9727 | 44.5692 | 3.4554 | 0.76558 | 0.33133 | 4.5524 | 10.21% | 10.87% | 7.344% | 1.1138 | 1.1219 | 1.0793
2010-09-06 | 44 | 32.3709 | 9.2492 | 41.6201 | 3.0133 | 0.76558 | 0.30941 | 4.0883 | 9.823% | 10.45% | 7.063% | 1.1089 | 1.1167 | 1.076
2010-09-06 | 45 | 29.2384 | 8.2123 | 37.4507 | 2.4398 | 0.76558 | 0.27841 | 3.4838 | 9.302% | 9.898% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-09-06 | 46 | 26.2359 | 7.1709 | 33.4068 | 1.9414 | 0.76558 | 0.24835 | 2.9553 | 8.846% | 9.413% | 6.361% | 1.097 | 1.1039 | 1.0679
2010-09-06 | 47 | 25.7353 | 7.2558 | 32.9912 | 1.8933 | 0.76558 | 0.24526 | 2.9042 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-06 | 48 | 27.1278 | 7.7501 | 34.8779 | 2.1161 | 0.76558 | 0.25929 | 3.141 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2010-09-07 | 1 | 25.6929 | 7.1845 | 32.8773 | 1.8803 | 0.76558 | 0.24441 | 2.8903 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-09-07 | 2 | 23.9978 | 6.6312 | 30.6291 | 1.6319 | 0.76558 | 0.2277 | 2.6252 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2010-09-07 | 3 | 23.2354 | 6.272 | 29.5074 | 1.5146 | 0.76558 | 0.21936 | 2.4995 | 8.471% | 9.013% | 6.091% | 1.0925 | 1.0991 | 1.0649
2010-09-07 | 4 | 22.6252 | 6.1608 | 28.786 | 1.4414 | 0.76558 | 0.214 | 2.421 | 8.41% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-09-07 | 5 | 22.4086 | 5.9651 | 28.3737 | 1.4004 | 0.76558 | 0.21093 | 2.377 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-09-07 | 6 | 22.1001 | 5.8506 | 27.9507 | 1.359 | 0.76558 | 0.20779 | 2.3324 | 8.345% | 8.879% | 6% | 1.091 | 1.0974 | 1.0638
2010-09-07 | 7 | 22.3224 | 5.8129 | 28.1353 | 1.377 | 0.76558 | 0.20916 | 2.3518 | 8.359% | 8.894% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-09-07 | 8 | 22.2219 | 5.7404 | 27.9622 | 1.3601 | 0.76558 | 0.20787 | 2.3336 | 8.345% | 8.88% | 6% | 1.0911 | 1.0974 | 1.0638
2010-09-07 | 9 | 22.2858 | 5.8937 | 28.1795 | 1.3813 | 0.76558 | 0.20949 | 2.3564 | 8.362% | 8.897% | 6.012% | 1.0913 | 1.0977 | 1.064
2010-09-07 | 10 | 22.5942 | 5.9988 | 28.593 | 1.4222 | 0.76558 | 0.21256 | 2.4003 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-09-07 | 11 | 23.5593 | 6.1918 | 29.7511 | 1.5397 | 0.76558 | 0.22117 | 2.5265 | 8.492% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-09-07 | 12 | 24.4215 | 6.626 | 31.0475 | 1.6768 | 0.76558 | 0.23081 | 2.6732 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-09-07 | 13 | 26.5477 | 7.6023 | 34.1499 | 2.0287 | 0.76558 | 0.25387 | 3.0481 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-09-07 | 14 | 30.0293 | 9.1962 | 39.2255 | 2.6765 | 0.76558 | 0.29161 | 3.7337 | 9.519% | 10.13% | 6.844% | 1.1052 | 1.1127 | 1.0735
2010-09-07 | 15 | 34.4834 | 11.495 | 45.9784 | 3.6774 | 0.76558 | 0.34181 | 4.7848 | 10.41% | 11.07% | 7.482% | 1.1162 | 1.1245 | 1.0809
2010-09-07 | 16 | 35.9132 | 12.5593 | 48.4725 | 4.0872 | 0.76558 | 0.36035 | 5.2131 | 10.75% | 11.44% | 7.733% | 1.1205 | 1.1292 | 1.0838
2010-09-07 | 17 | 37.6504 | 13.4028 | 51.0532 | 4.534 | 0.76558 | 0.37954 | 5.6791 | 11.12% | 11.84% | 7.998% | 1.1252 | 1.1342 | 1.0869
2010-09-07 | 18 | 38.0121 | 13.2952 | 51.3072 | 4.5792 | 0.76558 | 0.38142 | 5.7262 | 11.16% | 11.87% | 8.025% | 1.1256 | 1.1348 | 1.0872
2010-09-07 | 19 | 37.8104 | 12.9773 | 50.7876 | 4.4869 | 0.76558 | 0.37756 | 5.6301 | 11.09% | 11.8% | 7.971% | 1.1247 | 1.1337 | 1.0866
2010-09-07 | 20 | 36.7649 | 12.4329 | 49.1978 | 4.2104 | 0.76558 | 0.36574 | 5.3417 | 10.86% | 11.55% | 7.807% | 1.1218 | 1.1306 | 1.0847
2010-09-07 | 21 | 37.554 | 12.1246 | 49.6786 | 4.2931 | 0.76558 | 0.36932 | 5.428 | 10.93% | 11.63% | 7.856% | 1.1227 | 1.1315 | 1.0853
2010-09-07 | 22 | 36.6771 | 11.8182 | 48.4953 | 4.091 | 0.76558 | 0.36052 | 5.2171 | 10.76% | 11.45% | 7.735% | 1.1205 | 1.1293 | 1.0838
2010-09-07 | 23 | 35.039 | 11.1897 | 46.2286 | 3.7176 | 0.76558 | 0.34367 | 4.8268 | 10.44% | 11.11% | 7.507% | 1.1166 | 1.125 | 1.0812
2010-09-07 | 24 | 33.6164 | 10.7239 | 44.3403 | 3.42 | 0.76558 | 0.32963 | 4.5153 | 10.18% | 10.83% | 7.322% | 1.1134 | 1.1215 | 1.079
2010-09-07 | 25 | 31.4474 | 10.3996 | 41.847 | 3.0462 | 0.76558 | 0.3111 | 4.1229 | 9.852% | 10.48% | 7.084% | 1.1093 | 1.1171 | 1.0762
2010-09-07 | 26 | 29.9529 | 9.7763 | 39.7292 | 2.7457 | 0.76558 | 0.29535 | 3.8066 | 9.581% | 10.19% | 6.889% | 1.106 | 1.1135 | 1.074
2010-09-07 | 27 | 30.1256 | 9.8775 | 40.0031 | 2.7837 | 0.76558 | 0.29739 | 3.8467 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-09-07 | 28 | 30.1828 | 10.0096 | 40.1924 | 2.8101 | 0.76558 | 0.2988 | 3.8745 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-09-07 | 29 | 29.5197 | 9.8035 | 39.3232 | 2.6899 | 0.76558 | 0.29233 | 3.7478 | 9.531% | 10.14% | 6.853% | 1.1053 | 1.1129 | 1.0736
2010-09-07 | 30 | 28.7295 | 9.4619 | 38.1915 | 2.5373 | 0.76558 | 0.28392 | 3.5868 | 9.392% | 9.993% | 6.753% | 1.1036 | 1.111 | 1.0724
2010-09-07 | 31 | 29.851 | 9.5463 | 39.3973 | 2.7 | 0.76558 | 0.29288 | 3.7585 | 9.54% | 10.15% | 6.859% | 1.1055 | 1.113 | 1.0736
2010-09-07 | 32 | 29.4057 | 9.6643 | 39.0699 | 2.6553 | 0.76558 | 0.29045 | 3.7114 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-09-07 | 33 | 28.3126 | 10.1784 | 38.491 | 2.5772 | 0.76558 | 0.28615 | 3.629 | 9.428% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-09-07 | 34 | 28.5283 | 10.3919 | 38.9202 | 2.635 | 0.76558 | 0.28934 | 3.6899 | 9.481% | 10.09% | 6.817% | 1.1047 | 1.1122 | 1.0732
2010-09-07 | 35 | 29.2452 | 10.9378 | 40.183 | 2.8088 | 0.76558 | 0.29873 | 3.8731 | 9.639% | 10.26% | 6.93% | 1.1067 | 1.1143 | 1.0745
2010-09-07 | 36 | 31.3282 | 12.0952 | 43.4234 | 3.2801 | 0.76558 | 0.32282 | 4.3685 | 10.06% | 10.7% | 7.233% | 1.1119 | 1.1199 | 1.078
2010-09-07 | 37 | 33.8863 | 12.6069 | 46.4931 | 3.7602 | 0.76558 | 0.34564 | 4.8714 | 10.48% | 11.15% | 7.533% | 1.117 | 1.1255 | 1.0815
2010-09-07 | 38 | 36.5854 | 12.7539 | 49.3394 | 4.2347 | 0.76558 | 0.36679 | 5.3671 | 10.88% | 11.57% | 7.821% | 1.1221 | 1.1309 | 1.0848
2010-09-07 | 39 | 36.9727 | 12.5502 | 49.5229 | 4.2663 | 0.76558 | 0.36816 | 5.4 | 10.9% | 11.6% | 7.84% | 1.1224 | 1.1312 | 1.0851
2010-09-07 | 40 | 36.3398 | 11.9004 | 48.2401 | 4.0481 | 0.76558 | 0.35862 | 5.1723 | 10.72% | 11.41% | 7.709% | 1.1201 | 1.1288 | 1.0835
2010-09-07 | 41 | 36.5555 | 11.4423 | 47.9978 | 4.0075 | 0.76558 | 0.35682 | 5.1299 | 10.69% | 11.37% | 7.685% | 1.1197 | 1.1283 | 1.0832
2010-09-07 | 42 | 36.0503 | 10.7962 | 46.8465 | 3.8176 | 0.76558 | 0.34826 | 4.9314 | 10.53% | 11.2% | 7.569% | 1.1177 | 1.1261 | 1.0819
2010-09-07 | 43 | 34.5127 | 10.17 | 44.6826 | 3.4731 | 0.76558 | 0.33218 | 4.5708 | 10.23% | 10.88% | 7.355% | 1.114 | 1.1221 | 1.0794
2010-09-07 | 44 | 32.0551 | 9.5084 | 41.5635 | 3.0051 | 0.76558 | 0.30899 | 4.0797 | 9.816% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-09-07 | 45 | 28.6483 | 8.4392 | 37.0875 | 2.3927 | 0.76558 | 0.27571 | 3.434 | 9.259% | 9.852% | 6.657% | 1.102 | 1.1093 | 1.0713
2010-09-07 | 46 | 26.0905 | 7.4857 | 33.5762 | 1.9611 | 0.76558 | 0.24961 | 2.9763 | 8.864% | 9.432% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-09-07 | 47 | 25.6443 | 7.6028 | 33.2471 | 1.9228 | 0.76558 | 0.24716 | 2.9356 | 8.83% | 9.395% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-09-07 | 48 | 26.8349 | 7.8551 | 34.69 | 2.0934 | 0.76558 | 0.25789 | 3.1168 | 8.985% | 9.56% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-09-08 | 1 | 25.412 | 7.0869 | 32.4989 | 1.8373 | 0.76558 | 0.2416 | 2.8444 | 8.752% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-09-08 | 2 | 23.974 | 6.6186 | 30.5926 | 1.6281 | 0.76558 | 0.22743 | 2.6211 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-09-08 | 3 | 23.0246 | 6.3182 | 29.3428 | 1.4977 | 0.76558 | 0.21814 | 2.4815 | 8.457% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-09-08 | 4 | 22.4571 | 6.0392 | 28.4963 | 1.4126 | 0.76558 | 0.21184 | 2.39 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2010-09-08 | 5 | 22.3561 | 5.9442 | 28.3003 | 1.3932 | 0.76558 | 0.21039 | 2.3692 | 8.372% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-09-08 | 6 | 21.8587 | 5.7838 | 27.6425 | 1.3292 | 0.76558 | 0.2055 | 2.3003 | 8.322% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-09-08 | 7 | 21.5937 | 5.7212 | 27.315 | 1.2979 | 0.76558 | 0.20306 | 2.2665 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-09-08 | 8 | 21.5635 | 5.759 | 27.3225 | 1.2986 | 0.76558 | 0.20312 | 2.2673 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0635
2010-09-08 | 9 | 21.1962 | 5.8874 | 27.0836 | 1.276 | 0.76558 | 0.20134 | 2.2429 | 8.281% | 8.811% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-09-08 | 10 | 21.5919 | 5.8856 | 27.4775 | 1.3134 | 0.76558 | 0.20427 | 2.2832 | 8.309% | 8.841% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-09-08 | 11 | 21.9489 | 6.0578 | 28.0067 | 1.3645 | 0.76558 | 0.20821 | 2.3382 | 8.349% | 8.883% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-09-08 | 12 | 22.6597 | 6.5508 | 29.2105 | 1.4843 | 0.76558 | 0.21715 | 2.467 | 8.446% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-09-08 | 13 | 24.1388 | 7.5528 | 31.6916 | 1.7471 | 0.76558 | 0.2356 | 2.7483 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2010-09-08 | 14 | 27.4138 | 9.3176 | 36.7314 | 2.347 | 0.76558 | 0.27307 | 3.3856 | 9.217% | 9.807% | 6.627% | 1.1015 | 1.1087 | 1.071
2010-09-08 | 15 | 32.0096 | 11.2595 | 43.2691 | 3.2568 | 0.76558 | 0.32167 | 4.344 | 10.04% | 10.68% | 7.218% | 1.1116 | 1.1196 | 1.0778
2010-09-08 | 16 | 33.2875 | 11.9556 | 45.2431 | 3.5607 | 0.76558 | 0.33634 | 4.6627 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-09-08 | 17 | 34.2073 | 12.2886 | 46.4959 | 3.7607 | 0.76558 | 0.34566 | 4.8719 | 10.48% | 11.15% | 7.534% | 1.117 | 1.1255 | 1.0815
2010-09-08 | 18 | 34.1479 | 11.639 | 45.7869 | 3.6468 | 0.76558 | 0.34039 | 4.7528 | 10.38% | 11.04% | 7.463% | 1.1158 | 1.1242 | 1.0807
2010-09-08 | 19 | 33.4304 | 11.1843 | 44.6147 | 3.4625 | 0.76558 | 0.33167 | 4.5598 | 10.22% | 10.87% | 7.348% | 1.1138 | 1.122 | 1.0793
2010-09-08 | 20 | 31.822 | 10.4452 | 42.2672 | 3.1077 | 0.76558 | 0.31422 | 4.1875 | 9.907% | 10.54% | 7.123% | 1.11 | 1.1178 | 1.0767
2010-09-08 | 21 | 32.2243 | 10.0919 | 42.3162 | 3.1149 | 0.76558 | 0.31458 | 4.1951 | 9.914% | 10.55% | 7.128% | 1.11 | 1.1179 | 1.0767
2010-09-08 | 22 | 31.3048 | 9.9969 | 41.3017 | 2.9674 | 0.76558 | 0.30704 | 4.04 | 9.782% | 10.41% | 7.033% | 1.1084 | 1.1162 | 1.0757
2010-09-08 | 23 | 29.8976 | 9.5757 | 39.4733 | 2.7105 | 0.76558 | 0.29345 | 3.7695 | 9.549% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-09-08 | 24 | 29.1251 | 9.3932 | 38.5183 | 2.5809 | 0.76558 | 0.28635 | 3.6328 | 9.431% | 10.04% | 6.781% | 1.1041 | 1.1115 | 1.0727
2010-09-08 | 25 | 27.6309 | 9.3823 | 37.0132 | 2.3831 | 0.76558 | 0.27516 | 3.4239 | 9.25% | 9.842% | 6.651% | 1.1019 | 1.1092 | 1.0712
2010-09-08 | 26 | 26.5963 | 8.5941 | 35.1903 | 2.1542 | 0.76558 | 0.26161 | 3.1814 | 9.04% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2010-09-08 | 27 | 26.5552 | 8.7841 | 35.3393 | 2.1725 | 0.76558 | 0.26272 | 3.2008 | 9.057% | 9.637% | 6.512% | 1.0996 | 1.1066 | 1.0697
2010-09-08 | 28 | 26.5293 | 8.7779 | 35.3072 | 2.1685 | 0.76558 | 0.26248 | 3.1966 | 9.054% | 9.633% | 6.51% | 1.0995 | 1.1066 | 1.0696
2010-09-08 | 29 | 25.9138 | 8.3405 | 34.2543 | 2.0411 | 0.76558 | 0.25465 | 3.0613 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2010-09-08 | 30 | 25.8724 | 8.1798 | 34.0522 | 2.0171 | 0.76558 | 0.25315 | 3.0358 | 8.915% | 9.486% | 6.41% | 1.0979 | 1.1048 | 1.0685
2010-09-08 | 31 | 27.1104 | 8.1159 | 35.2263 | 2.1586 | 0.76558 | 0.26188 | 3.186 | 9.044% | 9.623% | 6.503% | 1.0994 | 1.1065 | 1.0696
2010-09-08 | 32 | 27.1142 | 8.1848 | 35.299 | 2.1675 | 0.76558 | 0.26242 | 3.1955 | 9.053% | 9.632% | 6.509% | 1.0995 | 1.1066 | 1.0696
2010-09-08 | 33 | 26.8034 | 8.474 | 35.2773 | 2.1648 | 0.76558 | 0.26226 | 3.1927 | 9.05% | 9.629% | 6.507% | 1.0995 | 1.1066 | 1.0696
2010-09-08 | 34 | 27.2238 | 8.7376 | 35.9613 | 2.2496 | 0.76558 | 0.26734 | 3.2825 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2010-09-08 | 35 | 27.4618 | 9.1991 | 36.6608 | 2.338 | 0.76558 | 0.27254 | 3.3761 | 9.209% | 9.798% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-09-08 | 36 | 28.6519 | 9.9098 | 38.5617 | 2.5867 | 0.76558 | 0.28667 | 3.639 | 9.437% | 10.04% | 6.785% | 1.1042 | 1.1116 | 1.0728
2010-09-08 | 37 | 31.7539 | 10.9165 | 42.6704 | 3.1673 | 0.76558 | 0.31722 | 4.2501 | 9.96% | 10.6% | 7.161% | 1.1106 | 1.1185 | 1.0771
2010-09-08 | 38 | 34.3082 | 11.7938 | 46.102 | 3.6972 | 0.76558 | 0.34273 | 4.8055 | 10.42% | 11.09% | 7.495% | 1.1164 | 1.1247 | 1.081
2010-09-08 | 39 | 34.7192 | 11.8102 | 46.5295 | 3.7661 | 0.76558 | 0.34591 | 4.8776 | 10.48% | 11.15% | 7.537% | 1.1171 | 1.1255 | 1.0815
2010-09-08 | 40 | 34.0949 | 11.323 | 45.4179 | 3.5883 | 0.76558 | 0.33764 | 4.6915 | 10.33% | 10.99% | 7.427% | 1.1152 | 1.1235 | 1.0802
2010-09-08 | 41 | 34.2891 | 10.9219 | 45.211 | 3.5557 | 0.76558 | 0.3361 | 4.6574 | 10.3% | 10.96% | 7.407% | 1.1148 | 1.1231 | 1.08
2010-09-08 | 42 | 33.8451 | 10.4822 | 44.3272 | 3.418 | 0.76558 | 0.32953 | 4.5131 | 10.18% | 10.83% | 7.32% | 1.1134 | 1.1215 | 1.079
2010-09-08 | 43 | 32.3971 | 9.9412 | 42.3383 | 3.1182 | 0.76558 | 0.31475 | 4.1985 | 9.917% | 10.55% | 7.13% | 1.1101 | 1.118 | 1.0768
2010-09-08 | 44 | 30.6157 | 9.3359 | 39.9516 | 2.7765 | 0.76558 | 0.297 | 3.8391 | 9.609% | 10.22% | 6.909% | 1.1063 | 1.1139 | 1.0742
2010-09-08 | 45 | 27.3002 | 8.3712 | 35.6715 | 2.2135 | 0.76558 | 0.26519 | 3.2443 | 9.095% | 9.677% | 6.539% | 1.1 | 1.1071 | 1.07
2010-09-08 | 46 | 24.7006 | 7.3935 | 32.0941 | 1.7918 | 0.76558 | 0.23859 | 2.7959 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-09-08 | 47 | 24.1263 | 7.4041 | 31.5304 | 1.7294 | 0.76558 | 0.2344 | 2.7294 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2010-09-08 | 48 | 24.9037 | 7.7989 | 32.7025 | 1.8604 | 0.76558 | 0.24311 | 2.8691 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-09-09 | 1 | 22.9633 | 6.8976 | 29.8608 | 1.5511 | 0.76558 | 0.22199 | 2.5387 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-09-09 | 2 | 21.4694 | 6.4332 | 27.9026 | 1.3543 | 0.76558 | 0.20743 | 2.3273 | 8.341% | 8.875% | 5.997% | 1.091 | 1.0974 | 1.0638
2010-09-09 | 3 | 20.4996 | 6.0876 | 26.5872 | 1.2296 | 0.76558 | 0.19765 | 2.1929 | 8.248% | 8.776% | 5.93% | 1.0899 | 1.0962 | 1.063
2010-09-09 | 4 | 20.1273 | 5.8513 | 25.9786 | 1.174 | 0.76558 | 0.19313 | 2.1327 | 8.209% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-09-09 | 5 | 19.5875 | 5.7619 | 25.3494 | 1.1178 | 0.76558 | 0.18845 | 2.0718 | 8.173% | 8.696% | 5.876% | 1.089 | 1.0952 | 1.0624
2010-09-09 | 6 | 19.4375 | 5.5765 | 25.014 | 1.0884 | 0.76558 | 0.18596 | 2.04 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-09-09 | 7 | 19.3078 | 5.5314 | 24.8392 | 1.0733 | 0.76558 | 0.18466 | 2.0235 | 8.146% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-09-09 | 8 | 19.1571 | 5.6343 | 24.7913 | 1.0691 | 0.76558 | 0.1843 | 2.019 | 8.144% | 8.665% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-09-09 | 9 | 19.2552 | 5.7588 | 25.014 | 1.0884 | 0.76558 | 0.18596 | 2.04 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-09-09 | 10 | 19.6515 | 5.9324 | 25.5839 | 1.1386 | 0.76558 | 0.19019 | 2.0944 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-09-09 | 11 | 20.6466 | 6.1583 | 26.8049 | 1.2499 | 0.76558 | 0.19927 | 2.2147 | 8.262% | 8.791% | 5.941% | 1.0901 | 1.0964 | 1.0632
2010-09-09 | 12 | 21.5516 | 6.6204 | 28.1721 | 1.3806 | 0.76558 | 0.20943 | 2.3556 | 8.362% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-09-09 | 13 | 23.553 | 7.8065 | 31.3595 | 1.7107 | 0.76558 | 0.23313 | 2.7094 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-09-09 | 14 | 26.9276 | 9.5077 | 36.4353 | 2.3093 | 0.76558 | 0.27086 | 3.3457 | 9.183% | 9.77% | 6.602% | 1.1011 | 1.1083 | 1.0707
2010-09-09 | 15 | 31.306 | 11.9865 | 43.2924 | 3.2603 | 0.76558 | 0.32184 | 4.3477 | 10.04% | 10.69% | 7.221% | 1.1116 | 1.1196 | 1.0778
2010-09-09 | 16 | 33.1002 | 12.9021 | 46.0023 | 3.6812 | 0.76558 | 0.34199 | 4.7888 | 10.41% | 11.08% | 7.485% | 1.1162 | 1.1246 | 1.0809
2010-09-09 | 17 | 33.3685 | 13.1922 | 46.5608 | 3.7712 | 0.76558 | 0.34614 | 4.8829 | 10.49% | 11.16% | 7.54% | 1.1172 | 1.1256 | 1.0816
2010-09-09 | 18 | 33.4108 | 12.857 | 46.2678 | 3.7239 | 0.76558 | 0.34396 | 4.8334 | 10.45% | 11.12% | 7.511% | 1.1167 | 1.1251 | 1.0812
2010-09-09 | 19 | 33.4944 | 12.0836 | 45.578 | 3.6136 | 0.76558 | 0.33883 | 4.7181 | 10.35% | 11.01% | 7.443% | 1.1155 | 1.1238 | 1.0804
2010-09-09 | 20 | 32.3275 | 11.2896 | 43.6172 | 3.3094 | 0.76558 | 0.32426 | 4.3992 | 10.09% | 10.73% | 7.252% | 1.1122 | 1.1202 | 1.0782
2010-09-09 | 21 | 33.1296 | 10.764 | 43.8936 | 3.3515 | 0.76558 | 0.32631 | 4.4434 | 10.12% | 10.77% | 7.278% | 1.1126 | 1.1207 | 1.0785
2010-09-09 | 22 | 32.0071 | 10.2625 | 42.2695 | 3.1081 | 0.76558 | 0.31424 | 4.1879 | 9.908% | 10.54% | 7.124% | 1.11 | 1.1178 | 1.0767
2010-09-09 | 23 | 30.8988 | 9.8078 | 40.7066 | 2.8825 | 0.76558 | 0.30262 | 3.9507 | 9.705% | 10.33% | 6.978% | 1.1075 | 1.1152 | 1.075
2010-09-09 | 24 | 29.4461 | 9.7064 | 39.1525 | 2.6666 | 0.76558 | 0.29106 | 3.7232 | 9.51% | 10.12% | 6.837% | 1.1051 | 1.1126 | 1.0734
2010-09-09 | 25 | 27.9053 | 9.4016 | 37.3069 | 2.4211 | 0.76558 | 0.27734 | 3.464 | 9.285% | 9.879% | 6.676% | 1.1024 | 1.1096 | 1.0715
2010-09-09 | 26 | 26.6837 | 8.8118 | 35.4955 | 2.1917 | 0.76558 | 0.26388 | 3.2212 | 9.075% | 9.656% | 6.525% | 1.0998 | 1.1069 | 1.0698
2010-09-09 | 27 | 26.8256 | 8.9285 | 35.7541 | 2.2238 | 0.76558 | 0.2658 | 3.2551 | 9.104% | 9.687% | 6.546% | 1.1002 | 1.1073 | 1.07
2010-09-09 | 28 | 27.1097 | 9.044 | 36.1537 | 2.2737 | 0.76558 | 0.26877 | 3.3081 | 9.15% | 9.736% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-09-09 | 29 | 27.008 | 8.7124 | 35.7204 | 2.2196 | 0.76558 | 0.26555 | 3.2507 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-09-09 | 30 | 26.8634 | 8.3812 | 35.2446 | 2.1608 | 0.76558 | 0.26201 | 3.1884 | 9.047% | 9.626% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-09-09 | 31 | 28.0991 | 8.3756 | 36.4747 | 2.3143 | 0.76558 | 0.27116 | 3.351 | 9.187% | 9.775% | 6.606% | 1.1012 | 1.1083 | 1.0707
2010-09-09 | 32 | 28.1422 | 8.3972 | 36.5395 | 2.3225 | 0.76558 | 0.27164 | 3.3597 | 9.195% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2010-09-09 | 33 | 27.8271 | 8.7471 | 36.5742 | 2.3269 | 0.76558 | 0.2719 | 3.3644 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-09-09 | 34 | 28.0291 | 9.0429 | 37.072 | 2.3907 | 0.76558 | 0.2756 | 3.4319 | 9.257% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-09-09 | 35 | 28.2604 | 9.6519 | 37.9123 | 2.5003 | 0.76558 | 0.28184 | 3.5477 | 9.358% | 9.957% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-09-09 | 36 | 30.5024 | 10.3886 | 40.891 | 2.9086 | 0.76558 | 0.30399 | 3.9782 | 9.729% | 10.35% | 6.995% | 1.1078 | 1.1155 | 1.0752
2010-09-09 | 37 | 33.5482 | 11.2382 | 44.7864 | 3.4892 | 0.76558 | 0.33295 | 4.5877 | 10.24% | 10.9% | 7.365% | 1.1141 | 1.1223 | 1.0795
2010-09-09 | 38 | 35.3439 | 11.938 | 47.2819 | 3.8889 | 0.76558 | 0.3515 | 5.006 | 10.59% | 11.27% | 7.612% | 1.1184 | 1.127 | 1.0824
2010-09-09 | 39 | 35.5561 | 11.775 | 47.3311 | 3.897 | 0.76558 | 0.35187 | 5.0144 | 10.59% | 11.27% | 7.617% | 1.1185 | 1.127 | 1.0825
2010-09-09 | 40 | 34.9538 | 11.4593 | 46.4131 | 3.7473 | 0.76558 | 0.34504 | 4.8579 | 10.47% | 11.14% | 7.526% | 1.1169 | 1.1253 | 1.0814
2010-09-09 | 41 | 34.9527 | 11.0646 | 46.0173 | 3.6836 | 0.76558 | 0.3421 | 4.7913 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-09-09 | 42 | 34.4643 | 10.8065 | 45.2708 | 3.5651 | 0.76558 | 0.33655 | 4.6672 | 10.31% | 10.97% | 7.413% | 1.1149 | 1.1232 | 1.0801
2010-09-09 | 43 | 32.7251 | 10.1826 | 42.9077 | 3.2026 | 0.76558 | 0.31898 | 4.2872 | 9.992% | 10.63% | 7.184% | 1.111 | 1.119 | 1.0774
2010-09-09 | 44 | 30.9547 | 9.7071 | 40.6619 | 2.8761 | 0.76558 | 0.30229 | 3.944 | 9.7% | 10.32% | 6.974% | 1.1074 | 1.1151 | 1.075
2010-09-09 | 45 | 27.6508 | 8.7176 | 36.3684 | 2.3008 | 0.76558 | 0.27037 | 3.3368 | 9.175% | 9.762% | 6.597% | 1.101 | 1.1082 | 1.0706
2010-09-09 | 46 | 24.9215 | 7.9069 | 32.8285 | 1.8747 | 0.76558 | 0.24405 | 2.8843 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-09-09 | 47 | 24.502 | 7.8015 | 32.3035 | 1.8152 | 0.76558 | 0.24015 | 2.821 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-09-09 | 48 | 25.0778 | 7.9468 | 33.0246 | 1.8972 | 0.76558 | 0.24551 | 2.9083 | 8.806% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-09-10 | 1 | 22.9206 | 7.1389 | 30.0595 | 1.5718 | 0.76558 | 0.22347 | 2.5608 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0653
2010-09-10 | 2 | 21.3691 | 6.4369 | 27.806 | 1.345 | 0.76558 | 0.20671 | 2.3173 | 8.334% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-09-10 | 3 | 20.3622 | 6.0566 | 26.4188 | 1.2141 | 0.76558 | 0.1964 | 2.1761 | 8.237% | 8.764% | 5.922% | 1.0898 | 1.0961 | 1.063
2010-09-10 | 4 | 19.6852 | 5.8548 | 25.5399 | 1.1347 | 0.76558 | 0.18987 | 2.0901 | 8.184% | 8.708% | 5.884% | 1.0891 | 1.0954 | 1.0625
2010-09-10 | 5 | 19.5258 | 5.7225 | 25.2484 | 1.1089 | 0.76558 | 0.1877 | 2.0622 | 8.168% | 8.69% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-09-10 | 6 | 19.3671 | 5.6638 | 25.031 | 1.0899 | 0.76558 | 0.18608 | 2.0416 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-09-10 | 7 | 18.9788 | 5.5488 | 24.5276 | 1.0465 | 0.76558 | 0.18234 | 1.9944 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-09-10 | 8 | 18.9061 | 5.513 | 24.4191 | 1.0373 | 0.76558 | 0.18153 | 1.9844 | 8.126% | 8.646% | 5.843% | 1.0885 | 1.0946 | 1.0621
2010-09-10 | 9 | 18.8897 | 5.7012 | 24.5909 | 1.0519 | 0.76558 | 0.18281 | 2.0003 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0948 | 1.0621
2010-09-10 | 10 | 19.1919 | 5.7545 | 24.9464 | 1.0826 | 0.76558 | 0.18545 | 2.0336 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2010-09-10 | 11 | 19.678 | 5.9021 | 25.58 | 1.1382 | 0.76558 | 0.19016 | 2.094 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-09-10 | 12 | 20.6411 | 6.4142 | 27.0553 | 1.2733 | 0.76558 | 0.20113 | 2.24 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-09-10 | 13 | 22.7229 | 7.393 | 30.1159 | 1.5777 | 0.76558 | 0.22388 | 2.5672 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-09-10 | 14 | 25.7813 | 8.905 | 34.6862 | 2.0929 | 0.76558 | 0.25786 | 3.1163 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2010-09-10 | 15 | 29.9305 | 10.8577 | 40.7882 | 2.894 | 0.76558 | 0.30322 | 3.9628 | 9.716% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-09-10 | 16 | 31.6844 | 11.8983 | 43.5826 | 3.3042 | 0.76558 | 0.324 | 4.3937 | 10.08% | 10.73% | 7.249% | 1.1121 | 1.1202 | 1.0782
2010-09-10 | 17 | 32.9742 | 12.4731 | 45.4473 | 3.593 | 0.76558 | 0.33786 | 4.6964 | 10.33% | 11% | 7.43% | 1.1152 | 1.1235 | 1.0803
2010-09-10 | 18 | 33.2611 | 12.4178 | 45.6789 | 3.6297 | 0.76558 | 0.33958 | 4.7348 | 10.37% | 11.03% | 7.453% | 1.1156 | 1.124 | 1.0805
2010-09-10 | 19 | 33.1749 | 12.1297 | 45.3047 | 3.5704 | 0.76558 | 0.3368 | 4.6728 | 10.31% | 10.97% | 7.416% | 1.115 | 1.1233 | 1.0801
2010-09-10 | 20 | 32.3393 | 11.6077 | 43.947 | 3.3596 | 0.76558 | 0.32671 | 4.4519 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-09-10 | 21 | 33.4449 | 11.2327 | 44.6776 | 3.4723 | 0.76558 | 0.33214 | 4.57 | 10.23% | 10.88% | 7.355% | 1.1139 | 1.1221 | 1.0794
2010-09-10 | 22 | 32.8559 | 11.0946 | 43.9505 | 3.3602 | 0.76558 | 0.32673 | 4.4525 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-09-10 | 23 | 31.2439 | 10.5896 | 41.8335 | 3.0443 | 0.76558 | 0.311 | 4.1208 | 9.851% | 10.48% | 7.083% | 1.1093 | 1.1171 | 1.0762
2010-09-10 | 24 | 29.5343 | 10.4652 | 39.9995 | 2.7832 | 0.76558 | 0.29736 | 3.8461 | 9.615% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-09-10 | 25 | 27.6367 | 10.4021 | 38.0388 | 2.517 | 0.76558 | 0.28279 | 3.5654 | 9.373% | 9.973% | 6.739% | 1.1034 | 1.1108 | 1.0723
2010-09-10 | 26 | 26.5305 | 10.0618 | 36.5923 | 2.3292 | 0.76558 | 0.27203 | 3.3668 | 9.201% | 9.79% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-09-10 | 27 | 27.1483 | 9.8286 | 36.9769 | 2.3785 | 0.76558 | 0.27489 | 3.4189 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-09-10 | 28 | 27.1477 | 9.6375 | 36.7853 | 2.3539 | 0.76558 | 0.27347 | 3.3929 | 9.224% | 9.814% | 6.632% | 1.1016 | 1.1088 | 1.071
2010-09-10 | 29 | 26.847 | 9.2249 | 36.0719 | 2.2635 | 0.76558 | 0.26816 | 3.2972 | 9.141% | 9.726% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-09-10 | 30 | 26.4464 | 8.9266 | 35.373 | 2.1766 | 0.76558 | 0.26297 | 3.2051 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-09-10 | 31 | 27.4281 | 8.9589 | 36.387 | 2.3032 | 0.76558 | 0.27051 | 3.3393 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2010-09-10 | 32 | 27.7878 | 9.0067 | 36.7945 | 2.3551 | 0.76558 | 0.27353 | 3.3942 | 9.225% | 9.815% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-09-10 | 33 | 27.8368 | 9.3602 | 37.1971 | 2.4069 | 0.76558 | 0.27653 | 3.449 | 9.272% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-09-10 | 34 | 28.2015 | 9.6459 | 37.8474 | 2.4918 | 0.76558 | 0.28136 | 3.5387 | 9.35% | 9.948% | 6.723% | 1.1031 | 1.1105 | 1.0721
2010-09-10 | 35 | 28.5682 | 10.2578 | 38.826 | 2.6223 | 0.76558 | 0.28864 | 3.6765 | 9.469% | 10.08% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-09-10 | 36 | 30.3284 | 10.934 | 41.2624 | 2.9617 | 0.76558 | 0.30675 | 4.034 | 9.777% | 10.4% | 7.029% | 1.1084 | 1.1161 | 1.0756
2010-09-10 | 37 | 32.1317 | 11.66 | 43.7917 | 3.3359 | 0.76558 | 0.32555 | 4.4271 | 10.11% | 10.76% | 7.269% | 1.1125 | 1.1205 | 1.0784
2010-09-10 | 38 | 33.9069 | 11.8444 | 45.7513 | 3.6412 | 0.76558 | 0.34012 | 4.7469 | 10.38% | 11.04% | 7.46% | 1.1158 | 1.1241 | 1.0806
2010-09-10 | 39 | 34.0726 | 11.7475 | 45.8201 | 3.6521 | 0.76558 | 0.34063 | 4.7583 | 10.38% | 11.05% | 7.467% | 1.1159 | 1.1242 | 1.0807
2010-09-10 | 40 | 33.6504 | 11.2916 | 44.942 | 3.5135 | 0.76558 | 0.3341 | 4.6132 | 10.26% | 10.92% | 7.38% | 1.1144 | 1.1226 | 1.0797
2010-09-10 | 41 | 33.6854 | 10.8638 | 44.5492 | 3.4523 | 0.76558 | 0.33118 | 4.5491 | 10.21% | 10.86% | 7.342% | 1.1137 | 1.1219 | 1.0792
2010-09-10 | 42 | 33.1041 | 10.563 | 43.6671 | 3.317 | 0.76558 | 0.32463 | 4.4072 | 10.09% | 10.74% | 7.257% | 1.1123 | 1.1203 | 1.0782
2010-09-10 | 43 | 31.2837 | 9.9141 | 41.1978 | 2.9525 | 0.76558 | 0.30627 | 4.0243 | 9.768% | 10.39% | 7.023% | 1.1083 | 1.116 | 1.0755
2010-09-10 | 44 | 29.6021 | 9.3271 | 38.9292 | 2.6362 | 0.76558 | 0.2894 | 3.6912 | 9.482% | 10.09% | 6.817% | 1.1048 | 1.1122 | 1.0732
2010-09-10 | 45 | 26.315 | 8.6099 | 34.9249 | 2.1218 | 0.76558 | 0.25964 | 3.147 | 9.011% | 9.588% | 6.479% | 1.099 | 1.106 | 1.0693
2010-09-10 | 46 | 23.8451 | 7.7485 | 31.5936 | 1.7363 | 0.76558 | 0.23487 | 2.7368 | 8.662% | 9.217% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-09-10 | 47 | 23.3723 | 7.6724 | 31.0447 | 1.6765 | 0.76558 | 0.23079 | 2.6729 | 8.61% | 9.161% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-09-10 | 48 | 23.6458 | 7.8428 | 31.4886 | 1.7248 | 0.76558 | 0.23409 | 2.7245 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-09-11 | 1 | 22.0798 | 6.8743 | 28.9541 | 1.4583 | 0.76558 | 0.21525 | 2.4392 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-09-11 | 2 | 20.5139 | 6.326 | 26.8399 | 1.2531 | 0.76558 | 0.19953 | 2.2182 | 8.265% | 8.794% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-09-11 | 3 | 19.3497 | 5.8461 | 25.1958 | 1.1043 | 0.76558 | 0.18731 | 2.0572 | 8.165% | 8.687% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-09-11 | 4 | 18.8436 | 5.6579 | 24.5015 | 1.0443 | 0.76558 | 0.18215 | 1.992 | 8.13% | 8.65% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-09-11 | 5 | 18.4104 | 5.5108 | 23.9212 | 0.99541 | 0.76558 | 0.17783 | 1.9388 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-09-11 | 6 | 18.095 | 5.4031 | 23.4981 | 0.9605 | 0.76558 | 0.17469 | 1.9008 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-09-11 | 7 | 17.9523 | 5.3562 | 23.3085 | 0.94507 | 0.76558 | 0.17328 | 1.8839 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-09-11 | 8 | 17.8649 | 5.4016 | 23.2664 | 0.94166 | 0.76558 | 0.17297 | 1.8802 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-09-11 | 9 | 17.7784 | 5.6248 | 23.4032 | 0.95276 | 0.76558 | 0.17398 | 1.8923 | 8.086% | 8.603% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-09-11 | 10 | 18.0509 | 5.6526 | 23.7035 | 0.97737 | 0.76558 | 0.17621 | 1.9192 | 8.097% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-09-11 | 11 | 18.5818 | 5.8628 | 24.4446 | 1.0394 | 0.76558 | 0.18172 | 1.9867 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-09-11 | 12 | 19.6862 | 6.3438 | 26.03 | 1.1786 | 0.76558 | 0.19351 | 2.1377 | 8.213% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-09-11 | 13 | 21.6845 | 7.3168 | 29.0013 | 1.4631 | 0.76558 | 0.2156 | 2.4443 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-09-11 | 14 | 24.8012 | 8.6477 | 33.4489 | 1.9463 | 0.76558 | 0.24866 | 2.9605 | 8.851% | 9.417% | 6.364% | 1.0971 | 1.104 | 1.068
2010-09-11 | 15 | 29.0373 | 10.7025 | 39.7398 | 2.7472 | 0.76558 | 0.29543 | 3.8082 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-09-11 | 16 | 30.5453 | 11.5341 | 42.0794 | 3.0802 | 0.76558 | 0.31282 | 4.1586 | 9.883% | 10.52% | 7.106% | 1.1097 | 1.1175 | 1.0765
2010-09-11 | 17 | 31.5371 | 11.5832 | 43.1203 | 3.2344 | 0.76558 | 0.32056 | 4.3206 | 10.02% | 10.66% | 7.204% | 1.1114 | 1.1193 | 1.0776
2010-09-11 | 18 | 31.3367 | 11.3183 | 42.655 | 3.165 | 0.76558 | 0.3171 | 4.2477 | 9.958% | 10.6% | 7.16% | 1.1106 | 1.1185 | 1.0771
2010-09-11 | 19 | 30.6045 | 10.9162 | 41.5207 | 2.9989 | 0.76558 | 0.30867 | 4.0732 | 9.81% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-09-11 | 20 | 29.9998 | 10.3673 | 40.3671 | 2.8346 | 0.76558 | 0.30009 | 3.9003 | 9.662% | 10.28% | 6.947% | 1.107 | 1.1146 | 1.0747
2010-09-11 | 21 | 30.7117 | 9.8173 | 40.529 | 2.8574 | 0.76558 | 0.3013 | 3.9242 | 9.683% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-09-11 | 22 | 30.0711 | 9.5817 | 39.6528 | 2.7352 | 0.76558 | 0.29478 | 3.7955 | 9.572% | 10.18% | 6.882% | 1.1059 | 1.1134 | 1.0739
2010-09-11 | 23 | 28.9915 | 9.1052 | 38.0967 | 2.5247 | 0.76558 | 0.28322 | 3.5735 | 9.38% | 9.98% | 6.744% | 1.1035 | 1.1109 | 1.0723
2010-09-11 | 24 | 28.3742 | 9.0472 | 37.4214 | 2.436 | 0.76558 | 0.2782 | 3.4798 | 9.299% | 9.894% | 6.686% | 1.1025 | 1.1098 | 1.0716
2010-09-11 | 25 | 27.4542 | 9.0603 | 36.5145 | 2.3193 | 0.76558 | 0.27145 | 3.3564 | 9.192% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2010-09-11 | 26 | 26.4627 | 8.7421 | 35.2047 | 2.1559 | 0.76558 | 0.26172 | 3.1832 | 9.042% | 9.621% | 6.501% | 1.0994 | 1.1064 | 1.0695
2010-09-11 | 27 | 26.2051 | 9.0885 | 35.2936 | 2.1668 | 0.76558 | 0.26238 | 3.1948 | 9.052% | 9.631% | 6.508% | 1.0995 | 1.1066 | 1.0696
2010-09-11 | 28 | 26.449 | 9.147 | 35.596 | 2.2041 | 0.76558 | 0.26463 | 3.2343 | 9.086% | 9.668% | 6.533% | 1.0999 | 1.107 | 1.0699
2010-09-11 | 29 | 26.2336 | 8.678 | 34.9117 | 2.1202 | 0.76558 | 0.25954 | 3.1453 | 9.009% | 9.586% | 6.478% | 1.099 | 1.106 | 1.0693
2010-09-11 | 30 | 25.9039 | 8.3933 | 34.2972 | 2.0462 | 0.76558 | 0.25497 | 3.0668 | 8.942% | 9.514% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-09-11 | 31 | 26.8929 | 8.2867 | 35.1796 | 2.1529 | 0.76558 | 0.26153 | 3.18 | 9.039% | 9.618% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-09-11 | 32 | 26.6631 | 8.3934 | 35.0565 | 2.1378 | 0.76558 | 0.26061 | 3.164 | 9.025% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-09-11 | 33 | 26.2548 | 8.5735 | 34.8282 | 2.1101 | 0.76558 | 0.25892 | 3.1346 | 9% | 9.576% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-09-11 | 34 | 26.6052 | 8.4699 | 35.0751 | 2.1401 | 0.76558 | 0.26075 | 3.1664 | 9.028% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-09-11 | 35 | 26.2857 | 8.6074 | 34.893 | 2.1179 | 0.76558 | 0.2594 | 3.1429 | 9.007% | 9.584% | 6.476% | 1.099 | 1.106 | 1.0692
2010-09-11 | 36 | 27.2763 | 8.8956 | 36.1719 | 2.276 | 0.76558 | 0.26891 | 3.3105 | 9.152% | 9.738% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-09-11 | 37 | 29.4302 | 9.8321 | 39.2623 | 2.6815 | 0.76558 | 0.29188 | 3.739 | 9.523% | 10.13% | 6.847% | 1.1053 | 1.1128 | 1.0735
2010-09-11 | 38 | 31.3087 | 10.6313 | 41.94 | 3.0598 | 0.76558 | 0.31179 | 4.1371 | 9.864% | 10.5% | 7.093% | 1.1094 | 1.1173 | 1.0763
2010-09-11 | 39 | 31.6406 | 10.795 | 42.4356 | 3.1325 | 0.76558 | 0.31547 | 4.2136 | 9.929% | 10.56% | 7.139% | 1.1102 | 1.1181 | 1.0769
2010-09-11 | 40 | 31.4395 | 10.4721 | 41.9116 | 3.0556 | 0.76558 | 0.31158 | 4.1328 | 9.861% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-09-11 | 41 | 31.829 | 10.1178 | 41.9467 | 3.0608 | 0.76558 | 0.31184 | 4.1382 | 9.865% | 10.5% | 7.093% | 1.1095 | 1.1173 | 1.0763
2010-09-11 | 42 | 31.2968 | 9.7826 | 41.0794 | 2.9355 | 0.76558 | 0.30539 | 4.0065 | 9.753% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-09-11 | 43 | 29.8596 | 9.5657 | 39.4253 | 2.7039 | 0.76558 | 0.29309 | 3.7625 | 9.543% | 10.15% | 6.862% | 1.1055 | 1.113 | 1.0737
2010-09-11 | 44 | 28.2517 | 9.0568 | 37.3085 | 2.4213 | 0.76558 | 0.27736 | 3.4642 | 9.285% | 9.88% | 6.676% | 1.1024 | 1.1096 | 1.0715
2010-09-11 | 45 | 26.0941 | 8.3184 | 34.4125 | 2.06 | 0.76558 | 0.25583 | 3.0814 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-09-11 | 46 | 23.6229 | 7.4651 | 31.088 | 1.6812 | 0.76558 | 0.23111 | 2.6779 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2010-09-11 | 47 | 23.5128 | 7.3766 | 30.8894 | 1.6598 | 0.76558 | 0.22964 | 2.655 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-09-11 | 48 | 24.2884 | 7.7127 | 32.0011 | 1.7814 | 0.76558 | 0.2379 | 2.7849 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2010-09-12 | 1 | 22.6081 | 6.787 | 29.395 | 1.5031 | 0.76558 | 0.21853 | 2.4872 | 8.461% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-09-12 | 2 | 21.0545 | 6.2181 | 27.2727 | 1.2939 | 0.76558 | 0.20275 | 2.2622 | 8.295% | 8.826% | 5.964% | 1.0904 | 1.0968 | 1.0634
2010-09-12 | 3 | 19.8914 | 5.8177 | 25.7091 | 1.1498 | 0.76558 | 0.19112 | 2.1065 | 8.193% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-09-12 | 4 | 19.1167 | 5.5513 | 24.668 | 1.0585 | 0.76558 | 0.18338 | 2.0075 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-09-12 | 5 | 18.4841 | 5.466 | 23.9501 | 0.99781 | 0.76558 | 0.17805 | 1.9414 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-09-12 | 6 | 18.3266 | 5.3239 | 23.6505 | 0.97301 | 0.76558 | 0.17582 | 1.9144 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-09-12 | 7 | 18.312 | 5.2914 | 23.6034 | 0.96913 | 0.76558 | 0.17547 | 1.9102 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-09-12 | 8 | 18.0518 | 5.3644 | 23.4161 | 0.95382 | 0.76558 | 0.17408 | 1.8935 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-09-12 | 9 | 18.1953 | 5.4059 | 23.6012 | 0.96895 | 0.76558 | 0.17545 | 1.91 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-09-12 | 10 | 18.1958 | 5.6633 | 23.8591 | 0.99025 | 0.76558 | 0.17737 | 1.9332 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-09-12 | 11 | 18.4857 | 5.8072 | 24.2929 | 1.0266 | 0.76558 | 0.1806 | 1.9728 | 8.121% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-09-12 | 12 | 18.9142 | 6.0084 | 24.9226 | 1.0805 | 0.76558 | 0.18528 | 2.0314 | 8.151% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0623
2010-09-12 | 13 | 20.3372 | 6.5168 | 26.854 | 1.2544 | 0.76558 | 0.19964 | 2.2197 | 8.266% | 8.795% | 5.943% | 1.0901 | 1.0964 | 1.0632
2010-09-12 | 14 | 22.2479 | 7.1827 | 29.4307 | 1.5067 | 0.76558 | 0.21879 | 2.4911 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-09-12 | 15 | 23.9266 | 8.3235 | 32.2501 | 1.8092 | 0.76558 | 0.23975 | 2.8146 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-09-12 | 16 | 24.687 | 9.3162 | 34.0032 | 2.0113 | 0.76558 | 0.25278 | 3.0297 | 8.91% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-09-12 | 17 | 26.6722 | 10.2003 | 36.8725 | 2.3651 | 0.76558 | 0.27411 | 3.4047 | 9.234% | 9.825% | 6.639% | 1.1017 | 1.109 | 1.0711
2010-09-12 | 18 | 28.2799 | 10.9758 | 39.2557 | 2.6807 | 0.76558 | 0.29183 | 3.7381 | 9.522% | 10.13% | 6.847% | 1.1052 | 1.1127 | 1.0735
2010-09-12 | 19 | 29.2396 | 11.3586 | 40.5983 | 2.8671 | 0.76558 | 0.30181 | 3.9345 | 9.691% | 10.31% | 6.968% | 1.1073 | 1.115 | 1.0749
2010-09-12 | 20 | 29.2406 | 11.4803 | 40.721 | 2.8845 | 0.76558 | 0.30272 | 3.9528 | 9.707% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2010-09-12 | 21 | 30.4455 | 11.4024 | 41.8479 | 3.0464 | 0.76558 | 0.3111 | 4.123 | 9.852% | 10.48% | 7.084% | 1.1093 | 1.1171 | 1.0762
2010-09-12 | 22 | 30.0747 | 11.375 | 41.4497 | 2.9887 | 0.76558 | 0.30814 | 4.0624 | 9.801% | 10.43% | 7.047% | 1.1087 | 1.1164 | 1.0758
2010-09-12 | 23 | 28.7666 | 10.5256 | 39.2922 | 2.6856 | 0.76558 | 0.2921 | 3.7433 | 9.527% | 10.14% | 6.85% | 1.1053 | 1.1128 | 1.0735
2010-09-12 | 24 | 27.7609 | 9.8789 | 37.6398 | 2.4645 | 0.76558 | 0.27982 | 3.5099 | 9.325% | 9.922% | 6.705% | 1.1028 | 1.1101 | 1.0719
2010-09-12 | 25 | 26.21 | 9.5411 | 35.7511 | 2.2234 | 0.76558 | 0.26578 | 3.2547 | 9.104% | 9.687% | 6.546% | 1.1002 | 1.1073 | 1.07
2010-09-12 | 26 | 25.262 | 8.9546 | 34.2166 | 2.0366 | 0.76558 | 0.25437 | 3.0566 | 8.933% | 9.505% | 6.423% | 1.0981 | 1.105 | 1.0686
2010-09-12 | 27 | 25.1045 | 8.9762 | 34.0807 | 2.0205 | 0.76558 | 0.25336 | 3.0394 | 8.918% | 9.489% | 6.412% | 1.0979 | 1.1048 | 1.0685
2010-09-12 | 28 | 24.7889 | 8.7697 | 33.5587 | 1.959 | 0.76558 | 0.24948 | 2.9741 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-09-12 | 29 | 24.2863 | 8.2405 | 32.5268 | 1.8404 | 0.76558 | 0.24181 | 2.8478 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-09-12 | 30 | 24.0709 | 7.9243 | 31.9952 | 1.7808 | 0.76558 | 0.23786 | 2.7842 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2010-09-12 | 31 | 25.1468 | 7.8439 | 32.9906 | 1.8933 | 0.76558 | 0.24526 | 2.9041 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-12 | 32 | 25.2198 | 7.7184 | 32.9382 | 1.8873 | 0.76558 | 0.24487 | 2.8977 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-09-12 | 33 | 25.1469 | 7.9959 | 33.1428 | 1.9108 | 0.76558 | 0.24639 | 2.9228 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2010-09-12 | 34 | 25.263 | 8.1197 | 33.3826 | 1.9385 | 0.76558 | 0.24817 | 2.9523 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-09-12 | 35 | 26.0682 | 8.5732 | 34.6414 | 2.0875 | 0.76558 | 0.25753 | 3.1106 | 8.979% | 9.554% | 6.456% | 1.0987 | 1.1056 | 1.069
2010-09-12 | 36 | 27.332 | 9.5224 | 36.8544 | 2.3627 | 0.76558 | 0.27398 | 3.4023 | 9.232% | 9.823% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-09-12 | 37 | 29.1696 | 10.2989 | 39.4685 | 2.7098 | 0.76558 | 0.29341 | 3.7688 | 9.549% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-09-12 | 38 | 30.9645 | 10.9982 | 41.9626 | 3.0631 | 0.76558 | 0.31196 | 4.1406 | 9.867% | 10.5% | 7.095% | 1.1095 | 1.1173 | 1.0764
2010-09-12 | 39 | 31.0934 | 11.0649 | 42.1582 | 3.0917 | 0.76558 | 0.31341 | 4.1707 | 9.893% | 10.53% | 7.113% | 1.1098 | 1.1176 | 1.0766
2010-09-12 | 40 | 30.0594 | 10.3328 | 40.3921 | 2.8381 | 0.76558 | 0.30028 | 3.904 | 9.665% | 10.28% | 6.949% | 1.107 | 1.1146 | 1.0747
2010-09-12 | 41 | 29.8719 | 9.7809 | 39.6529 | 2.7352 | 0.76558 | 0.29478 | 3.7955 | 9.572% | 10.18% | 6.882% | 1.1059 | 1.1134 | 1.0739
2010-09-12 | 42 | 29.1982 | 9.3271 | 38.5254 | 2.5818 | 0.76558 | 0.2864 | 3.6338 | 9.432% | 10.04% | 6.782% | 1.1041 | 1.1116 | 1.0728
2010-09-12 | 43 | 27.5155 | 8.8832 | 36.3987 | 2.3047 | 0.76558 | 0.27059 | 3.3408 | 9.178% | 9.766% | 6.599% | 1.1011 | 1.1082 | 1.0707
2010-09-12 | 44 | 26.0794 | 8.4712 | 34.5505 | 2.0766 | 0.76558 | 0.25685 | 3.099 | 8.969% | 9.543% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-09-12 | 45 | 23.941 | 7.8012 | 31.7422 | 1.7527 | 0.76558 | 0.23598 | 2.7543 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-09-12 | 46 | 21.9997 | 7.1258 | 29.1255 | 1.4756 | 0.76558 | 0.21652 | 2.4577 | 8.438% | 8.979% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-09-12 | 47 | 21.9602 | 7.2559 | 29.2162 | 1.4848 | 0.76558 | 0.2172 | 2.4676 | 8.446% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-09-12 | 48 | 22.8659 | 7.65 | 30.5159 | 1.6199 | 0.76558 | 0.22686 | 2.6123 | 8.561% | 9.108% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-09-13 | 1 | 21.2438 | 6.9312 | 28.1749 | 1.3809 | 0.76558 | 0.20946 | 2.3559 | 8.362% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-09-13 | 2 | 20.0221 | 6.372 | 26.3941 | 1.2118 | 0.76558 | 0.19622 | 2.1736 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-09-13 | 3 | 19.0588 | 5.9502 | 25.009 | 1.088 | 0.76558 | 0.18592 | 2.0395 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-09-13 | 4 | 18.1818 | 5.6805 | 23.8623 | 0.99051 | 0.76558 | 0.17739 | 1.9335 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-09-13 | 5 | 17.6209 | 5.4562 | 23.0772 | 0.9264 | 0.76558 | 0.17156 | 1.8635 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-09-13 | 6 | 17.2322 | 5.3486 | 22.5808 | 0.88698 | 0.76558 | 0.16787 | 1.8204 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-09-13 | 7 | 17.0164 | 5.2921 | 22.3084 | 0.86571 | 0.76558 | 0.16584 | 1.7971 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-09-13 | 8 | 17.2047 | 5.2491 | 22.4538 | 0.87703 | 0.76558 | 0.16692 | 1.8095 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-09-13 | 9 | 17.06 | 5.246 | 22.306 | 0.86552 | 0.76558 | 0.16583 | 1.7969 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-09-13 | 10 | 17.2736 | 5.4066 | 22.6802 | 0.89481 | 0.76558 | 0.16861 | 1.829 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-09-13 | 11 | 17.5475 | 5.3041 | 22.8516 | 0.90838 | 0.76558 | 0.16988 | 1.8438 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-09-13 | 12 | 17.8379 | 5.3647 | 23.2025 | 0.9365 | 0.76558 | 0.17249 | 1.8746 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-09-13 | 13 | 18.6266 | 5.8713 | 24.4978 | 1.044 | 0.76558 | 0.18212 | 1.9917 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-09-13 | 14 | 19.806 | 6.3605 | 26.1665 | 1.191 | 0.76558 | 0.19452 | 2.1511 | 8.221% | 8.747% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-09-13 | 15 | 21.7307 | 6.9736 | 28.7043 | 1.4333 | 0.76558 | 0.21339 | 2.4122 | 8.404% | 8.942% | 6.042% | 1.0917 | 1.0982 | 1.0643
2010-09-13 | 16 | 22.6196 | 7.641 | 30.2606 | 1.5929 | 0.76558 | 0.22496 | 2.5834 | 8.537% | 9.084% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-09-13 | 17 | 24.1147 | 8.58 | 32.6948 | 1.8595 | 0.76558 | 0.24306 | 2.8681 | 8.772% | 9.334% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-09-13 | 18 | 25.7526 | 9.2472 | 34.9998 | 2.1309 | 0.76558 | 0.26019 | 3.1567 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1062 | 1.0693
2010-09-13 | 19 | 26.7015 | 9.463 | 36.1645 | 2.2751 | 0.76558 | 0.26885 | 3.3095 | 9.151% | 9.737% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-09-13 | 20 | 27.1305 | 9.592 | 36.7225 | 2.3458 | 0.76558 | 0.273 | 3.3844 | 9.216% | 9.806% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-09-13 | 21 | 28.2958 | 9.5586 | 37.8545 | 2.4927 | 0.76558 | 0.28141 | 3.5397 | 9.351% | 9.949% | 6.723% | 1.1032 | 1.1105 | 1.0721
2010-09-13 | 22 | 28.0088 | 9.4384 | 37.4471 | 2.4393 | 0.76558 | 0.27839 | 3.4833 | 9.302% | 9.897% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-09-13 | 23 | 26.9006 | 9.1704 | 36.071 | 2.2633 | 0.76558 | 0.26816 | 3.2971 | 9.141% | 9.726% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-09-13 | 24 | 25.8812 | 8.9673 | 34.8485 | 2.1125 | 0.76558 | 0.25907 | 3.1372 | 9.002% | 9.578% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-09-13 | 25 | 24.1727 | 9.0083 | 33.181 | 1.9152 | 0.76558 | 0.24667 | 2.9274 | 8.823% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-09-13 | 26 | 23.167 | 8.4589 | 31.6259 | 1.7399 | 0.76558 | 0.23511 | 2.7406 | 8.666% | 9.22% | 6.231% | 1.0949 | 1.1016 | 1.0664
2010-09-13 | 27 | 23.3683 | 8.652 | 32.0203 | 1.7836 | 0.76558 | 0.23804 | 2.7872 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-09-13 | 28 | 22.8632 | 8.3711 | 31.2343 | 1.6971 | 0.76558 | 0.2322 | 2.6948 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-09-13 | 29 | 22.118 | 7.8928 | 30.0108 | 1.5667 | 0.76558 | 0.2231 | 2.5554 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-09-13 | 30 | 21.9607 | 7.5952 | 29.5559 | 1.5196 | 0.76558 | 0.21972 | 2.5049 | 8.475% | 9.017% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-09-13 | 31 | 22.6505 | 7.629 | 30.2795 | 1.5949 | 0.76558 | 0.2251 | 2.5856 | 8.539% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-09-13 | 32 | 22.7375 | 7.7214 | 30.4589 | 1.6139 | 0.76558 | 0.22644 | 2.6059 | 8.555% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2010-09-13 | 33 | 22.5633 | 8.1567 | 30.72 | 1.6416 | 0.76558 | 0.22838 | 2.6356 | 8.579% | 9.128% | 6.169% | 1.0938 | 1.1005 | 1.0657
2010-09-13 | 34 | 22.8503 | 8.1692 | 31.0195 | 1.6738 | 0.76558 | 0.2306 | 2.67 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-09-13 | 35 | 23.4811 | 9.2354 | 32.7165 | 1.8619 | 0.76558 | 0.24322 | 2.8707 | 8.775% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-09-13 | 36 | 24.7882 | 10.2903 | 35.0785 | 2.1405 | 0.76558 | 0.26078 | 3.1669 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-09-13 | 37 | 26.8978 | 10.8094 | 37.7072 | 2.4733 | 0.76558 | 0.28032 | 3.5192 | 9.333% | 9.93% | 6.71% | 1.1029 | 1.1103 | 1.0719
2010-09-13 | 38 | 28.8519 | 10.9578 | 39.8097 | 2.7568 | 0.76558 | 0.29595 | 3.8184 | 9.592% | 10.21% | 6.896% | 1.1061 | 1.1137 | 1.0741
2010-09-13 | 39 | 29.3971 | 10.793 | 40.1901 | 2.8098 | 0.76558 | 0.29878 | 3.8741 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-09-13 | 40 | 28.8383 | 10.4111 | 39.2494 | 2.6798 | 0.76558 | 0.29179 | 3.7372 | 9.522% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-09-13 | 41 | 29.0833 | 10.1369 | 39.2202 | 2.6758 | 0.76558 | 0.29157 | 3.733 | 9.518% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2010-09-13 | 42 | 28.2944 | 9.6206 | 37.915 | 2.5007 | 0.76558 | 0.28187 | 3.5481 | 9.358% | 9.957% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-09-13 | 43 | 26.5266 | 8.9377 | 35.4643 | 2.1879 | 0.76558 | 0.26365 | 3.2171 | 9.071% | 9.652% | 6.522% | 1.0998 | 1.1068 | 1.0698
2010-09-13 | 44 | 24.8448 | 8.2775 | 33.1223 | 1.9084 | 0.76558 | 0.24624 | 2.9202 | 8.817% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-09-13 | 45 | 22.5474 | 7.3466 | 29.8939 | 1.5545 | 0.76558 | 0.22224 | 2.5424 | 8.505% | 9.049% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-09-13 | 46 | 19.9771 | 6.5787 | 26.5558 | 1.2267 | 0.76558 | 0.19742 | 2.1897 | 8.246% | 8.774% | 5.929% | 1.0899 | 1.0962 | 1.063
2010-09-13 | 47 | 19.2448 | 6.5717 | 25.8165 | 1.1594 | 0.76558 | 0.19192 | 2.1169 | 8.2% | 8.725% | 5.896% | 1.0893 | 1.0956 | 1.0626
2010-09-13 | 48 | 19.6189 | 6.9255 | 26.5444 | 1.2257 | 0.76558 | 0.19733 | 2.1886 | 8.245% | 8.773% | 5.928% | 1.0899 | 1.0962 | 1.063
2010-09-14 | 1 | 18.526 | 6.157 | 24.6829 | 1.0598 | 0.76558 | 0.1835 | 2.0089 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-09-14 | 2 | 17.4206 | 5.928 | 23.3485 | 0.94832 | 0.76558 | 0.17358 | 1.8875 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-14 | 3 | 16.6297 | 5.5454 | 22.1751 | 0.85539 | 0.76558 | 0.16485 | 1.7858 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-09-14 | 4 | 16.1008 | 5.1402 | 21.241 | 0.78484 | 0.76558 | 0.15791 | 1.7083 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 5 | 15.8119 | 5.1871 | 20.999 | 0.76706 | 0.76558 | 0.15611 | 1.6888 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 6 | 15.2657 | 4.9198 | 20.1855 | 0.70878 | 0.76558 | 0.15006 | 1.6244 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 7 | 15.0794 | 4.8644 | 19.9438 | 0.69191 | 0.76558 | 0.14826 | 1.6058 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-09-14 | 8 | 14.9049 | 4.9093 | 19.8142 | 0.68295 | 0.76558 | 0.1473 | 1.5958 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-09-14 | 9 | 15.2645 | 4.9739 | 20.2384 | 0.7125 | 0.76558 | 0.15045 | 1.6285 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 10 | 15.4092 | 5.0161 | 20.4253 | 0.72572 | 0.76558 | 0.15184 | 1.6431 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 11 | 15.8693 | 5.1798 | 21.0491 | 0.77073 | 0.76558 | 0.15648 | 1.6928 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-14 | 12 | 16.6862 | 5.6627 | 22.3489 | 0.86885 | 0.76558 | 0.16614 | 1.8006 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-09-14 | 13 | 18.0939 | 6.7793 | 24.8733 | 1.0762 | 0.76558 | 0.18491 | 2.0267 | 8.148% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-09-14 | 14 | 20.4807 | 8.2631 | 28.7438 | 1.4372 | 0.76558 | 0.21368 | 2.4165 | 8.407% | 8.945% | 6.045% | 1.0918 | 1.0982 | 1.0643
2010-09-14 | 15 | 24.4025 | 10.1063 | 34.5088 | 2.0715 | 0.76558 | 0.25654 | 3.0937 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2010-09-14 | 16 | 26.3553 | 10.7669 | 37.1222 | 2.3972 | 0.76558 | 0.27597 | 3.4387 | 9.263% | 9.856% | 6.66% | 1.1021 | 1.1093 | 1.0714
2010-09-14 | 17 | 26.7411 | 11.0351 | 37.7763 | 2.4824 | 0.76558 | 0.28083 | 3.5288 | 9.341% | 9.939% | 6.716% | 1.103 | 1.1104 | 1.072
2010-09-14 | 18 | 26.5557 | 10.79 | 37.3458 | 2.4261 | 0.76558 | 0.27763 | 3.4694 | 9.29% | 9.884% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-09-14 | 19 | 26.2415 | 10.521 | 36.7625 | 2.351 | 0.76558 | 0.2733 | 3.3898 | 9.221% | 9.811% | 6.63% | 1.1016 | 1.1088 | 1.071
2010-09-14 | 20 | 25.5147 | 10.0402 | 35.5549 | 2.199 | 0.76558 | 0.26432 | 3.2289 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-09-14 | 21 | 25.9961 | 9.4019 | 35.398 | 2.1797 | 0.76558 | 0.26315 | 3.2084 | 9.064% | 9.644% | 6.517% | 1.0997 | 1.1067 | 1.0697
2010-09-14 | 22 | 25.1443 | 9.2789 | 34.4231 | 2.0613 | 0.76558 | 0.25591 | 3.0828 | 8.955% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-09-14 | 23 | 24.1032 | 8.9334 | 33.0366 | 1.8986 | 0.76558 | 0.2456 | 2.9097 | 8.808% | 9.371% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-09-14 | 24 | 22.5831 | 8.9161 | 31.4992 | 1.726 | 0.76558 | 0.23417 | 2.7257 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2010-09-14 | 25 | 21.894 | 8.8963 | 30.7904 | 1.6492 | 0.76558 | 0.2289 | 2.6436 | 8.586% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-09-14 | 26 | 22.3547 | 8.5425 | 30.8971 | 1.6606 | 0.76558 | 0.22969 | 2.6559 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-09-14 | 27 | 22.2386 | 8.6592 | 30.8978 | 1.6607 | 0.76558 | 0.2297 | 2.656 | 8.596% | 9.146% | 6.181% | 1.094 | 1.1007 | 1.0659
2010-09-14 | 28 | 22.4694 | 8.6739 | 31.1433 | 1.6872 | 0.76558 | 0.23152 | 2.6843 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-09-14 | 29 | 22.3111 | 8.3696 | 30.6807 | 1.6374 | 0.76558 | 0.22808 | 2.6311 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-09-14 | 30 | 22.0256 | 8.1891 | 30.2147 | 1.5881 | 0.76558 | 0.22462 | 2.5783 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-09-14 | 31 | 22.2133 | 7.7971 | 30.0104 | 1.5667 | 0.76558 | 0.2231 | 2.5553 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-09-14 | 32 | 22.5567 | 8.1971 | 30.7538 | 1.6452 | 0.76558 | 0.22863 | 2.6395 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-09-14 | 33 | 22.7433 | 8.5655 | 31.3088 | 1.7052 | 0.76558 | 0.23275 | 2.7035 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-09-14 | 34 | 23.1726 | 8.5853 | 31.7579 | 1.7544 | 0.76558 | 0.23609 | 2.7561 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-09-14 | 35 | 25.0116 | 9.4614 | 34.473 | 2.0673 | 0.76558 | 0.25628 | 3.0891 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-09-14 | 36 | 27.1771 | 10.1932 | 37.3703 | 2.4293 | 0.76558 | 0.27782 | 3.4727 | 9.293% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-09-14 | 37 | 29.027 | 10.9604 | 39.9874 | 2.7815 | 0.76558 | 0.29727 | 3.8444 | 9.614% | 10.23% | 6.912% | 1.1064 | 1.1139 | 1.0743
2010-09-14 | 38 | 30.2787 | 11.2806 | 41.5593 | 3.0045 | 0.76558 | 0.30896 | 4.079 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-09-14 | 39 | 29.634 | 10.9823 | 40.6163 | 2.8697 | 0.76558 | 0.30195 | 3.9372 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2010-09-14 | 40 | 29.0531 | 10.5603 | 39.6134 | 2.7297 | 0.76558 | 0.29449 | 3.7898 | 9.567% | 10.18% | 6.879% | 1.1058 | 1.1133 | 1.0739
2010-09-14 | 41 | 28.7497 | 10.1655 | 38.9152 | 2.6343 | 0.76558 | 0.2893 | 3.6892 | 9.48% | 10.09% | 6.816% | 1.1047 | 1.1122 | 1.0731
2010-09-14 | 42 | 28.2 | 9.6385 | 37.8385 | 2.4906 | 0.76558 | 0.2813 | 3.5375 | 9.349% | 9.947% | 6.722% | 1.1031 | 1.1105 | 1.0721
2010-09-14 | 43 | 26.7489 | 9.1435 | 35.8924 | 2.241 | 0.76558 | 0.26683 | 3.2734 | 9.12% | 9.704% | 6.557% | 1.1004 | 1.1075 | 1.0702
2010-09-14 | 44 | 25.1854 | 8.3305 | 33.5159 | 1.9541 | 0.76558 | 0.24916 | 2.9688 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-09-14 | 45 | 22.9165 | 7.3883 | 30.3048 | 1.5976 | 0.76558 | 0.22529 | 2.5884 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-09-14 | 46 | 20.6314 | 6.6423 | 27.2736 | 1.294 | 0.76558 | 0.20276 | 2.2623 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2010-09-14 | 47 | 19.7932 | 6.5895 | 26.3827 | 1.2108 | 0.76558 | 0.19613 | 2.1725 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-09-14 | 48 | 19.6651 | 6.8967 | 26.5618 | 1.2273 | 0.76558 | 0.19746 | 2.1903 | 8.246% | 8.774% | 5.929% | 1.0899 | 1.0962 | 1.063
2010-09-15 | 1 | 17.9404 | 6.2161 | 24.1565 | 1.0151 | 0.76558 | 0.17958 | 1.9602 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-09-15 | 2 | 16.9358 | 5.7587 | 22.6944 | 0.89593 | 0.76558 | 0.16871 | 1.8302 | 8.065% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-09-15 | 3 | 16.5195 | 5.4704 | 21.9899 | 0.84117 | 0.76558 | 0.16348 | 1.7702 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-09-15 | 4 | 16.0774 | 5.2645 | 21.3419 | 0.79232 | 0.76558 | 0.15866 | 1.7166 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-15 | 5 | 15.5045 | 5.115 | 20.6196 | 0.7396 | 0.76558 | 0.15329 | 1.6585 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-15 | 6 | 15.1775 | 5.0765 | 20.254 | 0.7136 | 0.76558 | 0.15057 | 1.6297 | 8.047% | 8.562% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-15 | 7 | 15.044 | 4.9918 | 20.0358 | 0.69831 | 0.76558 | 0.14895 | 1.6128 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-09-15 | 8 | 14.8026 | 4.895 | 19.6976 | 0.67493 | 0.76558 | 0.14643 | 1.5869 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-09-15 | 9 | 14.8316 | 4.9309 | 19.7625 | 0.67939 | 0.76558 | 0.14692 | 1.5919 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-09-15 | 10 | 15.0318 | 5.0728 | 20.1047 | 0.70312 | 0.76558 | 0.14946 | 1.6182 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-09-15 | 11 | 15.7216 | 5.332 | 21.0537 | 0.77106 | 0.76558 | 0.15652 | 1.6932 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-15 | 12 | 16.7078 | 5.8293 | 22.5371 | 0.88355 | 0.76558 | 0.16754 | 1.8167 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-09-15 | 13 | 18.5891 | 6.9116 | 25.5007 | 1.1312 | 0.76558 | 0.18958 | 2.0864 | 8.182% | 8.705% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-09-15 | 14 | 21.8082 | 8.4182 | 30.2264 | 1.5893 | 0.76558 | 0.22471 | 2.5796 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-09-15 | 15 | 26.0319 | 10.3175 | 36.3494 | 2.2984 | 0.76558 | 0.27023 | 3.3342 | 9.173% | 9.76% | 6.595% | 1.101 | 1.1082 | 1.0706
2010-09-15 | 16 | 27.3553 | 10.5607 | 37.916 | 2.5008 | 0.76558 | 0.28187 | 3.5483 | 9.358% | 9.957% | 6.729% | 1.1032 | 1.1106 | 1.0721
2010-09-15 | 17 | 27.7975 | 10.7826 | 38.5802 | 2.5892 | 0.76558 | 0.28681 | 3.6416 | 9.439% | 10.04% | 6.787% | 1.1042 | 1.1116 | 1.0728
2010-09-15 | 18 | 27.8112 | 10.5593 | 38.3705 | 2.5611 | 0.76558 | 0.28525 | 3.6119 | 9.413% | 10.02% | 6.768% | 1.1039 | 1.1113 | 1.0726
2010-09-15 | 19 | 27.3802 | 10.2322 | 37.6124 | 2.4609 | 0.76558 | 0.27962 | 3.5061 | 9.322% | 9.918% | 6.702% | 1.1028 | 1.1101 | 1.0718
2010-09-15 | 20 | 26.7066 | 9.8012 | 36.5078 | 2.3185 | 0.76558 | 0.2714 | 3.3555 | 9.191% | 9.779% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-09-15 | 21 | 27.1197 | 9.5176 | 36.6372 | 2.335 | 0.76558 | 0.27237 | 3.3729 | 9.206% | 9.795% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-09-15 | 22 | 26.4877 | 9.4554 | 35.9432 | 2.2473 | 0.76558 | 0.26721 | 3.2801 | 9.126% | 9.71% | 6.561% | 1.1004 | 1.1075 | 1.0702
2010-09-15 | 23 | 25.7972 | 9.0249 | 34.822 | 2.1093 | 0.76558 | 0.25887 | 3.1338 | 8.999% | 9.575% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-09-15 | 24 | 25.0317 | 8.9634 | 33.9951 | 2.0103 | 0.76558 | 0.25272 | 3.0286 | 8.909% | 9.479% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-09-15 | 25 | 24.0106 | 9.0133 | 33.0239 | 1.8971 | 0.76558 | 0.2455 | 2.9082 | 8.806% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-09-15 | 26 | 23.155 | 8.4809 | 31.636 | 1.741 | 0.76558 | 0.23519 | 2.7418 | 8.667% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2010-09-15 | 27 | 23.0282 | 8.8152 | 31.8435 | 1.7639 | 0.76558 | 0.23673 | 2.7662 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2010-09-15 | 28 | 22.9779 | 8.6698 | 31.6478 | 1.7423 | 0.76558 | 0.23527 | 2.7431 | 8.668% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-09-15 | 29 | 22.6267 | 8.4114 | 31.0381 | 1.6758 | 0.76558 | 0.23074 | 2.6721 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-09-15 | 30 | 22.45 | 8.2033 | 30.6534 | 1.6345 | 0.76558 | 0.22788 | 2.628 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-09-15 | 31 | 23.0449 | 8.2978 | 31.3428 | 1.7089 | 0.76558 | 0.23301 | 2.7075 | 8.638% | 9.191% | 6.211% | 1.0945 | 1.1012 | 1.0662
2010-09-15 | 32 | 23.0297 | 8.2505 | 31.2802 | 1.7021 | 0.76558 | 0.23254 | 2.7002 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-09-15 | 33 | 23.0859 | 8.5831 | 31.669 | 1.7446 | 0.76558 | 0.23543 | 2.7456 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-09-15 | 34 | 23.1066 | 8.7524 | 31.859 | 1.7656 | 0.76558 | 0.23684 | 2.768 | 8.688% | 9.244% | 6.247% | 1.0952 | 1.1019 | 1.0666
2010-09-15 | 35 | 23.4899 | 9.0154 | 32.5053 | 1.838 | 0.76558 | 0.24165 | 2.8452 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-09-15 | 36 | 25.193 | 9.806 | 34.999 | 2.1308 | 0.76558 | 0.26019 | 3.1566 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1061 | 1.0693
2010-09-15 | 37 | 27.3694 | 10.6446 | 38.0141 | 2.5138 | 0.76558 | 0.2826 | 3.5619 | 9.37% | 9.97% | 6.737% | 1.1034 | 1.1107 | 1.0722
2010-09-15 | 38 | 29.6977 | 11.4108 | 41.1086 | 2.9397 | 0.76558 | 0.30561 | 4.0109 | 9.757% | 10.38% | 7.015% | 1.1081 | 1.1158 | 1.0754
2010-09-15 | 39 | 30.9282 | 11.6795 | 42.6077 | 3.158 | 0.76558 | 0.31675 | 4.2403 | 9.952% | 10.59% | 7.155% | 1.1105 | 1.1184 | 1.0771
2010-09-15 | 40 | 31.0423 | 11.1931 | 42.2353 | 3.103 | 0.76558 | 0.31398 | 4.1826 | 9.903% | 10.54% | 7.12% | 1.1099 | 1.1178 | 1.0767
2010-09-15 | 41 | 30.8985 | 10.7091 | 41.6076 | 3.0115 | 0.76558 | 0.30932 | 4.0864 | 9.821% | 10.45% | 7.061% | 1.1089 | 1.1167 | 1.076
2010-09-15 | 42 | 30.4075 | 10.2888 | 40.6964 | 2.881 | 0.76558 | 0.30254 | 3.9491 | 9.704% | 10.32% | 6.977% | 1.1075 | 1.1151 | 1.075
2010-09-15 | 43 | 28.8615 | 9.4805 | 38.342 | 2.5573 | 0.76558 | 0.28504 | 3.6079 | 9.41% | 10.01% | 6.766% | 1.1039 | 1.1113 | 1.0726
2010-09-15 | 44 | 27.3802 | 8.8497 | 36.23 | 2.2833 | 0.76558 | 0.26934 | 3.3183 | 9.159% | 9.745% | 6.585% | 1.1008 | 1.108 | 1.0705
2010-09-15 | 45 | 24.8673 | 7.9796 | 32.8469 | 1.8768 | 0.76558 | 0.24419 | 2.8866 | 8.788% | 9.35% | 6.319% | 1.0963 | 1.1031 | 1.0674
2010-09-15 | 46 | 22.2196 | 7.1261 | 29.3457 | 1.498 | 0.76558 | 0.21816 | 2.4818 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-09-15 | 47 | 20.9893 | 6.9884 | 27.9777 | 1.3616 | 0.76558 | 0.20799 | 2.3352 | 8.347% | 8.881% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-09-15 | 48 | 21.073 | 7.2352 | 28.3081 | 1.394 | 0.76558 | 0.21045 | 2.37 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-09-16 | 1 | 19.579 | 6.499 | 26.078 | 1.183 | 0.76558 | 0.19387 | 2.1424 | 8.216% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-09-16 | 2 | 18.7738 | 6.0956 | 24.8694 | 1.0759 | 0.76558 | 0.18488 | 2.0263 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-09-16 | 3 | 18.1131 | 5.7506 | 23.8637 | 0.99063 | 0.76558 | 0.17741 | 1.9336 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-09-16 | 4 | 17.7826 | 5.563 | 23.3456 | 0.94808 | 0.76558 | 0.17355 | 1.8872 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-16 | 5 | 17.6094 | 5.4463 | 23.0556 | 0.92467 | 0.76558 | 0.1714 | 1.8617 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-09-16 | 6 | 17.895 | 5.3474 | 23.2425 | 0.93972 | 0.76558 | 0.17279 | 1.8781 | 8.08% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-09-16 | 7 | 17.6814 | 5.4039 | 23.0853 | 0.92706 | 0.76558 | 0.17162 | 1.8643 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-09-16 | 8 | 17.7955 | 5.2883 | 23.0838 | 0.92694 | 0.76558 | 0.17161 | 1.8641 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-09-16 | 9 | 19.0168 | 5.3705 | 24.3873 | 1.0346 | 0.76558 | 0.1813 | 1.9814 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-09-16 | 10 | 19.9353 | 5.6476 | 25.5829 | 1.1385 | 0.76558 | 0.19019 | 2.0943 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-09-16 | 11 | 20.4237 | 5.8876 | 26.3114 | 1.2043 | 0.76558 | 0.1956 | 2.1654 | 8.23% | 8.757% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-09-16 | 12 | 20.9993 | 6.338 | 27.3373 | 1.3 | 0.76558 | 0.20323 | 2.2688 | 8.299% | 8.83% | 5.967% | 1.0905 | 1.0969 | 1.0635
2010-09-16 | 13 | 22.2505 | 7.3803 | 29.6308 | 1.5273 | 0.76558 | 0.22028 | 2.5131 | 8.482% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-09-16 | 14 | 25.1796 | 9.0176 | 34.1972 | 2.0343 | 0.76558 | 0.25423 | 3.0541 | 8.931% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-09-16 | 15 | 28.9851 | 11.1121 | 40.0972 | 2.7968 | 0.76558 | 0.29809 | 3.8605 | 9.628% | 10.24% | 6.922% | 1.1065 | 1.1141 | 1.0744
2010-09-16 | 16 | 29.5146 | 11.5814 | 41.096 | 2.9379 | 0.76558 | 0.30551 | 4.009 | 9.755% | 10.38% | 7.014% | 1.1081 | 1.1158 | 1.0754
2010-09-16 | 17 | 30.3763 | 11.9539 | 42.3302 | 3.117 | 0.76558 | 0.31469 | 4.1973 | 9.916% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-09-16 | 18 | 30.3323 | 11.893 | 42.2254 | 3.1016 | 0.76558 | 0.31391 | 4.1811 | 9.902% | 10.54% | 7.119% | 1.1099 | 1.1178 | 1.0767
2010-09-16 | 19 | 29.3567 | 11.3379 | 40.6946 | 2.8808 | 0.76558 | 0.30253 | 3.9489 | 9.704% | 10.32% | 6.977% | 1.1075 | 1.1151 | 1.075
2010-09-16 | 20 | 28.3232 | 10.8379 | 39.1611 | 2.6677 | 0.76558 | 0.29113 | 3.7244 | 9.511% | 10.12% | 6.838% | 1.1051 | 1.1126 | 1.0734
2010-09-16 | 21 | 28.5809 | 10.4217 | 39.0026 | 2.6462 | 0.76558 | 0.28995 | 3.7017 | 9.491% | 10.1% | 6.824% | 1.1049 | 1.1123 | 1.0732
2010-09-16 | 22 | 27.4038 | 10.3756 | 37.7794 | 2.4828 | 0.76558 | 0.28086 | 3.5293 | 9.342% | 9.94% | 6.717% | 1.103 | 1.1104 | 1.072
2010-09-16 | 23 | 26.7141 | 9.9901 | 36.7042 | 2.3435 | 0.76558 | 0.27286 | 3.3819 | 9.214% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.0709
2010-09-16 | 24 | 26.0817 | 9.7556 | 35.8373 | 2.2341 | 0.76558 | 0.26642 | 3.2661 | 9.114% | 9.697% | 6.553% | 1.1003 | 1.1074 | 1.0701
2010-09-16 | 25 | 24.7463 | 9.7662 | 34.5124 | 2.072 | 0.76558 | 0.25657 | 3.0941 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2010-09-16 | 26 | 23.7993 | 9.4095 | 33.2088 | 1.9184 | 0.76558 | 0.24688 | 2.9309 | 8.826% | 9.39% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-09-16 | 27 | 23.6408 | 9.5115 | 33.1524 | 1.9119 | 0.76558 | 0.24646 | 2.9239 | 8.82% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2010-09-16 | 28 | 23.9015 | 9.5241 | 33.4256 | 1.9435 | 0.76558 | 0.24849 | 2.9576 | 8.848% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-09-16 | 29 | 23.4951 | 9.4466 | 32.9418 | 1.8877 | 0.76558 | 0.24489 | 2.8982 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-09-16 | 30 | 23.2884 | 8.9255 | 32.2138 | 1.8052 | 0.76558 | 0.23948 | 2.8102 | 8.724% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-09-16 | 31 | 24.1772 | 8.7621 | 32.9393 | 1.8874 | 0.76558 | 0.24487 | 2.8978 | 8.798% | 9.361% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-09-16 | 32 | 24.2571 | 8.7981 | 33.0552 | 1.9007 | 0.76558 | 0.24574 | 2.912 | 8.81% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-09-16 | 33 | 24.192 | 8.8549 | 33.0469 | 1.8997 | 0.76558 | 0.24567 | 2.911 | 8.809% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-09-16 | 34 | 24.5988 | 8.996 | 33.5948 | 1.9633 | 0.76558 | 0.24975 | 2.9786 | 8.866% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-09-16 | 35 | 24.8108 | 9.6582 | 34.469 | 2.0668 | 0.76558 | 0.25625 | 3.0886 | 8.96% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-09-16 | 36 | 26.4494 | 10.5283 | 36.9777 | 2.3786 | 0.76558 | 0.2749 | 3.419 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-09-16 | 37 | 28.7337 | 11.4557 | 40.1894 | 2.8097 | 0.76558 | 0.29877 | 3.874 | 9.639% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-09-16 | 38 | 30.6426 | 11.9095 | 42.5522 | 3.1498 | 0.76558 | 0.31634 | 4.2317 | 9.945% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-09-16 | 39 | 31.4762 | 11.9161 | 43.3922 | 3.2754 | 0.76558 | 0.32258 | 4.3635 | 10.06% | 10.7% | 7.23% | 1.1118 | 1.1198 | 1.0779
2010-09-16 | 40 | 30.943 | 11.7053 | 42.6483 | 3.164 | 0.76558 | 0.31705 | 4.2466 | 9.957% | 10.59% | 7.159% | 1.1106 | 1.1185 | 1.0771
2010-09-16 | 41 | 31.3445 | 11.3825 | 42.727 | 3.1757 | 0.76558 | 0.31764 | 4.2589 | 9.968% | 10.61% | 7.167% | 1.1107 | 1.1186 | 1.0772
2010-09-16 | 42 | 30.8695 | 10.8759 | 41.7454 | 3.0315 | 0.76558 | 0.31034 | 4.1074 | 9.839% | 10.47% | 7.074% | 1.1091 | 1.1169 | 1.0761
2010-09-16 | 43 | 29.0775 | 10.161 | 39.2385 | 2.6783 | 0.76558 | 0.2917 | 3.7356 | 9.52% | 10.13% | 6.845% | 1.1052 | 1.1127 | 1.0735
2010-09-16 | 44 | 27.4241 | 9.4404 | 36.8645 | 2.364 | 0.76558 | 0.27406 | 3.4037 | 9.233% | 9.824% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-09-16 | 45 | 24.5775 | 8.3521 | 32.9296 | 1.8863 | 0.76558 | 0.2448 | 2.8967 | 8.797% | 9.36% | 6.325% | 1.0964 | 1.1033 | 1.0675
2010-09-16 | 46 | 22.1487 | 7.3524 | 29.5011 | 1.5139 | 0.76558 | 0.21931 | 2.4988 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.0991 | 1.0649
2010-09-16 | 47 | 21.1138 | 7.2706 | 28.3844 | 1.4015 | 0.76558 | 0.21101 | 2.3781 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-09-16 | 48 | 20.8694 | 7.3996 | 28.269 | 1.3901 | 0.76558 | 0.21016 | 2.3659 | 8.369% | 8.905% | 6.017% | 1.0913 | 1.0978 | 1.064
2010-09-17 | 1 | 19.4605 | 6.6338 | 26.0943 | 1.1845 | 0.76558 | 0.19399 | 2.144 | 8.217% | 8.742% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-09-17 | 2 | 18.327 | 6.0835 | 24.4105 | 1.0365 | 0.76558 | 0.18147 | 1.9836 | 8.126% | 8.646% | 5.843% | 1.0884 | 1.0946 | 1.0621
2010-09-17 | 3 | 17.7652 | 5.8218 | 23.587 | 0.96779 | 0.76558 | 0.17535 | 1.9087 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-09-17 | 4 | 17.2614 | 5.7214 | 22.9828 | 0.91884 | 0.76558 | 0.17086 | 1.8553 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-09-17 | 5 | 17.0037 | 5.5994 | 22.6031 | 0.88873 | 0.76558 | 0.16803 | 1.8223 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-09-17 | 6 | 16.7595 | 5.623 | 22.3826 | 0.87147 | 0.76558 | 0.16639 | 1.8034 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-09-17 | 7 | 16.6298 | 5.557 | 22.1867 | 0.85629 | 0.76558 | 0.16494 | 1.7868 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-09-17 | 8 | 16.6292 | 5.5889 | 22.2182 | 0.85872 | 0.76558 | 0.16517 | 1.7895 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-09-17 | 9 | 17.0604 | 5.8362 | 22.8966 | 0.91196 | 0.76558 | 0.17022 | 1.8478 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-09-17 | 10 | 17.5929 | 5.8789 | 23.4718 | 0.95835 | 0.76558 | 0.17449 | 1.8984 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-09-17 | 11 | 18.2083 | 6.058 | 24.2663 | 1.0243 | 0.76558 | 0.1804 | 1.9703 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-09-17 | 12 | 19.1847 | 6.5195 | 25.7042 | 1.1493 | 0.76558 | 0.19109 | 2.106 | 8.193% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-09-17 | 13 | 21.311 | 7.8412 | 29.1522 | 1.4783 | 0.76558 | 0.21672 | 2.4606 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-09-17 | 14 | 24.4127 | 9.4979 | 33.9106 | 2.0004 | 0.76558 | 0.2521 | 3.018 | 8.9% | 9.47% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-09-17 | 15 | 28.9706 | 11.3959 | 40.3665 | 2.8345 | 0.76558 | 0.30009 | 3.9002 | 9.662% | 10.28% | 6.947% | 1.107 | 1.1146 | 1.0747
2010-09-17 | 16 | 29.7804 | 12.0967 | 41.8771 | 3.0506 | 0.76558 | 0.31132 | 4.1275 | 9.856% | 10.49% | 7.087% | 1.1093 | 1.1172 | 1.0763
2010-09-17 | 17 | 30.2283 | 12.4579 | 42.6862 | 3.1696 | 0.76558 | 0.31733 | 4.2526 | 9.962% | 10.6% | 7.163% | 1.1106 | 1.1186 | 1.0772
2010-09-17 | 18 | 30.2996 | 12.4253 | 42.7249 | 3.1754 | 0.76558 | 0.31762 | 4.2586 | 9.967% | 10.61% | 7.167% | 1.1107 | 1.1186 | 1.0772
2010-09-17 | 19 | 29.6235 | 11.9378 | 41.5613 | 3.0048 | 0.76558 | 0.30897 | 4.0793 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-09-17 | 20 | 28.2169 | 11.2719 | 39.4888 | 2.7126 | 0.76558 | 0.29356 | 3.7717 | 9.551% | 10.16% | 6.867% | 1.1056 | 1.1131 | 1.0737
2010-09-17 | 21 | 28.3746 | 10.6879 | 39.0625 | 2.6543 | 0.76558 | 0.2904 | 3.7103 | 9.498% | 10.11% | 6.829% | 1.105 | 1.1124 | 1.0733
2010-09-17 | 22 | 27.5555 | 10.3828 | 37.9383 | 2.5037 | 0.76558 | 0.28204 | 3.5514 | 9.361% | 9.96% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-09-17 | 23 | 26.0365 | 9.8911 | 35.9275 | 2.2454 | 0.76558 | 0.26709 | 3.278 | 9.124% | 9.708% | 6.56% | 1.1004 | 1.1075 | 1.0702
2010-09-17 | 24 | 25.4319 | 9.6635 | 35.0954 | 2.1426 | 0.76558 | 0.2609 | 3.1691 | 9.03% | 9.608% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-09-17 | 25 | 24.7122 | 9.4831 | 34.1953 | 2.0341 | 0.76558 | 0.25421 | 3.0539 | 8.931% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-09-17 | 26 | 23.521 | 9.0492 | 32.5702 | 1.8453 | 0.76558 | 0.24213 | 2.8531 | 8.76% | 9.32% | 6.298% | 1.096 | 1.1028 | 1.0672
2010-09-17 | 27 | 23.4632 | 9.1807 | 32.6439 | 1.8537 | 0.76558 | 0.24268 | 2.862 | 8.767% | 9.328% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-09-17 | 28 | 23.2097 | 9.2122 | 32.4219 | 1.8286 | 0.76558 | 0.24103 | 2.8352 | 8.745% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-09-17 | 29 | 22.6284 | 8.84 | 31.4684 | 1.7226 | 0.76558 | 0.23394 | 2.7221 | 8.65% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-09-17 | 30 | 22.4366 | 8.4728 | 30.9094 | 1.6619 | 0.76558 | 0.22978 | 2.6573 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-09-17 | 31 | 23.3543 | 8.3797 | 31.7341 | 1.7518 | 0.76558 | 0.23591 | 2.7533 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-09-17 | 32 | 23.5532 | 8.2587 | 31.8119 | 1.7604 | 0.76558 | 0.23649 | 2.7625 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-09-17 | 33 | 23.4253 | 8.4996 | 31.9249 | 1.7729 | 0.76558 | 0.23733 | 2.7759 | 8.695% | 9.251% | 6.252% | 1.0952 | 1.1019 | 1.0667
2010-09-17 | 34 | 23.996 | 8.6955 | 32.6915 | 1.8591 | 0.76558 | 0.24303 | 2.8677 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-09-17 | 35 | 25.0935 | 9.3281 | 34.4216 | 2.0611 | 0.76558 | 0.25589 | 3.0826 | 8.955% | 9.528% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-09-17 | 36 | 27.1185 | 10.0841 | 37.2026 | 2.4076 | 0.76558 | 0.27657 | 3.4497 | 9.273% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-09-17 | 37 | 29.5732 | 10.7752 | 40.3484 | 2.832 | 0.76558 | 0.29996 | 3.8975 | 9.66% | 10.28% | 6.945% | 1.1069 | 1.1146 | 1.0746
2010-09-17 | 38 | 31.2838 | 11.2388 | 42.5226 | 3.1454 | 0.76558 | 0.31612 | 4.2271 | 9.941% | 10.58% | 7.147% | 1.1104 | 1.1183 | 1.077
2010-09-17 | 39 | 31.2494 | 11.3724 | 42.6218 | 3.1601 | 0.76558 | 0.31686 | 4.2425 | 9.954% | 10.59% | 7.157% | 1.1105 | 1.1185 | 1.0771
2010-09-17 | 40 | 30.7241 | 11.1012 | 41.8253 | 3.0431 | 0.76558 | 0.31093 | 4.1196 | 9.85% | 10.48% | 7.082% | 1.1093 | 1.1171 | 1.0762
2010-09-17 | 41 | 30.8819 | 10.7021 | 41.5841 | 3.0081 | 0.76558 | 0.30914 | 4.0828 | 9.818% | 10.45% | 7.059% | 1.1089 | 1.1167 | 1.076
2010-09-17 | 42 | 30.1924 | 10.2167 | 40.4091 | 2.8405 | 0.76558 | 0.30041 | 3.9065 | 9.667% | 10.29% | 6.951% | 1.107 | 1.1147 | 1.0747
2010-09-17 | 43 | 28.6397 | 9.6559 | 38.2956 | 2.5511 | 0.76558 | 0.28469 | 3.6014 | 9.404% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2010-09-17 | 44 | 26.9561 | 8.8762 | 35.8323 | 2.2335 | 0.76558 | 0.26638 | 3.2654 | 9.113% | 9.696% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-09-17 | 45 | 24.2145 | 8.0345 | 32.2489 | 1.8091 | 0.76558 | 0.23974 | 2.8144 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.0669
2010-09-17 | 46 | 21.786 | 7.1957 | 28.9817 | 1.4611 | 0.76558 | 0.21545 | 2.4421 | 8.426% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-09-17 | 47 | 20.3483 | 6.9498 | 27.2981 | 1.2963 | 0.76558 | 0.20294 | 2.2648 | 8.297% | 8.828% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-09-17 | 48 | 20.2056 | 7.1768 | 27.3824 | 1.3043 | 0.76558 | 0.20356 | 2.2734 | 8.303% | 8.834% | 5.97% | 1.0905 | 1.0969 | 1.0635
2010-09-18 | 1 | 18.5408 | 6.2984 | 24.8392 | 1.0733 | 0.76558 | 0.18466 | 2.0235 | 8.146% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-09-18 | 2 | 17.6803 | 5.7341 | 23.4144 | 0.95368 | 0.76558 | 0.17407 | 1.8933 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-09-18 | 3 | 16.6988 | 5.6516 | 22.3505 | 0.86898 | 0.76558 | 0.16616 | 1.8007 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-09-18 | 4 | 16.1874 | 5.4197 | 21.6071 | 0.81213 | 0.76558 | 0.16063 | 1.7383 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 5 | 15.7242 | 5.2751 | 20.9993 | 0.76708 | 0.76558 | 0.15611 | 1.6888 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 6 | 15.2919 | 5.2258 | 20.5177 | 0.73231 | 0.76558 | 0.15253 | 1.6504 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 7 | 15.1495 | 5.1864 | 20.3359 | 0.71939 | 0.76558 | 0.15118 | 1.6361 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 8 | 14.9332 | 5.1916 | 20.1248 | 0.70453 | 0.76558 | 0.14961 | 1.6197 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-09-18 | 9 | 15.2504 | 5.2153 | 20.4657 | 0.7286 | 0.76558 | 0.15214 | 1.6463 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 10 | 15.7815 | 5.3166 | 21.0981 | 0.77432 | 0.76558 | 0.15685 | 1.6967 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 11 | 16.0541 | 5.5609 | 21.615 | 0.81273 | 0.76558 | 0.16069 | 1.739 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-18 | 12 | 16.9161 | 5.7854 | 22.7015 | 0.89649 | 0.76558 | 0.16877 | 1.8308 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-09-18 | 13 | 18.6983 | 6.7406 | 25.4389 | 1.1257 | 0.76558 | 0.18912 | 2.0804 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-09-18 | 14 | 21.1806 | 8.013 | 29.1936 | 1.4826 | 0.76558 | 0.21703 | 2.4652 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-09-18 | 15 | 25.4055 | 9.7608 | 35.1662 | 2.1512 | 0.76558 | 0.26143 | 3.1782 | 9.038% | 9.616% | 6.498% | 1.0994 | 1.1064 | 1.0695
2010-09-18 | 16 | 27.2168 | 10.4964 | 37.7132 | 2.4741 | 0.76558 | 0.28036 | 3.5201 | 9.334% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-09-18 | 17 | 28.4517 | 10.9004 | 39.3521 | 2.6938 | 0.76558 | 0.29255 | 3.752 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-09-18 | 18 | 29.3443 | 10.8 | 40.1443 | 2.8034 | 0.76558 | 0.29844 | 3.8674 | 9.634% | 10.25% | 6.927% | 1.1066 | 1.1142 | 1.0744
2010-09-18 | 19 | 29.3291 | 10.8435 | 40.1726 | 2.8073 | 0.76558 | 0.29865 | 3.8716 | 9.637% | 10.25% | 6.929% | 1.1067 | 1.1143 | 1.0745
2010-09-18 | 20 | 28.7272 | 10.4517 | 39.1789 | 2.6702 | 0.76558 | 0.29126 | 3.727 | 9.513% | 10.12% | 6.84% | 1.1051 | 1.1126 | 1.0734
2010-09-18 | 21 | 29.3145 | 10.1706 | 39.4851 | 2.7121 | 0.76558 | 0.29354 | 3.7712 | 9.551% | 10.16% | 6.867% | 1.1056 | 1.1131 | 1.0737
2010-09-18 | 22 | 28.4518 | 10.0691 | 38.5209 | 2.5812 | 0.76558 | 0.28637 | 3.6332 | 9.432% | 10.04% | 6.781% | 1.1041 | 1.1115 | 1.0727
2010-09-18 | 23 | 27.5761 | 9.8179 | 37.3939 | 2.4324 | 0.76558 | 0.27799 | 3.476 | 9.296% | 9.89% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-09-18 | 24 | 26.3722 | 9.4566 | 35.8289 | 2.2331 | 0.76558 | 0.26636 | 3.265 | 9.113% | 9.696% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-09-18 | 25 | 25.0934 | 9.1786 | 34.272 | 2.0432 | 0.76558 | 0.25478 | 3.0636 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-09-18 | 26 | 24.3179 | 8.6727 | 32.9905 | 1.8933 | 0.76558 | 0.24526 | 2.9041 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-18 | 27 | 24.1827 | 8.8399 | 33.0226 | 1.897 | 0.76558 | 0.24549 | 2.908 | 8.806% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-09-18 | 28 | 24.1038 | 8.8868 | 32.9906 | 1.8933 | 0.76558 | 0.24526 | 2.9041 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-18 | 29 | 23.3215 | 8.5358 | 31.8573 | 1.7654 | 0.76558 | 0.23683 | 2.7678 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-09-18 | 30 | 22.7669 | 8.33 | 31.0968 | 1.6822 | 0.76558 | 0.23118 | 2.6789 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-09-18 | 31 | 23.1553 | 8.1538 | 31.3092 | 1.7052 | 0.76558 | 0.23276 | 2.7035 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-09-18 | 32 | 23.2707 | 8.2983 | 31.569 | 1.7336 | 0.76558 | 0.23469 | 2.7339 | 8.66% | 9.214% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-09-18 | 33 | 23.0556 | 8.4951 | 31.5507 | 1.7316 | 0.76558 | 0.23455 | 2.7317 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-09-18 | 34 | 23.0256 | 8.612 | 31.6375 | 1.7412 | 0.76558 | 0.2352 | 2.7419 | 8.667% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2010-09-18 | 35 | 23.3605 | 9.0685 | 32.429 | 1.8294 | 0.76558 | 0.24108 | 2.836 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-09-18 | 36 | 24.4497 | 9.5425 | 33.9921 | 2.01 | 0.76558 | 0.2527 | 3.0283 | 8.909% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-09-18 | 37 | 26.1208 | 10.0168 | 36.1375 | 2.2717 | 0.76558 | 0.26865 | 3.3059 | 9.148% | 9.734% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-09-18 | 38 | 27.8279 | 10.7797 | 38.6076 | 2.5929 | 0.76558 | 0.28701 | 3.6455 | 9.442% | 10.05% | 6.789% | 1.1043 | 1.1117 | 1.0728
2010-09-18 | 39 | 28.7612 | 10.9958 | 39.757 | 2.7496 | 0.76558 | 0.29556 | 3.8107 | 9.585% | 10.2% | 6.892% | 1.106 | 1.1136 | 1.074
2010-09-18 | 40 | 28.7616 | 10.6094 | 39.3711 | 2.6964 | 0.76558 | 0.29269 | 3.7547 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-09-18 | 41 | 29.2627 | 10.2824 | 39.5451 | 2.7203 | 0.76558 | 0.29398 | 3.7799 | 9.558% | 10.17% | 6.872% | 1.1057 | 1.1132 | 1.0738
2010-09-18 | 42 | 28.7854 | 10.12 | 38.9054 | 2.633 | 0.76558 | 0.28923 | 3.6878 | 9.479% | 10.09% | 6.815% | 1.1047 | 1.1122 | 1.0731
2010-09-18 | 43 | 27.677 | 9.5086 | 37.1856 | 2.4054 | 0.76558 | 0.27644 | 3.4474 | 9.271% | 9.864% | 6.666% | 1.1022 | 1.1094 | 1.0714
2010-09-18 | 44 | 26.2556 | 8.9262 | 35.1818 | 2.1531 | 0.76558 | 0.26155 | 3.1803 | 9.039% | 9.618% | 6.499% | 1.0994 | 1.1064 | 1.0695
2010-09-18 | 45 | 24.2368 | 8.1946 | 32.4313 | 1.8296 | 0.76558 | 0.2411 | 2.8363 | 8.746% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-09-18 | 46 | 22.2521 | 7.4222 | 29.6743 | 1.5318 | 0.76558 | 0.2206 | 2.518 | 8.485% | 9.028% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-09-18 | 47 | 21.5353 | 7.2258 | 28.761 | 1.4389 | 0.76558 | 0.21381 | 2.4183 | 8.408% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0643
2010-09-18 | 48 | 21.3317 | 7.5123 | 28.844 | 1.4473 | 0.76558 | 0.21443 | 2.4273 | 8.415% | 8.954% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-09-19 | 1 | 19.6934 | 6.7141 | 26.4075 | 1.2131 | 0.76558 | 0.19632 | 2.175 | 8.236% | 8.763% | 5.922% | 1.0898 | 1.0961 | 1.0629
2010-09-19 | 2 | 18.4432 | 6.1554 | 24.5986 | 1.0526 | 0.76558 | 0.18287 | 2.001 | 8.135% | 8.655% | 5.849% | 1.0886 | 1.0948 | 1.0621
2010-09-19 | 3 | 17.781 | 5.9725 | 23.7535 | 0.9815 | 0.76558 | 0.17659 | 1.9237 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-09-19 | 4 | 17.1224 | 5.7846 | 22.907 | 0.91279 | 0.76558 | 0.17029 | 1.8487 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-09-19 | 5 | 16.9074 | 5.7142 | 22.6215 | 0.89018 | 0.76558 | 0.16817 | 1.8239 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-09-19 | 6 | 16.7215 | 5.8304 | 22.5519 | 0.88471 | 0.76558 | 0.16765 | 1.8179 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-09-19 | 7 | 16.6053 | 6.081 | 22.6863 | 0.89529 | 0.76558 | 0.16865 | 1.8295 | 8.064% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-09-19 | 8 | 16.4214 | 6.2929 | 22.7143 | 0.8975 | 0.76558 | 0.16886 | 1.8319 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-09-19 | 9 | 16.7052 | 6.8918 | 23.5969 | 0.9686 | 0.76558 | 0.17542 | 1.9096 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-09-19 | 10 | 17.1069 | 7.3911 | 24.498 | 1.044 | 0.76558 | 0.18212 | 1.9917 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-09-19 | 11 | 18.4564 | 7.77 | 26.2264 | 1.1965 | 0.76558 | 0.19497 | 2.157 | 8.225% | 8.751% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-09-19 | 12 | 20.1357 | 8.0422 | 28.1779 | 1.3812 | 0.76558 | 0.20948 | 2.3562 | 8.362% | 8.897% | 6.012% | 1.0913 | 1.0977 | 1.064
2010-09-19 | 13 | 22.1894 | 8.9253 | 31.1147 | 1.6841 | 0.76558 | 0.23131 | 2.681 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-09-19 | 14 | 24.1299 | 9.3045 | 33.4344 | 1.9446 | 0.76558 | 0.24856 | 2.9587 | 8.849% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.0679
2010-09-19 | 15 | 26.4304 | 10.3709 | 36.8012 | 2.3559 | 0.76558 | 0.27358 | 3.3951 | 9.225% | 9.816% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-09-19 | 16 | 26.0973 | 10.8628 | 36.9601 | 2.3763 | 0.76558 | 0.27477 | 3.4166 | 9.244% | 9.836% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-09-19 | 17 | 26.8017 | 10.91 | 37.7117 | 2.4739 | 0.76558 | 0.28035 | 3.5199 | 9.334% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-09-19 | 18 | 27.722 | 10.0324 | 37.7544 | 2.4795 | 0.76558 | 0.28067 | 3.5258 | 9.339% | 9.936% | 6.715% | 1.103 | 1.1103 | 1.072
2010-09-19 | 19 | 28.6428 | 10.1969 | 38.8396 | 2.6241 | 0.76558 | 0.28874 | 3.6784 | 9.471% | 10.08% | 6.81% | 1.1046 | 1.1121 | 1.0731
2010-09-19 | 20 | 28.4134 | 10.0774 | 38.4908 | 2.5772 | 0.76558 | 0.28615 | 3.6289 | 9.428% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-09-19 | 21 | 28.9999 | 9.9663 | 38.9662 | 2.6413 | 0.76558 | 0.28968 | 3.6965 | 9.486% | 10.09% | 6.821% | 1.1048 | 1.1123 | 1.0732
2010-09-19 | 22 | 28.2261 | 9.798 | 38.024 | 2.5151 | 0.76558 | 0.28268 | 3.5633 | 9.371% | 9.971% | 6.738% | 1.1034 | 1.1108 | 1.0722
2010-09-19 | 23 | 27.079 | 9.3918 | 36.4709 | 2.3138 | 0.76558 | 0.27113 | 3.3505 | 9.187% | 9.775% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-09-19 | 24 | 26.2756 | 9.1578 | 35.4334 | 2.184 | 0.76558 | 0.26342 | 3.213 | 9.068% | 9.648% | 6.52% | 1.0997 | 1.1068 | 1.0697
2010-09-19 | 25 | 24.7812 | 8.9852 | 33.7664 | 1.9834 | 0.76558 | 0.25102 | 3 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-09-19 | 26 | 23.7621 | 8.5544 | 32.3165 | 1.8167 | 0.76558 | 0.24025 | 2.8225 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1025 | 1.067
2010-09-19 | 27 | 23.7925 | 8.5732 | 32.3657 | 1.8222 | 0.76558 | 0.24061 | 2.8284 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-09-19 | 28 | 23.4043 | 8.5288 | 31.9332 | 1.7739 | 0.76558 | 0.2374 | 2.7768 | 8.696% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-09-19 | 29 | 22.6918 | 8.0512 | 30.743 | 1.6441 | 0.76558 | 0.22855 | 2.6382 | 8.582% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-09-19 | 30 | 22.0312 | 7.7987 | 29.8298 | 1.5479 | 0.76558 | 0.22176 | 2.5352 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-09-19 | 31 | 22.6048 | 7.8085 | 30.4134 | 1.609 | 0.76558 | 0.2261 | 2.6007 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-09-19 | 32 | 22.6375 | 7.6873 | 30.3248 | 1.5997 | 0.76558 | 0.22544 | 2.5907 | 8.543% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-09-19 | 33 | 22.5579 | 7.9695 | 30.5274 | 1.6211 | 0.76558 | 0.22694 | 2.6136 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-09-19 | 34 | 23.1149 | 8.0956 | 31.2106 | 1.6945 | 0.76558 | 0.23202 | 2.6921 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.101 | 1.0661
2010-09-19 | 35 | 23.7965 | 8.5585 | 32.355 | 1.821 | 0.76558 | 0.24053 | 2.8271 | 8.738% | 9.297% | 6.283% | 1.0957 | 1.1025 | 1.067
2010-09-19 | 36 | 25.5648 | 9.2061 | 34.7709 | 2.1031 | 0.76558 | 0.25849 | 3.1272 | 8.994% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-09-19 | 37 | 27.1261 | 9.8015 | 36.9276 | 2.3721 | 0.76558 | 0.27452 | 3.4122 | 9.24% | 9.832% | 6.644% | 1.1018 | 1.109 | 1.0712
2010-09-19 | 38 | 29.1805 | 10.5032 | 39.6838 | 2.7394 | 0.76558 | 0.29501 | 3.8 | 9.576% | 10.19% | 6.885% | 1.1059 | 1.1134 | 1.0739
2010-09-19 | 39 | 30.1995 | 10.5963 | 40.7958 | 2.8951 | 0.76558 | 0.30328 | 3.964 | 9.717% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-09-19 | 40 | 29.0372 | 10.0734 | 39.1106 | 2.6609 | 0.76558 | 0.29075 | 3.7172 | 9.504% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0733
2010-09-19 | 41 | 28.7372 | 9.6028 | 38.34 | 2.557 | 0.76558 | 0.28502 | 3.6077 | 9.41% | 10.01% | 6.766% | 1.1039 | 1.1113 | 1.0726
2010-09-19 | 42 | 28.2913 | 9.2074 | 37.4987 | 2.4461 | 0.76558 | 0.27877 | 3.4904 | 9.308% | 9.904% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-09-19 | 43 | 27.2261 | 8.6737 | 35.8998 | 2.2419 | 0.76558 | 0.26688 | 3.2744 | 9.121% | 9.705% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-09-19 | 44 | 26.3665 | 8.446 | 34.8125 | 2.1082 | 0.76558 | 0.2588 | 3.1325 | 8.998% | 9.574% | 6.47% | 1.0989 | 1.1059 | 1.0692
2010-09-19 | 45 | 24.4835 | 7.9262 | 32.4097 | 1.8272 | 0.76558 | 0.24094 | 2.8337 | 8.743% | 9.303% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-09-19 | 46 | 22.2005 | 7.2345 | 29.435 | 1.5072 | 0.76558 | 0.21882 | 2.4916 | 8.465% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-09-19 | 47 | 21.8004 | 7.2394 | 29.0398 | 1.467 | 0.76558 | 0.21589 | 2.4484 | 8.431% | 8.971% | 6.062% | 1.0921 | 1.0985 | 1.0645
2010-09-19 | 48 | 21.7412 | 7.4431 | 29.1843 | 1.4816 | 0.76558 | 0.21696 | 2.4641 | 8.443% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-09-20 | 1 | 20.1194 | 6.7182 | 26.8375 | 1.2529 | 0.76558 | 0.19951 | 2.218 | 8.265% | 8.793% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-09-20 | 2 | 19.0569 | 6.4568 | 25.5137 | 1.1324 | 0.76558 | 0.18967 | 2.0876 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-09-20 | 3 | 18.4089 | 6.2951 | 24.704 | 1.0616 | 0.76558 | 0.18365 | 2.0108 | 8.14% | 8.661% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-09-20 | 4 | 17.9787 | 6.4307 | 24.4094 | 1.0365 | 0.76558 | 0.18146 | 1.9835 | 8.126% | 8.646% | 5.843% | 1.0884 | 1.0946 | 1.0621
2010-09-20 | 5 | 17.4766 | 6.8406 | 24.3173 | 1.0286 | 0.76558 | 0.18078 | 1.975 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-09-20 | 6 | 17.3194 | 7.0757 | 24.3951 | 1.0352 | 0.76558 | 0.18136 | 1.9822 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-09-20 | 7 | 17.1184 | 7.5822 | 24.7006 | 1.0613 | 0.76558 | 0.18363 | 2.0105 | 8.14% | 8.661% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-09-20 | 8 | 17.0029 | 8.4121 | 25.4151 | 1.1236 | 0.76558 | 0.18894 | 2.0781 | 8.177% | 8.7% | 5.879% | 1.089 | 1.0953 | 1.0625
2010-09-20 | 9 | 17.2045 | 8.803 | 26.0076 | 1.1766 | 0.76558 | 0.19334 | 2.1355 | 8.211% | 8.737% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-09-20 | 10 | 17.2314 | 9.0499 | 26.2813 | 1.2015 | 0.76558 | 0.19538 | 2.1625 | 8.228% | 8.755% | 5.916% | 1.0897 | 1.0959 | 1.0629
2010-09-20 | 11 | 17.8064 | 9.621 | 27.4273 | 1.3086 | 0.76558 | 0.2039 | 2.2781 | 8.306% | 8.837% | 5.972% | 1.0906 | 1.0969 | 1.0635
2010-09-20 | 12 | 18.4391 | 10.2318 | 28.6708 | 1.4299 | 0.76558 | 0.21314 | 2.4087 | 8.401% | 8.939% | 6.04% | 1.0917 | 1.0982 | 1.0643
2010-09-20 | 13 | 19.6735 | 10.5777 | 30.2512 | 1.5919 | 0.76558 | 0.22489 | 2.5824 | 8.536% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-09-20 | 14 | 20.5347 | 10.9357 | 31.4704 | 1.7228 | 0.76558 | 0.23395 | 2.7224 | 8.651% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-09-20 | 15 | 22.6767 | 11.4812 | 34.158 | 2.0296 | 0.76558 | 0.25393 | 3.0492 | 8.927% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-09-20 | 16 | 23.5536 | 11.5239 | 35.0775 | 2.1404 | 0.76558 | 0.26077 | 3.1667 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-09-20 | 17 | 25.2484 | 11.112 | 36.3605 | 2.2998 | 0.76558 | 0.27031 | 3.3357 | 9.174% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-09-20 | 18 | 26.7289 | 10.0202 | 36.7491 | 2.3492 | 0.76558 | 0.2732 | 3.388 | 9.219% | 9.809% | 6.629% | 1.1016 | 1.1088 | 1.071
2010-09-20 | 19 | 27.5897 | 10.0265 | 37.6163 | 2.4614 | 0.76558 | 0.27964 | 3.5066 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-09-20 | 20 | 27.518 | 10.0358 | 37.5538 | 2.4533 | 0.76558 | 0.27918 | 3.498 | 9.315% | 9.911% | 6.697% | 1.1027 | 1.11 | 1.0718
2010-09-20 | 21 | 28.3214 | 9.7206 | 38.042 | 2.5175 | 0.76558 | 0.28281 | 3.5658 | 9.373% | 9.973% | 6.739% | 1.1034 | 1.1108 | 1.0723
2010-09-20 | 22 | 28.1922 | 9.4231 | 37.6153 | 2.4613 | 0.76558 | 0.27964 | 3.5065 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-09-20 | 23 | 27.0719 | 9.1254 | 36.1973 | 2.2792 | 0.76558 | 0.2691 | 3.3139 | 9.155% | 9.741% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-09-20 | 24 | 25.6224 | 8.9747 | 34.5972 | 2.0822 | 0.76558 | 0.2572 | 3.1049 | 8.975% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-09-20 | 25 | 24.5405 | 8.8249 | 33.3653 | 1.9365 | 0.76558 | 0.24804 | 2.9502 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-09-20 | 26 | 23.3198 | 8.4189 | 31.7387 | 1.7523 | 0.76558 | 0.23595 | 2.7538 | 8.677% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-09-20 | 27 | 23.1106 | 8.3769 | 31.4875 | 1.7247 | 0.76558 | 0.23408 | 2.7244 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-09-20 | 28 | 22.8093 | 8.3289 | 31.1382 | 1.6866 | 0.76558 | 0.23149 | 2.6837 | 8.619% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-09-20 | 29 | 21.99 | 8.0228 | 30.0129 | 1.5669 | 0.76558 | 0.22312 | 2.5556 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-09-20 | 30 | 21.3165 | 7.7892 | 29.1057 | 1.4736 | 0.76558 | 0.21638 | 2.4556 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-09-20 | 31 | 22.2207 | 7.6984 | 29.9191 | 1.5572 | 0.76558 | 0.22242 | 2.5452 | 8.507% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-09-20 | 32 | 22.179 | 7.5152 | 29.6942 | 1.5338 | 0.76558 | 0.22075 | 2.5202 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-09-20 | 33 | 22.078 | 7.8216 | 29.8996 | 1.5551 | 0.76558 | 0.22228 | 2.543 | 8.505% | 9.049% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-09-20 | 34 | 22.5027 | 7.9295 | 30.4322 | 1.611 | 0.76558 | 0.22624 | 2.6028 | 8.553% | 9.1% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-09-20 | 35 | 23.1684 | 8.6311 | 31.7995 | 1.759 | 0.76558 | 0.2364 | 2.761 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-09-20 | 36 | 24.5919 | 9.1544 | 33.7463 | 1.981 | 0.76558 | 0.25087 | 2.9975 | 8.882% | 9.451% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-09-20 | 37 | 26.3917 | 9.7752 | 36.1669 | 2.2754 | 0.76558 | 0.26887 | 3.3098 | 9.152% | 9.737% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-09-20 | 38 | 28.662 | 10.2594 | 38.9214 | 2.6352 | 0.76558 | 0.28935 | 3.6901 | 9.481% | 10.09% | 6.817% | 1.1047 | 1.1122 | 1.0732
2010-09-20 | 39 | 29.2953 | 10.5563 | 39.8516 | 2.7627 | 0.76558 | 0.29626 | 3.8245 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-09-20 | 40 | 29.5251 | 10.3979 | 39.923 | 2.7726 | 0.76558 | 0.29679 | 3.8349 | 9.606% | 10.22% | 6.907% | 1.1063 | 1.1138 | 1.0742
2010-09-20 | 41 | 29.3617 | 10.0133 | 39.3749 | 2.697 | 0.76558 | 0.29272 | 3.7553 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-09-20 | 42 | 28.7165 | 9.4099 | 38.1264 | 2.5286 | 0.76558 | 0.28344 | 3.5777 | 9.384% | 9.984% | 6.747% | 1.1036 | 1.1109 | 1.0723
2010-09-20 | 43 | 27.3679 | 8.7142 | 36.0821 | 2.2647 | 0.76558 | 0.26824 | 3.2986 | 9.142% | 9.727% | 6.573% | 1.1006 | 1.1077 | 1.0704
2010-09-20 | 44 | 26.1058 | 8.044 | 34.1498 | 2.0287 | 0.76558 | 0.25387 | 3.0481 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-09-20 | 45 | 23.6553 | 7.3754 | 31.0307 | 1.675 | 0.76558 | 0.23069 | 2.6713 | 8.608% | 9.159% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-09-20 | 46 | 21.0993 | 6.6105 | 27.7098 | 1.3357 | 0.76558 | 0.206 | 2.3072 | 8.326% | 8.859% | 5.987% | 1.0908 | 1.0972 | 1.0637
2010-09-20 | 47 | 20.1156 | 6.5357 | 26.6513 | 1.2356 | 0.76558 | 0.19813 | 2.1993 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0963 | 1.0631
2010-09-20 | 48 | 20.2739 | 6.7098 | 26.9837 | 1.2666 | 0.76558 | 0.2006 | 2.2328 | 8.275% | 8.804% | 5.949% | 1.0902 | 1.0965 | 1.0633
2010-09-21 | 1 | 18.3067 | 6.0167 | 24.3235 | 1.0292 | 0.76558 | 0.18082 | 1.9756 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-09-21 | 2 | 17.2808 | 5.6385 | 22.9193 | 0.91377 | 0.76558 | 0.17038 | 1.8497 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-09-21 | 3 | 16.5334 | 5.3849 | 21.9183 | 0.83569 | 0.76558 | 0.16294 | 1.7642 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-09-21 | 4 | 16.2254 | 5.2006 | 21.426 | 0.79858 | 0.76558 | 0.15928 | 1.7234 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 5 | 16.0381 | 5.1075 | 21.1456 | 0.77781 | 0.76558 | 0.1572 | 1.7006 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 6 | 15.9521 | 5.1354 | 21.0875 | 0.77354 | 0.76558 | 0.15677 | 1.6959 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 7 | 15.8658 | 5.0932 | 20.959 | 0.76415 | 0.76558 | 0.15581 | 1.6855 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 8 | 15.6502 | 5.039 | 20.6892 | 0.7446 | 0.76558 | 0.15381 | 1.664 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 9 | 15.7942 | 5.3569 | 21.1511 | 0.77821 | 0.76558 | 0.15724 | 1.701 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 10 | 16.1833 | 5.4553 | 21.6386 | 0.8145 | 0.76558 | 0.16086 | 1.7409 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-21 | 11 | 16.8284 | 5.5851 | 22.4135 | 0.87388 | 0.76558 | 0.16662 | 1.8061 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-09-21 | 12 | 18.0794 | 6.1196 | 24.1991 | 1.0187 | 0.76558 | 0.1799 | 1.9641 | 8.117% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-09-21 | 13 | 19.9607 | 7.0426 | 27.0034 | 1.2684 | 0.76558 | 0.20075 | 2.2348 | 8.276% | 8.806% | 5.95% | 1.0902 | 1.0966 | 1.0633
2010-09-21 | 14 | 22.9903 | 8.3978 | 31.3881 | 1.7138 | 0.76558 | 0.23334 | 2.7127 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-09-21 | 15 | 27.1285 | 10.3646 | 37.4931 | 2.4453 | 0.76558 | 0.27873 | 3.4896 | 9.307% | 9.903% | 6.692% | 1.1026 | 1.1099 | 1.0717
2010-09-21 | 16 | 28.7949 | 11.0788 | 39.8737 | 2.7657 | 0.76558 | 0.29643 | 3.8277 | 9.6% | 10.21% | 6.902% | 1.1062 | 1.1138 | 1.0741
2010-09-21 | 17 | 29.3695 | 11.4533 | 40.8227 | 2.8989 | 0.76558 | 0.30348 | 3.968 | 9.72% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-09-21 | 18 | 28.9967 | 10.5709 | 39.5677 | 2.7234 | 0.76558 | 0.29415 | 3.7832 | 9.561% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-09-21 | 19 | 31.6105 | 10.9371 | 42.5475 | 3.1491 | 0.76558 | 0.3163 | 4.231 | 9.944% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-09-21 | 20 | 30.9222 | 10.69 | 41.6122 | 3.0121 | 0.76558 | 0.30935 | 4.0871 | 9.822% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-09-21 | 21 | 31.4813 | 10.3947 | 41.8759 | 3.0504 | 0.76558 | 0.31131 | 4.1273 | 9.856% | 10.49% | 7.087% | 1.1093 | 1.1172 | 1.0763
2010-09-21 | 22 | 30.3334 | 10.3448 | 40.6782 | 2.8784 | 0.76558 | 0.30241 | 3.9464 | 9.702% | 10.32% | 6.975% | 1.1074 | 1.1151 | 1.075
2010-09-21 | 23 | 28.105 | 10.0964 | 38.2014 | 2.5386 | 0.76558 | 0.28399 | 3.5882 | 9.393% | 9.994% | 6.753% | 1.1037 | 1.111 | 1.0724
2010-09-21 | 24 | 27.1604 | 9.8248 | 36.9852 | 2.3795 | 0.76558 | 0.27495 | 3.4201 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-09-21 | 25 | 26.1188 | 9.6217 | 35.7405 | 2.2221 | 0.76558 | 0.2657 | 3.2533 | 9.103% | 9.685% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-09-21 | 26 | 25.421 | 9.0697 | 34.4907 | 2.0694 | 0.76558 | 0.25641 | 3.0914 | 8.963% | 9.537% | 6.444% | 1.0985 | 1.1054 | 1.0689
2010-09-21 | 27 | 25.6144 | 9.1 | 34.7144 | 2.0963 | 0.76558 | 0.25807 | 3.12 | 8.987% | 9.563% | 6.462% | 1.0988 | 1.1057 | 1.0691
2010-09-21 | 28 | 25.7103 | 9.1289 | 34.8392 | 2.1114 | 0.76558 | 0.259 | 3.136 | 9.001% | 9.577% | 6.472% | 1.0989 | 1.1059 | 1.0692
2010-09-21 | 29 | 26.1259 | 9.071 | 35.1968 | 2.155 | 0.76558 | 0.26166 | 3.1822 | 9.041% | 9.62% | 6.501% | 1.0994 | 1.1064 | 1.0695
2010-09-21 | 30 | 26.1987 | 8.7884 | 34.9871 | 2.1294 | 0.76558 | 0.2601 | 3.155 | 9.018% | 9.595% | 6.484% | 1.0991 | 1.1061 | 1.0693
2010-09-21 | 31 | 27.0879 | 8.5424 | 35.6303 | 2.2084 | 0.76558 | 0.26488 | 3.2388 | 9.09% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-09-21 | 32 | 27.1603 | 8.8259 | 35.9862 | 2.2527 | 0.76558 | 0.26753 | 3.2858 | 9.131% | 9.715% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-09-21 | 33 | 26.9147 | 9.2167 | 36.1313 | 2.2709 | 0.76558 | 0.2686 | 3.3051 | 9.147% | 9.733% | 6.577% | 1.1007 | 1.1078 | 1.0704
2010-09-21 | 34 | 27.1275 | 9.452 | 36.5796 | 2.3276 | 0.76558 | 0.27194 | 3.3651 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-09-21 | 35 | 27.6448 | 10.1719 | 37.8167 | 2.4877 | 0.76558 | 0.28113 | 3.5344 | 9.346% | 9.944% | 6.72% | 1.1031 | 1.1104 | 1.072
2010-09-21 | 36 | 29.0669 | 10.9702 | 40.0371 | 2.7884 | 0.76558 | 0.29764 | 3.8516 | 9.62% | 10.24% | 6.917% | 1.1064 | 1.114 | 1.0743
2010-09-21 | 37 | 30.7904 | 11.3227 | 42.1132 | 3.0851 | 0.76558 | 0.31307 | 4.1638 | 9.887% | 10.52% | 7.109% | 1.1097 | 1.1176 | 1.0765
2010-09-21 | 38 | 31.9842 | 11.2017 | 43.1859 | 3.2443 | 0.76558 | 0.32105 | 4.3309 | 10.03% | 10.67% | 7.211% | 1.1115 | 1.1194 | 1.0777
2010-09-21 | 39 | 31.4661 | 10.846 | 42.3122 | 3.1143 | 0.76558 | 0.31455 | 4.1945 | 9.913% | 10.55% | 7.128% | 1.11 | 1.1179 | 1.0767
2010-09-21 | 40 | 33.2621 | 11.7973 | 45.0594 | 3.5319 | 0.76558 | 0.33498 | 4.6324 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-09-21 | 41 | 34.4832 | 11.5346 | 46.0178 | 3.6837 | 0.76558 | 0.3421 | 4.7914 | 10.41% | 11.08% | 7.486% | 1.1162 | 1.1246 | 1.0809
2010-09-21 | 42 | 33.4632 | 10.666 | 44.1291 | 3.3875 | 0.76558 | 0.32806 | 4.4812 | 10.15% | 10.8% | 7.301% | 1.113 | 1.1211 | 1.0788
2010-09-21 | 43 | 31.2819 | 9.9592 | 41.241 | 2.9587 | 0.76558 | 0.30659 | 4.0308 | 9.774% | 10.4% | 7.027% | 1.1083 | 1.1161 | 1.0756
2010-09-21 | 44 | 29.1838 | 9.1061 | 38.2898 | 2.5504 | 0.76558 | 0.28465 | 3.6006 | 9.404% | 10.01% | 6.761% | 1.1038 | 1.1112 | 1.0725
2010-09-21 | 45 | 26.3399 | 8.3056 | 34.6455 | 2.088 | 0.76558 | 0.25756 | 3.1111 | 8.98% | 9.555% | 6.457% | 1.0987 | 1.1056 | 1.069
2010-09-21 | 46 | 23.5539 | 7.4083 | 30.9621 | 1.6676 | 0.76558 | 0.23018 | 2.6634 | 8.602% | 9.153% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-09-21 | 47 | 22.3762 | 7.2219 | 29.5981 | 1.5239 | 0.76558 | 0.22004 | 2.5095 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-09-21 | 48 | 22.2903 | 7.3192 | 29.6095 | 1.5251 | 0.76558 | 0.22012 | 2.5108 | 8.48% | 9.022% | 6.097% | 1.0927 | 1.0992 | 1.0649
2010-09-22 | 1 | 20.4511 | 6.5047 | 26.9558 | 1.264 | 0.76558 | 0.20039 | 2.2299 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-09-22 | 2 | 19.1722 | 6.1128 | 25.285 | 1.1121 | 0.76558 | 0.18797 | 2.0657 | 8.17% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-09-22 | 3 | 18.2515 | 5.8936 | 24.1451 | 1.0141 | 0.76558 | 0.1795 | 1.9592 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-09-22 | 4 | 17.8947 | 5.6742 | 23.5688 | 0.9663 | 0.76558 | 0.17521 | 1.9071 | 8.092% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-09-22 | 5 | 17.4478 | 5.555 | 23.0027 | 0.92044 | 0.76558 | 0.17101 | 1.857 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-09-22 | 6 | 16.9451 | 5.4604 | 22.4055 | 0.87326 | 0.76558 | 0.16657 | 1.8054 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-09-22 | 7 | 16.5855 | 5.4552 | 22.0407 | 0.84505 | 0.76558 | 0.16385 | 1.7745 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-09-22 | 8 | 16.4282 | 5.5831 | 22.0113 | 0.8428 | 0.76558 | 0.16363 | 1.772 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-09-22 | 9 | 16.6575 | 5.6189 | 22.2763 | 0.86322 | 0.76558 | 0.16561 | 1.7944 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-09-22 | 10 | 16.829 | 5.6007 | 22.4297 | 0.87515 | 0.76558 | 0.16675 | 1.8075 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-09-22 | 11 | 17.8494 | 5.8117 | 23.6611 | 0.97388 | 0.76558 | 0.1759 | 1.9154 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-09-22 | 12 | 18.7414 | 6.512 | 25.2534 | 1.1094 | 0.76558 | 0.18774 | 2.0627 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-09-22 | 13 | 20.8667 | 7.4743 | 28.3409 | 1.3972 | 0.76558 | 0.21069 | 2.3735 | 8.375% | 8.911% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-09-22 | 14 | 24.0114 | 8.9806 | 32.992 | 1.8934 | 0.76558 | 0.24527 | 2.9043 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-22 | 15 | 28.0048 | 10.9378 | 38.9427 | 2.6381 | 0.76558 | 0.2895 | 3.6932 | 9.484% | 10.09% | 6.819% | 1.1048 | 1.1122 | 1.0732
2010-09-22 | 16 | 29.6436 | 11.7117 | 41.3553 | 2.9751 | 0.76558 | 0.30744 | 4.0481 | 9.789% | 10.42% | 7.038% | 1.1085 | 1.1163 | 1.0757
2010-09-22 | 17 | 28.7099 | 11.1989 | 39.9087 | 2.7706 | 0.76558 | 0.29669 | 3.8328 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-09-22 | 18 | 30.9061 | 11.6402 | 42.5462 | 3.1489 | 0.76558 | 0.31629 | 4.2308 | 9.944% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-09-22 | 19 | 34.0519 | 11.9293 | 45.9812 | 3.6779 | 0.76558 | 0.34183 | 4.7853 | 10.41% | 11.07% | 7.483% | 1.1162 | 1.1245 | 1.0809
2010-09-22 | 20 | 32.5022 | 11.185 | 43.6872 | 3.32 | 0.76558 | 0.32478 | 4.4104 | 10.1% | 10.74% | 7.259% | 1.1123 | 1.1203 | 1.0783
2010-09-22 | 21 | 32.6739 | 10.7254 | 43.3993 | 3.2764 | 0.76558 | 0.32264 | 4.3646 | 10.06% | 10.7% | 7.231% | 1.1118 | 1.1198 | 1.0779
2010-09-22 | 22 | 31.682 | 10.6406 | 42.3226 | 3.1159 | 0.76558 | 0.31463 | 4.1961 | 9.915% | 10.55% | 7.129% | 1.1101 | 1.1179 | 1.0768
2010-09-22 | 23 | 30.231 | 9.9364 | 40.1674 | 2.8066 | 0.76558 | 0.29861 | 3.8708 | 9.637% | 10.25% | 6.929% | 1.1066 | 1.1142 | 1.0744
2010-09-22 | 24 | 29.0397 | 10.3221 | 39.3618 | 2.6952 | 0.76558 | 0.29262 | 3.7534 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-09-22 | 25 | 28.2218 | 10.4823 | 38.7041 | 2.6058 | 0.76558 | 0.28773 | 3.6591 | 9.454% | 10.06% | 6.798% | 1.1044 | 1.1118 | 1.0729
2010-09-22 | 26 | 27.3737 | 9.6371 | 37.0108 | 2.3828 | 0.76558 | 0.27514 | 3.4235 | 9.25% | 9.842% | 6.651% | 1.1019 | 1.1092 | 1.0712
2010-09-22 | 27 | 27.1431 | 9.593 | 36.7361 | 2.3476 | 0.76558 | 0.2731 | 3.3863 | 9.218% | 9.808% | 6.628% | 1.1015 | 1.1087 | 1.071
2010-09-22 | 28 | 26.5826 | 9.5413 | 36.124 | 2.27 | 0.76558 | 0.26855 | 3.3041 | 9.147% | 9.732% | 6.576% | 1.1007 | 1.1078 | 1.0704
2010-09-22 | 29 | 26.2674 | 9.1576 | 35.4249 | 2.183 | 0.76558 | 0.26335 | 3.2119 | 9.067% | 9.647% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-09-22 | 30 | 25.5807 | 8.9924 | 34.5731 | 2.0793 | 0.76558 | 0.25702 | 3.1019 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-09-22 | 31 | 25.7086 | 8.8002 | 34.5088 | 2.0715 | 0.76558 | 0.25654 | 3.0937 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2010-09-22 | 32 | 25.9894 | 8.8908 | 34.8802 | 2.1164 | 0.76558 | 0.2593 | 3.1413 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2010-09-22 | 33 | 26.3119 | 9.5532 | 35.8651 | 2.2376 | 0.76558 | 0.26663 | 3.2698 | 9.117% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-09-22 | 34 | 26.5522 | 10.2632 | 36.8154 | 2.3577 | 0.76558 | 0.27369 | 3.397 | 9.227% | 9.818% | 6.634% | 1.1017 | 1.1089 | 1.0711
2010-09-22 | 35 | 27.3948 | 11.2049 | 38.5997 | 2.5918 | 0.76558 | 0.28695 | 3.6443 | 9.441% | 10.05% | 6.788% | 1.1043 | 1.1117 | 1.0728
2010-09-22 | 36 | 28.8889 | 11.5129 | 40.4019 | 2.8395 | 0.76558 | 0.30035 | 3.9054 | 9.666% | 10.29% | 6.95% | 1.107 | 1.1146 | 1.0747
2010-09-22 | 37 | 31.1752 | 12.0054 | 43.1806 | 3.2435 | 0.76558 | 0.32101 | 4.3301 | 10.03% | 10.67% | 7.21% | 1.1115 | 1.1194 | 1.0777
2010-09-22 | 38 | 32.6684 | 11.6774 | 44.3458 | 3.4209 | 0.76558 | 0.32967 | 4.5161 | 10.18% | 10.84% | 7.322% | 1.1134 | 1.1215 | 1.079
2010-09-22 | 39 | 31.4495 | 10.7106 | 42.1601 | 3.092 | 0.76558 | 0.31342 | 4.171 | 9.893% | 10.53% | 7.113% | 1.1098 | 1.1176 | 1.0766
2010-09-22 | 40 | 32.0679 | 11.0825 | 43.1504 | 3.239 | 0.76558 | 0.32079 | 4.3253 | 10.02% | 10.67% | 7.207% | 1.1114 | 1.1194 | 1.0777
2010-09-22 | 41 | 36.1315 | 11.3715 | 47.5029 | 3.9253 | 0.76558 | 0.35314 | 5.044 | 10.62% | 11.3% | 7.635% | 1.1188 | 1.1274 | 1.0827
2010-09-22 | 42 | 38.1994 | 11.6825 | 49.8819 | 4.3283 | 0.76558 | 0.37083 | 5.4647 | 10.96% | 11.66% | 7.877% | 1.123 | 1.1319 | 1.0855
2010-09-22 | 43 | 36.6062 | 11.1249 | 47.7312 | 3.9631 | 0.76558 | 0.35484 | 5.0836 | 10.65% | 11.33% | 7.658% | 1.1192 | 1.1278 | 1.0829
2010-09-22 | 44 | 34.1782 | 9.9879 | 44.1661 | 3.3932 | 0.76558 | 0.32834 | 4.4871 | 10.16% | 10.81% | 7.305% | 1.1131 | 1.1212 | 1.0788
2010-09-22 | 45 | 31.0617 | 8.8767 | 39.9384 | 2.7747 | 0.76558 | 0.29691 | 3.8372 | 9.608% | 10.22% | 6.908% | 1.1063 | 1.1139 | 1.0742
2010-09-22 | 46 | 28.2043 | 7.8046 | 36.0089 | 2.2556 | 0.76558 | 0.26769 | 3.2888 | 9.133% | 9.718% | 6.567% | 1.1005 | 1.1076 | 1.0703
2010-09-22 | 47 | 26.6943 | 7.5979 | 34.2921 | 2.0456 | 0.76558 | 0.25493 | 3.0661 | 8.941% | 9.513% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-09-22 | 48 | 26.6393 | 7.6267 | 34.2661 | 2.0425 | 0.76558 | 0.25474 | 3.0628 | 8.938% | 9.51% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-09-23 | 1 | 24.8155 | 6.952 | 31.7675 | 1.7555 | 0.76558 | 0.23616 | 2.7572 | 8.679% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2010-09-23 | 2 | 23.4931 | 6.4046 | 29.8978 | 1.5549 | 0.76558 | 0.22226 | 2.5428 | 8.505% | 9.049% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-09-23 | 3 | 22.4856 | 6.2305 | 28.7161 | 1.4345 | 0.76558 | 0.21348 | 2.4135 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-09-23 | 4 | 21.7834 | 6.3736 | 28.157 | 1.3791 | 0.76558 | 0.20932 | 2.354 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-09-23 | 5 | 21.5837 | 7.2206 | 28.8043 | 1.4433 | 0.76558 | 0.21413 | 2.423 | 8.412% | 8.95% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-09-23 | 6 | 21.611 | 8.1468 | 29.7578 | 1.5404 | 0.76558 | 0.22122 | 2.5272 | 8.493% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-09-23 | 7 | 21.5255 | 8.4837 | 30.0092 | 1.5665 | 0.76558 | 0.22309 | 2.5552 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-09-23 | 8 | 21.3391 | 8.7594 | 30.0985 | 1.5759 | 0.76558 | 0.22376 | 2.5652 | 8.523% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-09-23 | 9 | 21.5111 | 9.0449 | 30.556 | 1.6242 | 0.76558 | 0.22716 | 2.6169 | 8.564% | 9.112% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-09-23 | 10 | 21.5252 | 9.409 | 30.9343 | 1.6646 | 0.76558 | 0.22997 | 2.6602 | 8.599% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-09-23 | 11 | 22.1875 | 9.8789 | 32.0664 | 1.7887 | 0.76558 | 0.23839 | 2.7927 | 8.709% | 9.266% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-09-23 | 12 | 23.0804 | 10.2871 | 33.3675 | 1.9368 | 0.76558 | 0.24806 | 2.9504 | 8.842% | 9.408% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-09-23 | 13 | 25.3197 | 11.2681 | 36.5879 | 2.3287 | 0.76558 | 0.272 | 3.3663 | 9.2% | 9.789% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-09-23 | 14 | 28.8819 | 13.0433 | 41.9252 | 3.0576 | 0.76558 | 0.31168 | 4.1349 | 9.863% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-09-23 | 15 | 33.7658 | 15.2679 | 49.0337 | 4.1824 | 0.76558 | 0.36452 | 5.3125 | 10.83% | 11.53% | 7.79% | 1.1215 | 1.1303 | 1.0845
2010-09-23 | 16 | 31.7841 | 14.5569 | 46.341 | 3.7356 | 0.76558 | 0.3445 | 4.8457 | 10.46% | 11.13% | 7.518% | 1.1168 | 1.1252 | 1.0813
2010-09-23 | 17 | 31.4115 | 13.7987 | 45.2102 | 3.5556 | 0.76558 | 0.3361 | 4.6572 | 10.3% | 10.96% | 7.407% | 1.1148 | 1.1231 | 1.08
2010-09-23 | 18 | 33.1201 | 13.2338 | 46.3539 | 3.7377 | 0.76558 | 0.3446 | 4.8479 | 10.46% | 11.13% | 7.52% | 1.1168 | 1.1252 | 1.0813
2010-09-23 | 19 | 32.6169 | 12.2444 | 44.8613 | 3.5009 | 0.76558 | 0.3335 | 4.6 | 10.25% | 10.91% | 7.372% | 1.1143 | 1.1225 | 1.0796
2010-09-23 | 20 | 31.8127 | 11.2906 | 43.1033 | 3.2319 | 0.76558 | 0.32044 | 4.3179 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-09-23 | 21 | 32.6332 | 11.2698 | 43.903 | 3.3529 | 0.76558 | 0.32638 | 4.4449 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-09-23 | 22 | 31.7135 | 11.4648 | 43.1783 | 3.2431 | 0.76558 | 0.32099 | 4.3297 | 10.03% | 10.67% | 7.21% | 1.1115 | 1.1194 | 1.0777
2010-09-23 | 23 | 32.2732 | 11.63 | 43.9032 | 3.3529 | 0.76558 | 0.32638 | 4.4449 | 10.12% | 10.77% | 7.279% | 1.1126 | 1.1207 | 1.0785
2010-09-23 | 24 | 32.9504 | 12.5098 | 45.4603 | 3.595 | 0.76558 | 0.33796 | 4.6985 | 10.34% | 11% | 7.431% | 1.1153 | 1.1236 | 1.0803
2010-09-23 | 25 | 30.9956 | 11.6396 | 42.6352 | 3.1621 | 0.76558 | 0.31695 | 4.2446 | 9.956% | 10.59% | 7.158% | 1.1106 | 1.1185 | 1.0771
2010-09-23 | 26 | 29.2854 | 10.7621 | 40.0476 | 2.7899 | 0.76558 | 0.29772 | 3.8532 | 9.622% | 10.24% | 6.918% | 1.1065 | 1.114 | 1.0743
2010-09-23 | 27 | 28.9281 | 10.5411 | 39.4692 | 2.7099 | 0.76558 | 0.29342 | 3.7689 | 9.549% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-09-23 | 28 | 28.1513 | 10.7484 | 38.8997 | 2.6322 | 0.76558 | 0.28918 | 3.687 | 9.478% | 10.08% | 6.815% | 1.1047 | 1.1122 | 1.0731
2010-09-23 | 29 | 27.6793 | 10.4436 | 38.1228 | 2.5282 | 0.76558 | 0.28341 | 3.5771 | 9.383% | 9.984% | 6.747% | 1.1035 | 1.1109 | 1.0723
2010-09-23 | 30 | 27.3914 | 10.5316 | 37.923 | 2.5017 | 0.76558 | 0.28192 | 3.5492 | 9.359% | 9.958% | 6.729% | 1.1033 | 1.1106 | 1.0721
2010-09-23 | 31 | 28.8716 | 10.1972 | 39.0688 | 2.6552 | 0.76558 | 0.29044 | 3.7112 | 9.499% | 10.11% | 6.83% | 1.105 | 1.1124 | 1.0733
2010-09-23 | 32 | 29.7917 | 10.2469 | 40.0385 | 2.7886 | 0.76558 | 0.29765 | 3.8519 | 9.62% | 10.24% | 6.917% | 1.1064 | 1.114 | 1.0743
2010-09-23 | 33 | 29.3894 | 10.6837 | 40.0731 | 2.7934 | 0.76558 | 0.29791 | 3.8569 | 9.625% | 10.24% | 6.92% | 1.1065 | 1.1141 | 1.0743
2010-09-23 | 34 | 29.9313 | 11.0715 | 41.0028 | 2.9246 | 0.76558 | 0.30482 | 3.995 | 9.743% | 10.37% | 7.005% | 1.1079 | 1.1157 | 1.0753
2010-09-23 | 35 | 29.6744 | 11.254 | 40.9284 | 2.914 | 0.76558 | 0.30427 | 3.9838 | 9.734% | 10.36% | 6.998% | 1.1078 | 1.1155 | 1.0753
2010-09-23 | 36 | 30.4943 | 11.3917 | 41.886 | 3.0519 | 0.76558 | 0.31139 | 4.1289 | 9.857% | 10.49% | 7.087% | 1.1094 | 1.1172 | 1.0763
2010-09-23 | 37 | 31.5555 | 11.0691 | 42.6246 | 3.1605 | 0.76558 | 0.31688 | 4.2429 | 9.954% | 10.59% | 7.157% | 1.1105 | 1.1185 | 1.0771
2010-09-23 | 38 | 32.819 | 11.2086 | 44.0276 | 3.372 | 0.76558 | 0.32731 | 4.4649 | 10.14% | 10.79% | 7.291% | 1.1129 | 1.121 | 1.0786
2010-09-23 | 39 | 34.8601 | 11.7981 | 46.6581 | 3.7869 | 0.76558 | 0.34686 | 4.8994 | 10.5% | 11.17% | 7.55% | 1.1173 | 1.1258 | 1.0817
2010-09-23 | 40 | 35.8794 | 11.9403 | 47.8197 | 3.9779 | 0.76558 | 0.3555 | 5.0989 | 10.66% | 11.35% | 7.667% | 1.1194 | 1.128 | 1.083
2010-09-23 | 41 | 40.3623 | 13.0814 | 53.4438 | 4.9685 | 0.76558 | 0.39731 | 6.1314 | 11.47% | 12.21% | 8.249% | 1.1296 | 1.139 | 1.0899
2010-09-23 | 42 | 42.3121 | 13.7873 | 56.0994 | 5.4746 | 0.76558 | 0.41705 | 6.6572 | 11.87% | 12.63% | 8.532% | 1.1346 | 1.1445 | 1.0933
2010-09-23 | 43 | 40.0723 | 12.3402 | 52.4125 | 4.7786 | 0.76558 | 0.38964 | 5.9339 | 11.32% | 12.05% | 8.14% | 1.1277 | 1.137 | 1.0886
2010-09-23 | 44 | 37.1715 | 11.0543 | 48.2258 | 4.0457 | 0.76558 | 0.35852 | 5.1698 | 10.72% | 11.41% | 7.708% | 1.1201 | 1.1287 | 1.0835
2010-09-23 | 45 | 33.1193 | 9.7997 | 42.919 | 3.2043 | 0.76558 | 0.31906 | 4.2889 | 9.993% | 10.63% | 7.185% | 1.111 | 1.119 | 1.0774
2010-09-23 | 46 | 29.3855 | 8.6017 | 37.9872 | 2.5102 | 0.76558 | 0.2824 | 3.5582 | 9.367% | 9.966% | 6.735% | 1.1033 | 1.1107 | 1.0722
2010-09-23 | 47 | 27.3745 | 8.0421 | 35.4167 | 2.182 | 0.76558 | 0.26329 | 3.2108 | 9.066% | 9.646% | 6.518% | 1.0997 | 1.1068 | 1.0697
2010-09-23 | 48 | 27.1441 | 8.1966 | 35.3407 | 2.1726 | 0.76558 | 0.26273 | 3.2009 | 9.057% | 9.637% | 6.512% | 1.0996 | 1.1066 | 1.0697
2010-09-24 | 1 | 25.033 | 7.2517 | 32.2847 | 1.8131 | 0.76558 | 0.24001 | 2.8187 | 8.731% | 9.29% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-09-24 | 2 | 23.3966 | 6.8258 | 30.2225 | 1.5889 | 0.76558 | 0.22468 | 2.5791 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-09-24 | 3 | 22.4754 | 7.0349 | 29.5103 | 1.5149 | 0.76558 | 0.21938 | 2.4999 | 8.471% | 9.013% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-09-24 | 4 | 22.1604 | 7.4209 | 29.5812 | 1.5222 | 0.76558 | 0.21991 | 2.5077 | 8.477% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-09-24 | 5 | 21.4857 | 7.8267 | 29.3124 | 1.4946 | 0.76558 | 0.21791 | 2.4781 | 8.454% | 8.995% | 6.079% | 1.0923 | 1.0988 | 1.0647
2010-09-24 | 6 | 21.4427 | 10.0415 | 31.4842 | 1.7243 | 0.76558 | 0.23406 | 2.724 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-09-24 | 7 | 21.2983 | 10.851 | 32.1492 | 1.7979 | 0.76558 | 0.239 | 2.8025 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-09-24 | 8 | 20.9824 | 11.3829 | 32.3652 | 1.8222 | 0.76558 | 0.24061 | 2.8284 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-09-24 | 9 | 21.096 | 11.6486 | 32.7446 | 1.8651 | 0.76558 | 0.24343 | 2.8742 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-09-24 | 10 | 21.4121 | 11.7624 | 33.1745 | 1.9144 | 0.76558 | 0.24662 | 2.9266 | 8.822% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-09-24 | 11 | 22.2318 | 11.881 | 34.1129 | 2.0243 | 0.76558 | 0.2536 | 3.0435 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-09-24 | 12 | 23.5227 | 12.3443 | 35.8669 | 2.2378 | 0.76558 | 0.26664 | 3.27 | 9.117% | 9.701% | 6.555% | 1.1003 | 1.1074 | 1.0702
2010-09-24 | 13 | 26.0515 | 13.4232 | 39.4747 | 2.7106 | 0.76558 | 0.29346 | 3.7697 | 9.55% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-09-24 | 14 | 29.9941 | 15.251 | 45.2451 | 3.561 | 0.76558 | 0.33636 | 4.663 | 10.31% | 10.97% | 7.41% | 1.1149 | 1.1232 | 1.08
2010-09-24 | 15 | 34.4601 | 17.7242 | 52.1843 | 4.7371 | 0.76558 | 0.38794 | 5.8906 | 11.29% | 12.01% | 8.116% | 1.1272 | 1.1365 | 1.0883
2010-09-24 | 16 | 32.9601 | 17.7466 | 50.7068 | 4.4727 | 0.76558 | 0.37696 | 5.6152 | 11.07% | 11.78% | 7.962% | 1.1245 | 1.1336 | 1.0865
2010-09-24 | 17 | 34.1154 | 18.1242 | 52.2396 | 4.7472 | 0.76558 | 0.38836 | 5.9011 | 11.3% | 12.02% | 8.122% | 1.1273 | 1.1366 | 1.0884
2010-09-24 | 18 | 37.1436 | 18.1559 | 55.2996 | 5.3196 | 0.76558 | 0.4111 | 6.4963 | 11.75% | 12.5% | 8.446% | 1.1331 | 1.1428 | 1.0923
2010-09-24 | 19 | 35.0906 | 15.2523 | 50.3429 | 4.4087 | 0.76558 | 0.37426 | 5.5485 | 11.02% | 11.73% | 7.924% | 1.1239 | 1.1328 | 1.0861
2010-09-24 | 20 | 33.8785 | 12.9092 | 46.7877 | 3.808 | 0.76558 | 0.34783 | 4.9214 | 10.52% | 11.19% | 7.563% | 1.1176 | 1.126 | 1.0818
2010-09-24 | 21 | 37.0532 | 12.9153 | 49.9685 | 4.3434 | 0.76558 | 0.37147 | 5.4804 | 10.97% | 11.67% | 7.886% | 1.1232 | 1.1321 | 1.0856
2010-09-24 | 22 | 38.8494 | 13.36 | 52.2093 | 4.7417 | 0.76558 | 0.38813 | 5.8954 | 11.29% | 12.01% | 8.119% | 1.1273 | 1.1366 | 1.0884
2010-09-24 | 23 | 37.5641 | 12.8814 | 50.4455 | 4.4267 | 0.76558 | 0.37502 | 5.5673 | 11.04% | 11.74% | 7.935% | 1.1241 | 1.133 | 1.0862
2010-09-24 | 24 | 35.043 | 12.5341 | 47.5771 | 3.9376 | 0.76558 | 0.35369 | 5.0569 | 10.63% | 11.31% | 7.642% | 1.1189 | 1.1275 | 1.0827
2010-09-24 | 25 | 32.1935 | 12.1868 | 44.3803 | 3.4262 | 0.76558 | 0.32993 | 4.5217 | 10.19% | 10.84% | 7.326% | 1.1134 | 1.1216 | 1.079
2010-09-24 | 26 | 30.318 | 11.3131 | 41.6312 | 3.0149 | 0.76558 | 0.30949 | 4.09 | 9.824% | 10.45% | 7.064% | 1.1089 | 1.1167 | 1.076
2010-09-24 | 27 | 29.9295 | 10.9333 | 40.8628 | 2.9046 | 0.76558 | 0.30378 | 3.974 | 9.725% | 10.35% | 6.992% | 1.1077 | 1.1154 | 1.0752
2010-09-24 | 28 | 29.837 | 10.6992 | 40.5362 | 2.8584 | 0.76558 | 0.30135 | 3.9253 | 9.683% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-09-24 | 29 | 28.9391 | 10.4068 | 39.3459 | 2.693 | 0.76558 | 0.2925 | 3.7511 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2010-09-24 | 30 | 27.834 | 10.0994 | 37.9334 | 2.5031 | 0.76558 | 0.282 | 3.5507 | 9.36% | 9.959% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-09-24 | 31 | 28.661 | 10.0227 | 38.6837 | 2.6031 | 0.76558 | 0.28758 | 3.6563 | 9.452% | 10.06% | 6.796% | 1.1044 | 1.1118 | 1.0729
2010-09-24 | 32 | 28.4172 | 9.8948 | 38.312 | 2.5533 | 0.76558 | 0.28482 | 3.6037 | 9.406% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2010-09-24 | 33 | 28.497 | 10.2377 | 38.7347 | 2.61 | 0.76558 | 0.28796 | 3.6635 | 9.458% | 10.06% | 6.8% | 1.1045 | 1.1119 | 1.073
2010-09-24 | 34 | 29.389 | 10.7189 | 40.1078 | 2.7983 | 0.76558 | 0.29817 | 3.862 | 9.629% | 10.25% | 6.923% | 1.1066 | 1.1141 | 1.0744
2010-09-24 | 35 | 30.5224 | 11.2969 | 41.8193 | 3.0422 | 0.76558 | 0.31089 | 4.1187 | 9.849% | 10.48% | 7.081% | 1.1092 | 1.1171 | 1.0762
2010-09-24 | 36 | 32.49 | 12.0172 | 44.5072 | 3.4458 | 0.76558 | 0.33087 | 4.5423 | 10.21% | 10.86% | 7.338% | 1.1137 | 1.1218 | 1.0792
2010-09-24 | 37 | 34.4859 | 12.6461 | 47.1319 | 3.8643 | 0.76558 | 0.35038 | 4.9802 | 10.57% | 11.24% | 7.597% | 1.1181 | 1.1267 | 1.0822
2010-09-24 | 38 | 34.9017 | 12.5114 | 47.4132 | 3.9105 | 0.76558 | 0.35248 | 5.0286 | 10.61% | 11.28% | 7.626% | 1.1186 | 1.1272 | 1.0826
2010-09-24 | 39 | 37.8023 | 13.5756 | 51.3779 | 4.5919 | 0.76558 | 0.38195 | 5.7394 | 11.17% | 11.89% | 8.032% | 1.1258 | 1.1349 | 1.0873
2010-09-24 | 40 | 36.7981 | 12.6755 | 49.4736 | 4.2578 | 0.76558 | 0.36779 | 5.3911 | 10.9% | 11.59% | 7.835% | 1.1223 | 1.1312 | 1.085
2010-09-24 | 41 | 37.2725 | 12.7319 | 50.0044 | 4.3496 | 0.76558 | 0.37174 | 5.4869 | 10.97% | 11.68% | 7.89% | 1.1233 | 1.1322 | 1.0857
2010-09-24 | 42 | 36.7944 | 11.9273 | 48.7217 | 4.1293 | 0.76558 | 0.3622 | 5.2571 | 10.79% | 11.48% | 7.758% | 1.121 | 1.1297 | 1.0841
2010-09-24 | 43 | 36.2295 | 12.2736 | 48.5032 | 4.0924 | 0.76558 | 0.36058 | 5.2185 | 10.76% | 11.45% | 7.736% | 1.1206 | 1.1293 | 1.0838
2010-09-24 | 44 | 34.086 | 11.1804 | 45.2663 | 3.5644 | 0.76558 | 0.33652 | 4.6665 | 10.31% | 10.97% | 7.412% | 1.1149 | 1.1232 | 1.0801
2010-09-24 | 45 | 30.4105 | 9.8711 | 40.2816 | 2.8226 | 0.76558 | 0.29946 | 3.8876 | 9.651% | 10.27% | 6.939% | 1.1068 | 1.1144 | 1.0746
2010-09-24 | 46 | 27.0735 | 8.8209 | 35.8943 | 2.2412 | 0.76558 | 0.26684 | 3.2736 | 9.12% | 9.704% | 6.557% | 1.1004 | 1.1075 | 1.0702
2010-09-24 | 47 | 25.6806 | 8.4725 | 34.153 | 2.0291 | 0.76558 | 0.2539 | 3.0485 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-09-24 | 48 | 26.4986 | 8.5712 | 35.0697 | 2.1394 | 0.76558 | 0.26071 | 3.1657 | 9.027% | 9.605% | 6.49% | 1.0992 | 1.1063 | 1.0694
2010-09-25 | 1 | 24.4705 | 7.6397 | 32.1102 | 1.7936 | 0.76558 | 0.23871 | 2.7979 | 8.713% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-09-25 | 2 | 23.0648 | 7.1789 | 30.2436 | 1.5911 | 0.76558 | 0.22483 | 2.5815 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-09-25 | 3 | 22.0018 | 6.9558 | 28.9576 | 1.4587 | 0.76558 | 0.21527 | 2.4395 | 8.424% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-09-25 | 4 | 22.1725 | 6.7319 | 28.9044 | 1.4533 | 0.76558 | 0.21488 | 2.4338 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-09-25 | 5 | 21.0959 | 6.5868 | 27.6827 | 1.3331 | 0.76558 | 0.2058 | 2.3044 | 8.324% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2010-09-25 | 6 | 20.676 | 6.3742 | 27.0502 | 1.2728 | 0.76558 | 0.20109 | 2.2395 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-09-25 | 7 | 20.3578 | 6.2539 | 26.6117 | 1.2319 | 0.76558 | 0.19783 | 2.1953 | 8.249% | 8.777% | 5.931% | 1.0899 | 1.0962 | 1.0631
2010-09-25 | 8 | 20.5742 | 6.2083 | 26.7824 | 1.2478 | 0.76558 | 0.1991 | 2.2125 | 8.261% | 8.79% | 5.94% | 1.09 | 1.0964 | 1.0631
2010-09-25 | 9 | 20.76 | 6.2495 | 27.0095 | 1.269 | 0.76558 | 0.20079 | 2.2354 | 8.276% | 8.806% | 5.951% | 1.0902 | 1.0966 | 1.0633
2010-09-25 | 10 | 21.1344 | 6.3183 | 27.4526 | 1.311 | 0.76558 | 0.20409 | 2.2807 | 8.308% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-09-25 | 11 | 21.8254 | 6.5939 | 28.4193 | 1.4049 | 0.76558 | 0.21127 | 2.3818 | 8.381% | 8.917% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-09-25 | 12 | 22.8724 | 7.0303 | 29.9027 | 1.5554 | 0.76558 | 0.2223 | 2.5433 | 8.505% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-09-25 | 13 | 24.7991 | 7.8402 | 32.6393 | 1.8532 | 0.76558 | 0.24264 | 2.8614 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-09-25 | 14 | 27.9139 | 9.5137 | 37.4275 | 2.4368 | 0.76558 | 0.27824 | 3.4806 | 9.3% | 9.895% | 6.686% | 1.1025 | 1.1098 | 1.0717
2010-09-25 | 15 | 32.1244 | 12.0204 | 44.1448 | 3.39 | 0.76558 | 0.32818 | 4.4837 | 10.16% | 10.81% | 7.303% | 1.1131 | 1.1212 | 1.0788
2010-09-25 | 16 | 34.1901 | 13.2079 | 47.398 | 3.908 | 0.76558 | 0.35236 | 5.0259 | 10.6% | 11.28% | 7.624% | 1.1186 | 1.1272 | 1.0825
2010-09-25 | 17 | 34.9802 | 13.6409 | 48.6211 | 4.1123 | 0.76558 | 0.36146 | 5.2393 | 10.78% | 11.47% | 7.748% | 1.1208 | 1.1295 | 1.084
2010-09-25 | 18 | 35.9966 | 13.7601 | 49.7567 | 4.3066 | 0.76558 | 0.3699 | 5.4421 | 10.94% | 11.64% | 7.864% | 1.1228 | 1.1317 | 1.0854
2010-09-25 | 19 | 35.8935 | 13.2606 | 49.1542 | 4.203 | 0.76558 | 0.36542 | 5.334 | 10.85% | 11.55% | 7.802% | 1.1217 | 1.1305 | 1.0846
2010-09-25 | 20 | 34.6413 | 12.2209 | 46.8623 | 3.8202 | 0.76558 | 0.34838 | 4.9341 | 10.53% | 11.2% | 7.57% | 1.1177 | 1.1262 | 1.0819
2010-09-25 | 21 | 34.505 | 11.5341 | 46.0391 | 3.6871 | 0.76558 | 0.34226 | 4.795 | 10.41% | 11.08% | 7.488% | 1.1163 | 1.1246 | 1.0809
2010-09-25 | 22 | 33.4806 | 11.2554 | 44.736 | 3.4814 | 0.76558 | 0.33257 | 4.5795 | 10.24% | 10.89% | 7.36% | 1.114 | 1.1222 | 1.0794
2010-09-25 | 23 | 31.8564 | 10.5719 | 42.4283 | 3.1315 | 0.76558 | 0.31542 | 4.2124 | 9.928% | 10.56% | 7.139% | 1.1102 | 1.1181 | 1.0769
2010-09-25 | 24 | 30.848 | 10.3868 | 41.2347 | 2.9577 | 0.76558 | 0.30654 | 4.0299 | 9.773% | 10.4% | 7.027% | 1.1083 | 1.1161 | 1.0756
2010-09-25 | 25 | 29.3265 | 10.3162 | 39.6426 | 2.7338 | 0.76558 | 0.29471 | 3.794 | 9.571% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-09-25 | 26 | 28.2349 | 9.6448 | 37.8797 | 2.496 | 0.76558 | 0.2816 | 3.5432 | 9.354% | 9.952% | 6.725% | 1.1032 | 1.1105 | 1.0721
2010-09-25 | 27 | 28.0863 | 9.7892 | 37.8755 | 2.4955 | 0.76558 | 0.28157 | 3.5426 | 9.353% | 9.952% | 6.725% | 1.1032 | 1.1105 | 1.0721
2010-09-25 | 28 | 28.3084 | 9.8472 | 38.1555 | 2.5325 | 0.76558 | 0.28365 | 3.5817 | 9.387% | 9.988% | 6.749% | 1.1036 | 1.111 | 1.0724
2010-09-25 | 29 | 28.0501 | 9.6165 | 37.6666 | 2.468 | 0.76558 | 0.28002 | 3.5136 | 9.328% | 9.925% | 6.707% | 1.1029 | 1.1102 | 1.0719
2010-09-25 | 30 | 27.5057 | 9.5304 | 37.036 | 2.3861 | 0.76558 | 0.27533 | 3.427 | 9.253% | 9.845% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-09-25 | 31 | 28.5664 | 9.5762 | 38.1426 | 2.5308 | 0.76558 | 0.28356 | 3.5799 | 9.386% | 9.986% | 6.748% | 1.1036 | 1.1109 | 1.0724
2010-09-25 | 32 | 28.5758 | 9.449 | 38.0248 | 2.5152 | 0.76558 | 0.28268 | 3.5634 | 9.371% | 9.971% | 6.738% | 1.1034 | 1.1108 | 1.0722
2010-09-25 | 33 | 27.821 | 9.6055 | 37.4265 | 2.4366 | 0.76558 | 0.27823 | 3.4805 | 9.299% | 9.895% | 6.686% | 1.1025 | 1.1098 | 1.0717
2010-09-25 | 34 | 27.631 | 9.702 | 37.333 | 2.4245 | 0.76558 | 0.27754 | 3.4676 | 9.288% | 9.883% | 6.678% | 1.1024 | 1.1097 | 1.0716
2010-09-25 | 35 | 27.5937 | 10.334 | 37.9277 | 2.5023 | 0.76558 | 0.28196 | 3.5499 | 9.36% | 9.959% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-09-25 | 36 | 28.8271 | 10.9131 | 39.7402 | 2.7472 | 0.76558 | 0.29543 | 3.8082 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-09-25 | 37 | 30.6232 | 11.3856 | 42.0088 | 3.0698 | 0.76558 | 0.3123 | 4.1477 | 9.873% | 10.51% | 7.099% | 1.1096 | 1.1174 | 1.0764
2010-09-25 | 38 | 32.693 | 12.0449 | 44.7379 | 3.4817 | 0.76558 | 0.33259 | 4.5798 | 10.24% | 10.89% | 7.36% | 1.114 | 1.1222 | 1.0795
2010-09-25 | 39 | 33.4683 | 12.5081 | 45.9765 | 3.6771 | 0.76558 | 0.34179 | 4.7845 | 10.41% | 11.07% | 7.482% | 1.1162 | 1.1245 | 1.0809
2010-09-25 | 40 | 33.4233 | 12.2633 | 45.6867 | 3.6309 | 0.76558 | 0.33964 | 4.7361 | 10.37% | 11.03% | 7.454% | 1.1157 | 1.124 | 1.0805
2010-09-25 | 41 | 33.9129 | 11.8293 | 45.7422 | 3.6397 | 0.76558 | 0.34005 | 4.7454 | 10.37% | 11.04% | 7.459% | 1.1157 | 1.1241 | 1.0806
2010-09-25 | 42 | 33.8579 | 11.4837 | 45.3415 | 3.5762 | 0.76558 | 0.33707 | 4.6789 | 10.32% | 10.98% | 7.42% | 1.1151 | 1.1233 | 1.0801
2010-09-25 | 43 | 32.4669 | 11.0672 | 43.5341 | 3.2968 | 0.76558 | 0.32364 | 4.386 | 10.07% | 10.72% | 7.244% | 1.112 | 1.1201 | 1.0781
2010-09-25 | 44 | 30.9728 | 10.5388 | 41.5116 | 2.9976 | 0.76558 | 0.3086 | 4.0718 | 9.809% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-09-25 | 45 | 28.9324 | 9.7667 | 38.6992 | 2.6052 | 0.76558 | 0.28769 | 3.6585 | 9.454% | 10.06% | 6.797% | 1.1044 | 1.1118 | 1.0729
2010-09-25 | 46 | 26.3197 | 8.9623 | 35.282 | 2.1654 | 0.76558 | 0.26229 | 3.1933 | 9.051% | 9.63% | 6.507% | 1.0995 | 1.1066 | 1.0696
2010-09-25 | 47 | 25.1685 | 8.6647 | 33.8332 | 1.9912 | 0.76558 | 0.25152 | 3.0083 | 8.892% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-09-25 | 48 | 25.3565 | 8.8134 | 34.1699 | 2.0311 | 0.76558 | 0.25402 | 3.0507 | 8.928% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-09-26 | 1 | 23.2591 | 7.8185 | 31.0776 | 1.6801 | 0.76558 | 0.23103 | 2.6767 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-09-26 | 2 | 21.7662 | 7.167 | 28.9332 | 1.4562 | 0.76558 | 0.21509 | 2.4369 | 8.422% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-09-26 | 3 | 20.8758 | 6.9391 | 27.8149 | 1.3458 | 0.76558 | 0.20678 | 2.3182 | 8.334% | 8.868% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-09-26 | 4 | 20.5163 | 6.6891 | 27.2054 | 1.2875 | 0.76558 | 0.20225 | 2.2553 | 8.29% | 8.821% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-09-26 | 5 | 19.7564 | 6.6346 | 26.3909 | 1.2116 | 0.76558 | 0.19619 | 2.1733 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-09-26 | 6 | 19.442 | 6.4743 | 25.9164 | 1.1684 | 0.76558 | 0.19267 | 2.1266 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-09-26 | 7 | 19.4126 | 6.6232 | 26.0358 | 1.1792 | 0.76558 | 0.19355 | 2.1383 | 8.213% | 8.739% | 5.905% | 1.0895 | 1.0958 | 1.0628
2010-09-26 | 8 | 19.0826 | 7.3764 | 26.459 | 1.2178 | 0.76558 | 0.1967 | 2.1801 | 8.24% | 8.767% | 5.924% | 1.0898 | 1.0961 | 1.063
2010-09-26 | 9 | 19.2552 | 8.1534 | 27.4087 | 1.3068 | 0.76558 | 0.20376 | 2.2761 | 8.304% | 8.836% | 5.971% | 1.0906 | 1.0969 | 1.0635
2010-09-26 | 10 | 19.3672 | 8.6883 | 28.0555 | 1.3692 | 0.76558 | 0.20857 | 2.3434 | 8.353% | 8.887% | 6.006% | 1.0911 | 1.0975 | 1.0639
2010-09-26 | 11 | 19.8967 | 8.9257 | 28.8224 | 1.4451 | 0.76558 | 0.21427 | 2.4249 | 8.413% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-09-26 | 12 | 20.9296 | 9.5432 | 30.4728 | 1.6153 | 0.76558 | 0.22654 | 2.6074 | 8.557% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-09-26 | 13 | 22.3345 | 9.9272 | 32.2617 | 1.8105 | 0.76558 | 0.23984 | 2.816 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-09-26 | 14 | 24.2156 | 10.6616 | 34.8772 | 2.116 | 0.76558 | 0.25928 | 3.1409 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2010-09-26 | 15 | 26.4005 | 12.0205 | 38.421 | 2.5679 | 0.76558 | 0.28563 | 3.6191 | 9.42% | 10.02% | 6.773% | 1.104 | 1.1114 | 1.0726
2010-09-26 | 16 | 27.1037 | 12.6366 | 39.7403 | 2.7472 | 0.76558 | 0.29543 | 3.8083 | 9.583% | 10.2% | 6.89% | 1.106 | 1.1135 | 1.074
2010-09-26 | 17 | 28.5527 | 12.2366 | 40.7893 | 2.8942 | 0.76558 | 0.30323 | 3.963 | 9.716% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-09-26 | 18 | 29.386 | 12.4448 | 41.8308 | 3.0439 | 0.76558 | 0.31098 | 4.1204 | 9.85% | 10.48% | 7.082% | 1.1093 | 1.1171 | 1.0762
2010-09-26 | 19 | 30.1181 | 12.3709 | 42.489 | 3.1404 | 0.76558 | 0.31587 | 4.2219 | 9.936% | 10.57% | 7.144% | 1.1103 | 1.1182 | 1.0769
2010-09-26 | 20 | 29.701 | 12.2045 | 41.9056 | 3.0548 | 0.76558 | 0.31153 | 4.1319 | 9.86% | 10.49% | 7.089% | 1.1094 | 1.1172 | 1.0763
2010-09-26 | 21 | 30.3569 | 11.831 | 42.1879 | 3.0961 | 0.76558 | 0.31363 | 4.1753 | 9.897% | 10.53% | 7.116% | 1.1098 | 1.1177 | 1.0766
2010-09-26 | 22 | 29.8563 | 11.4483 | 41.3046 | 2.9678 | 0.76558 | 0.30706 | 4.0404 | 9.782% | 10.41% | 7.033% | 1.1084 | 1.1162 | 1.0757
2010-09-26 | 23 | 28.4066 | 10.3983 | 38.8049 | 2.6194 | 0.76558 | 0.28848 | 3.6735 | 9.467% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-09-26 | 24 | 27.4287 | 9.5519 | 36.9805 | 2.3789 | 0.76558 | 0.27492 | 3.4194 | 9.247% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-09-26 | 25 | 25.92 | 8.9676 | 34.8876 | 2.1173 | 0.76558 | 0.25936 | 3.1422 | 9.007% | 9.583% | 6.476% | 1.099 | 1.106 | 1.0692
2010-09-26 | 26 | 24.7011 | 8.5848 | 33.2858 | 1.9273 | 0.76558 | 0.24745 | 2.9403 | 8.834% | 9.399% | 6.351% | 1.0969 | 1.1037 | 1.0678
2010-09-26 | 27 | 24.5123 | 8.7323 | 33.2445 | 1.9225 | 0.76558 | 0.24714 | 2.9353 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-09-26 | 28 | 24.2842 | 8.7028 | 32.987 | 1.8929 | 0.76558 | 0.24523 | 2.9037 | 8.802% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-26 | 29 | 23.7157 | 8.541 | 32.2567 | 1.81 | 0.76558 | 0.2398 | 2.8154 | 8.728% | 9.287% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-09-26 | 30 | 23.2108 | 8.4294 | 31.6402 | 1.7415 | 0.76558 | 0.23522 | 2.7423 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-09-26 | 31 | 23.7788 | 8.4197 | 32.1984 | 1.8034 | 0.76558 | 0.23937 | 2.8084 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-09-26 | 32 | 23.2581 | 8.4861 | 31.7443 | 1.7529 | 0.76558 | 0.23599 | 2.7545 | 8.677% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-09-26 | 33 | 22.8811 | 8.8587 | 31.7398 | 1.7524 | 0.76558 | 0.23596 | 2.754 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-09-26 | 34 | 23.4935 | 8.8481 | 32.3416 | 1.8195 | 0.76558 | 0.24043 | 2.8255 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-09-26 | 35 | 24.0814 | 9.3453 | 33.4266 | 1.9437 | 0.76558 | 0.2485 | 2.9577 | 8.848% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-09-26 | 36 | 25.7067 | 10.2278 | 35.9345 | 2.2463 | 0.76558 | 0.26714 | 3.279 | 9.125% | 9.709% | 6.561% | 1.1004 | 1.1075 | 1.0702
2010-09-26 | 37 | 27.5314 | 10.7724 | 38.3038 | 2.5522 | 0.76558 | 0.28476 | 3.6026 | 9.405% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2010-09-26 | 38 | 29.1558 | 11.495 | 40.6508 | 2.8746 | 0.76558 | 0.3022 | 3.9424 | 9.698% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-09-26 | 39 | 30.5504 | 12.1412 | 42.6916 | 3.1704 | 0.76558 | 0.31737 | 4.2534 | 9.963% | 10.6% | 7.163% | 1.1107 | 1.1186 | 1.0772
2010-09-26 | 40 | 30.7078 | 11.8277 | 42.5356 | 3.1473 | 0.76558 | 0.31621 | 4.2291 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-09-26 | 41 | 30.8651 | 11.2323 | 42.0974 | 3.0828 | 0.76558 | 0.31296 | 4.1613 | 9.885% | 10.52% | 7.107% | 1.1097 | 1.1175 | 1.0765
2010-09-26 | 42 | 30.4212 | 10.6284 | 41.0496 | 2.9313 | 0.76558 | 0.30517 | 4.002 | 9.749% | 10.37% | 7.01% | 1.108 | 1.1157 | 1.0754
2010-09-26 | 43 | 28.8549 | 10.2591 | 39.114 | 2.6613 | 0.76558 | 0.29078 | 3.7177 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2010-09-26 | 44 | 27.3608 | 9.7165 | 37.0773 | 2.3914 | 0.76558 | 0.27564 | 3.4326 | 9.258% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-09-26 | 45 | 24.5452 | 8.9133 | 33.4585 | 1.9474 | 0.76558 | 0.24873 | 2.9617 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2010-09-26 | 46 | 22.8082 | 8.1951 | 31.0033 | 1.6721 | 0.76558 | 0.23048 | 2.6681 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-09-26 | 47 | 22.0591 | 8.0673 | 30.1264 | 1.5788 | 0.76558 | 0.22396 | 2.5683 | 8.525% | 9.071% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-09-26 | 48 | 22.5183 | 8.2508 | 30.7691 | 1.6469 | 0.76558 | 0.22874 | 2.6412 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2010-09-27 | 1 | 20.8944 | 7.443 | 28.3373 | 1.3969 | 0.76558 | 0.21066 | 2.3731 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-09-27 | 2 | 19.6441 | 6.8285 | 26.4725 | 1.2191 | 0.76558 | 0.1968 | 2.1814 | 8.24% | 8.768% | 5.925% | 1.0898 | 1.0961 | 1.063
2010-09-27 | 3 | 18.9979 | 6.4539 | 25.4518 | 1.1269 | 0.76558 | 0.18921 | 2.0817 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-09-27 | 4 | 18.2515 | 6.2611 | 24.5126 | 1.0452 | 0.76558 | 0.18223 | 1.993 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-09-27 | 5 | 18.2515 | 6.1 | 24.3515 | 1.0315 | 0.76558 | 0.18103 | 1.9781 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-09-27 | 6 | 18.2515 | 6.1 | 24.3515 | 1.0315 | 0.76558 | 0.18103 | 1.9781 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-09-27 | 7 | 17.5608 | 6.013 | 23.5738 | 0.9667 | 0.76558 | 0.17525 | 1.9075 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-09-27 | 8 | 17.4023 | 5.9433 | 23.3456 | 0.94808 | 0.76558 | 0.17355 | 1.8872 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-27 | 9 | 17.4302 | 5.8973 | 23.3275 | 0.94661 | 0.76558 | 0.17342 | 1.8856 | 8.083% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-27 | 10 | 17.5176 | 5.818 | 23.3356 | 0.94727 | 0.76558 | 0.17348 | 1.8863 | 8.083% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-27 | 11 | 17.9631 | 5.8793 | 23.8424 | 0.98886 | 0.76558 | 0.17725 | 1.9317 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-09-27 | 12 | 18.4241 | 6.0007 | 24.4248 | 1.0378 | 0.76558 | 0.18158 | 1.9849 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2010-09-27 | 13 | 19.1852 | 6.1881 | 25.3733 | 1.1199 | 0.76558 | 0.18863 | 2.0741 | 8.174% | 8.698% | 5.877% | 1.089 | 1.0953 | 1.0624
2010-09-27 | 14 | 20.1593 | 6.3051 | 26.4644 | 1.2183 | 0.76558 | 0.19674 | 2.1806 | 8.24% | 8.767% | 5.924% | 1.0898 | 1.0961 | 1.063
2010-09-27 | 15 | 21.38 | 6.5562 | 27.9362 | 1.3576 | 0.76558 | 0.20768 | 2.3309 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-09-27 | 16 | 22.4307 | 7.288 | 29.7187 | 1.5364 | 0.76558 | 0.22093 | 2.5229 | 8.489% | 9.032% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-09-27 | 17 | 24.3843 | 8.6619 | 33.0462 | 1.8997 | 0.76558 | 0.24567 | 2.9109 | 8.809% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-09-27 | 18 | 26.4526 | 9.7447 | 36.1974 | 2.2792 | 0.76558 | 0.2691 | 3.3139 | 9.155% | 9.741% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-09-27 | 19 | 28.2179 | 10.4892 | 38.7071 | 2.6062 | 0.76558 | 0.28775 | 3.6596 | 9.455% | 10.06% | 6.798% | 1.1044 | 1.1118 | 1.0729
2010-09-27 | 20 | 28.8942 | 11.1471 | 40.0413 | 2.789 | 0.76558 | 0.29767 | 3.8523 | 9.621% | 10.24% | 6.917% | 1.1064 | 1.114 | 1.0743
2010-09-27 | 21 | 30.844 | 11.4396 | 42.2837 | 3.1101 | 0.76558 | 0.31434 | 4.1901 | 9.909% | 10.54% | 7.125% | 1.11 | 1.1179 | 1.0767
2010-09-27 | 22 | 31.2487 | 11.1846 | 42.4332 | 3.1322 | 0.76558 | 0.31545 | 4.2132 | 9.929% | 10.56% | 7.139% | 1.1102 | 1.1181 | 1.0769
2010-09-27 | 23 | 30.8032 | 10.8458 | 41.649 | 3.0175 | 0.76558 | 0.30962 | 4.0927 | 9.827% | 10.46% | 7.065% | 1.109 | 1.1168 | 1.076
2010-09-27 | 24 | 30.2439 | 10.6352 | 40.879 | 2.9069 | 0.76558 | 0.3039 | 3.9764 | 9.727% | 10.35% | 6.994% | 1.1078 | 1.1154 | 1.0752
2010-09-27 | 25 | 28.4623 | 10.4003 | 38.8626 | 2.6272 | 0.76558 | 0.28891 | 3.6817 | 9.474% | 10.08% | 6.812% | 1.1047 | 1.1121 | 1.0731
2010-09-27 | 26 | 27.4422 | 10.046 | 37.4883 | 2.4447 | 0.76558 | 0.27869 | 3.489 | 9.307% | 9.902% | 6.692% | 1.1026 | 1.1099 | 1.0717
2010-09-27 | 27 | 27.7883 | 10.0712 | 37.8595 | 2.4934 | 0.76558 | 0.28145 | 3.5404 | 9.351% | 9.95% | 6.724% | 1.1032 | 1.1105 | 1.0721
2010-09-27 | 28 | 27.527 | 9.8204 | 37.3473 | 2.4264 | 0.76558 | 0.27764 | 3.4696 | 9.29% | 9.885% | 6.68% | 1.1024 | 1.1097 | 1.0716
2010-09-27 | 29 | 27.2563 | 9.2601 | 36.5164 | 2.3196 | 0.76558 | 0.27147 | 3.3566 | 9.192% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2010-09-27 | 30 | 26.4675 | 8.7402 | 35.2077 | 2.1563 | 0.76558 | 0.26174 | 3.1836 | 9.042% | 9.621% | 6.501% | 1.0994 | 1.1065 | 1.0695
2010-09-27 | 31 | 27.4002 | 8.701 | 36.1011 | 2.2671 | 0.76558 | 0.26838 | 3.3011 | 9.144% | 9.729% | 6.575% | 1.1006 | 1.1078 | 1.0704
2010-09-27 | 32 | 27.7437 | 8.6794 | 36.4231 | 2.3077 | 0.76558 | 0.27077 | 3.3441 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-09-27 | 33 | 27.8882 | 8.9803 | 36.8686 | 2.3645 | 0.76558 | 0.27409 | 3.4042 | 9.233% | 9.824% | 6.639% | 1.1017 | 1.1089 | 1.0711
2010-09-27 | 34 | 28.6638 | 9.0617 | 37.7255 | 2.4757 | 0.76558 | 0.28046 | 3.5218 | 9.335% | 9.933% | 6.712% | 1.103 | 1.1103 | 1.0719
2010-09-27 | 35 | 28.9364 | 9.6415 | 38.5778 | 2.5889 | 0.76558 | 0.28679 | 3.6412 | 9.439% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-09-27 | 36 | 30.159 | 10.5278 | 40.6869 | 2.8797 | 0.76558 | 0.30247 | 3.9477 | 9.703% | 10.32% | 6.976% | 1.1075 | 1.1151 | 1.075
2010-09-27 | 37 | 30.7047 | 10.8543 | 41.559 | 3.0044 | 0.76558 | 0.30895 | 4.079 | 9.815% | 10.44% | 7.057% | 1.1088 | 1.1166 | 1.0759
2010-09-27 | 38 | 30.6184 | 11.1026 | 41.721 | 3.0279 | 0.76558 | 0.31016 | 4.1037 | 9.836% | 10.47% | 7.072% | 1.1091 | 1.1169 | 1.0761
2010-09-27 | 39 | 30.6171 | 10.6732 | 41.2903 | 2.9657 | 0.76558 | 0.30696 | 4.0383 | 9.78% | 10.41% | 7.032% | 1.1084 | 1.1161 | 1.0756
2010-09-27 | 40 | 30.9898 | 10.8109 | 41.8008 | 3.0395 | 0.76558 | 0.31075 | 4.1158 | 9.846% | 10.48% | 7.08% | 1.1092 | 1.117 | 1.0762
2010-09-27 | 41 | 31.9387 | 11.2505 | 43.1891 | 3.2448 | 0.76558 | 0.32107 | 4.3314 | 10.03% | 10.67% | 7.211% | 1.1115 | 1.1195 | 1.0777
2010-09-27 | 42 | 31.7087 | 10.8559 | 42.5646 | 3.1516 | 0.76558 | 0.31643 | 4.2336 | 9.946% | 10.58% | 7.151% | 1.1104 | 1.1184 | 1.077
2010-09-27 | 43 | 30.6332 | 10.2469 | 40.8801 | 2.9071 | 0.76558 | 0.30391 | 3.9766 | 9.727% | 10.35% | 6.994% | 1.1078 | 1.1154 | 1.0752
2010-09-27 | 44 | 29.1258 | 9.451 | 38.5768 | 2.5887 | 0.76558 | 0.28678 | 3.6411 | 9.439% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-09-27 | 45 | 26.8413 | 8.5781 | 35.4194 | 2.1823 | 0.76558 | 0.26331 | 3.2112 | 9.066% | 9.646% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-09-27 | 46 | 24.5856 | 7.7827 | 32.3683 | 1.8225 | 0.76558 | 0.24063 | 2.8287 | 8.739% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.067
2010-09-27 | 47 | 23.3651 | 7.5462 | 30.9112 | 1.6621 | 0.76558 | 0.2298 | 2.6575 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-09-27 | 48 | 23.2798 | 7.7029 | 30.9826 | 1.6698 | 0.76558 | 0.23033 | 2.6657 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-09-28 | 1 | 21.3679 | 6.8224 | 28.1903 | 1.3824 | 0.76558 | 0.20957 | 2.3575 | 8.363% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-09-28 | 2 | 19.782 | 6.249 | 26.031 | 1.1787 | 0.76558 | 0.19352 | 2.1378 | 8.213% | 8.738% | 5.905% | 1.0895 | 1.0957 | 1.0628
2010-09-28 | 3 | 18.6961 | 5.9433 | 24.6394 | 1.0561 | 0.76558 | 0.18317 | 2.0048 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-09-28 | 4 | 17.9678 | 5.6302 | 23.598 | 0.96869 | 0.76558 | 0.17543 | 1.9097 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-09-28 | 5 | 17.6954 | 5.4708 | 23.1662 | 0.93356 | 0.76558 | 0.17222 | 1.8714 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-09-28 | 6 | 17.5519 | 5.406 | 22.9578 | 0.91685 | 0.76558 | 0.17067 | 1.8531 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-09-28 | 7 | 17.2782 | 5.4812 | 22.7594 | 0.90107 | 0.76558 | 0.1692 | 1.8358 | 8.066% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-09-28 | 8 | 17.1765 | 5.4476 | 22.624 | 0.89038 | 0.76558 | 0.16819 | 1.8241 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-09-28 | 9 | 17.1468 | 5.3602 | 22.507 | 0.88119 | 0.76558 | 0.16732 | 1.8141 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-09-28 | 10 | 17.2063 | 5.4974 | 22.7037 | 0.89666 | 0.76558 | 0.16878 | 1.831 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-09-28 | 11 | 17.7507 | 5.6511 | 23.4018 | 0.95265 | 0.76558 | 0.17397 | 1.8922 | 8.086% | 8.603% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-09-28 | 12 | 18.267 | 5.9121 | 24.1791 | 1.017 | 0.76558 | 0.17975 | 1.9623 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-09-28 | 13 | 19.9471 | 6.5981 | 26.5452 | 1.2258 | 0.76558 | 0.19734 | 2.1887 | 8.245% | 8.773% | 5.928% | 1.0899 | 1.0962 | 1.063
2010-09-28 | 14 | 21.9156 | 7.6158 | 29.5314 | 1.5171 | 0.76558 | 0.21954 | 2.5022 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-09-28 | 15 | 25.4223 | 9.153 | 34.5752 | 2.0795 | 0.76558 | 0.25704 | 3.1021 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-09-28 | 16 | 28.1494 | 10.4451 | 38.5945 | 2.5911 | 0.76558 | 0.28692 | 3.6436 | 9.441% | 10.04% | 6.788% | 1.1042 | 1.1117 | 1.0728
2010-09-28 | 17 | 30.7083 | 11.5898 | 42.2982 | 3.1123 | 0.76558 | 0.31445 | 4.1923 | 9.911% | 10.55% | 7.126% | 1.11 | 1.1179 | 1.0767
2010-09-28 | 18 | 32.0582 | 12.0542 | 44.1124 | 3.385 | 0.76558 | 0.32794 | 4.4785 | 10.15% | 10.8% | 7.3% | 1.113 | 1.1211 | 1.0787
2010-09-28 | 19 | 32.8185 | 12.4075 | 45.226 | 3.558 | 0.76558 | 0.33622 | 4.6598 | 10.3% | 10.96% | 7.408% | 1.1149 | 1.1231 | 1.08
2010-09-28 | 20 | 32.014 | 12.1437 | 44.1577 | 3.3919 | 0.76558 | 0.32827 | 4.4858 | 10.16% | 10.81% | 7.304% | 1.1131 | 1.1212 | 1.0788
2010-09-28 | 21 | 32.7627 | 11.9145 | 44.6773 | 3.4722 | 0.76558 | 0.33214 | 4.5699 | 10.23% | 10.88% | 7.354% | 1.1139 | 1.1221 | 1.0794
2010-09-28 | 22 | 32.0578 | 12.013 | 44.0708 | 3.3786 | 0.76558 | 0.32763 | 4.4718 | 10.15% | 10.8% | 7.296% | 1.1129 | 1.121 | 1.0787
2010-09-28 | 23 | 31.2099 | 11.7283 | 42.9383 | 3.2072 | 0.76558 | 0.31921 | 4.292 | 9.996% | 10.64% | 7.187% | 1.1111 | 1.119 | 1.0774
2010-09-28 | 24 | 30.5637 | 11.3623 | 41.9259 | 3.0577 | 0.76558 | 0.31168 | 4.135 | 9.863% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-09-28 | 25 | 29.6583 | 10.9114 | 40.5697 | 2.8631 | 0.76558 | 0.3016 | 3.9303 | 9.688% | 10.31% | 6.965% | 1.1073 | 1.1149 | 1.0749
2010-09-28 | 26 | 28.7971 | 10.2391 | 39.0363 | 2.6508 | 0.76558 | 0.2902 | 3.7065 | 9.495% | 10.1% | 6.827% | 1.1049 | 1.1124 | 1.0733
2010-09-28 | 27 | 28.2516 | 10.3374 | 38.589 | 2.5904 | 0.76558 | 0.28688 | 3.6428 | 9.44% | 10.04% | 6.787% | 1.1042 | 1.1117 | 1.0728
2010-09-28 | 28 | 27.4107 | 10.2049 | 37.6156 | 2.4613 | 0.76558 | 0.27964 | 3.5066 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-09-28 | 29 | 26.4688 | 9.7616 | 36.2304 | 2.2834 | 0.76558 | 0.26934 | 3.3183 | 9.159% | 9.745% | 6.585% | 1.1008 | 1.108 | 1.0705
2010-09-28 | 30 | 25.6579 | 9.4001 | 35.058 | 2.138 | 0.76558 | 0.26063 | 3.1642 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-09-28 | 31 | 26.2055 | 9.1806 | 35.3861 | 2.1782 | 0.76558 | 0.26306 | 3.2069 | 9.062% | 9.642% | 6.516% | 1.0997 | 1.1067 | 1.0697
2010-09-28 | 32 | 25.7882 | 9.0945 | 34.8827 | 2.1167 | 0.76558 | 0.25932 | 3.1416 | 9.006% | 9.583% | 6.475% | 1.099 | 1.106 | 1.0692
2010-09-28 | 33 | 25.0033 | 9.2937 | 34.297 | 2.0462 | 0.76558 | 0.25497 | 3.0667 | 8.942% | 9.514% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-09-28 | 34 | 24.9387 | 9.1876 | 34.1262 | 2.0259 | 0.76558 | 0.2537 | 3.0451 | 8.923% | 9.494% | 6.416% | 1.098 | 1.1049 | 1.0686
2010-09-28 | 35 | 25.0022 | 9.5841 | 34.5863 | 2.0809 | 0.76558 | 0.25712 | 3.1036 | 8.973% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-09-28 | 36 | 26.2067 | 10.5859 | 36.7926 | 2.3548 | 0.76558 | 0.27352 | 3.3939 | 9.224% | 9.815% | 6.632% | 1.1016 | 1.1088 | 1.071
2010-09-28 | 37 | 27.1132 | 11.1148 | 38.228 | 2.5421 | 0.76558 | 0.28419 | 3.5919 | 9.396% | 9.997% | 6.756% | 1.1037 | 1.1111 | 1.0725
2010-09-28 | 38 | 27.3967 | 11.6539 | 39.0507 | 2.6527 | 0.76558 | 0.29031 | 3.7086 | 9.497% | 10.1% | 6.828% | 1.1049 | 1.1124 | 1.0733
2010-09-28 | 39 | 27.8053 | 11.8346 | 39.6399 | 2.7334 | 0.76558 | 0.29469 | 3.7936 | 9.57% | 10.18% | 6.881% | 1.1058 | 1.1134 | 1.0739
2010-09-28 | 40 | 29.5941 | 11.7155 | 41.3096 | 2.9685 | 0.76558 | 0.3071 | 4.0412 | 9.783% | 10.41% | 7.034% | 1.1084 | 1.1162 | 1.0757
2010-09-28 | 41 | 31.5616 | 11.5334 | 43.095 | 3.2306 | 0.76558 | 0.32037 | 4.3166 | 10.02% | 10.66% | 7.202% | 1.1113 | 1.1193 | 1.0776
2010-09-28 | 42 | 31.5765 | 10.9782 | 42.5548 | 3.1502 | 0.76558 | 0.31636 | 4.2321 | 9.945% | 10.58% | 7.15% | 1.1104 | 1.1183 | 1.077
2010-09-28 | 43 | 30.3263 | 10.4266 | 40.7529 | 2.889 | 0.76558 | 0.30296 | 3.9576 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2010-09-28 | 44 | 29.0773 | 9.698 | 38.7753 | 2.6154 | 0.76558 | 0.28826 | 3.6693 | 9.463% | 10.07% | 6.804% | 1.1045 | 1.112 | 1.073
2010-09-28 | 45 | 26.7643 | 8.6123 | 35.3767 | 2.177 | 0.76558 | 0.26299 | 3.2056 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-09-28 | 46 | 24.2081 | 7.8592 | 32.0672 | 1.7888 | 0.76558 | 0.23839 | 2.7928 | 8.709% | 9.266% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-09-28 | 47 | 22.7281 | 7.6025 | 30.3307 | 1.6003 | 0.76558 | 0.22548 | 2.5913 | 8.544% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-09-28 | 48 | 22.3002 | 7.7119 | 30.0121 | 1.5669 | 0.76558 | 0.22311 | 2.5555 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-09-29 | 1 | 20.0575 | 6.8024 | 26.8599 | 1.255 | 0.76558 | 0.19968 | 2.2203 | 8.266% | 8.795% | 5.943% | 1.0901 | 1.0964 | 1.0632
2010-09-29 | 2 | 18.8048 | 6.2253 | 25.0302 | 1.0898 | 0.76558 | 0.18608 | 2.0415 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-09-29 | 3 | 17.9152 | 5.9342 | 23.8493 | 0.98944 | 0.76558 | 0.1773 | 1.9323 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-09-29 | 4 | 17.1387 | 5.7012 | 22.8398 | 0.90745 | 0.76558 | 0.16979 | 1.8428 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-09-29 | 5 | 16.797 | 5.6248 | 22.4218 | 0.87453 | 0.76558 | 0.16669 | 1.8068 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-09-29 | 6 | 16.4669 | 5.4481 | 21.9149 | 0.83544 | 0.76558 | 0.16292 | 1.7639 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-09-29 | 7 | 16.1071 | 5.5326 | 21.6397 | 0.81459 | 0.76558 | 0.16087 | 1.741 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-29 | 8 | 15.9351 | 5.4269 | 21.3621 | 0.79382 | 0.76558 | 0.15881 | 1.7182 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-29 | 9 | 15.9774 | 5.6514 | 21.6288 | 0.81376 | 0.76558 | 0.16079 | 1.7401 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-09-29 | 10 | 16.3225 | 5.7325 | 22.055 | 0.84615 | 0.76558 | 0.16396 | 1.7757 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-09-29 | 11 | 16.9534 | 5.9309 | 22.8844 | 0.91099 | 0.76558 | 0.17013 | 1.8467 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-09-29 | 12 | 17.6251 | 6.174 | 23.7991 | 0.98527 | 0.76558 | 0.17693 | 1.9278 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-09-29 | 13 | 19.0184 | 6.8984 | 25.9169 | 1.1684 | 0.76558 | 0.19267 | 2.1267 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-09-29 | 14 | 21.3035 | 7.8596 | 29.1631 | 1.4795 | 0.76558 | 0.2168 | 2.4618 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-09-29 | 15 | 24.8814 | 9.3932 | 34.2746 | 2.0435 | 0.76558 | 0.2548 | 3.0639 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-09-29 | 16 | 27.5119 | 10.605 | 38.1169 | 2.5274 | 0.76558 | 0.28337 | 3.5763 | 9.383% | 9.983% | 6.746% | 1.1035 | 1.1109 | 1.0723
2010-09-29 | 17 | 29.8106 | 11.7888 | 41.5994 | 3.0103 | 0.76558 | 0.30925 | 4.0851 | 9.82% | 10.45% | 7.061% | 1.1089 | 1.1167 | 1.076
2010-09-29 | 18 | 31.2579 | 12.1339 | 43.3918 | 3.2753 | 0.76558 | 0.32258 | 4.3634 | 10.06% | 10.7% | 7.23% | 1.1118 | 1.1198 | 1.0779
2010-09-29 | 19 | 31.2151 | 12.1108 | 43.3259 | 3.2654 | 0.76558 | 0.32209 | 4.353 | 10.05% | 10.69% | 7.224% | 1.1117 | 1.1197 | 1.0779
2010-09-29 | 20 | 29.8461 | 11.8264 | 41.6725 | 3.0209 | 0.76558 | 0.3098 | 4.0963 | 9.83% | 10.46% | 7.068% | 1.109 | 1.1168 | 1.0761
2010-09-29 | 21 | 29.9891 | 11.437 | 41.4261 | 2.9853 | 0.76558 | 0.30797 | 4.0588 | 9.798% | 10.42% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-09-29 | 22 | 29.4175 | 11.1099 | 40.5273 | 2.8571 | 0.76558 | 0.30129 | 3.924 | 9.682% | 10.3% | 6.962% | 1.1072 | 1.1149 | 1.0748
2010-09-29 | 23 | 28.1288 | 10.5848 | 38.7136 | 2.6071 | 0.76558 | 0.2878 | 3.6605 | 9.455% | 10.06% | 6.798% | 1.1044 | 1.1119 | 1.0729
2010-09-29 | 24 | 27.2933 | 10.3741 | 37.6674 | 2.4681 | 0.76558 | 0.28002 | 3.5137 | 9.328% | 9.925% | 6.707% | 1.1029 | 1.1102 | 1.0719
2010-09-29 | 25 | 26.2866 | 10.032 | 36.3186 | 2.2945 | 0.76558 | 0.27 | 3.3301 | 9.169% | 9.756% | 6.593% | 1.1009 | 1.1081 | 1.0706
2010-09-29 | 26 | 25.3951 | 9.4636 | 34.8587 | 2.1138 | 0.76558 | 0.25914 | 3.1385 | 9.003% | 9.58% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-09-29 | 27 | 25.3537 | 9.5288 | 34.8825 | 2.1167 | 0.76558 | 0.25932 | 3.1416 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2010-09-29 | 28 | 24.9305 | 9.3946 | 34.3251 | 2.0495 | 0.76558 | 0.25518 | 3.0703 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-09-29 | 29 | 24.4633 | 8.7807 | 33.244 | 1.9225 | 0.76558 | 0.24714 | 2.9352 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-09-29 | 30 | 23.7351 | 8.7064 | 32.4415 | 1.8308 | 0.76558 | 0.24117 | 2.8375 | 8.747% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2010-09-29 | 31 | 24.1334 | 8.8594 | 32.9928 | 1.8935 | 0.76558 | 0.24527 | 2.9044 | 8.803% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-09-29 | 32 | 24.0002 | 8.9438 | 32.944 | 1.8879 | 0.76558 | 0.24491 | 2.8984 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-09-29 | 33 | 23.835 | 8.9595 | 32.7945 | 1.8708 | 0.76558 | 0.2438 | 2.8802 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-09-29 | 34 | 23.7822 | 8.9852 | 32.7673 | 1.8677 | 0.76558 | 0.2436 | 2.8769 | 8.78% | 9.342% | 6.313% | 1.0962 | 1.103 | 1.0674
2010-09-29 | 35 | 23.8272 | 9.5372 | 33.3644 | 1.9364 | 0.76558 | 0.24803 | 2.95 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-09-29 | 36 | 24.6022 | 10.0713 | 34.6735 | 2.0914 | 0.76558 | 0.25777 | 3.1147 | 8.983% | 9.558% | 6.459% | 1.0987 | 1.1057 | 1.069
2010-09-29 | 37 | 25.7609 | 10.2859 | 36.0469 | 2.2603 | 0.76558 | 0.26798 | 3.2939 | 9.138% | 9.723% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-09-29 | 38 | 26.7675 | 10.2968 | 37.0643 | 2.3897 | 0.76558 | 0.27554 | 3.4308 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-09-29 | 39 | 27.3324 | 10.0954 | 37.4279 | 2.4368 | 0.76558 | 0.27824 | 3.4806 | 9.3% | 9.895% | 6.686% | 1.1025 | 1.1098 | 1.0717
2010-09-29 | 40 | 28.7429 | 10.1946 | 38.9375 | 2.6374 | 0.76558 | 0.28947 | 3.6924 | 9.483% | 10.09% | 6.818% | 1.1048 | 1.1122 | 1.0732
2010-09-29 | 41 | 30.5676 | 10.502 | 41.0696 | 2.9341 | 0.76558 | 0.30532 | 4.005 | 9.752% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-09-29 | 42 | 30.8273 | 10.3917 | 41.219 | 2.9555 | 0.76558 | 0.30643 | 4.0275 | 9.771% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2010-09-29 | 43 | 29.8806 | 9.8129 | 39.6935 | 2.7408 | 0.76558 | 0.29509 | 3.8014 | 9.577% | 10.19% | 6.886% | 1.1059 | 1.1135 | 1.074
2010-09-29 | 44 | 28.7593 | 9.3064 | 38.0657 | 2.5206 | 0.76558 | 0.28299 | 3.5692 | 9.376% | 9.976% | 6.742% | 1.1035 | 1.1108 | 1.0723
2010-09-29 | 45 | 26.2733 | 8.3641 | 34.6374 | 2.087 | 0.76558 | 0.2575 | 3.1101 | 8.979% | 9.554% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-09-29 | 46 | 23.7466 | 7.516 | 31.2627 | 1.7001 | 0.76558 | 0.23241 | 2.6981 | 8.631% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-09-29 | 47 | 22.4237 | 7.1355 | 29.5592 | 1.5199 | 0.76558 | 0.21975 | 2.5052 | 8.475% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-09-29 | 48 | 22.1093 | 7.3544 | 29.4637 | 1.5101 | 0.76558 | 0.21904 | 2.4947 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-09-30 | 1 | 20.3706 | 6.6281 | 26.9987 | 1.268 | 0.76558 | 0.20071 | 2.2343 | 8.276% | 8.805% | 5.95% | 1.0902 | 1.0966 | 1.0633
2010-09-30 | 2 | 18.9474 | 5.8634 | 24.8108 | 1.0708 | 0.76558 | 0.18445 | 2.0208 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-09-30 | 3 | 17.971 | 5.6123 | 23.5833 | 0.96748 | 0.76558 | 0.17532 | 1.9084 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-09-30 | 4 | 17.3399 | 5.4498 | 22.7897 | 0.90347 | 0.76558 | 0.16942 | 1.8385 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-09-30 | 5 | 16.6356 | 5.3667 | 22.0023 | 0.84211 | 0.76558 | 0.16357 | 1.7713 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-09-30 | 6 | 16.1759 | 5.2802 | 21.4561 | 0.80082 | 0.76558 | 0.15951 | 1.7259 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-09-30 | 7 | 15.846 | 5.2052 | 21.0512 | 0.77089 | 0.76558 | 0.1565 | 1.693 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-30 | 8 | 15.9176 | 5.2417 | 21.1593 | 0.77882 | 0.76558 | 0.1573 | 1.7017 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-09-30 | 9 | 16.0619 | 5.2377 | 21.2996 | 0.78918 | 0.76558 | 0.15834 | 1.7131 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-09-30 | 10 | 16.4941 | 5.3051 | 21.7993 | 0.82664 | 0.76558 | 0.16206 | 1.7543 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-09-30 | 11 | 16.8235 | 5.5509 | 22.3744 | 0.87084 | 0.76558 | 0.16633 | 1.8027 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-09-30 | 12 | 17.4695 | 5.8732 | 23.3426 | 0.94784 | 0.76558 | 0.17353 | 1.8869 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-09-30 | 13 | 18.8638 | 6.5027 | 25.3665 | 1.1193 | 0.76558 | 0.18858 | 2.0735 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2010-09-30 | 14 | 21.1769 | 7.5015 | 28.6785 | 1.4307 | 0.76558 | 0.2132 | 2.4095 | 8.402% | 8.939% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-09-30 | 15 | 24.6699 | 9.026 | 33.6959 | 1.9751 | 0.76558 | 0.2505 | 2.9912 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-09-30 | 16 | 27.1612 | 10.1377 | 37.2989 | 2.4201 | 0.76558 | 0.27728 | 3.4629 | 9.284% | 9.878% | 6.675% | 1.1023 | 1.1096 | 1.0715
2010-09-30 | 17 | 29.2348 | 11.1421 | 40.3769 | 2.836 | 0.76558 | 0.30017 | 3.9017 | 9.663% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2010-09-30 | 18 | 30.4668 | 11.4449 | 41.9117 | 3.0557 | 0.76558 | 0.31158 | 4.1328 | 9.861% | 10.49% | 7.09% | 1.1094 | 1.1172 | 1.0763
2010-09-30 | 19 | 30.7986 | 11.4518 | 42.2504 | 3.1053 | 0.76558 | 0.31409 | 4.1849 | 9.905% | 10.54% | 7.122% | 1.1099 | 1.1178 | 1.0767
2010-09-30 | 20 | 30.1669 | 10.9309 | 41.0978 | 2.9381 | 0.76558 | 0.30553 | 4.0092 | 9.755% | 10.38% | 7.014% | 1.1081 | 1.1158 | 1.0754
2010-09-30 | 21 | 30.2402 | 10.5921 | 40.8323 | 2.9003 | 0.76558 | 0.30355 | 3.9694 | 9.721% | 10.34% | 6.99% | 1.1077 | 1.1154 | 1.0751
2010-09-30 | 22 | 29.6674 | 10.218 | 39.8854 | 2.7673 | 0.76558 | 0.29651 | 3.8294 | 9.601% | 10.22% | 6.903% | 1.1062 | 1.1138 | 1.0742
2010-09-30 | 23 | 28.2013 | 9.8105 | 38.0118 | 2.5135 | 0.76558 | 0.28258 | 3.5616 | 9.37% | 9.969% | 6.737% | 1.1034 | 1.1107 | 1.0722
2010-09-30 | 24 | 26.8765 | 9.6861 | 36.5627 | 2.3255 | 0.76558 | 0.27181 | 3.3629 | 9.198% | 9.786% | 6.613% | 1.1013 | 1.1085 | 1.0708
2010-09-30 | 25 | 25.5922 | 9.4526 | 35.0448 | 2.1364 | 0.76558 | 0.26053 | 3.1625 | 9.024% | 9.602% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-09-30 | 26 | 24.6054 | 8.8831 | 33.4885 | 1.9509 | 0.76558 | 0.24896 | 2.9654 | 8.855% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2010-09-30 | 27 | 24.3994 | 9.0437 | 33.4431 | 1.9456 | 0.76558 | 0.24862 | 2.9598 | 8.85% | 9.417% | 6.363% | 1.0971 | 1.104 | 1.068
2010-09-30 | 28 | 24.4111 | 9.0219 | 33.433 | 1.9444 | 0.76558 | 0.24854 | 2.9585 | 8.849% | 9.415% | 6.363% | 1.0971 | 1.1039 | 1.0679
2010-09-30 | 29 | 23.9016 | 8.7808 | 32.6824 | 1.8581 | 0.76558 | 0.24297 | 2.8666 | 8.771% | 9.332% | 6.306% | 1.0961 | 1.1029 | 1.0673
2010-09-30 | 30 | 23.7344 | 8.5925 | 32.3269 | 1.8179 | 0.76558 | 0.24032 | 2.8238 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2010-09-30 | 31 | 24.4533 | 8.5761 | 33.0295 | 1.8977 | 0.76558 | 0.24555 | 2.9089 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-09-30 | 32 | 24.2049 | 8.541 | 32.746 | 1.8653 | 0.76558 | 0.24344 | 2.8743 | 8.778% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-09-30 | 33 | 23.5365 | 8.8054 | 32.3418 | 1.8196 | 0.76558 | 0.24043 | 2.8256 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-09-30 | 34 | 23.4491 | 8.9735 | 32.4227 | 1.8287 | 0.76558 | 0.24103 | 2.8353 | 8.745% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-09-30 | 35 | 23.8066 | 9.4113 | 33.2178 | 1.9195 | 0.76558 | 0.24695 | 2.932 | 8.827% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-09-30 | 36 | 24.7947 | 10.0021 | 34.7968 | 2.1063 | 0.76558 | 0.25868 | 3.1305 | 8.997% | 9.572% | 6.469% | 1.0989 | 1.1059 | 1.0692
2010-09-30 | 37 | 26.0279 | 10.3729 | 36.4008 | 2.3049 | 0.76558 | 0.27061 | 3.3411 | 9.179% | 9.766% | 6.599% | 1.1011 | 1.1082 | 1.0707
2010-09-30 | 38 | 27.2224 | 10.4478 | 37.6702 | 2.4685 | 0.76558 | 0.28004 | 3.5141 | 9.329% | 9.926% | 6.707% | 1.1029 | 1.1102 | 1.0719
2010-09-30 | 39 | 27.6829 | 10.328 | 38.0109 | 2.5133 | 0.76558 | 0.28258 | 3.5615 | 9.37% | 9.969% | 6.737% | 1.1034 | 1.1107 | 1.0722
2010-09-30 | 40 | 28.3 | 10.3694 | 38.6694 | 2.6012 | 0.76558 | 0.28747 | 3.6542 | 9.45% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-09-30 | 41 | 29.6641 | 10.6356 | 40.2998 | 2.8251 | 0.76558 | 0.29959 | 3.8903 | 9.653% | 10.27% | 6.941% | 1.1068 | 1.1145 | 1.0746
2010-09-30 | 42 | 29.8229 | 10.451 | 40.2738 | 2.8215 | 0.76558 | 0.2994 | 3.8865 | 9.65% | 10.27% | 6.938% | 1.1068 | 1.1144 | 1.0746
2010-09-30 | 43 | 28.9884 | 9.9438 | 38.9322 | 2.6366 | 0.76558 | 0.28943 | 3.6916 | 9.482% | 10.09% | 6.818% | 1.1048 | 1.1122 | 1.0732
2010-09-30 | 44 | 27.7824 | 9.3646 | 37.147 | 2.4004 | 0.76558 | 0.27616 | 3.4421 | 9.266% | 9.859% | 6.662% | 1.1021 | 1.1094 | 1.0714
2010-09-30 | 45 | 25.5563 | 8.7154 | 34.2717 | 2.0432 | 0.76558 | 0.25478 | 3.0635 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-09-30 | 46 | 23.3301 | 7.8428 | 31.1729 | 1.6904 | 0.76558 | 0.23174 | 2.6877 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2010-09-30 | 47 | 22.2252 | 7.4561 | 29.6813 | 1.5325 | 0.76558 | 0.22065 | 2.5187 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0993 | 1.065
2010-09-30 | 48 | 21.735 | 7.5557 | 29.2908 | 1.4924 | 0.76558 | 0.21775 | 2.4758 | 8.452% | 8.993% | 6.077% | 1.0923 | 1.0988 | 1.0647
2010-10-01 | 1 | 19.798 | 6.6346 | 26.4326 | 1.2154 | 0.76558 | 0.1965 | 2.1775 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-10-01 | 2 | 18.0462 | 6.0435 | 24.0898 | 1.0095 | 0.76558 | 0.17909 | 1.9541 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-10-01 | 3 | 17.1842 | 5.7866 | 22.9709 | 0.91789 | 0.76558 | 0.17077 | 1.8542 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-10-01 | 4 | 16.6086 | 5.5358 | 22.1444 | 0.85302 | 0.76558 | 0.16462 | 1.7832 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-01 | 5 | 16.5227 | 5.4576 | 21.9803 | 0.84043 | 0.76558 | 0.1634 | 1.7694 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-01 | 6 | 16.4668 | 5.3339 | 21.8008 | 0.82676 | 0.76558 | 0.16207 | 1.7544 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-01 | 7 | 16.0795 | 5.2447 | 21.3242 | 0.791 | 0.76558 | 0.15853 | 1.7151 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-01 | 8 | 16.1214 | 5.3633 | 21.4847 | 0.80296 | 0.76558 | 0.15972 | 1.7283 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-01 | 9 | 16.1936 | 5.5034 | 21.697 | 0.8189 | 0.76558 | 0.1613 | 1.7458 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-01 | 10 | 16.3257 | 5.5529 | 21.8786 | 0.83267 | 0.76558 | 0.16265 | 1.7609 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-01 | 11 | 16.8895 | 5.7429 | 22.6323 | 0.89103 | 0.76558 | 0.16825 | 1.8249 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-01 | 12 | 17.7624 | 5.3651 | 23.1275 | 0.93044 | 0.76558 | 0.17193 | 1.868 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-10-01 | 13 | 19.4688 | 6.0254 | 25.4942 | 1.1306 | 0.76558 | 0.18953 | 2.0857 | 8.181% | 8.705% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-10-01 | 14 | 22.0216 | 8.3359 | 30.3575 | 1.6031 | 0.76558 | 0.22568 | 2.5944 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2010-10-01 | 15 | 25.6828 | 9.8555 | 35.5384 | 2.197 | 0.76558 | 0.2642 | 3.2268 | 9.08% | 9.661% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-10-01 | 16 | 28.1126 | 11.075 | 39.1876 | 2.6714 | 0.76558 | 0.29133 | 3.7283 | 9.514% | 10.12% | 6.84% | 1.1051 | 1.1126 | 1.0734
2010-10-01 | 17 | 29.7145 | 11.7137 | 41.4282 | 2.9856 | 0.76558 | 0.30798 | 4.0591 | 9.798% | 10.43% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-10-01 | 18 | 30.6186 | 11.7927 | 42.4113 | 3.1289 | 0.76558 | 0.31529 | 4.2098 | 9.926% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-10-01 | 19 | 30.9183 | 11.5943 | 42.5126 | 3.1439 | 0.76558 | 0.31604 | 4.2255 | 9.939% | 10.58% | 7.146% | 1.1104 | 1.1183 | 1.077
2010-10-01 | 20 | 30.0711 | 11.5258 | 41.5969 | 3.0099 | 0.76558 | 0.30924 | 4.0847 | 9.82% | 10.45% | 7.06% | 1.1089 | 1.1167 | 1.076
2010-10-01 | 21 | 30.2974 | 11.2553 | 41.5527 | 3.0035 | 0.76558 | 0.30891 | 4.078 | 9.814% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-10-01 | 22 | 29.5494 | 11.1543 | 40.7037 | 2.8821 | 0.76558 | 0.3026 | 3.9502 | 9.705% | 10.33% | 6.978% | 1.1075 | 1.1151 | 1.075
2010-10-01 | 23 | 28.1335 | 10.831 | 38.9645 | 2.641 | 0.76558 | 0.28967 | 3.6963 | 9.486% | 10.09% | 6.821% | 1.1048 | 1.1123 | 1.0732
2010-10-01 | 24 | 26.81 | 10.1119 | 36.922 | 2.3714 | 0.76558 | 0.27448 | 3.4115 | 9.24% | 9.831% | 6.643% | 1.1018 | 1.109 | 1.0712
2010-10-01 | 25 | 25.4992 | 9.7516 | 35.2507 | 2.1616 | 0.76558 | 0.26206 | 3.1892 | 9.047% | 9.626% | 6.505% | 1.0995 | 1.1065 | 1.0696
2010-10-01 | 26 | 24.4662 | 9.1252 | 33.5914 | 1.9629 | 0.76558 | 0.24972 | 2.9782 | 8.866% | 9.433% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-10-01 | 27 | 24.231 | 9.2763 | 33.5073 | 1.9531 | 0.76558 | 0.2491 | 2.9677 | 8.857% | 9.424% | 6.368% | 1.0972 | 1.104 | 1.068
2010-10-01 | 28 | 24.1706 | 9.3293 | 33.5 | 1.9522 | 0.76558 | 0.24904 | 2.9668 | 8.856% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2010-10-01 | 29 | 23.5368 | 8.8711 | 32.4079 | 1.827 | 0.76558 | 0.24092 | 2.8335 | 8.743% | 9.303% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-10-01 | 30 | 23.1526 | 8.5762 | 31.7288 | 1.7512 | 0.76558 | 0.23588 | 2.7527 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-10-01 | 31 | 24.144 | 8.533 | 32.677 | 1.8575 | 0.76558 | 0.24292 | 2.866 | 8.771% | 9.332% | 6.306% | 1.0961 | 1.1029 | 1.0673
2010-10-01 | 32 | 24.0391 | 8.4178 | 32.4569 | 1.8325 | 0.76558 | 0.24129 | 2.8394 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-10-01 | 33 | 23.3809 | 8.7822 | 32.1632 | 1.7995 | 0.76558 | 0.2391 | 2.8042 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-10-01 | 34 | 23.145 | 8.7672 | 31.9122 | 1.7715 | 0.76558 | 0.23724 | 2.7743 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-10-01 | 35 | 23.2127 | 9.241 | 32.4537 | 1.8322 | 0.76558 | 0.24126 | 2.839 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-10-01 | 36 | 24.1749 | 9.8117 | 33.9866 | 2.0093 | 0.76558 | 0.25266 | 3.0276 | 8.908% | 9.478% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-10-01 | 37 | 25.6986 | 10.009 | 35.7076 | 2.218 | 0.76558 | 0.26545 | 3.249 | 9.099% | 9.681% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-10-01 | 38 | 26.793 | 10.0377 | 36.8307 | 2.3597 | 0.76558 | 0.2738 | 3.3991 | 9.229% | 9.82% | 6.636% | 1.1017 | 1.1089 | 1.0711
2010-10-01 | 39 | 27.4663 | 9.8528 | 37.3191 | 2.4227 | 0.76558 | 0.27743 | 3.4657 | 9.287% | 9.881% | 6.677% | 1.1024 | 1.1096 | 1.0715
2010-10-01 | 40 | 28.3628 | 9.8088 | 38.1715 | 2.5346 | 0.76558 | 0.28377 | 3.584 | 9.389% | 9.99% | 6.751% | 1.1036 | 1.111 | 1.0724
2010-10-01 | 41 | 29.6852 | 10.1804 | 39.8656 | 2.7646 | 0.76558 | 0.29637 | 3.8265 | 9.599% | 10.21% | 6.901% | 1.1062 | 1.1137 | 1.0741
2010-10-01 | 42 | 29.8111 | 10.2175 | 40.0286 | 2.7872 | 0.76558 | 0.29758 | 3.8504 | 9.619% | 10.23% | 6.916% | 1.1064 | 1.114 | 1.0743
2010-10-01 | 43 | 28.4467 | 9.7763 | 38.223 | 2.5415 | 0.76558 | 0.28415 | 3.5912 | 9.395% | 9.997% | 6.755% | 1.1037 | 1.1111 | 1.0724
2010-10-01 | 44 | 27.163 | 9.231 | 36.394 | 2.3041 | 0.76558 | 0.27056 | 3.3402 | 9.178% | 9.765% | 6.599% | 1.1011 | 1.1082 | 1.0707
2010-10-01 | 45 | 25.1604 | 8.4428 | 33.6032 | 1.9642 | 0.76558 | 0.24981 | 2.9796 | 8.867% | 9.435% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-10-01 | 46 | 22.7781 | 7.6439 | 30.422 | 1.6099 | 0.76558 | 0.22616 | 2.6017 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-10-01 | 47 | 21.4128 | 7.4679 | 28.8806 | 1.4509 | 0.76558 | 0.2147 | 2.4312 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-10-01 | 48 | 21.0212 | 7.6552 | 28.6765 | 1.4305 | 0.76558 | 0.21318 | 2.4093 | 8.402% | 8.939% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-10-02 | 1 | 19.2415 | 6.7403 | 25.9817 | 1.1743 | 0.76558 | 0.19315 | 2.133 | 8.21% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-10-02 | 2 | 17.8474 | 6.2474 | 24.0949 | 1.0099 | 0.76558 | 0.17912 | 1.9546 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-10-02 | 3 | 16.7135 | 5.8712 | 22.5847 | 0.88729 | 0.76558 | 0.1679 | 1.8208 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-02 | 4 | 16.1818 | 5.7823 | 21.9641 | 0.83919 | 0.76558 | 0.16328 | 1.7681 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-02 | 5 | 15.7652 | 5.6823 | 21.4476 | 0.80019 | 0.76558 | 0.15944 | 1.7252 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 6 | 15.6652 | 5.4428 | 21.108 | 0.77505 | 0.76558 | 0.15692 | 1.6975 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 7 | 15.349 | 5.4407 | 20.7897 | 0.75185 | 0.76558 | 0.15455 | 1.672 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 8 | 15.3794 | 5.4346 | 20.814 | 0.75361 | 0.76558 | 0.15473 | 1.6739 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 9 | 15.5124 | 5.5152 | 21.0276 | 0.76916 | 0.76558 | 0.15632 | 1.6911 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 10 | 15.4095 | 5.5561 | 20.9656 | 0.76463 | 0.76558 | 0.15586 | 1.6861 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 11 | 15.6179 | 5.6531 | 21.271 | 0.78707 | 0.76558 | 0.15813 | 1.7108 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-02 | 12 | 16.4409 | 5.9191 | 22.36 | 0.86972 | 0.76558 | 0.16623 | 1.8015 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-02 | 13 | 18.0167 | 6.7138 | 24.7305 | 1.0639 | 0.76558 | 0.18385 | 2.0133 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-10-02 | 14 | 20.4905 | 7.8936 | 28.3841 | 1.4015 | 0.76558 | 0.21101 | 2.3781 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-10-02 | 15 | 23.5614 | 9.3475 | 32.9089 | 1.8839 | 0.76558 | 0.24465 | 2.8941 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2010-10-02 | 16 | 26.0477 | 9.9986 | 36.0464 | 2.2603 | 0.76558 | 0.26797 | 3.2938 | 9.138% | 9.723% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-10-02 | 17 | 28.018 | 10.4677 | 38.4857 | 2.5765 | 0.76558 | 0.28611 | 3.6282 | 9.427% | 10.03% | 6.778% | 1.1041 | 1.1115 | 1.0727
2010-10-02 | 18 | 28.5212 | 10.7611 | 39.2823 | 2.6843 | 0.76558 | 0.29203 | 3.7419 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-10-02 | 19 | 28.7949 | 10.765 | 39.5599 | 2.7224 | 0.76558 | 0.29409 | 3.782 | 9.56% | 10.17% | 6.874% | 1.1057 | 1.1132 | 1.0738
2010-10-02 | 20 | 28.3572 | 10.4062 | 38.7635 | 2.6138 | 0.76558 | 0.28817 | 3.6676 | 9.461% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2010-10-02 | 21 | 28.3594 | 10.0849 | 38.4444 | 2.571 | 0.76558 | 0.2858 | 3.6224 | 9.422% | 10.03% | 6.775% | 1.104 | 1.1114 | 1.0727
2010-10-02 | 22 | 27.9869 | 9.9433 | 37.9303 | 2.5027 | 0.76558 | 0.28198 | 3.5502 | 9.36% | 9.959% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-10-02 | 23 | 26.7751 | 9.6996 | 36.4747 | 2.3143 | 0.76558 | 0.27116 | 3.351 | 9.187% | 9.775% | 6.606% | 1.1012 | 1.1083 | 1.0707
2010-10-02 | 24 | 25.4535 | 9.5054 | 34.959 | 2.1259 | 0.76558 | 0.25989 | 3.1514 | 9.015% | 9.592% | 6.481% | 1.0991 | 1.1061 | 1.0693
2010-10-02 | 25 | 24.4091 | 9.4095 | 33.8185 | 1.9895 | 0.76558 | 0.25141 | 3.0065 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-10-02 | 26 | 23.7597 | 8.9961 | 32.7558 | 1.8664 | 0.76558 | 0.24351 | 2.8755 | 8.779% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-10-02 | 27 | 23.7626 | 9.2036 | 32.9662 | 1.8905 | 0.76558 | 0.24507 | 2.9011 | 8.8% | 9.364% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-10-02 | 28 | 23.6518 | 9.2089 | 32.8608 | 1.8784 | 0.76558 | 0.24429 | 2.8883 | 8.789% | 9.352% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-10-02 | 29 | 23.4227 | 8.786 | 32.2087 | 1.8046 | 0.76558 | 0.23944 | 2.8096 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-10-02 | 30 | 22.7182 | 8.7052 | 31.4234 | 1.7177 | 0.76558 | 0.23361 | 2.7169 | 8.646% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-10-02 | 31 | 23.6397 | 8.7602 | 32.3999 | 1.8261 | 0.76558 | 0.24086 | 2.8325 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-10-02 | 32 | 23.719 | 8.75 | 32.469 | 1.8339 | 0.76558 | 0.24138 | 2.8408 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1026 | 1.0671
2010-10-02 | 33 | 23.7693 | 8.7704 | 32.5396 | 1.8419 | 0.76558 | 0.2419 | 2.8494 | 8.757% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-10-02 | 34 | 24.0555 | 8.8239 | 32.8794 | 1.8805 | 0.76558 | 0.24443 | 2.8906 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-10-02 | 35 | 24.3416 | 9.1162 | 33.4578 | 1.9473 | 0.76558 | 0.24873 | 2.9616 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2010-10-02 | 36 | 25.3274 | 9.426 | 34.7534 | 2.101 | 0.76558 | 0.25836 | 3.125 | 8.992% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-10-02 | 37 | 26.8446 | 9.6164 | 36.461 | 2.3126 | 0.76558 | 0.27106 | 3.3492 | 9.186% | 9.774% | 6.604% | 1.1011 | 1.1083 | 1.0707
2010-10-02 | 38 | 27.9258 | 9.7029 | 37.6288 | 2.4631 | 0.76558 | 0.27974 | 3.5084 | 9.324% | 9.92% | 6.704% | 1.1028 | 1.1101 | 1.0719
2010-10-02 | 39 | 28.5393 | 9.6724 | 38.2118 | 2.54 | 0.76558 | 0.28407 | 3.5896 | 9.394% | 9.995% | 6.754% | 1.1037 | 1.1111 | 1.0724
2010-10-02 | 40 | 29.4009 | 9.8822 | 39.2831 | 2.6844 | 0.76558 | 0.29204 | 3.742 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-10-02 | 41 | 30.2063 | 10.1275 | 40.3338 | 2.8299 | 0.76558 | 0.29985 | 3.8953 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-10-02 | 42 | 31.0097 | 10.1504 | 41.16 | 2.947 | 0.76558 | 0.30599 | 4.0186 | 9.763% | 10.39% | 7.02% | 1.1082 | 1.1159 | 1.0755
2010-10-02 | 43 | 30.0743 | 9.7598 | 39.8342 | 2.7602 | 0.76558 | 0.29613 | 3.8219 | 9.595% | 10.21% | 6.899% | 1.1061 | 1.1137 | 1.0741
2010-10-02 | 44 | 28.8629 | 9.3769 | 38.2398 | 2.5437 | 0.76558 | 0.28428 | 3.5936 | 9.397% | 9.999% | 6.757% | 1.1037 | 1.1111 | 1.0725
2010-10-02 | 45 | 26.8154 | 8.5393 | 35.3548 | 2.1744 | 0.76558 | 0.26283 | 3.2028 | 9.059% | 9.639% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-10-02 | 46 | 24.6839 | 7.8006 | 32.4845 | 1.8356 | 0.76558 | 0.24149 | 2.8427 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-10-02 | 47 | 23.556 | 7.6493 | 31.2053 | 1.6939 | 0.76558 | 0.23198 | 2.6915 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-10-02 | 48 | 23.5238 | 7.7582 | 31.282 | 1.7023 | 0.76558 | 0.23255 | 2.7004 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-10-03 | 1 | 21.5491 | 6.9311 | 28.4803 | 1.411 | 0.76558 | 0.21173 | 2.3883 | 8.386% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-10-03 | 2 | 20.3292 | 6.3973 | 26.7264 | 1.2426 | 0.76558 | 0.19869 | 2.2068 | 8.257% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-10-03 | 3 | 19.3098 | 6.0235 | 25.3333 | 1.1164 | 0.76558 | 0.18833 | 2.0703 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2010-10-03 | 4 | 18.5366 | 5.8024 | 24.339 | 1.0305 | 0.76558 | 0.18094 | 1.977 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-10-03 | 5 | 18.0254 | 5.6558 | 23.6811 | 0.97553 | 0.76558 | 0.17605 | 1.9172 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-10-03 | 6 | 17.9251 | 5.5553 | 23.4804 | 0.95906 | 0.76558 | 0.17456 | 1.8992 | 8.088% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-10-03 | 7 | 17.3411 | 5.4838 | 22.8249 | 0.90626 | 0.76558 | 0.16968 | 1.8415 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-10-03 | 8 | 17.307 | 5.4374 | 22.7443 | 0.89987 | 0.76558 | 0.16908 | 1.8345 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-03 | 9 | 17.8169 | 5.4754 | 23.2924 | 0.94376 | 0.76558 | 0.17316 | 1.8825 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-10-03 | 10 | 18.1369 | 5.7132 | 23.8501 | 0.9895 | 0.76558 | 0.1773 | 1.9324 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-10-03 | 11 | 18.5809 | 6.2876 | 24.8685 | 1.0758 | 0.76558 | 0.18488 | 2.0263 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-10-03 | 12 | 18.9991 | 6.5589 | 25.558 | 1.1363 | 0.76558 | 0.19 | 2.0919 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-10-03 | 13 | 19.941 | 6.9527 | 26.8937 | 1.2582 | 0.76558 | 0.19993 | 2.2237 | 8.268% | 8.798% | 5.945% | 1.0901 | 1.0965 | 1.0632
2010-10-03 | 14 | 21.2469 | 7.5217 | 28.7687 | 1.4397 | 0.76558 | 0.21387 | 2.4192 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2010-10-03 | 15 | 22.7587 | 8.5723 | 31.331 | 1.7076 | 0.76558 | 0.23292 | 2.7061 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-10-03 | 16 | 24.3705 | 9.2474 | 33.6179 | 1.966 | 0.76558 | 0.24992 | 2.9815 | 8.869% | 9.436% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-10-03 | 17 | 27.8246 | 10.0889 | 37.9135 | 2.5005 | 0.76558 | 0.28185 | 3.5479 | 9.358% | 9.957% | 6.728% | 1.1032 | 1.1106 | 1.0721
2010-10-03 | 18 | 31.5705 | 11.2083 | 42.7787 | 3.1834 | 0.76558 | 0.31802 | 4.267 | 9.975% | 10.61% | 7.172% | 1.1108 | 1.1187 | 1.0773
2010-10-03 | 19 | 34.3205 | 11.9717 | 46.2922 | 3.7278 | 0.76558 | 0.34414 | 4.8375 | 10.45% | 11.12% | 7.513% | 1.1167 | 1.1251 | 1.0812
2010-10-03 | 20 | 35.0568 | 12.2249 | 47.2817 | 3.8888 | 0.76558 | 0.3515 | 5.0059 | 10.59% | 11.27% | 7.612% | 1.1184 | 1.127 | 1.0824
2010-10-03 | 21 | 36.8046 | 12.0724 | 48.877 | 4.1557 | 0.76558 | 0.36336 | 5.2846 | 10.81% | 11.5% | 7.774% | 1.1212 | 1.13 | 1.0843
2010-10-03 | 22 | 37.4725 | 11.674 | 49.1465 | 4.2016 | 0.76558 | 0.36536 | 5.3326 | 10.85% | 11.54% | 7.801% | 1.1217 | 1.1305 | 1.0846
2010-10-03 | 23 | 37.2487 | 11.3844 | 48.6331 | 4.1143 | 0.76558 | 0.36154 | 5.2415 | 10.78% | 11.47% | 7.749% | 1.1208 | 1.1295 | 1.084
2010-10-03 | 24 | 35.4545 | 11.0064 | 46.4609 | 3.755 | 0.76558 | 0.3454 | 4.866 | 10.47% | 11.14% | 7.53% | 1.117 | 1.1254 | 1.0814
2010-10-03 | 25 | 33.4886 | 10.4439 | 43.9325 | 3.3574 | 0.76558 | 0.3266 | 4.4496 | 10.13% | 10.78% | 7.282% | 1.1127 | 1.1208 | 1.0785
2010-10-03 | 26 | 30.7926 | 9.9565 | 40.7491 | 2.8885 | 0.76558 | 0.30293 | 3.957 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2010-10-03 | 27 | 29.4688 | 9.8947 | 39.3635 | 2.6954 | 0.76558 | 0.29263 | 3.7536 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-10-03 | 28 | 29.3109 | 9.683 | 38.9939 | 2.645 | 0.76558 | 0.28989 | 3.7005 | 9.49% | 10.1% | 6.823% | 1.1048 | 1.1123 | 1.0732
2010-10-03 | 29 | 29.5089 | 9.2243 | 38.7333 | 2.6098 | 0.76558 | 0.28795 | 3.6633 | 9.458% | 10.06% | 6.8% | 1.1045 | 1.1119 | 1.073
2010-10-03 | 30 | 28.281 | 9.1281 | 37.4091 | 2.4344 | 0.76558 | 0.2781 | 3.4781 | 9.297% | 9.892% | 6.685% | 1.1025 | 1.1098 | 1.0716
2010-10-03 | 31 | 28.9311 | 8.7201 | 37.6511 | 2.466 | 0.76558 | 0.2799 | 3.5115 | 9.326% | 9.923% | 6.706% | 1.1029 | 1.1102 | 1.0719
2010-10-03 | 32 | 28.7091 | 8.6255 | 37.3346 | 2.4247 | 0.76558 | 0.27755 | 3.4678 | 9.289% | 9.883% | 6.678% | 1.1024 | 1.1097 | 1.0716
2010-10-03 | 33 | 27.9331 | 8.8707 | 36.8038 | 2.3562 | 0.76558 | 0.2736 | 3.3954 | 9.226% | 9.816% | 6.633% | 1.1016 | 1.1088 | 1.071
2010-10-03 | 34 | 27.663 | 8.775 | 36.438 | 2.3096 | 0.76558 | 0.27088 | 3.3461 | 9.183% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-10-03 | 35 | 27.4232 | 9.2033 | 36.6265 | 2.3336 | 0.76558 | 0.27229 | 3.3715 | 9.205% | 9.794% | 6.618% | 1.1014 | 1.1086 | 1.0709
2010-10-03 | 36 | 28.7152 | 9.6931 | 38.4083 | 2.5662 | 0.76558 | 0.28553 | 3.6173 | 9.418% | 10.02% | 6.772% | 1.104 | 1.1114 | 1.0726
2010-10-03 | 37 | 29.2132 | 10.0871 | 39.3003 | 2.6867 | 0.76558 | 0.29216 | 3.7445 | 9.528% | 10.14% | 6.851% | 1.1053 | 1.1128 | 1.0735
2010-10-03 | 38 | 30.1536 | 9.9612 | 40.1148 | 2.7993 | 0.76558 | 0.29822 | 3.8631 | 9.63% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-10-03 | 39 | 30.7773 | 10.051 | 40.8282 | 2.8997 | 0.76558 | 0.30352 | 3.9688 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-10-03 | 40 | 31.3873 | 9.9349 | 41.3223 | 2.9703 | 0.76558 | 0.30719 | 4.0431 | 9.784% | 10.41% | 7.035% | 1.1085 | 1.1162 | 1.0757
2010-10-03 | 41 | 32.8653 | 10.1198 | 42.9851 | 3.2142 | 0.76558 | 0.31956 | 4.2993 | 10% | 10.64% | 7.191% | 1.1111 | 1.1191 | 1.0775
2010-10-03 | 42 | 33.2134 | 10.0032 | 43.2167 | 3.2489 | 0.76558 | 0.32128 | 4.3358 | 10.03% | 10.67% | 7.213% | 1.1115 | 1.1195 | 1.0777
2010-10-03 | 43 | 31.7895 | 9.6371 | 41.4266 | 2.9853 | 0.76558 | 0.30797 | 4.0589 | 9.798% | 10.42% | 7.045% | 1.1086 | 1.1164 | 1.0758
2010-10-03 | 44 | 30.5816 | 9.1457 | 39.7273 | 2.7454 | 0.76558 | 0.29534 | 3.8064 | 9.581% | 10.19% | 6.889% | 1.106 | 1.1135 | 1.074
2010-10-03 | 45 | 28.1916 | 8.5112 | 36.7028 | 2.3433 | 0.76558 | 0.27285 | 3.3818 | 9.214% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.0709
2010-10-03 | 46 | 25.9516 | 8.0058 | 33.9574 | 2.0059 | 0.76558 | 0.25244 | 3.0239 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2010-10-03 | 47 | 25.7036 | 7.9676 | 33.6712 | 1.9722 | 0.76558 | 0.25032 | 2.9881 | 8.874% | 9.442% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-10-03 | 48 | 26.2356 | 8.2239 | 34.4595 | 2.0656 | 0.76558 | 0.25618 | 3.0874 | 8.959% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2010-10-04 | 1 | 24.0876 | 7.1622 | 31.2499 | 1.6988 | 0.76558 | 0.23232 | 2.6967 | 8.629% | 9.182% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-10-04 | 2 | 22.5736 | 6.6268 | 29.2003 | 1.4832 | 0.76558 | 0.21708 | 2.4659 | 8.445% | 8.985% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-10-04 | 3 | 21.1796 | 6.2412 | 27.4208 | 1.308 | 0.76558 | 0.20385 | 2.2774 | 8.305% | 8.837% | 5.972% | 1.0906 | 1.0969 | 1.0635
2010-10-04 | 4 | 20.5977 | 6.0226 | 26.6202 | 1.2327 | 0.76558 | 0.1979 | 2.1962 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2010-10-04 | 5 | 20.2896 | 5.8645 | 26.1541 | 1.1899 | 0.76558 | 0.19443 | 2.1499 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-10-04 | 6 | 19.9657 | 5.7297 | 25.6954 | 1.1485 | 0.76558 | 0.19102 | 2.1051 | 8.193% | 8.717% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-10-04 | 7 | 19.6917 | 5.7122 | 25.4038 | 1.1226 | 0.76558 | 0.18886 | 2.0771 | 8.176% | 8.699% | 5.879% | 1.089 | 1.0953 | 1.0625
2010-10-04 | 8 | 19.5499 | 5.7475 | 25.2974 | 1.1132 | 0.76558 | 0.18806 | 2.0669 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-10-04 | 9 | 19.2919 | 5.7376 | 25.0295 | 1.0898 | 0.76558 | 0.18607 | 2.0414 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-10-04 | 10 | 19.338 | 5.8348 | 25.1727 | 1.1023 | 0.76558 | 0.18714 | 2.055 | 8.164% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-10-04 | 11 | 19.9317 | 5.9422 | 25.8739 | 1.1645 | 0.76558 | 0.19235 | 2.1225 | 8.203% | 8.728% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-10-04 | 12 | 20.4497 | 6.0497 | 26.4993 | 1.2215 | 0.76558 | 0.197 | 2.1841 | 8.242% | 8.77% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-10-04 | 13 | 21.3417 | 6.2961 | 27.6378 | 1.3287 | 0.76558 | 0.20546 | 2.2998 | 8.321% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-10-04 | 14 | 22.3674 | 6.4965 | 28.8638 | 1.4492 | 0.76558 | 0.21458 | 2.4294 | 8.417% | 8.955% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-10-04 | 15 | 23.6158 | 7.1893 | 30.8051 | 1.6507 | 0.76558 | 0.22901 | 2.6453 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-10-04 | 16 | 25.0558 | 8.1039 | 33.1597 | 1.9127 | 0.76558 | 0.24651 | 2.9248 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-10-04 | 17 | 27.3758 | 9.3752 | 36.751 | 2.3495 | 0.76558 | 0.27321 | 3.3883 | 9.22% | 9.81% | 6.629% | 1.1016 | 1.1088 | 1.071
2010-10-04 | 18 | 29.0278 | 10.2435 | 39.2713 | 2.6828 | 0.76558 | 0.29195 | 3.7403 | 9.524% | 10.13% | 6.848% | 1.1053 | 1.1128 | 1.0735
2010-10-04 | 19 | 30.2178 | 10.6103 | 40.828 | 2.8997 | 0.76558 | 0.30352 | 3.9688 | 9.721% | 10.34% | 6.989% | 1.1077 | 1.1154 | 1.0751
2010-10-04 | 20 | 31.3317 | 10.7894 | 42.1211 | 3.0863 | 0.76558 | 0.31313 | 4.165 | 9.888% | 10.52% | 7.11% | 1.1097 | 1.1176 | 1.0765
2010-10-04 | 21 | 33.1117 | 10.9161 | 44.0278 | 3.372 | 0.76558 | 0.32731 | 4.4649 | 10.14% | 10.79% | 7.291% | 1.1129 | 1.121 | 1.0786
2010-10-04 | 22 | 33.2058 | 10.9925 | 44.1983 | 3.3982 | 0.76558 | 0.32858 | 4.4923 | 10.16% | 10.81% | 7.308% | 1.1131 | 1.1213 | 1.0788
2010-10-04 | 23 | 32.6119 | 11.0177 | 43.6296 | 3.3113 | 0.76558 | 0.32435 | 4.4012 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2010-10-04 | 24 | 31.3698 | 10.7767 | 42.1465 | 3.09 | 0.76558 | 0.31332 | 4.1689 | 9.891% | 10.52% | 7.112% | 1.1098 | 1.1176 | 1.0766
2010-10-04 | 25 | 29.7781 | 10.5408 | 40.3188 | 2.8278 | 0.76558 | 0.29974 | 3.8931 | 9.656% | 10.27% | 6.943% | 1.1069 | 1.1145 | 1.0746
2010-10-04 | 26 | 28.366 | 9.9333 | 38.2993 | 2.5516 | 0.76558 | 0.28472 | 3.6019 | 9.405% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2010-10-04 | 27 | 27.898 | 9.8914 | 37.7895 | 2.4841 | 0.76558 | 0.28093 | 3.5306 | 9.343% | 9.941% | 6.718% | 1.1031 | 1.1104 | 1.072
2010-10-04 | 28 | 27.2974 | 9.6255 | 36.9229 | 2.3715 | 0.76558 | 0.27449 | 3.4116 | 9.24% | 9.831% | 6.643% | 1.1018 | 1.109 | 1.0712
2010-10-04 | 29 | 26.3259 | 9.0808 | 35.4067 | 2.1808 | 0.76558 | 0.26322 | 3.2095 | 9.065% | 9.645% | 6.518% | 1.0997 | 1.1067 | 1.0697
2010-10-04 | 30 | 25.4539 | 8.7389 | 34.1928 | 2.0338 | 0.76558 | 0.25419 | 3.0535 | 8.93% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-10-04 | 31 | 26.4379 | 8.4542 | 34.8921 | 2.1178 | 0.76558 | 0.25939 | 3.1428 | 9.007% | 9.584% | 6.476% | 1.099 | 1.106 | 1.0692
2010-10-04 | 32 | 26.2201 | 8.2599 | 34.48 | 2.0681 | 0.76558 | 0.25633 | 3.09 | 8.962% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-10-04 | 33 | 25.7381 | 8.4169 | 34.155 | 2.0293 | 0.76558 | 0.25391 | 3.0488 | 8.926% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-10-04 | 34 | 25.2902 | 8.4284 | 33.7186 | 1.9778 | 0.76558 | 0.25067 | 2.994 | 8.879% | 9.448% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-10-04 | 35 | 25.2482 | 8.8324 | 34.0806 | 2.0205 | 0.76558 | 0.25336 | 3.0394 | 8.918% | 9.489% | 6.412% | 1.0979 | 1.1048 | 1.0685
2010-10-04 | 36 | 25.9961 | 9.8286 | 35.8247 | 2.2325 | 0.76558 | 0.26633 | 3.2644 | 9.112% | 9.695% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-10-04 | 37 | 27.2262 | 10.4891 | 37.7153 | 2.4744 | 0.76558 | 0.28038 | 3.5204 | 9.334% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2010-10-04 | 38 | 28.4443 | 10.0814 | 38.5256 | 2.5819 | 0.76558 | 0.2864 | 3.6339 | 9.432% | 10.04% | 6.782% | 1.1041 | 1.1116 | 1.0728
2010-10-04 | 39 | 28.9964 | 9.8177 | 38.814 | 2.6207 | 0.76558 | 0.28855 | 3.6748 | 9.468% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2010-10-04 | 40 | 29.8965 | 10.1052 | 40.0016 | 2.7835 | 0.76558 | 0.29738 | 3.8464 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-10-04 | 41 | 32.1142 | 10.5368 | 42.651 | 3.1644 | 0.76558 | 0.31707 | 4.2471 | 9.958% | 10.6% | 7.16% | 1.1106 | 1.1185 | 1.0771
2010-10-04 | 42 | 32.5302 | 10.37 | 42.9002 | 3.2015 | 0.76558 | 0.31893 | 4.286 | 9.991% | 10.63% | 7.183% | 1.111 | 1.1189 | 1.0774
2010-10-04 | 43 | 31.1441 | 9.8838 | 41.0279 | 2.9282 | 0.76558 | 0.30501 | 3.9987 | 9.746% | 10.37% | 7.008% | 1.108 | 1.1157 | 1.0754
2010-10-04 | 44 | 30.0682 | 9.2884 | 39.3566 | 2.6944 | 0.76558 | 0.29258 | 3.7526 | 9.535% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-10-04 | 45 | 27.6402 | 8.3876 | 36.0279 | 2.2579 | 0.76558 | 0.26784 | 3.2913 | 9.136% | 9.72% | 6.568% | 1.1005 | 1.1077 | 1.0703
2010-10-04 | 46 | 25.2703 | 7.5459 | 32.8161 | 1.8733 | 0.76558 | 0.24396 | 2.8828 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-10-04 | 47 | 24.1823 | 7.1345 | 31.3168 | 1.706 | 0.76558 | 0.23281 | 2.7044 | 8.636% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-10-04 | 48 | 24.3343 | 7.3411 | 31.6754 | 1.7453 | 0.76558 | 0.23548 | 2.7464 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-10-05 | 1 | 22.5243 | 6.6701 | 29.1944 | 1.4826 | 0.76558 | 0.21703 | 2.4652 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-10-05 | 2 | 21.3183 | 6.2579 | 27.5762 | 1.3228 | 0.76558 | 0.205 | 2.2934 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-10-05 | 3 | 20.2841 | 5.9525 | 26.2366 | 1.1974 | 0.76558 | 0.19505 | 2.1581 | 8.225% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-10-05 | 4 | 19.8543 | 6.1629 | 26.0172 | 1.1775 | 0.76558 | 0.19341 | 2.1365 | 8.212% | 8.737% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-10-05 | 5 | 19.3782 | 7.0303 | 26.4085 | 1.2132 | 0.76558 | 0.19632 | 2.1751 | 8.236% | 8.763% | 5.922% | 1.0898 | 1.0961 | 1.0629
2010-10-05 | 6 | 19.4524 | 7.4224 | 26.8748 | 1.2564 | 0.76558 | 0.19979 | 2.2218 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2010-10-05 | 7 | 19.2465 | 7.5075 | 26.754 | 1.2451 | 0.76558 | 0.19889 | 2.2096 | 8.259% | 8.787% | 5.938% | 1.09 | 1.0963 | 1.0631
2010-10-05 | 8 | 19.2462 | 7.543 | 26.7892 | 1.2484 | 0.76558 | 0.19915 | 2.2131 | 8.261% | 8.79% | 5.94% | 1.0901 | 1.0964 | 1.0631
2010-10-05 | 9 | 19.4882 | 7.6547 | 27.1429 | 1.2816 | 0.76558 | 0.20178 | 2.2489 | 8.286% | 8.816% | 5.957% | 1.0903 | 1.0967 | 1.0633
2010-10-05 | 10 | 19.7761 | 8.1935 | 27.9696 | 1.3608 | 0.76558 | 0.20793 | 2.3343 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-10-05 | 11 | 20.1721 | 10.8375 | 31.0095 | 1.6727 | 0.76558 | 0.23053 | 2.6688 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-10-05 | 12 | 20.666 | 11.8194 | 32.4853 | 1.8357 | 0.76558 | 0.2415 | 2.8428 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-10-05 | 13 | 22.306 | 12.8916 | 35.1975 | 2.1551 | 0.76558 | 0.26166 | 3.1823 | 9.041% | 9.62% | 6.501% | 1.0994 | 1.1064 | 1.0695
2010-10-05 | 14 | 25.3099 | 14.2369 | 39.5468 | 2.7206 | 0.76558 | 0.294 | 3.7801 | 9.559% | 10.17% | 6.873% | 1.1057 | 1.1132 | 1.0738
2010-10-05 | 15 | 28.7699 | 16.0356 | 44.8055 | 3.4922 | 0.76558 | 0.33309 | 4.5909 | 10.25% | 10.9% | 7.367% | 1.1142 | 1.1224 | 1.0795
2010-10-05 | 16 | 31.1818 | 16.3656 | 47.5474 | 3.9327 | 0.76558 | 0.35347 | 5.0517 | 10.62% | 11.3% | 7.639% | 1.1189 | 1.1275 | 1.0827
2010-10-05 | 17 | 33.6318 | 16.2665 | 49.8983 | 4.3312 | 0.76558 | 0.37095 | 5.4677 | 10.96% | 11.66% | 7.879% | 1.1231 | 1.132 | 1.0855
2010-10-05 | 18 | 34.4757 | 15.9644 | 50.4402 | 4.4258 | 0.76558 | 0.37498 | 5.5663 | 11.04% | 11.74% | 7.935% | 1.124 | 1.133 | 1.0862
2010-10-05 | 19 | 34.4718 | 14.3142 | 48.786 | 4.1402 | 0.76558 | 0.36268 | 5.2685 | 10.8% | 11.49% | 7.765% | 1.1211 | 1.1298 | 1.0842
2010-10-05 | 20 | 33.5158 | 12.4199 | 45.9357 | 3.6706 | 0.76558 | 0.34149 | 4.7777 | 10.4% | 11.07% | 7.478% | 1.1161 | 1.1244 | 1.0808
2010-10-05 | 21 | 33.2818 | 11.5307 | 44.8125 | 3.4933 | 0.76558 | 0.33314 | 4.592 | 10.25% | 10.9% | 7.368% | 1.1142 | 1.1224 | 1.0795
2010-10-05 | 22 | 31.9074 | 11.1471 | 43.0545 | 3.2246 | 0.76558 | 0.32007 | 4.3102 | 10.01% | 10.65% | 7.198% | 1.1112 | 1.1192 | 1.0776
2010-10-05 | 23 | 30.4504 | 10.4687 | 40.9191 | 2.9126 | 0.76558 | 0.3042 | 3.9824 | 9.732% | 10.36% | 6.998% | 1.1078 | 1.1155 | 1.0752
2010-10-05 | 24 | 29.5171 | 10.3116 | 39.8287 | 2.7595 | 0.76558 | 0.29609 | 3.8211 | 9.594% | 10.21% | 6.898% | 1.1061 | 1.1137 | 1.0741
2010-10-05 | 25 | 28.1075 | 10.0991 | 38.2066 | 2.5393 | 0.76558 | 0.28403 | 3.5889 | 9.393% | 9.995% | 6.754% | 1.1037 | 1.111 | 1.0724
2010-10-05 | 26 | 26.6918 | 9.7889 | 36.4807 | 2.3151 | 0.76558 | 0.2712 | 3.3518 | 9.188% | 9.776% | 6.606% | 1.1012 | 1.1084 | 1.0707
2010-10-05 | 27 | 26.2801 | 9.8502 | 36.1304 | 2.2708 | 0.76558 | 0.2686 | 3.305 | 9.147% | 9.733% | 6.577% | 1.1007 | 1.1078 | 1.0704
2010-10-05 | 28 | 26.1708 | 9.5126 | 35.6833 | 2.215 | 0.76558 | 0.26527 | 3.2458 | 9.096% | 9.678% | 6.54% | 1.1001 | 1.1072 | 1.07
2010-10-05 | 29 | 25.498 | 9.0498 | 34.5478 | 2.0762 | 0.76558 | 0.25683 | 3.0986 | 8.969% | 9.543% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-10-05 | 30 | 24.5162 | 8.8811 | 33.3973 | 1.9402 | 0.76558 | 0.24828 | 2.9541 | 8.845% | 9.411% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-10-05 | 31 | 24.8406 | 8.9127 | 33.7533 | 1.9818 | 0.76558 | 0.25093 | 2.9983 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-10-05 | 32 | 24.8433 | 8.8709 | 33.7143 | 1.9773 | 0.76558 | 0.25064 | 2.9935 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-10-05 | 33 | 24.5402 | 9.0082 | 33.5484 | 1.9578 | 0.76558 | 0.2494 | 2.9728 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2010-10-05 | 34 | 23.8472 | 9.0917 | 32.9389 | 1.8874 | 0.76558 | 0.24487 | 2.8978 | 8.798% | 9.361% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-10-05 | 35 | 23.7385 | 9.4833 | 33.2218 | 1.9199 | 0.76558 | 0.24698 | 2.9325 | 8.827% | 9.392% | 6.347% | 1.0968 | 1.1037 | 1.0678
2010-10-05 | 36 | 24.3968 | 9.8718 | 34.2686 | 2.0428 | 0.76558 | 0.25476 | 3.0631 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-10-05 | 37 | 25.9937 | 10.1853 | 36.179 | 2.2769 | 0.76558 | 0.26896 | 3.3115 | 9.153% | 9.739% | 6.581% | 1.1008 | 1.1079 | 1.0704
2010-10-05 | 38 | 27.1301 | 10.1147 | 37.2448 | 2.413 | 0.76558 | 0.27688 | 3.4555 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-10-05 | 39 | 28.0547 | 9.9875 | 38.0422 | 2.5175 | 0.76558 | 0.28281 | 3.5659 | 9.373% | 9.973% | 6.74% | 1.1034 | 1.1108 | 1.0723
2010-10-05 | 40 | 28.9807 | 10.2527 | 39.2334 | 2.6776 | 0.76558 | 0.29167 | 3.7348 | 9.52% | 10.13% | 6.845% | 1.1052 | 1.1127 | 1.0735
2010-10-05 | 41 | 31.37 | 10.8673 | 42.2374 | 3.1033 | 0.76558 | 0.314 | 4.1829 | 9.903% | 10.54% | 7.121% | 1.1099 | 1.1178 | 1.0767
2010-10-05 | 42 | 32.3875 | 10.7233 | 43.1108 | 3.233 | 0.76558 | 0.32049 | 4.3191 | 10.02% | 10.66% | 7.203% | 1.1113 | 1.1193 | 1.0776
2010-10-05 | 43 | 31.275 | 10.2655 | 41.5405 | 3.0018 | 0.76558 | 0.30882 | 4.0762 | 9.813% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-10-05 | 44 | 30.0075 | 9.6132 | 39.6207 | 2.7307 | 0.76558 | 0.29454 | 3.7908 | 9.568% | 10.18% | 6.879% | 1.1058 | 1.1133 | 1.0739
2010-10-05 | 45 | 27.5976 | 8.8275 | 36.4251 | 2.308 | 0.76558 | 0.27079 | 3.3444 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-10-05 | 46 | 24.6256 | 7.9957 | 32.6213 | 1.8511 | 0.76558 | 0.24251 | 2.8592 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1028 | 1.0673
2010-10-05 | 47 | 23.3262 | 7.5886 | 30.9149 | 1.6625 | 0.76558 | 0.22982 | 2.6579 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-10-05 | 48 | 23.2085 | 7.592 | 30.8005 | 1.6502 | 0.76558 | 0.22897 | 2.6448 | 8.587% | 9.136% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-10-06 | 1 | 21.6846 | 6.8757 | 28.5603 | 1.4189 | 0.76558 | 0.21232 | 2.3968 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2010-10-06 | 2 | 20.3112 | 6.4877 | 26.7988 | 1.2493 | 0.76558 | 0.19923 | 2.2141 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2010-10-06 | 3 | 19.4147 | 6.2351 | 25.6499 | 1.1445 | 0.76558 | 0.19068 | 2.1007 | 8.19% | 8.714% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-10-06 | 4 | 18.8494 | 5.9464 | 24.7958 | 1.0695 | 0.76558 | 0.18434 | 2.0194 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-10-06 | 5 | 18.2238 | 6.4119 | 24.6357 | 1.0558 | 0.76558 | 0.18314 | 2.0045 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-10-06 | 6 | 18.0652 | 8.0558 | 26.1209 | 1.1869 | 0.76558 | 0.19419 | 2.1467 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-10-06 | 7 | 17.823 | 9.2649 | 27.0879 | 1.2764 | 0.76558 | 0.20138 | 2.2434 | 8.282% | 8.812% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-10-06 | 8 | 18.1235 | 10.2232 | 28.3466 | 1.3978 | 0.76558 | 0.21073 | 2.3741 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-10-06 | 9 | 18.5508 | 10.764 | 29.3149 | 1.4949 | 0.76558 | 0.21793 | 2.4784 | 8.454% | 8.996% | 6.079% | 1.0924 | 1.0988 | 1.0647
2010-10-06 | 10 | 18.7148 | 11.4007 | 30.1155 | 1.5777 | 0.76558 | 0.22388 | 2.5671 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-10-06 | 11 | 19.3072 | 11.9174 | 31.2246 | 1.696 | 0.76558 | 0.23213 | 2.6937 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-10-06 | 12 | 20.0175 | 12.4521 | 32.4696 | 1.834 | 0.76558 | 0.24138 | 2.8409 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1027 | 1.0671
2010-10-06 | 13 | 21.6171 | 13.3827 | 34.9998 | 2.1309 | 0.76558 | 0.26019 | 3.1567 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1062 | 1.0693
2010-10-06 | 14 | 24.2935 | 14.2178 | 38.5113 | 2.5799 | 0.76558 | 0.2863 | 3.6318 | 9.431% | 10.03% | 6.781% | 1.1041 | 1.1115 | 1.0727
2010-10-06 | 15 | 27.8514 | 15.2264 | 43.0778 | 3.2281 | 0.76558 | 0.32025 | 4.3139 | 10.01% | 10.66% | 7.2% | 1.1113 | 1.1193 | 1.0776
2010-10-06 | 16 | 30.4493 | 15.443 | 45.8923 | 3.6637 | 0.76558 | 0.34117 | 4.7704 | 10.39% | 11.06% | 7.474% | 1.116 | 1.1244 | 1.0808
2010-10-06 | 17 | 32.692 | 14.6143 | 47.3062 | 3.8929 | 0.76558 | 0.35168 | 5.0101 | 10.59% | 11.27% | 7.615% | 1.1185 | 1.127 | 1.0824
2010-10-06 | 18 | 33.8355 | 13.9175 | 47.753 | 3.9668 | 0.76558 | 0.355 | 5.0873 | 10.65% | 11.34% | 7.66% | 1.1192 | 1.1278 | 1.083
2010-10-06 | 19 | 34.3737 | 13.7255 | 48.0992 | 4.0245 | 0.76558 | 0.35758 | 5.1476 | 10.7% | 11.39% | 7.695% | 1.1198 | 1.1285 | 1.0834
2010-10-06 | 20 | 34.2818 | 13.5681 | 47.8499 | 3.9829 | 0.76558 | 0.35572 | 5.1042 | 10.67% | 11.35% | 7.67% | 1.1194 | 1.128 | 1.0831
2010-10-06 | 21 | 34.5936 | 12.9475 | 47.5411 | 3.9316 | 0.76558 | 0.35343 | 5.0506 | 10.62% | 11.3% | 7.638% | 1.1189 | 1.1274 | 1.0827
2010-10-06 | 22 | 33.7677 | 12.6672 | 46.4349 | 3.7508 | 0.76558 | 0.3452 | 4.8616 | 10.47% | 11.14% | 7.528% | 1.1169 | 1.1254 | 1.0814
2010-10-06 | 23 | 32.6042 | 12.0173 | 44.6215 | 3.4636 | 0.76558 | 0.33172 | 4.5609 | 10.22% | 10.88% | 7.349% | 1.1138 | 1.122 | 1.0793
2010-10-06 | 24 | 30.9882 | 11.6976 | 42.6858 | 3.1696 | 0.76558 | 0.31733 | 4.2525 | 9.962% | 10.6% | 7.163% | 1.1106 | 1.1186 | 1.0772
2010-10-06 | 25 | 29.518 | 11.2204 | 40.7384 | 2.887 | 0.76558 | 0.30285 | 3.9554 | 9.709% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.075
2010-10-06 | 26 | 28.0584 | 10.3273 | 38.3858 | 2.5632 | 0.76558 | 0.28536 | 3.6141 | 9.415% | 10.02% | 6.77% | 1.1039 | 1.1113 | 1.0726
2010-10-06 | 27 | 27.5844 | 10.3127 | 37.897 | 2.4983 | 0.76558 | 0.28173 | 3.5456 | 9.356% | 9.955% | 6.727% | 1.1032 | 1.1106 | 1.0721
2010-10-06 | 28 | 27.1321 | 9.8899 | 37.0219 | 2.3843 | 0.76558 | 0.27523 | 3.4251 | 9.251% | 9.844% | 6.652% | 1.1019 | 1.1092 | 1.0713
2010-10-06 | 29 | 26.193 | 9.4456 | 35.6386 | 2.2094 | 0.76558 | 0.26494 | 3.2399 | 9.091% | 9.673% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-10-06 | 30 | 25.0465 | 9.1431 | 34.1896 | 2.0334 | 0.76558 | 0.25417 | 3.0531 | 8.93% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2010-10-06 | 31 | 25.2704 | 8.9369 | 34.2073 | 2.0355 | 0.76558 | 0.2543 | 3.0554 | 8.932% | 9.504% | 6.422% | 1.0981 | 1.105 | 1.0686
2010-10-06 | 32 | 24.8498 | 8.9608 | 33.8106 | 1.9886 | 0.76558 | 0.25135 | 3.0055 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-10-06 | 33 | 24.369 | 9.2115 | 33.5805 | 1.9616 | 0.76558 | 0.24964 | 2.9768 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2010-10-06 | 34 | 23.6189 | 9.0833 | 32.7022 | 1.8603 | 0.76558 | 0.24311 | 2.869 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-10-06 | 35 | 23.694 | 9.7397 | 33.4337 | 1.9445 | 0.76558 | 0.24855 | 2.9586 | 8.849% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.0679
2010-10-06 | 36 | 24.7192 | 10.1892 | 34.9084 | 2.1198 | 0.76558 | 0.25951 | 3.1449 | 9.009% | 9.586% | 6.477% | 1.099 | 1.106 | 1.0693
2010-10-06 | 37 | 25.9707 | 10.5653 | 36.536 | 2.3221 | 0.76558 | 0.27161 | 3.3593 | 9.194% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2010-10-06 | 38 | 27.503 | 10.7198 | 38.2229 | 2.5414 | 0.76558 | 0.28415 | 3.5912 | 9.395% | 9.997% | 6.755% | 1.1037 | 1.1111 | 1.0724
2010-10-06 | 39 | 28.2629 | 10.5603 | 38.8231 | 2.6219 | 0.76558 | 0.28862 | 3.6761 | 9.469% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.0731
2010-10-06 | 40 | 29.0558 | 10.8506 | 39.9064 | 2.7703 | 0.76558 | 0.29667 | 3.8325 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-10-06 | 41 | 31.3782 | 11.2137 | 42.5919 | 3.1557 | 0.76558 | 0.31663 | 4.2379 | 9.95% | 10.59% | 7.154% | 1.1105 | 1.1184 | 1.0771
2010-10-06 | 42 | 32.0634 | 11.4535 | 43.5168 | 3.2942 | 0.76558 | 0.32351 | 4.3833 | 10.07% | 10.72% | 7.242% | 1.112 | 1.12 | 1.0781
2010-10-06 | 43 | 31.114 | 11.0724 | 42.1864 | 3.0958 | 0.76558 | 0.31362 | 4.175 | 9.897% | 10.53% | 7.116% | 1.1098 | 1.1177 | 1.0766
2010-10-06 | 44 | 29.7143 | 10.3965 | 40.1108 | 2.7987 | 0.76558 | 0.29819 | 3.8625 | 9.63% | 10.25% | 6.924% | 1.1066 | 1.1142 | 1.0744
2010-10-06 | 45 | 27.5506 | 9.4413 | 36.9918 | 2.3804 | 0.76558 | 0.275 | 3.421 | 9.248% | 9.84% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-10-06 | 46 | 25.2331 | 8.5552 | 33.7883 | 1.9859 | 0.76558 | 0.25119 | 3.0027 | 8.887% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2010-10-06 | 47 | 23.8492 | 8.283 | 32.1322 | 1.796 | 0.76558 | 0.23887 | 2.8005 | 8.716% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2010-10-06 | 48 | 23.4213 | 8.3077 | 31.729 | 1.7512 | 0.76558 | 0.23588 | 2.7527 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-10-07 | 1 | 21.5155 | 7.6095 | 29.125 | 1.4756 | 0.76558 | 0.21652 | 2.4577 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-10-07 | 2 | 20.06 | 7.548 | 27.608 | 1.3259 | 0.76558 | 0.20524 | 2.2967 | 8.319% | 8.851% | 5.981% | 1.0907 | 1.0971 | 1.0636
2010-10-07 | 3 | 19.0266 | 8.0855 | 27.1121 | 1.2787 | 0.76558 | 0.20155 | 2.2458 | 8.283% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-10-07 | 4 | 18.367 | 8.5433 | 26.9104 | 1.2597 | 0.76558 | 0.20005 | 2.2254 | 8.269% | 8.799% | 5.946% | 1.0901 | 1.0965 | 1.0632
2010-10-07 | 5 | 18.1931 | 8.984 | 27.1771 | 1.2848 | 0.76558 | 0.20204 | 2.2524 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-10-07 | 6 | 18.0933 | 9.802 | 27.8953 | 1.3536 | 0.76558 | 0.20738 | 2.3266 | 8.34% | 8.874% | 5.997% | 1.091 | 1.0974 | 1.0638
2010-10-07 | 7 | 17.9161 | 10.4151 | 28.3312 | 1.3963 | 0.76558 | 0.21062 | 2.3725 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-10-07 | 8 | 17.988 | 10.7514 | 28.7393 | 1.4368 | 0.76558 | 0.21365 | 2.416 | 8.407% | 8.945% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-10-07 | 9 | 18.2264 | 11.1824 | 29.4087 | 1.5045 | 0.76558 | 0.21863 | 2.4887 | 8.462% | 9.004% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-10-07 | 10 | 18.4915 | 11.8061 | 30.2976 | 1.5968 | 0.76558 | 0.22524 | 2.5876 | 8.541% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-10-07 | 11 | 18.8199 | 12.2146 | 31.0346 | 1.6754 | 0.76558 | 0.23071 | 2.6717 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-10-07 | 12 | 19.6605 | 12.8651 | 32.5256 | 1.8403 | 0.76558 | 0.2418 | 2.8477 | 8.755% | 9.315% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-10-07 | 13 | 21.4341 | 13.6953 | 35.1294 | 2.1467 | 0.76558 | 0.26116 | 3.1735 | 9.034% | 9.612% | 6.495% | 1.0993 | 1.1063 | 1.0695
2010-10-07 | 14 | 24.6761 | 15.1776 | 39.8537 | 2.7629 | 0.76558 | 0.29628 | 3.8248 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-10-07 | 15 | 28.1683 | 16.3808 | 44.5491 | 3.4523 | 0.76558 | 0.33118 | 4.5491 | 10.21% | 10.86% | 7.342% | 1.1137 | 1.1219 | 1.0792
2010-10-07 | 16 | 30.5206 | 16.3502 | 46.8708 | 3.8215 | 0.76558 | 0.34844 | 4.9356 | 10.53% | 11.2% | 7.571% | 1.1177 | 1.1262 | 1.0819
2010-10-07 | 17 | 31.363 | 16.2571 | 47.6201 | 3.9447 | 0.76558 | 0.35401 | 5.0643 | 10.63% | 11.32% | 7.646% | 1.119 | 1.1276 | 1.0828
2010-10-07 | 18 | 32.7193 | 16.2433 | 48.9626 | 4.1703 | 0.76558 | 0.36399 | 5.2998 | 10.82% | 11.52% | 7.783% | 1.1214 | 1.1302 | 1.0844
2010-10-07 | 19 | 32.8677 | 14.6851 | 47.5528 | 3.9336 | 0.76558 | 0.35351 | 5.0527 | 10.63% | 11.31% | 7.64% | 1.1189 | 1.1275 | 1.0827
2010-10-07 | 20 | 31.6616 | 13.378 | 45.0396 | 3.5288 | 0.76558 | 0.33483 | 4.6292 | 10.28% | 10.94% | 7.39% | 1.1146 | 1.1228 | 1.0798
2010-10-07 | 21 | 31.4757 | 12.4791 | 43.9548 | 3.3608 | 0.76558 | 0.32677 | 4.4532 | 10.13% | 10.78% | 7.284% | 1.1127 | 1.1208 | 1.0786
2010-10-07 | 22 | 30.1299 | 11.675 | 41.8049 | 3.0401 | 0.76558 | 0.31078 | 4.1165 | 9.847% | 10.48% | 7.08% | 1.1092 | 1.117 | 1.0762
2010-10-07 | 23 | 28.5241 | 10.8722 | 39.3963 | 2.6999 | 0.76558 | 0.29288 | 3.7583 | 9.54% | 10.15% | 6.859% | 1.1055 | 1.113 | 1.0736
2010-10-07 | 24 | 27.4806 | 10.4787 | 37.9593 | 2.5065 | 0.76558 | 0.28219 | 3.5543 | 9.363% | 9.963% | 6.732% | 1.1033 | 1.1107 | 1.0722
2010-10-07 | 25 | 26.2023 | 10.241 | 36.4432 | 2.3103 | 0.76558 | 0.27092 | 3.3468 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-10-07 | 26 | 25.1118 | 9.6718 | 34.7836 | 2.1047 | 0.76558 | 0.25859 | 3.1288 | 8.995% | 9.571% | 6.468% | 1.0988 | 1.1058 | 1.0691
2010-10-07 | 27 | 24.6803 | 9.7377 | 34.4181 | 2.0607 | 0.76558 | 0.25587 | 3.0821 | 8.955% | 9.528% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-10-07 | 28 | 24.0729 | 9.6132 | 33.6861 | 1.9739 | 0.76558 | 0.25043 | 2.99 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-10-07 | 29 | 23.6883 | 9.1986 | 32.8869 | 1.8814 | 0.76558 | 0.24449 | 2.8915 | 8.792% | 9.355% | 6.322% | 1.0964 | 1.1032 | 1.0675
2010-10-07 | 30 | 23.1708 | 8.8059 | 31.9767 | 1.7787 | 0.76558 | 0.23772 | 2.782 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-10-07 | 31 | 23.7359 | 8.6789 | 32.4148 | 1.8278 | 0.76558 | 0.24098 | 2.8343 | 8.744% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-10-07 | 32 | 23.5662 | 8.8253 | 32.3915 | 1.8251 | 0.76558 | 0.2408 | 2.8315 | 8.742% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-10-07 | 33 | 22.9391 | 8.9976 | 31.9366 | 1.7742 | 0.76558 | 0.23742 | 2.7772 | 8.696% | 9.253% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-10-07 | 34 | 23.1549 | 8.7759 | 31.9307 | 1.7736 | 0.76558 | 0.23738 | 2.7765 | 8.696% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-10-07 | 35 | 23.3262 | 9.2706 | 32.5968 | 1.8484 | 0.76558 | 0.24233 | 2.8563 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-10-07 | 36 | 24.217 | 9.6649 | 33.8819 | 1.997 | 0.76558 | 0.25188 | 3.0144 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-10-07 | 37 | 25.7502 | 10.3179 | 36.0682 | 2.263 | 0.76558 | 0.26814 | 3.2967 | 9.14% | 9.725% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-10-07 | 38 | 26.7101 | 10.5349 | 37.245 | 2.4131 | 0.76558 | 0.27688 | 3.4555 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-10-07 | 39 | 27.2503 | 10.7473 | 37.9976 | 2.5116 | 0.76558 | 0.28248 | 3.5596 | 9.368% | 9.968% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-10-07 | 40 | 27.9622 | 10.8331 | 38.7953 | 2.6181 | 0.76558 | 0.28841 | 3.6721 | 9.465% | 10.07% | 6.806% | 1.1045 | 1.112 | 1.073
2010-10-07 | 41 | 29.5411 | 11.2019 | 40.743 | 2.8876 | 0.76558 | 0.30289 | 3.9561 | 9.71% | 10.33% | 6.981% | 1.1075 | 1.1152 | 1.0751
2010-10-07 | 42 | 30.0971 | 11.2658 | 41.363 | 2.9762 | 0.76558 | 0.3075 | 4.0492 | 9.79% | 10.42% | 7.039% | 1.1085 | 1.1163 | 1.0757
2010-10-07 | 43 | 28.701 | 10.8659 | 39.5669 | 2.7233 | 0.76558 | 0.29415 | 3.783 | 9.561% | 10.17% | 6.874% | 1.1057 | 1.1133 | 1.0738
2010-10-07 | 44 | 27.5323 | 10.1412 | 37.6735 | 2.4689 | 0.76558 | 0.28007 | 3.5146 | 9.329% | 9.926% | 6.708% | 1.1029 | 1.1102 | 1.0719
2010-10-07 | 45 | 25.1324 | 9.0354 | 34.1678 | 2.0308 | 0.76558 | 0.25401 | 3.0504 | 8.928% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-10-07 | 46 | 22.7571 | 8.1292 | 30.8863 | 1.6595 | 0.76558 | 0.22961 | 2.6546 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-10-07 | 47 | 21.6391 | 7.8476 | 29.4867 | 1.5125 | 0.76558 | 0.21921 | 2.4973 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-10-07 | 48 | 21.2095 | 8.0424 | 29.252 | 1.4885 | 0.76558 | 0.21746 | 2.4715 | 8.449% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-10-08 | 1 | 19.2723 | 7.3291 | 26.6014 | 1.231 | 0.76558 | 0.19776 | 2.1943 | 8.249% | 8.777% | 5.931% | 1.0899 | 1.0962 | 1.063
2010-10-08 | 2 | 17.8926 | 6.7059 | 24.5985 | 1.0526 | 0.76558 | 0.18287 | 2.001 | 8.135% | 8.655% | 5.849% | 1.0886 | 1.0948 | 1.0621
2010-10-08 | 3 | 17.4183 | 6.3544 | 23.7726 | 0.98308 | 0.76558 | 0.17673 | 1.9254 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-10-08 | 4 | 16.8531 | 6.1111 | 22.9642 | 0.91735 | 0.76558 | 0.17072 | 1.8537 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-10-08 | 5 | 16.3983 | 6.0002 | 22.3985 | 0.87272 | 0.76558 | 0.16651 | 1.8048 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-08 | 6 | 16.0255 | 5.8603 | 21.8858 | 0.83322 | 0.76558 | 0.1627 | 1.7615 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-08 | 7 | 15.7617 | 5.8289 | 21.5906 | 0.8109 | 0.76558 | 0.16051 | 1.737 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-08 | 8 | 15.4698 | 5.8001 | 21.2699 | 0.78698 | 0.76558 | 0.15812 | 1.7107 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-08 | 9 | 15.5924 | 5.9291 | 21.5214 | 0.80571 | 0.76558 | 0.15999 | 1.7313 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-08 | 10 | 15.8506 | 5.9081 | 21.7587 | 0.82357 | 0.76558 | 0.16176 | 1.7509 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-08 | 11 | 16.5364 | 5.9351 | 22.4715 | 0.87841 | 0.76558 | 0.16706 | 1.811 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-10-08 | 12 | 17.2915 | 6.3765 | 23.668 | 0.97444 | 0.76558 | 0.17595 | 1.916 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2010-10-08 | 13 | 18.8075 | 7.1269 | 25.9344 | 1.17 | 0.76558 | 0.1928 | 2.1284 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-10-08 | 14 | 20.9358 | 8.2413 | 29.1771 | 1.4809 | 0.76558 | 0.21691 | 2.4634 | 8.443% | 8.983% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-10-08 | 15 | 24.518 | 10.001 | 34.519 | 2.0728 | 0.76558 | 0.25662 | 3.095 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-10-08 | 16 | 26.8727 | 10.8446 | 37.7174 | 2.4747 | 0.76558 | 0.2804 | 3.5206 | 9.334% | 9.932% | 6.711% | 1.103 | 1.1103 | 1.0719
2010-10-08 | 17 | 28.5816 | 11.659 | 40.2406 | 2.8168 | 0.76558 | 0.29915 | 3.8816 | 9.646% | 10.26% | 6.935% | 1.1068 | 1.1144 | 1.0745
2010-10-08 | 18 | 29.9054 | 12.0151 | 41.9205 | 3.0569 | 0.76558 | 0.31164 | 4.1342 | 9.862% | 10.49% | 7.091% | 1.1094 | 1.1172 | 1.0763
2010-10-08 | 19 | 30.0613 | 11.9229 | 41.9843 | 3.0663 | 0.76558 | 0.31212 | 4.1439 | 9.87% | 10.5% | 7.097% | 1.1095 | 1.1173 | 1.0764
2010-10-08 | 20 | 29.6373 | 11.6864 | 41.3238 | 2.9705 | 0.76558 | 0.30721 | 4.0433 | 9.784% | 10.41% | 7.035% | 1.1085 | 1.1162 | 1.0757
2010-10-08 | 21 | 30.1654 | 11.5328 | 41.6983 | 3.0246 | 0.76558 | 0.30999 | 4.1002 | 9.833% | 10.46% | 7.07% | 1.1091 | 1.1168 | 1.0761
2010-10-08 | 22 | 29.4595 | 11.599 | 41.0585 | 2.9325 | 0.76558 | 0.30523 | 4.0033 | 9.75% | 10.37% | 7.01% | 1.108 | 1.1158 | 1.0754
2010-10-08 | 23 | 28.4614 | 11.318 | 39.7794 | 2.7527 | 0.76558 | 0.29572 | 3.814 | 9.588% | 10.2% | 6.894% | 1.106 | 1.1136 | 1.074
2010-10-08 | 24 | 27.2976 | 11.4258 | 38.7234 | 2.6085 | 0.76558 | 0.28787 | 3.6619 | 9.457% | 10.06% | 6.799% | 1.1044 | 1.1119 | 1.073
2010-10-08 | 25 | 26.4598 | 11.5124 | 37.9722 | 2.5082 | 0.76558 | 0.28229 | 3.5561 | 9.365% | 9.964% | 6.733% | 1.1033 | 1.1107 | 1.0722
2010-10-08 | 26 | 25.794 | 11.0934 | 36.8874 | 2.367 | 0.76558 | 0.27423 | 3.4068 | 9.236% | 9.827% | 6.64% | 1.1018 | 1.109 | 1.0711
2010-10-08 | 27 | 26.7283 | 11.2403 | 37.9686 | 2.5078 | 0.76558 | 0.28226 | 3.5556 | 9.365% | 9.964% | 6.733% | 1.1033 | 1.1107 | 1.0722
2010-10-08 | 28 | 26.8927 | 11.1319 | 38.0246 | 2.5152 | 0.76558 | 0.28268 | 3.5634 | 9.371% | 9.971% | 6.738% | 1.1034 | 1.1108 | 1.0722
2010-10-08 | 29 | 26.2973 | 10.6469 | 36.9442 | 2.3743 | 0.76558 | 0.27465 | 3.4145 | 9.242% | 9.834% | 6.645% | 1.1018 | 1.1091 | 1.0712
2010-10-08 | 30 | 25.3587 | 10.2909 | 35.6495 | 2.2108 | 0.76558 | 0.26502 | 3.2414 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-10-08 | 31 | 25.4065 | 10.2161 | 35.6226 | 2.2074 | 0.76558 | 0.26482 | 3.2378 | 9.089% | 9.671% | 6.535% | 1.1 | 1.1071 | 1.0699
2010-10-08 | 32 | 25.2886 | 9.9004 | 35.189 | 2.154 | 0.76558 | 0.2616 | 3.1812 | 9.04% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2010-10-08 | 33 | 25.2891 | 10.1783 | 35.4674 | 2.1882 | 0.76558 | 0.26367 | 3.2175 | 9.072% | 9.652% | 6.523% | 1.0998 | 1.1068 | 1.0698
2010-10-08 | 34 | 25.3637 | 10.3643 | 35.7281 | 2.2205 | 0.76558 | 0.26561 | 3.2517 | 9.101% | 9.684% | 6.544% | 1.1001 | 1.1072 | 1.07
2010-10-08 | 35 | 25.9496 | 11.0044 | 36.954 | 2.3755 | 0.76558 | 0.27472 | 3.4158 | 9.243% | 9.835% | 6.646% | 1.1018 | 1.1091 | 1.0712
2010-10-08 | 36 | 28.0842 | 11.5128 | 39.597 | 2.7275 | 0.76558 | 0.29437 | 3.7874 | 9.565% | 10.18% | 6.877% | 1.1058 | 1.1133 | 1.0739
2010-10-08 | 37 | 30.4385 | 11.7857 | 42.2242 | 3.1014 | 0.76558 | 0.3139 | 4.1809 | 9.902% | 10.54% | 7.119% | 1.1099 | 1.1178 | 1.0766
2010-10-08 | 38 | 31.6546 | 11.8199 | 43.4745 | 3.2878 | 0.76558 | 0.32319 | 4.3766 | 10.07% | 10.71% | 7.238% | 1.1119 | 1.12 | 1.078
2010-10-08 | 39 | 31.937 | 11.7821 | 43.7191 | 3.3249 | 0.76558 | 0.32501 | 4.4155 | 10.1% | 10.75% | 7.262% | 1.1123 | 1.1204 | 1.0783
2010-10-08 | 40 | 32.2293 | 11.6482 | 43.8775 | 3.349 | 0.76558 | 0.32619 | 4.4408 | 10.12% | 10.77% | 7.277% | 1.1126 | 1.1207 | 1.0785
2010-10-08 | 41 | 32.9098 | 11.5501 | 44.4599 | 3.4385 | 0.76558 | 0.33052 | 4.5346 | 10.2% | 10.85% | 7.333% | 1.1136 | 1.1217 | 1.0791
2010-10-08 | 42 | 32.6463 | 11.2817 | 43.9279 | 3.3567 | 0.76558 | 0.32657 | 4.4489 | 10.13% | 10.78% | 7.282% | 1.1127 | 1.1208 | 1.0785
2010-10-08 | 43 | 31.4106 | 10.9404 | 42.351 | 3.1201 | 0.76558 | 0.31484 | 4.2005 | 9.918% | 10.55% | 7.131% | 1.1101 | 1.118 | 1.0768
2010-10-08 | 44 | 30.1306 | 10.2168 | 40.3474 | 2.8318 | 0.76558 | 0.29995 | 3.8973 | 9.659% | 10.28% | 6.945% | 1.1069 | 1.1145 | 1.0746
2010-10-08 | 45 | 27.3808 | 9.1513 | 36.5322 | 2.3216 | 0.76558 | 0.27158 | 3.3588 | 9.194% | 9.782% | 6.61% | 1.1012 | 1.1084 | 1.0708
2010-10-08 | 46 | 24.851 | 8.1604 | 33.0114 | 1.8957 | 0.76558 | 0.24541 | 2.9067 | 8.805% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2010-10-08 | 47 | 23.7317 | 7.9131 | 31.6448 | 1.742 | 0.76558 | 0.23525 | 2.7428 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-08 | 48 | 23.5016 | 8.1108 | 31.6124 | 1.7384 | 0.76558 | 0.23501 | 2.739 | 8.664% | 9.219% | 6.23% | 1.0949 | 1.1015 | 1.0664
2010-10-09 | 1 | 21.7194 | 7.2874 | 29.0069 | 1.4636 | 0.76558 | 0.21564 | 2.4449 | 8.429% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-10-09 | 2 | 20.0106 | 6.7655 | 26.7761 | 1.2472 | 0.76558 | 0.19906 | 2.2118 | 8.26% | 8.789% | 5.939% | 1.09 | 1.0964 | 1.0631
2010-10-09 | 3 | 18.9819 | 6.4655 | 25.4474 | 1.1265 | 0.76558 | 0.18918 | 2.0812 | 8.179% | 8.702% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-10-09 | 4 | 18.4007 | 6.2465 | 24.6472 | 1.0567 | 0.76558 | 0.18323 | 2.0056 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-10-09 | 5 | 18.4446 | 6.1327 | 24.5773 | 1.0508 | 0.76558 | 0.18271 | 1.9991 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-10-09 | 6 | 18.2064 | 6.0595 | 24.2659 | 1.0243 | 0.76558 | 0.1804 | 1.9703 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-10-09 | 7 | 17.777 | 5.9634 | 23.7404 | 0.98042 | 0.76558 | 0.17649 | 1.9225 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-10-09 | 8 | 17.5911 | 5.9682 | 23.5593 | 0.96551 | 0.76558 | 0.17514 | 1.9062 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-10-09 | 9 | 17.649 | 5.9952 | 23.6442 | 0.97249 | 0.76558 | 0.17577 | 1.9138 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-10-09 | 10 | 17.7309 | 6.0727 | 23.8036 | 0.98565 | 0.76558 | 0.17696 | 1.9282 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-10-09 | 11 | 18.141 | 6.345 | 24.4859 | 1.043 | 0.76558 | 0.18203 | 1.9906 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-10-09 | 12 | 18.8949 | 6.6807 | 25.5756 | 1.1379 | 0.76558 | 0.19013 | 2.0936 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2010-10-09 | 13 | 20.5191 | 7.4405 | 27.9597 | 1.3599 | 0.76558 | 0.20786 | 2.3333 | 8.345% | 8.879% | 6% | 1.0911 | 1.0974 | 1.0638
2010-10-09 | 14 | 23.1451 | 8.6771 | 31.8221 | 1.7615 | 0.76558 | 0.23657 | 2.7637 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-10-09 | 15 | 26.9069 | 10.4117 | 37.3186 | 2.4226 | 0.76558 | 0.27743 | 3.4656 | 9.287% | 9.881% | 6.677% | 1.1024 | 1.1096 | 1.0715
2010-10-09 | 16 | 29.3066 | 11.4821 | 40.7887 | 2.8941 | 0.76558 | 0.30323 | 3.9629 | 9.716% | 10.34% | 6.986% | 1.1076 | 1.1153 | 1.0751
2010-10-09 | 17 | 31.5247 | 12.847 | 44.3717 | 3.4249 | 0.76558 | 0.32986 | 4.5203 | 10.19% | 10.84% | 7.325% | 1.1134 | 1.1216 | 1.079
2010-10-09 | 18 | 32.765 | 13.2774 | 46.0424 | 3.6877 | 0.76558 | 0.34228 | 4.7955 | 10.42% | 11.08% | 7.489% | 1.1163 | 1.1246 | 1.0809
2010-10-09 | 19 | 32.9674 | 12.9004 | 45.8678 | 3.6597 | 0.76558 | 0.34099 | 4.7663 | 10.39% | 11.06% | 7.471% | 1.116 | 1.1243 | 1.0807
2010-10-09 | 20 | 32.469 | 12.5942 | 45.0632 | 3.5325 | 0.76558 | 0.33501 | 4.633 | 10.28% | 10.94% | 7.392% | 1.1146 | 1.1228 | 1.0798
2010-10-09 | 21 | 34.1327 | 12.5918 | 46.7245 | 3.7977 | 0.76558 | 0.34736 | 4.9107 | 10.51% | 11.18% | 7.557% | 1.1174 | 1.1259 | 1.0817
2010-10-09 | 22 | 33.6836 | 12.3997 | 46.0833 | 3.6942 | 0.76558 | 0.34259 | 4.8024 | 10.42% | 11.09% | 7.493% | 1.1163 | 1.1247 | 1.081
2010-10-09 | 23 | 32.6972 | 11.9454 | 44.6426 | 3.4668 | 0.76558 | 0.33188 | 4.5643 | 10.22% | 10.88% | 7.351% | 1.1139 | 1.1221 | 1.0793
2010-10-09 | 24 | 31.7845 | 11.9537 | 43.7382 | 3.3278 | 0.76558 | 0.32515 | 4.4185 | 10.1% | 10.75% | 7.263% | 1.1124 | 1.1204 | 1.0783
2010-10-09 | 25 | 30.7423 | 11.8008 | 42.5431 | 3.1484 | 0.76558 | 0.31627 | 4.2303 | 9.943% | 10.58% | 7.149% | 1.1104 | 1.1183 | 1.077
2010-10-09 | 26 | 29.7107 | 10.8521 | 40.5627 | 2.8621 | 0.76558 | 0.30155 | 3.9293 | 9.687% | 10.31% | 6.965% | 1.1073 | 1.1149 | 1.0749
2010-10-09 | 27 | 29.4743 | 10.8581 | 40.3324 | 2.8297 | 0.76558 | 0.29984 | 3.8951 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-10-09 | 28 | 29.335 | 10.5335 | 39.8686 | 2.765 | 0.76558 | 0.29639 | 3.827 | 9.599% | 10.21% | 6.902% | 1.1062 | 1.1138 | 1.0741
2010-10-09 | 29 | 28.6517 | 9.9819 | 38.6337 | 2.5964 | 0.76558 | 0.28721 | 3.6492 | 9.446% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-10-09 | 30 | 27.9638 | 9.856 | 37.8198 | 2.4881 | 0.76558 | 0.28116 | 3.5349 | 9.347% | 9.945% | 6.72% | 1.1031 | 1.1104 | 1.072
2010-10-09 | 31 | 28.8537 | 9.7257 | 38.5794 | 2.5891 | 0.76558 | 0.2868 | 3.6415 | 9.439% | 10.04% | 6.787% | 1.1042 | 1.1116 | 1.0728
2010-10-09 | 32 | 28.6727 | 9.7467 | 38.4194 | 2.5676 | 0.76558 | 0.28561 | 3.6188 | 9.419% | 10.02% | 6.772% | 1.104 | 1.1114 | 1.0726
2010-10-09 | 33 | 28.3715 | 10.0252 | 38.3967 | 2.5646 | 0.76558 | 0.28545 | 3.6156 | 9.417% | 10.02% | 6.77% | 1.104 | 1.1113 | 1.0726
2010-10-09 | 34 | 28.4141 | 10.1483 | 38.5624 | 2.5868 | 0.76558 | 0.28668 | 3.6391 | 9.437% | 10.04% | 6.785% | 1.1042 | 1.1116 | 1.0728
2010-10-09 | 35 | 28.1289 | 10.2237 | 38.3526 | 2.5587 | 0.76558 | 0.28512 | 3.6094 | 9.411% | 10.01% | 6.767% | 1.1039 | 1.1113 | 1.0726
2010-10-09 | 36 | 28.7514 | 10.7064 | 39.4578 | 2.7083 | 0.76558 | 0.29333 | 3.7672 | 9.548% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2010-10-09 | 37 | 29.8234 | 10.8221 | 40.6455 | 2.8738 | 0.76558 | 0.30216 | 3.9416 | 9.697% | 10.32% | 6.972% | 1.1074 | 1.1151 | 1.075
2010-10-09 | 38 | 31.1337 | 10.6458 | 41.7795 | 3.0364 | 0.76558 | 0.31059 | 4.1126 | 9.844% | 10.47% | 7.078% | 1.1092 | 1.117 | 1.0762
2010-10-09 | 39 | 31.372 | 10.8355 | 42.2075 | 3.099 | 0.76558 | 0.31378 | 4.1783 | 9.899% | 10.53% | 7.118% | 1.1099 | 1.1177 | 1.0766
2010-10-09 | 40 | 31.6702 | 10.996 | 42.6662 | 3.1667 | 0.76558 | 0.31719 | 4.2494 | 9.96% | 10.6% | 7.161% | 1.1106 | 1.1185 | 1.0771
2010-10-09 | 41 | 32.8718 | 11.2732 | 44.1451 | 3.39 | 0.76558 | 0.32818 | 4.4838 | 10.16% | 10.81% | 7.303% | 1.1131 | 1.1212 | 1.0788
2010-10-09 | 42 | 33.4665 | 11.0196 | 44.4861 | 3.4426 | 0.76558 | 0.33071 | 4.5389 | 10.2% | 10.86% | 7.336% | 1.1136 | 1.1218 | 1.0792
2010-10-09 | 43 | 32.9362 | 10.6838 | 43.62 | 3.3098 | 0.76558 | 0.32428 | 4.3997 | 10.09% | 10.73% | 7.252% | 1.1122 | 1.1202 | 1.0782
2010-10-09 | 44 | 31.4825 | 10.071 | 41.5535 | 3.0037 | 0.76558 | 0.30891 | 4.0781 | 9.814% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-10-09 | 45 | 29.2643 | 9.3137 | 38.578 | 2.5889 | 0.76558 | 0.28679 | 3.6413 | 9.439% | 10.04% | 6.786% | 1.1042 | 1.1116 | 1.0728
2010-10-09 | 46 | 26.8635 | 8.4844 | 35.3479 | 2.1735 | 0.76558 | 0.26278 | 3.2019 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-10-09 | 47 | 25.8621 | 8.2404 | 34.1024 | 2.023 | 0.76558 | 0.25352 | 3.0421 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2010-10-09 | 48 | 25.8133 | 8.4734 | 34.2868 | 2.045 | 0.76558 | 0.25489 | 3.0654 | 8.941% | 9.513% | 6.428% | 1.0982 | 1.1051 | 1.0687
2010-10-10 | 1 | 23.8739 | 7.4843 | 31.3581 | 1.7105 | 0.76558 | 0.23312 | 2.7092 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-10-10 | 2 | 22.4102 | 7.0279 | 29.4381 | 1.5075 | 0.76558 | 0.21885 | 2.4919 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-10-10 | 3 | 21.448 | 6.7737 | 28.2217 | 1.3855 | 0.76558 | 0.2098 | 2.3609 | 8.365% | 8.901% | 6.015% | 1.0913 | 1.0977 | 1.064
2010-10-10 | 4 | 20.9887 | 6.3319 | 27.3206 | 1.2984 | 0.76558 | 0.2031 | 2.2671 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-10-10 | 5 | 20.1529 | 6.1798 | 26.3327 | 1.2062 | 0.76558 | 0.19576 | 2.1676 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2010-10-10 | 6 | 19.7957 | 5.9984 | 25.7941 | 1.1574 | 0.76558 | 0.19176 | 2.1147 | 8.198% | 8.723% | 5.895% | 1.0893 | 1.0956 | 1.0626
2010-10-10 | 7 | 19.5221 | 5.9989 | 25.521 | 1.133 | 0.76558 | 0.18973 | 2.0883 | 8.183% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-10-10 | 8 | 19.2004 | 5.9838 | 25.1841 | 1.1033 | 0.76558 | 0.18722 | 2.0561 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-10-10 | 9 | 19.3761 | 5.9195 | 25.2956 | 1.1131 | 0.76558 | 0.18805 | 2.0667 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-10-10 | 10 | 19.5038 | 5.894 | 25.3978 | 1.1221 | 0.76558 | 0.18881 | 2.0765 | 8.176% | 8.699% | 5.878% | 1.089 | 1.0953 | 1.0625
2010-10-10 | 11 | 19.9554 | 6.064 | 26.0195 | 1.1777 | 0.76558 | 0.19343 | 2.1367 | 8.212% | 8.737% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-10-10 | 12 | 20.2873 | 6.4801 | 26.7674 | 1.2464 | 0.76558 | 0.19899 | 2.2109 | 8.26% | 8.788% | 5.939% | 1.09 | 1.0964 | 1.0631
2010-10-10 | 13 | 21.4074 | 7.1837 | 28.5911 | 1.422 | 0.76558 | 0.21255 | 2.4001 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-10-10 | 14 | 22.5994 | 7.7524 | 30.3517 | 1.6025 | 0.76558 | 0.22564 | 2.5937 | 8.546% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-10-10 | 15 | 24.2318 | 8.8892 | 33.121 | 1.9083 | 0.76558 | 0.24623 | 2.9201 | 8.816% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-10-10 | 16 | 25.3898 | 9.8396 | 35.2294 | 2.159 | 0.76558 | 0.2619 | 3.1864 | 9.045% | 9.624% | 6.503% | 1.0994 | 1.1065 | 1.0696
2010-10-10 | 17 | 27.6334 | 10.7041 | 38.3375 | 2.5567 | 0.76558 | 0.28501 | 3.6073 | 9.409% | 10.01% | 6.765% | 1.1039 | 1.1113 | 1.0726
2010-10-10 | 18 | 29.8239 | 11.2559 | 41.0798 | 2.9356 | 0.76558 | 0.30539 | 4.0065 | 9.753% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-10-10 | 19 | 31.4197 | 12.2091 | 43.6288 | 3.3112 | 0.76558 | 0.32434 | 4.4011 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2010-10-10 | 20 | 31.9982 | 12.4619 | 44.4601 | 3.4386 | 0.76558 | 0.33052 | 4.5347 | 10.2% | 10.85% | 7.333% | 1.1136 | 1.1217 | 1.0791
2010-10-10 | 21 | 33.1037 | 12.0834 | 45.1871 | 3.5519 | 0.76558 | 0.33593 | 4.6534 | 10.3% | 10.96% | 7.404% | 1.1148 | 1.1231 | 1.08
2010-10-10 | 22 | 32.1703 | 11.499 | 43.6693 | 3.3173 | 0.76558 | 0.32464 | 4.4075 | 10.09% | 10.74% | 7.257% | 1.1123 | 1.1203 | 1.0782
2010-10-10 | 23 | 30.8284 | 10.6851 | 41.5134 | 2.9979 | 0.76558 | 0.30862 | 4.0721 | 9.809% | 10.44% | 7.053% | 1.1088 | 1.1165 | 1.0759
2010-10-10 | 24 | 29.624 | 10.3166 | 39.9406 | 2.775 | 0.76558 | 0.29692 | 3.8375 | 9.608% | 10.22% | 6.908% | 1.1063 | 1.1139 | 1.0742
2010-10-10 | 25 | 27.3763 | 9.8235 | 37.1999 | 2.4072 | 0.76558 | 0.27655 | 3.4494 | 9.272% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-10-10 | 26 | 26.0045 | 9.1013 | 35.1058 | 2.1438 | 0.76558 | 0.26098 | 3.1704 | 9.031% | 9.609% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-10-10 | 27 | 25.602 | 9.1784 | 34.7804 | 2.1043 | 0.76558 | 0.25856 | 3.1284 | 8.995% | 9.57% | 6.467% | 1.0988 | 1.1058 | 1.0691
2010-10-10 | 28 | 25.0155 | 8.8557 | 33.8711 | 1.9957 | 0.76558 | 0.2518 | 3.0131 | 8.896% | 9.465% | 6.396% | 1.0976 | 1.1045 | 1.0683
2010-10-10 | 29 | 24.0158 | 8.276 | 32.2919 | 1.8139 | 0.76558 | 0.24006 | 2.8196 | 8.732% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-10-10 | 30 | 23.6672 | 7.9089 | 31.5761 | 1.7344 | 0.76558 | 0.23474 | 2.7347 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-10-10 | 31 | 24.3649 | 7.8991 | 32.264 | 1.8108 | 0.76558 | 0.23985 | 2.8162 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-10-10 | 32 | 24.3437 | 7.7857 | 32.1294 | 1.7957 | 0.76558 | 0.23885 | 2.8002 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2010-10-10 | 33 | 24.0576 | 8.0079 | 32.0654 | 1.7886 | 0.76558 | 0.23838 | 2.7925 | 8.709% | 9.266% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-10-10 | 34 | 24.677 | 8.1524 | 32.8294 | 1.8748 | 0.76558 | 0.24406 | 2.8845 | 8.786% | 9.349% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-10-10 | 35 | 24.6389 | 8.468 | 33.1069 | 1.9067 | 0.76558 | 0.24612 | 2.9183 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-10-10 | 36 | 25.5393 | 9.1256 | 34.6649 | 2.0903 | 0.76558 | 0.2577 | 3.1136 | 8.982% | 9.557% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-10-10 | 37 | 26.7849 | 9.5342 | 36.3191 | 2.2946 | 0.76558 | 0.27 | 3.3302 | 9.169% | 9.756% | 6.593% | 1.1009 | 1.1081 | 1.0706
2010-10-10 | 38 | 27.407 | 9.5436 | 36.9507 | 2.3751 | 0.76558 | 0.2747 | 3.4154 | 9.243% | 9.835% | 6.646% | 1.1018 | 1.1091 | 1.0712
2010-10-10 | 39 | 27.7271 | 9.5245 | 37.2517 | 2.4139 | 0.76558 | 0.27693 | 3.4564 | 9.279% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-10-10 | 40 | 28.0795 | 9.8243 | 37.9038 | 2.4992 | 0.76558 | 0.28178 | 3.5466 | 9.357% | 9.956% | 6.727% | 1.1032 | 1.1106 | 1.0721
2010-10-10 | 41 | 29.5292 | 9.9052 | 39.4343 | 2.7051 | 0.76558 | 0.29316 | 3.7638 | 9.545% | 10.16% | 6.863% | 1.1055 | 1.113 | 1.0737
2010-10-10 | 42 | 30.0531 | 9.7924 | 39.8454 | 2.7618 | 0.76558 | 0.29622 | 3.8236 | 9.596% | 10.21% | 6.9% | 1.1061 | 1.1137 | 1.0741
2010-10-10 | 43 | 29.057 | 9.5037 | 38.5607 | 2.5866 | 0.76558 | 0.28666 | 3.6388 | 9.437% | 10.04% | 6.785% | 1.1042 | 1.1116 | 1.0728
2010-10-10 | 44 | 27.9209 | 8.9981 | 36.9191 | 2.371 | 0.76558 | 0.27446 | 3.4111 | 9.239% | 9.831% | 6.643% | 1.1018 | 1.109 | 1.0712
2010-10-10 | 45 | 26.1113 | 8.3948 | 34.5061 | 2.0712 | 0.76558 | 0.25652 | 3.0933 | 8.965% | 9.538% | 6.446% | 1.0985 | 1.1054 | 1.0689
2010-10-10 | 46 | 24.1537 | 7.8452 | 31.9988 | 1.7812 | 0.76558 | 0.23788 | 2.7846 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2010-10-10 | 47 | 23.3878 | 7.7474 | 31.1352 | 1.6863 | 0.76558 | 0.23146 | 2.6834 | 8.618% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-10-10 | 48 | 23.5958 | 8.0534 | 31.6492 | 1.7424 | 0.76558 | 0.23528 | 2.7433 | 8.668% | 9.223% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-11 | 1 | 21.7659 | 7.1853 | 28.9512 | 1.458 | 0.76558 | 0.21523 | 2.4388 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-10-11 | 2 | 20.522 | 6.5678 | 27.0898 | 1.2766 | 0.76558 | 0.20139 | 2.2435 | 8.282% | 8.812% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-10-11 | 3 | 19.562 | 6.2986 | 25.8606 | 1.1634 | 0.76558 | 0.19225 | 2.1212 | 8.202% | 8.727% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-10-11 | 4 | 19.0415 | 6.0976 | 25.1391 | 1.0993 | 0.76558 | 0.18689 | 2.0518 | 8.162% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-10-11 | 5 | 18.5695 | 6.0562 | 24.6258 | 1.0549 | 0.76558 | 0.18307 | 2.0036 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-10-11 | 6 | 18.2739 | 6.4696 | 24.7435 | 1.065 | 0.76558 | 0.18395 | 2.0145 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2010-10-11 | 7 | 17.9524 | 7.022 | 24.9744 | 1.085 | 0.76558 | 0.18566 | 2.0362 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-10-11 | 8 | 17.9664 | 7.7733 | 25.7397 | 1.1525 | 0.76558 | 0.19135 | 2.1094 | 8.195% | 8.72% | 5.892% | 1.0893 | 1.0955 | 1.0626
2010-10-11 | 9 | 18.0126 | 8.4696 | 26.4822 | 1.22 | 0.76558 | 0.19687 | 2.1824 | 8.241% | 8.768% | 5.925% | 1.0898 | 1.0961 | 1.063
2010-10-11 | 10 | 18.2448 | 8.6742 | 26.919 | 1.2605 | 0.76558 | 0.20012 | 2.2262 | 8.27% | 8.799% | 5.946% | 1.0902 | 1.0965 | 1.0632
2010-10-11 | 11 | 18.8468 | 8.8831 | 27.7298 | 1.3376 | 0.76558 | 0.20615 | 2.3093 | 8.328% | 8.861% | 5.988% | 1.0908 | 1.0972 | 1.0637
2010-10-11 | 12 | 19.0412 | 9.0217 | 28.0629 | 1.3699 | 0.76558 | 0.20862 | 2.3441 | 8.353% | 8.888% | 6.006% | 1.0911 | 1.0975 | 1.0639
2010-10-11 | 13 | 20.0996 | 9.4778 | 29.5774 | 1.5218 | 0.76558 | 0.21988 | 2.5072 | 8.477% | 9.019% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-10-11 | 14 | 20.9178 | 9.983 | 30.9008 | 1.661 | 0.76558 | 0.22972 | 2.6563 | 8.596% | 9.146% | 6.181% | 1.094 | 1.1007 | 1.0659
2010-10-11 | 15 | 22.142 | 10.7378 | 32.8798 | 1.8806 | 0.76558 | 0.24443 | 2.8906 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-10-11 | 16 | 23.1782 | 11.2946 | 34.4728 | 2.0672 | 0.76558 | 0.25627 | 3.0891 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-10-11 | 17 | 25.0825 | 11.1035 | 36.186 | 2.2778 | 0.76558 | 0.26901 | 3.3124 | 9.154% | 9.74% | 6.582% | 1.1008 | 1.1079 | 1.0705
2010-10-11 | 18 | 26.6178 | 10.7249 | 37.3427 | 2.4257 | 0.76558 | 0.27761 | 3.4689 | 9.289% | 9.884% | 6.679% | 1.1024 | 1.1097 | 1.0716
2010-10-11 | 19 | 27.8081 | 10.6526 | 38.4607 | 2.5732 | 0.76558 | 0.28592 | 3.6247 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1115 | 1.0727
2010-10-11 | 20 | 28.0166 | 10.9109 | 38.9275 | 2.636 | 0.76558 | 0.28939 | 3.691 | 9.482% | 10.09% | 6.817% | 1.1047 | 1.1122 | 1.0732
2010-10-11 | 21 | 29.1345 | 10.7231 | 39.8576 | 2.7635 | 0.76558 | 0.29631 | 3.8254 | 9.598% | 10.21% | 6.901% | 1.1062 | 1.1137 | 1.0741
2010-10-11 | 22 | 28.5603 | 10.5881 | 39.1484 | 2.666 | 0.76558 | 0.29103 | 3.7226 | 9.509% | 10.12% | 6.837% | 1.1051 | 1.1126 | 1.0734
2010-10-11 | 23 | 27.4366 | 10.1607 | 37.5973 | 2.4589 | 0.76558 | 0.2795 | 3.504 | 9.32% | 9.916% | 6.701% | 1.1028 | 1.1101 | 1.0718
2010-10-11 | 24 | 26.3765 | 9.7895 | 36.166 | 2.2753 | 0.76558 | 0.26886 | 3.3097 | 9.151% | 9.737% | 6.58% | 1.1007 | 1.1079 | 1.0704
2010-10-11 | 25 | 24.6297 | 9.4789 | 34.1086 | 2.0238 | 0.76558 | 0.25357 | 3.0429 | 8.921% | 9.492% | 6.414% | 1.098 | 1.1049 | 1.0685
2010-10-11 | 26 | 23.1599 | 8.9651 | 32.1249 | 1.7952 | 0.76558 | 0.23882 | 2.7996 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0668
2010-10-11 | 27 | 22.6812 | 9.1279 | 31.8091 | 1.7601 | 0.76558 | 0.23647 | 2.7622 | 8.684% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-10-11 | 28 | 22.6493 | 8.9543 | 31.6036 | 1.7374 | 0.76558 | 0.23494 | 2.738 | 8.663% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-10-11 | 29 | 21.8066 | 8.5918 | 30.3984 | 1.6074 | 0.76558 | 0.22599 | 2.599 | 8.55% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-10-11 | 30 | 21.1654 | 8.3269 | 29.4923 | 1.513 | 0.76558 | 0.21925 | 2.4979 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-10-11 | 31 | 21.498 | 8.2114 | 29.7094 | 1.5354 | 0.76558 | 0.22086 | 2.5218 | 8.488% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-10-11 | 32 | 21.1391 | 8.0307 | 29.1698 | 1.4801 | 0.76558 | 0.21685 | 2.4626 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-10-11 | 33 | 20.7628 | 8.1549 | 28.9177 | 1.4547 | 0.76558 | 0.21498 | 2.4352 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0645
2010-10-11 | 34 | 20.8542 | 8.058 | 28.9122 | 1.4541 | 0.76558 | 0.21494 | 2.4346 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0644
2010-10-11 | 35 | 20.877 | 8.5862 | 29.4632 | 1.5101 | 0.76558 | 0.21903 | 2.4947 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-10-11 | 36 | 21.4397 | 9.1226 | 30.5623 | 1.6248 | 0.76558 | 0.2272 | 2.6176 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-10-11 | 37 | 22.5689 | 9.0951 | 31.664 | 1.7441 | 0.76558 | 0.23539 | 2.745 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2010-10-11 | 38 | 23.5201 | 9.2114 | 32.7315 | 1.8637 | 0.76558 | 0.24333 | 2.8726 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-10-11 | 39 | 24.124 | 9.1697 | 33.2937 | 1.9282 | 0.76558 | 0.24751 | 2.9413 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-10-11 | 40 | 24.6244 | 9.402 | 34.0263 | 2.014 | 0.76558 | 0.25296 | 3.0326 | 8.912% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-10-11 | 41 | 26.0403 | 9.9208 | 35.9612 | 2.2496 | 0.76558 | 0.26734 | 3.2825 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2010-10-11 | 42 | 26.814 | 10.2381 | 37.0521 | 2.3881 | 0.76558 | 0.27545 | 3.4292 | 9.255% | 9.847% | 6.654% | 1.102 | 1.1092 | 1.0713
2010-10-11 | 43 | 26.2026 | 9.6724 | 35.875 | 2.2388 | 0.76558 | 0.2667 | 3.2711 | 9.118% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-10-11 | 44 | 25.0006 | 8.7886 | 33.7892 | 1.986 | 0.76558 | 0.25119 | 3.0028 | 8.887% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2010-10-11 | 45 | 22.9266 | 8.1464 | 31.073 | 1.6796 | 0.76558 | 0.231 | 2.6762 | 8.612% | 9.164% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-10-11 | 46 | 21.0433 | 7.3038 | 28.3471 | 1.3978 | 0.76558 | 0.21074 | 2.3741 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-10-11 | 47 | 20.3223 | 7.0661 | 27.3885 | 1.3049 | 0.76558 | 0.20361 | 2.2741 | 8.303% | 8.834% | 5.97% | 1.0905 | 1.0969 | 1.0635
2010-10-11 | 48 | 20.1264 | 7.1877 | 27.3141 | 1.2978 | 0.76558 | 0.20306 | 2.2664 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-10-12 | 1 | 18.4686 | 6.4946 | 24.9631 | 1.084 | 0.76558 | 0.18558 | 2.0352 | 8.153% | 8.674% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-10-12 | 2 | 17.3055 | 6.0715 | 23.377 | 0.95063 | 0.76558 | 0.17379 | 1.89 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-10-12 | 3 | 16.66 | 5.7613 | 22.4213 | 0.8745 | 0.76558 | 0.16668 | 1.8068 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-12 | 4 | 15.9264 | 5.68 | 21.6063 | 0.81208 | 0.76558 | 0.16062 | 1.7383 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-12 | 5 | 15.4504 | 5.667 | 21.1174 | 0.77574 | 0.76558 | 0.15699 | 1.6983 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-12 | 6 | 15.195 | 6.4607 | 21.6558 | 0.8158 | 0.76558 | 0.16099 | 1.7424 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-12 | 7 | 15.2256 | 7.9745 | 23.2001 | 0.9363 | 0.76558 | 0.17247 | 1.8744 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-10-12 | 8 | 15.5043 | 9.1239 | 24.6282 | 1.0551 | 0.76558 | 0.18309 | 2.0038 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-10-12 | 9 | 15.66 | 9.9954 | 25.6553 | 1.145 | 0.76558 | 0.19072 | 2.1013 | 8.19% | 8.715% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-10-12 | 10 | 15.9623 | 10.4348 | 26.3971 | 1.2121 | 0.76558 | 0.19624 | 2.1739 | 8.236% | 8.763% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-10-12 | 11 | 16.4138 | 10.7921 | 27.2059 | 1.2875 | 0.76558 | 0.20225 | 2.2554 | 8.29% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2010-10-12 | 12 | 16.8083 | 11.3756 | 28.1839 | 1.3818 | 0.76558 | 0.20952 | 2.3569 | 8.362% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-10-12 | 13 | 18.5202 | 12.3124 | 30.8325 | 1.6537 | 0.76558 | 0.22921 | 2.6485 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-10-12 | 14 | 20.8206 | 13.9498 | 34.7703 | 2.1031 | 0.76558 | 0.25849 | 3.1271 | 8.994% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-10-12 | 15 | 25.4009 | 16.2952 | 41.6961 | 3.0243 | 0.76558 | 0.30997 | 4.0999 | 9.833% | 10.46% | 7.07% | 1.109 | 1.1168 | 1.0761
2010-10-12 | 16 | 28.1928 | 16.3887 | 44.5815 | 3.4574 | 0.76558 | 0.33142 | 4.5544 | 10.22% | 10.87% | 7.345% | 1.1138 | 1.122 | 1.0793
2010-10-12 | 17 | 29.2828 | 16.1265 | 45.4092 | 3.5869 | 0.76558 | 0.33758 | 4.6901 | 10.33% | 10.99% | 7.426% | 1.1152 | 1.1235 | 1.0802
2010-10-12 | 18 | 29.2706 | 14.4121 | 43.6827 | 3.3194 | 0.76558 | 0.32474 | 4.4097 | 10.09% | 10.74% | 7.258% | 1.1123 | 1.1203 | 1.0783
2010-10-12 | 19 | 28.5268 | 13.0827 | 41.6095 | 3.0118 | 0.76558 | 0.30933 | 4.0867 | 9.821% | 10.45% | 7.062% | 1.1089 | 1.1167 | 1.076
2010-10-12 | 20 | 27.5681 | 12.1929 | 39.761 | 2.7501 | 0.76558 | 0.29559 | 3.8113 | 9.585% | 10.2% | 6.892% | 1.106 | 1.1136 | 1.074
2010-10-12 | 21 | 27.5252 | 11.4938 | 39.019 | 2.6484 | 0.76558 | 0.29007 | 3.7041 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-10-12 | 22 | 26.4684 | 11.1505 | 37.6189 | 2.4618 | 0.76558 | 0.27966 | 3.507 | 9.322% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2010-10-12 | 23 | 25.2383 | 10.2868 | 35.5251 | 2.1954 | 0.76558 | 0.2641 | 3.225 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-10-12 | 24 | 24.0995 | 10.0153 | 34.1147 | 2.0245 | 0.76558 | 0.25361 | 3.0437 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-10-12 | 25 | 23.1614 | 9.6977 | 32.8591 | 1.8782 | 0.76558 | 0.24428 | 2.8881 | 8.789% | 9.352% | 6.319% | 1.0964 | 1.1032 | 1.0675
2010-10-12 | 26 | 22.5419 | 9.1464 | 31.6883 | 1.7468 | 0.76558 | 0.23557 | 2.7479 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2010-10-12 | 27 | 22.4128 | 9.3175 | 31.7303 | 1.7514 | 0.76558 | 0.23589 | 2.7529 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-10-12 | 28 | 22.0824 | 9.4837 | 31.5661 | 1.7333 | 0.76558 | 0.23467 | 2.7336 | 8.66% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-10-12 | 29 | 21.508 | 9.3357 | 30.8437 | 1.6549 | 0.76558 | 0.2293 | 2.6498 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-10-12 | 30 | 21.0262 | 9.1351 | 30.1613 | 1.5825 | 0.76558 | 0.22422 | 2.5723 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-10-12 | 31 | 21.3937 | 9.0274 | 30.4211 | 1.6099 | 0.76558 | 0.22615 | 2.6016 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-10-12 | 32 | 21.4317 | 8.9261 | 30.3578 | 1.6032 | 0.76558 | 0.22568 | 2.5944 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2010-10-12 | 33 | 21.3788 | 9.2696 | 30.6484 | 1.634 | 0.76558 | 0.22784 | 2.6274 | 8.573% | 9.121% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-10-12 | 34 | 21.2775 | 9.1779 | 30.4554 | 1.6135 | 0.76558 | 0.22641 | 2.6055 | 8.555% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2010-10-12 | 35 | 21.207 | 9.4505 | 30.6576 | 1.635 | 0.76558 | 0.22791 | 2.6285 | 8.574% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-10-12 | 36 | 22.0683 | 10.0322 | 32.1006 | 1.7925 | 0.76558 | 0.23864 | 2.7967 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-10-12 | 37 | 22.7817 | 10.4349 | 33.2166 | 1.9193 | 0.76558 | 0.24694 | 2.9318 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-10-12 | 38 | 23.6317 | 10.0795 | 33.7112 | 1.9769 | 0.76558 | 0.25061 | 2.9931 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-10-12 | 39 | 23.9666 | 9.9356 | 33.9022 | 1.9994 | 0.76558 | 0.25203 | 3.017 | 8.899% | 9.469% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-10-12 | 40 | 24.6788 | 9.9847 | 34.6635 | 2.0902 | 0.76558 | 0.25769 | 3.1134 | 8.982% | 9.557% | 6.458% | 1.0987 | 1.1057 | 1.069
2010-10-12 | 41 | 26.3411 | 10.2518 | 36.5929 | 2.3293 | 0.76558 | 0.27204 | 3.3669 | 9.201% | 9.79% | 6.616% | 1.1013 | 1.1085 | 1.0708
2010-10-12 | 42 | 27.166 | 10.1999 | 37.3659 | 2.4288 | 0.76558 | 0.27778 | 3.4721 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-10-12 | 43 | 26.3135 | 9.8685 | 36.182 | 2.2773 | 0.76558 | 0.26898 | 3.3119 | 9.153% | 9.739% | 6.581% | 1.1008 | 1.1079 | 1.0704
2010-10-12 | 44 | 25.1266 | 9.3201 | 34.4467 | 2.0641 | 0.76558 | 0.25608 | 3.0858 | 8.958% | 9.531% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-10-12 | 45 | 23.1741 | 8.3639 | 31.5381 | 1.7302 | 0.76558 | 0.23446 | 2.7303 | 8.657% | 9.211% | 6.224% | 1.0948 | 1.1015 | 1.0664
2010-10-12 | 46 | 20.97 | 7.5817 | 28.5517 | 1.4181 | 0.76558 | 0.21226 | 2.3959 | 8.391% | 8.929% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-10-12 | 47 | 20.1257 | 7.3851 | 27.5107 | 1.3166 | 0.76558 | 0.20452 | 2.2866 | 8.312% | 8.844% | 5.976% | 1.0907 | 1.097 | 1.0636
2010-10-12 | 48 | 19.4904 | 7.4416 | 26.932 | 1.2617 | 0.76558 | 0.20022 | 2.2275 | 8.271% | 8.8% | 5.947% | 1.0902 | 1.0965 | 1.0632
2010-10-13 | 1 | 17.9162 | 6.5777 | 24.494 | 1.0436 | 0.76558 | 0.18209 | 1.9913 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-10-13 | 2 | 16.6777 | 6.1345 | 22.8122 | 0.90525 | 0.76558 | 0.16959 | 1.8404 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-10-13 | 3 | 15.9226 | 5.8624 | 21.785 | 0.82557 | 0.76558 | 0.16195 | 1.7531 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-13 | 4 | 15.3386 | 5.7369 | 21.0755 | 0.77266 | 0.76558 | 0.15668 | 1.6949 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-13 | 5 | 14.7815 | 5.6625 | 20.444 | 0.72706 | 0.76558 | 0.15198 | 1.6446 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-13 | 6 | 14.3572 | 5.6021 | 19.9593 | 0.69299 | 0.76558 | 0.14838 | 1.6069 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-10-13 | 7 | 14.2073 | 5.4331 | 19.6404 | 0.67102 | 0.76558 | 0.14601 | 1.5826 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-13 | 8 | 14.3269 | 5.4286 | 19.7554 | 0.6789 | 0.76558 | 0.14686 | 1.5913 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-10-13 | 9 | 14.6186 | 5.5054 | 20.124 | 0.70447 | 0.76558 | 0.1496 | 1.6197 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-13 | 10 | 14.9439 | 5.5052 | 20.4492 | 0.72742 | 0.76558 | 0.15202 | 1.645 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-13 | 11 | 15.383 | 5.6986 | 21.0816 | 0.77311 | 0.76558 | 0.15672 | 1.6954 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-13 | 12 | 16.0551 | 6.0961 | 22.1512 | 0.85355 | 0.76558 | 0.16467 | 1.7838 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-13 | 13 | 17.6203 | 6.9385 | 24.5588 | 1.0492 | 0.76558 | 0.18257 | 1.9973 | 8.133% | 8.653% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-10-13 | 14 | 20.1669 | 8.0431 | 28.21 | 1.3843 | 0.76558 | 0.20972 | 2.3596 | 8.365% | 8.9% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-10-13 | 15 | 24.5356 | 10.1033 | 34.6389 | 2.0872 | 0.76558 | 0.25751 | 3.1103 | 8.979% | 9.554% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-10-13 | 16 | 27.0014 | 11.4409 | 38.4423 | 2.5707 | 0.76558 | 0.28578 | 3.6221 | 9.422% | 10.03% | 6.774% | 1.104 | 1.1114 | 1.0727
2010-10-13 | 17 | 27.8036 | 12.0852 | 39.8889 | 2.7678 | 0.76558 | 0.29654 | 3.8299 | 9.602% | 10.22% | 6.903% | 1.1062 | 1.1138 | 1.0742
2010-10-13 | 18 | 28.2431 | 12.3293 | 40.5725 | 2.8635 | 0.76558 | 0.30162 | 3.9307 | 9.688% | 10.31% | 6.966% | 1.1073 | 1.1149 | 1.0749
2010-10-13 | 19 | 28.0423 | 12.0557 | 40.098 | 2.7969 | 0.76558 | 0.29809 | 3.8606 | 9.628% | 10.24% | 6.922% | 1.1065 | 1.1141 | 1.0744
2010-10-13 | 20 | 26.8564 | 11.4769 | 38.3333 | 2.5561 | 0.76558 | 0.28497 | 3.6067 | 9.409% | 10.01% | 6.765% | 1.1039 | 1.1112 | 1.0726
2010-10-13 | 21 | 26.3871 | 10.8759 | 37.263 | 2.4154 | 0.76558 | 0.27702 | 3.458 | 9.28% | 9.874% | 6.672% | 1.1023 | 1.1096 | 1.0715
2010-10-13 | 22 | 25.5607 | 10.7291 | 36.2898 | 2.2909 | 0.76558 | 0.26978 | 3.3263 | 9.166% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0706
2010-10-13 | 23 | 24.3277 | 10.2289 | 34.5565 | 2.0773 | 0.76558 | 0.2569 | 3.0998 | 8.97% | 9.544% | 6.45% | 1.0985 | 1.1055 | 1.0689
2010-10-13 | 24 | 23.6478 | 10.1416 | 33.7893 | 1.9861 | 0.76558 | 0.25119 | 3.0028 | 8.887% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2010-10-13 | 25 | 22.5302 | 9.8838 | 32.414 | 1.8277 | 0.76558 | 0.24097 | 2.8342 | 8.744% | 9.303% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-10-13 | 26 | 21.9133 | 9.3287 | 31.242 | 1.6979 | 0.76558 | 0.23226 | 2.6957 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-10-13 | 27 | 21.9526 | 9.4478 | 31.4004 | 1.7152 | 0.76558 | 0.23343 | 2.7142 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-10-13 | 28 | 21.9871 | 9.4192 | 31.4063 | 1.7158 | 0.76558 | 0.23348 | 2.7149 | 8.644% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-10-13 | 29 | 21.3128 | 9.1628 | 30.4756 | 1.6156 | 0.76558 | 0.22656 | 2.6078 | 8.557% | 9.105% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-10-13 | 30 | 20.9621 | 9.0214 | 29.9835 | 1.5639 | 0.76558 | 0.2229 | 2.5523 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-10-13 | 31 | 21.362 | 8.8344 | 30.1964 | 1.5862 | 0.76558 | 0.22448 | 2.5762 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-10-13 | 32 | 21.3756 | 9.0556 | 30.4311 | 1.6109 | 0.76558 | 0.22623 | 2.6027 | 8.553% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-10-13 | 33 | 21.6249 | 9.2126 | 30.8375 | 1.6542 | 0.76558 | 0.22925 | 2.6491 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-10-13 | 34 | 21.6016 | 9.3888 | 30.9904 | 1.6707 | 0.76558 | 0.23039 | 2.6666 | 8.605% | 9.155% | 6.187% | 1.0941 | 1.1008 | 1.0659
2010-10-13 | 35 | 21.6112 | 9.6843 | 31.2955 | 1.7037 | 0.76558 | 0.23265 | 2.702 | 8.634% | 9.186% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-10-13 | 36 | 22.1991 | 10.336 | 32.5351 | 1.8414 | 0.76558 | 0.24187 | 2.8488 | 8.756% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-10-13 | 37 | 23.5471 | 10.7202 | 34.2673 | 2.0427 | 0.76558 | 0.25475 | 3.063 | 8.938% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-10-13 | 38 | 24.6838 | 10.7372 | 35.421 | 2.1825 | 0.76558 | 0.26332 | 3.2114 | 9.066% | 9.647% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-10-13 | 39 | 25.2205 | 10.5053 | 35.7258 | 2.2202 | 0.76558 | 0.26559 | 3.2514 | 9.101% | 9.683% | 6.544% | 1.1001 | 1.1072 | 1.07
2010-10-13 | 40 | 25.3081 | 10.3792 | 35.6873 | 2.2155 | 0.76558 | 0.2653 | 3.2463 | 9.097% | 9.679% | 6.54% | 1.1001 | 1.1072 | 1.07
2010-10-13 | 41 | 26.1726 | 10.6952 | 36.8678 | 2.3644 | 0.76558 | 0.27408 | 3.4041 | 9.233% | 9.824% | 6.639% | 1.1017 | 1.1089 | 1.0711
2010-10-13 | 42 | 26.8553 | 10.9203 | 37.7756 | 2.4823 | 0.76558 | 0.28083 | 3.5287 | 9.341% | 9.939% | 6.716% | 1.103 | 1.1104 | 1.072
2010-10-13 | 43 | 25.9231 | 10.4099 | 36.3331 | 2.2964 | 0.76558 | 0.2701 | 3.332 | 9.171% | 9.758% | 6.594% | 1.101 | 1.1081 | 1.0706
2010-10-13 | 44 | 25.3033 | 9.8399 | 35.1433 | 2.1484 | 0.76558 | 0.26126 | 3.1753 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-10-13 | 45 | 22.8075 | 8.836 | 31.6434 | 1.7418 | 0.76558 | 0.23524 | 2.7426 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-13 | 46 | 20.8828 | 8.136 | 29.0188 | 1.4649 | 0.76558 | 0.21573 | 2.4462 | 8.43% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-10-13 | 47 | 19.7382 | 7.7847 | 27.5228 | 1.3177 | 0.76558 | 0.20461 | 2.2879 | 8.313% | 8.845% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-10-13 | 48 | 19.1206 | 7.8322 | 26.9528 | 1.2637 | 0.76558 | 0.20037 | 2.2296 | 8.272% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-10-14 | 1 | 17.2771 | 6.9635 | 24.2406 | 1.0222 | 0.76558 | 0.18021 | 1.968 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-10-14 | 2 | 16.0101 | 6.4246 | 22.4347 | 0.87554 | 0.76558 | 0.16678 | 1.8079 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-14 | 3 | 15.3362 | 6.0482 | 21.3844 | 0.79548 | 0.76558 | 0.15897 | 1.72 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-14 | 4 | 15.028 | 5.8882 | 20.9162 | 0.76102 | 0.76558 | 0.15549 | 1.6821 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-14 | 5 | 14.729 | 5.6866 | 20.4156 | 0.72503 | 0.76558 | 0.15177 | 1.6424 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-14 | 6 | 14.4135 | 5.6378 | 20.0513 | 0.69939 | 0.76558 | 0.14906 | 1.614 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-14 | 7 | 14.1838 | 5.5154 | 19.6992 | 0.67504 | 0.76558 | 0.14645 | 1.5871 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-14 | 8 | 13.875 | 5.6098 | 19.4848 | 0.66043 | 0.76558 | 0.14485 | 1.5709 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-14 | 9 | 13.9989 | 5.7401 | 19.739 | 0.67778 | 0.76558 | 0.14674 | 1.5901 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-10-14 | 10 | 14.3729 | 5.6515 | 20.0244 | 0.69752 | 0.76558 | 0.14886 | 1.612 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-14 | 11 | 14.9408 | 5.8901 | 20.8309 | 0.75483 | 0.76558 | 0.15486 | 1.6753 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-14 | 12 | 15.6481 | 6.2762 | 21.9243 | 0.83615 | 0.76558 | 0.16299 | 1.7647 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-14 | 13 | 17.0661 | 7.0096 | 24.0757 | 1.0083 | 0.76558 | 0.17898 | 1.9529 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-10-14 | 14 | 19.3524 | 8.182 | 27.5344 | 1.3188 | 0.76558 | 0.20469 | 2.2891 | 8.314% | 8.846% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-10-14 | 15 | 23.4061 | 10.4289 | 33.8349 | 1.9914 | 0.76558 | 0.25153 | 3.0085 | 8.892% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-10-14 | 16 | 26.6059 | 11.8543 | 38.4602 | 2.5731 | 0.76558 | 0.28592 | 3.6246 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1115 | 1.0727
2010-10-14 | 17 | 28.4592 | 13.0944 | 41.5536 | 3.0037 | 0.76558 | 0.30891 | 4.0782 | 9.814% | 10.44% | 7.056% | 1.1088 | 1.1166 | 1.0759
2010-10-14 | 18 | 28.9647 | 12.9106 | 41.8753 | 3.0504 | 0.76558 | 0.31131 | 4.1272 | 9.856% | 10.49% | 7.086% | 1.1093 | 1.1172 | 1.0763
2010-10-14 | 19 | 28.7914 | 12.7177 | 41.5091 | 2.9972 | 0.76558 | 0.30858 | 4.0714 | 9.808% | 10.44% | 7.052% | 1.1088 | 1.1165 | 1.0759
2010-10-14 | 20 | 27.8397 | 12.0112 | 39.851 | 2.7626 | 0.76558 | 0.29626 | 3.8244 | 9.597% | 10.21% | 6.9% | 1.1062 | 1.1137 | 1.0741
2010-10-14 | 21 | 27.8061 | 11.6692 | 39.4754 | 2.7107 | 0.76558 | 0.29346 | 3.7698 | 9.55% | 10.16% | 6.866% | 1.1056 | 1.1131 | 1.0737
2010-10-14 | 22 | 27.1214 | 11.502 | 38.6234 | 2.595 | 0.76558 | 0.28713 | 3.6477 | 9.444% | 10.05% | 6.79% | 1.1043 | 1.1117 | 1.0729
2010-10-14 | 23 | 26.3727 | 10.7881 | 37.1608 | 2.4022 | 0.76558 | 0.27626 | 3.444 | 9.268% | 9.861% | 6.664% | 1.1021 | 1.1094 | 1.0714
2010-10-14 | 24 | 25.3249 | 10.443 | 35.7679 | 2.2255 | 0.76558 | 0.2659 | 3.2569 | 9.106% | 9.689% | 6.547% | 1.1002 | 1.1073 | 1.0701
2010-10-14 | 25 | 24.3908 | 10.3495 | 34.7404 | 2.0994 | 0.76558 | 0.25826 | 3.1233 | 8.99% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-10-14 | 26 | 23.5215 | 9.7909 | 33.3125 | 1.9304 | 0.76558 | 0.24765 | 2.9436 | 8.836% | 9.402% | 6.353% | 1.0969 | 1.1038 | 1.0678
2010-10-14 | 27 | 23.5455 | 9.9156 | 33.4611 | 1.9477 | 0.76558 | 0.24875 | 2.962 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2010-10-14 | 28 | 23.0483 | 9.6188 | 32.6671 | 1.8563 | 0.76558 | 0.24285 | 2.8648 | 8.77% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-10-14 | 29 | 23.0657 | 9.2445 | 32.3102 | 1.816 | 0.76558 | 0.2402 | 2.8218 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-10-14 | 30 | 22.5278 | 8.8648 | 31.3926 | 1.7143 | 0.76558 | 0.23338 | 2.7133 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-10-14 | 31 | 22.8166 | 8.7819 | 31.5985 | 1.7369 | 0.76558 | 0.23491 | 2.7374 | 8.663% | 9.217% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-10-14 | 32 | 22.6819 | 8.6398 | 31.3218 | 1.7066 | 0.76558 | 0.23285 | 2.705 | 8.636% | 9.189% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-10-14 | 33 | 22.7614 | 9.0511 | 31.8125 | 1.7605 | 0.76558 | 0.2365 | 2.7626 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-10-14 | 34 | 23.1025 | 9.2397 | 32.3422 | 1.8196 | 0.76558 | 0.24044 | 2.8256 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-10-14 | 35 | 23.4561 | 9.5695 | 33.0256 | 1.8973 | 0.76558 | 0.24552 | 2.9084 | 8.806% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-10-14 | 36 | 24.3326 | 10.2024 | 34.5349 | 2.0747 | 0.76558 | 0.25674 | 3.097 | 8.968% | 9.542% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-10-14 | 37 | 25.5649 | 10.5766 | 36.1415 | 2.2722 | 0.76558 | 0.26868 | 3.3065 | 9.149% | 9.734% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-10-14 | 38 | 26.5169 | 10.6734 | 37.1903 | 2.406 | 0.76558 | 0.27648 | 3.448 | 9.271% | 9.865% | 6.666% | 1.1022 | 1.1094 | 1.0714
2010-10-14 | 39 | 26.7399 | 10.4859 | 37.2258 | 2.4106 | 0.76558 | 0.27674 | 3.4529 | 9.276% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2010-10-14 | 40 | 27.0157 | 10.4371 | 37.4529 | 2.4401 | 0.76558 | 0.27843 | 3.4841 | 9.303% | 9.898% | 6.689% | 1.1026 | 1.1099 | 1.0717
2010-10-14 | 41 | 27.9148 | 10.5731 | 38.4879 | 2.5768 | 0.76558 | 0.28612 | 3.6285 | 9.428% | 10.03% | 6.778% | 1.1041 | 1.1115 | 1.0727
2010-10-14 | 42 | 28.2174 | 10.4484 | 38.6658 | 2.6007 | 0.76558 | 0.28745 | 3.6537 | 9.449% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2010-10-14 | 43 | 26.756 | 9.8342 | 36.5902 | 2.329 | 0.76558 | 0.27202 | 3.3666 | 9.201% | 9.79% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-10-14 | 44 | 25.517 | 9.2527 | 34.7697 | 2.103 | 0.76558 | 0.25848 | 3.1271 | 8.994% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-10-14 | 45 | 23.3887 | 8.3336 | 31.7223 | 1.7505 | 0.76558 | 0.23583 | 2.7519 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-10-14 | 46 | 21.3409 | 7.3356 | 28.6765 | 1.4305 | 0.76558 | 0.21318 | 2.4093 | 8.402% | 8.939% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-10-14 | 47 | 20.0866 | 7.1363 | 27.2229 | 1.2892 | 0.76558 | 0.20238 | 2.2571 | 8.291% | 8.822% | 5.961% | 1.0904 | 1.0968 | 1.0634
2010-10-14 | 48 | 19.704 | 7.218 | 26.922 | 1.2608 | 0.76558 | 0.20014 | 2.2265 | 8.27% | 8.8% | 5.946% | 1.0902 | 1.0965 | 1.0632
2010-10-15 | 1 | 17.8876 | 6.5138 | 24.4014 | 1.0358 | 0.76558 | 0.1814 | 1.9828 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-10-15 | 2 | 16.4494 | 6.0385 | 22.4879 | 0.87969 | 0.76558 | 0.16718 | 1.8124 | 8.06% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-10-15 | 3 | 15.6871 | 5.7231 | 21.4102 | 0.7974 | 0.76558 | 0.15917 | 1.7221 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-15 | 4 | 15.0234 | 5.4947 | 20.5181 | 0.73234 | 0.76558 | 0.15253 | 1.6504 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-15 | 5 | 15.0068 | 5.3064 | 20.3132 | 0.71778 | 0.76558 | 0.15101 | 1.6344 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-15 | 6 | 14.6942 | 5.2022 | 19.8965 | 0.68863 | 0.76558 | 0.14791 | 1.6021 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-15 | 7 | 14.7258 | 5.1841 | 19.9099 | 0.68956 | 0.76558 | 0.14801 | 1.6031 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-10-15 | 8 | 14.3555 | 5.1872 | 19.5426 | 0.66436 | 0.76558 | 0.14528 | 1.5752 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-10-15 | 9 | 14.3621 | 5.3898 | 19.7518 | 0.67865 | 0.76558 | 0.14684 | 1.5911 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-10-15 | 10 | 14.6703 | 5.4411 | 20.1114 | 0.70359 | 0.76558 | 0.14951 | 1.6187 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-15 | 11 | 15.1602 | 5.4097 | 20.5699 | 0.73604 | 0.76558 | 0.15292 | 1.6545 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-15 | 12 | 16.1338 | 5.7943 | 21.9281 | 0.83645 | 0.76558 | 0.16302 | 1.765 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-15 | 13 | 17.8805 | 6.6691 | 24.5496 | 1.0484 | 0.76558 | 0.1825 | 1.9965 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-10-15 | 14 | 20.25 | 8.0706 | 28.3207 | 1.3952 | 0.76558 | 0.21054 | 2.3713 | 8.373% | 8.909% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-10-15 | 15 | 24.4797 | 10.1166 | 34.5964 | 2.0821 | 0.76558 | 0.25719 | 3.1048 | 8.974% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-10-15 | 16 | 26.4293 | 11.1761 | 37.6055 | 2.46 | 0.76558 | 0.27956 | 3.5051 | 9.321% | 9.917% | 6.702% | 1.1028 | 1.1101 | 1.0718
2010-10-15 | 17 | 27.0296 | 11.4072 | 38.4367 | 2.57 | 0.76558 | 0.28574 | 3.6213 | 9.421% | 10.02% | 6.774% | 1.104 | 1.1114 | 1.0727
2010-10-15 | 18 | 26.7163 | 11.0496 | 37.7659 | 2.481 | 0.76558 | 0.28076 | 3.5274 | 9.34% | 9.938% | 6.716% | 1.103 | 1.1103 | 1.072
2010-10-15 | 19 | 26.3712 | 10.446 | 36.8171 | 2.3579 | 0.76558 | 0.2737 | 3.3972 | 9.227% | 9.818% | 6.634% | 1.1017 | 1.1089 | 1.0711
2010-10-15 | 20 | 25.4152 | 10.0292 | 35.4444 | 2.1854 | 0.76558 | 0.2635 | 3.2145 | 9.069% | 9.649% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-10-15 | 21 | 25.3161 | 9.6214 | 34.9376 | 2.1233 | 0.76558 | 0.25973 | 3.1486 | 9.012% | 9.589% | 6.48% | 1.099 | 1.1061 | 1.0693
2010-10-15 | 22 | 24.5276 | 9.4998 | 34.0274 | 2.0142 | 0.76558 | 0.25296 | 3.0327 | 8.913% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-10-15 | 23 | 23.6739 | 9.2033 | 32.8772 | 1.8803 | 0.76558 | 0.24441 | 2.8903 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-10-15 | 24 | 22.9358 | 9.1721 | 32.1079 | 1.7933 | 0.76558 | 0.23869 | 2.7976 | 8.713% | 9.271% | 6.265% | 1.0954 | 1.1022 | 1.0668
2010-10-15 | 25 | 22.0425 | 8.763 | 30.8055 | 1.6508 | 0.76558 | 0.22901 | 2.6454 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-10-15 | 26 | 21.1018 | 8.4158 | 29.5176 | 1.5156 | 0.76558 | 0.21944 | 2.5007 | 8.472% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-10-15 | 27 | 21.2021 | 8.6561 | 29.8582 | 1.5508 | 0.76558 | 0.22197 | 2.5384 | 8.501% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-10-15 | 28 | 21.3553 | 8.7424 | 30.0977 | 1.5758 | 0.76558 | 0.22375 | 2.5651 | 8.523% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-10-15 | 29 | 20.9752 | 8.6279 | 29.603 | 1.5244 | 0.76558 | 0.22007 | 2.5101 | 8.479% | 9.022% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-10-15 | 30 | 20.2942 | 8.3063 | 28.6006 | 1.4229 | 0.76558 | 0.21262 | 2.4011 | 8.395% | 8.933% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-10-15 | 31 | 20.7927 | 8.3353 | 29.1281 | 1.4759 | 0.76558 | 0.21654 | 2.458 | 8.439% | 8.979% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-10-15 | 32 | 20.3504 | 8.3691 | 28.7195 | 1.4348 | 0.76558 | 0.2135 | 2.4139 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-10-15 | 33 | 20.4764 | 8.7445 | 29.2209 | 1.4853 | 0.76558 | 0.21723 | 2.4681 | 8.446% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-10-15 | 34 | 20.4633 | 8.6488 | 29.1121 | 1.4743 | 0.76558 | 0.21642 | 2.4563 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-10-15 | 35 | 20.2983 | 8.8083 | 29.1066 | 1.4737 | 0.76558 | 0.21638 | 2.4557 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-10-15 | 36 | 20.8006 | 9.3225 | 30.1231 | 1.5785 | 0.76558 | 0.22394 | 2.568 | 8.525% | 9.071% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-10-15 | 37 | 21.8199 | 9.4781 | 31.298 | 1.704 | 0.76558 | 0.23267 | 2.7022 | 8.634% | 9.186% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-10-15 | 38 | 22.4321 | 9.5476 | 31.9797 | 1.779 | 0.76558 | 0.23774 | 2.7823 | 8.7% | 9.257% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-10-15 | 39 | 22.6462 | 9.4674 | 32.1136 | 1.794 | 0.76558 | 0.23874 | 2.7983 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-10-15 | 40 | 23.1493 | 9.291 | 32.4403 | 1.8306 | 0.76558 | 0.24117 | 2.8374 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2010-10-15 | 41 | 24.0925 | 9.4025 | 33.495 | 1.9516 | 0.76558 | 0.24901 | 2.9662 | 8.856% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2010-10-15 | 42 | 24.9833 | 9.6096 | 34.5929 | 2.0817 | 0.76558 | 0.25717 | 3.1044 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-10-15 | 43 | 24.505 | 9.3924 | 33.8973 | 1.9988 | 0.76558 | 0.252 | 3.0164 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-10-15 | 44 | 23.581 | 9.0377 | 32.6187 | 1.8508 | 0.76558 | 0.24249 | 2.8589 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1028 | 1.0673
2010-10-15 | 45 | 21.709 | 8.095 | 29.8039 | 1.5452 | 0.76558 | 0.22157 | 2.5323 | 8.497% | 9.04% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-10-15 | 46 | 19.6293 | 7.2448 | 26.8742 | 1.2563 | 0.76558 | 0.19979 | 2.2217 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2010-10-15 | 47 | 18.7561 | 6.9522 | 25.7083 | 1.1497 | 0.76558 | 0.19112 | 2.1064 | 8.193% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2010-10-15 | 48 | 18.0142 | 7.1019 | 25.1161 | 1.0973 | 0.76558 | 0.18672 | 2.0496 | 8.161% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-10-16 | 1 | 16.5495 | 6.2809 | 22.8304 | 0.90669 | 0.76558 | 0.16972 | 1.842 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-10-16 | 2 | 15.5348 | 5.6196 | 21.1544 | 0.77846 | 0.76558 | 0.15726 | 1.7013 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-16 | 3 | 14.4287 | 5.2911 | 19.7198 | 0.67645 | 0.76558 | 0.1466 | 1.5886 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-10-16 | 4 | 13.9889 | 5.1106 | 19.0995 | 0.63457 | 0.76558 | 0.14199 | 1.5421 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-10-16 | 5 | 13.4919 | 5.0327 | 18.5247 | 0.59695 | 0.76558 | 0.13771 | 1.5002 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-10-16 | 6 | 13.416 | 5.0126 | 18.4287 | 0.59078 | 0.76558 | 0.137 | 1.4934 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2010-10-16 | 7 | 13.2604 | 4.9569 | 18.2172 | 0.5773 | 0.76558 | 0.13543 | 1.4783 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-10-16 | 8 | 13.1881 | 4.9331 | 18.1212 | 0.57123 | 0.76558 | 0.13472 | 1.4715 | 8.12% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-10-16 | 9 | 13.2762 | 5.003 | 18.2792 | 0.58123 | 0.76558 | 0.13589 | 1.4827 | 8.111% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-10-16 | 10 | 13.3352 | 5.1706 | 18.5058 | 0.59573 | 0.76558 | 0.13757 | 1.4989 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-10-16 | 11 | 13.9423 | 5.2953 | 19.2376 | 0.64378 | 0.76558 | 0.14301 | 1.5524 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-16 | 12 | 14.5415 | 5.5898 | 20.1313 | 0.70499 | 0.76558 | 0.14966 | 1.6202 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-16 | 13 | 16.2325 | 6.5 | 22.7325 | 0.89894 | 0.76558 | 0.169 | 1.8335 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-16 | 14 | 18.5048 | 7.7201 | 26.2249 | 1.1964 | 0.76558 | 0.19496 | 2.1569 | 8.225% | 8.751% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-10-16 | 15 | 22.1493 | 9.6204 | 31.7697 | 1.7557 | 0.76558 | 0.23618 | 2.7575 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2010-10-16 | 16 | 24.6188 | 10.468 | 35.0868 | 2.1415 | 0.76558 | 0.26084 | 3.1679 | 9.029% | 9.607% | 6.492% | 1.0992 | 1.1063 | 1.0694
2010-10-16 | 17 | 25.861 | 10.7059 | 36.5669 | 2.326 | 0.76558 | 0.27184 | 3.3634 | 9.198% | 9.787% | 6.613% | 1.1013 | 1.1085 | 1.0708
2010-10-16 | 18 | 25.9121 | 10.6998 | 36.6119 | 2.3317 | 0.76558 | 0.27218 | 3.3695 | 9.203% | 9.792% | 6.617% | 1.1014 | 1.1086 | 1.0709
2010-10-16 | 19 | 25.5943 | 10.3606 | 35.9549 | 2.2488 | 0.76558 | 0.26729 | 3.2817 | 9.127% | 9.711% | 6.562% | 1.1004 | 1.1076 | 1.0702
2010-10-16 | 20 | 24.8103 | 10.1261 | 34.9364 | 2.1232 | 0.76558 | 0.25972 | 3.1485 | 9.012% | 9.589% | 6.48% | 1.099 | 1.1061 | 1.0693
2010-10-16 | 21 | 24.8353 | 9.559 | 34.3943 | 2.0578 | 0.76558 | 0.25569 | 3.0791 | 8.952% | 9.525% | 6.437% | 1.0983 | 1.1053 | 1.0688
2010-10-16 | 22 | 23.7958 | 9.5586 | 33.3544 | 1.9353 | 0.76558 | 0.24796 | 2.9488 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-10-16 | 23 | 23.0795 | 9.1617 | 32.2412 | 1.8082 | 0.76558 | 0.23968 | 2.8135 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2010-10-16 | 24 | 22.392 | 8.961 | 31.3531 | 1.71 | 0.76558 | 0.23308 | 2.7087 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-10-16 | 25 | 21.5946 | 8.8979 | 30.4925 | 1.6174 | 0.76558 | 0.22669 | 2.6097 | 8.558% | 9.106% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-10-16 | 26 | 20.9825 | 8.5836 | 29.5661 | 1.5206 | 0.76558 | 0.2198 | 2.506 | 8.476% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-10-16 | 27 | 20.8857 | 8.6956 | 29.5814 | 1.5222 | 0.76558 | 0.21991 | 2.5077 | 8.477% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-10-16 | 28 | 20.829 | 8.5875 | 29.4165 | 1.5053 | 0.76558 | 0.21869 | 2.4895 | 8.463% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-10-16 | 29 | 20.4076 | 8.3173 | 28.7249 | 1.4353 | 0.76558 | 0.21354 | 2.4145 | 8.405% | 8.943% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-10-16 | 30 | 19.8392 | 8.1667 | 28.006 | 1.3644 | 0.76558 | 0.2082 | 2.3382 | 8.349% | 8.883% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-10-16 | 31 | 20.3825 | 8.0736 | 28.456 | 1.4086 | 0.76558 | 0.21155 | 2.3857 | 8.384% | 8.92% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-10-16 | 32 | 20.7895 | 8.1472 | 28.9366 | 1.4566 | 0.76558 | 0.21512 | 2.4373 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-10-16 | 33 | 21.2766 | 8.4003 | 29.6769 | 1.532 | 0.76558 | 0.22062 | 2.5182 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-10-16 | 34 | 21.585 | 8.4776 | 30.0626 | 1.5721 | 0.76558 | 0.22349 | 2.5612 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-10-16 | 35 | 21.7183 | 9.0881 | 30.8063 | 1.6509 | 0.76558 | 0.22902 | 2.6455 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-10-16 | 36 | 22.611 | 9.4151 | 32.0261 | 1.7842 | 0.76558 | 0.23809 | 2.7879 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2010-10-16 | 37 | 24.2199 | 9.5503 | 33.7702 | 1.9838 | 0.76558 | 0.25105 | 3.0004 | 8.885% | 9.454% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-10-16 | 38 | 25.5005 | 9.6285 | 35.129 | 2.1467 | 0.76558 | 0.26115 | 3.1734 | 9.034% | 9.612% | 6.495% | 1.0993 | 1.1063 | 1.0695
2010-10-16 | 39 | 25.7608 | 9.669 | 35.4298 | 2.1836 | 0.76558 | 0.26339 | 3.2126 | 9.067% | 9.648% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-10-16 | 40 | 25.6075 | 9.7253 | 35.3329 | 2.1717 | 0.76558 | 0.26267 | 3.1999 | 9.056% | 9.636% | 6.512% | 1.0996 | 1.1066 | 1.0697
2010-10-16 | 41 | 25.9573 | 9.7744 | 35.7317 | 2.221 | 0.76558 | 0.26563 | 3.2522 | 9.102% | 9.684% | 6.544% | 1.1001 | 1.1072 | 1.07
2010-10-16 | 42 | 25.8726 | 9.6587 | 35.5313 | 2.1961 | 0.76558 | 0.26414 | 3.2258 | 9.079% | 9.66% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-10-16 | 43 | 24.6664 | 9.2775 | 33.9438 | 2.0043 | 0.76558 | 0.25234 | 3.0222 | 8.904% | 9.473% | 6.402% | 1.0977 | 1.1046 | 1.0684
2010-10-16 | 44 | 23.6721 | 8.8873 | 32.5594 | 1.8441 | 0.76558 | 0.24205 | 2.8517 | 8.759% | 9.319% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-10-16 | 45 | 22.0194 | 8.205 | 30.2245 | 1.5891 | 0.76558 | 0.22469 | 2.5794 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-10-16 | 46 | 20.2384 | 7.5254 | 27.7638 | 1.3409 | 0.76558 | 0.2064 | 2.3129 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-10-16 | 47 | 19.4095 | 7.242 | 26.6514 | 1.2356 | 0.76558 | 0.19813 | 2.1993 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0963 | 1.0631
2010-10-16 | 48 | 18.9125 | 7.38 | 26.2926 | 1.2025 | 0.76558 | 0.19546 | 2.1636 | 8.229% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-10-17 | 1 | 17.4132 | 6.7097 | 24.1229 | 1.0123 | 0.76558 | 0.17933 | 1.9572 | 8.113% | 8.633% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-10-17 | 2 | 16.1158 | 6.1555 | 22.2714 | 0.86284 | 0.76558 | 0.16557 | 1.794 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-10-17 | 3 | 15.2485 | 5.7385 | 20.987 | 0.76619 | 0.76558 | 0.15602 | 1.6878 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-17 | 4 | 14.7809 | 5.5287 | 20.3096 | 0.71753 | 0.76558 | 0.15098 | 1.6341 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-17 | 5 | 14.1868 | 5.4219 | 19.6087 | 0.66886 | 0.76558 | 0.14577 | 1.5802 | 8.059% | 8.574% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-10-17 | 6 | 13.6749 | 5.2919 | 18.9668 | 0.62578 | 0.76558 | 0.141 | 1.5324 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-10-17 | 7 | 13.6198 | 5.2686 | 18.8884 | 0.62062 | 0.76558 | 0.14042 | 1.5266 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-10-17 | 8 | 13.671 | 5.2614 | 18.9324 | 0.62351 | 0.76558 | 0.14075 | 1.5298 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-10-17 | 9 | 13.9555 | 5.3116 | 19.2671 | 0.64576 | 0.76558 | 0.14323 | 1.5546 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-10-17 | 10 | 13.9329 | 5.3012 | 19.2341 | 0.64354 | 0.76558 | 0.14299 | 1.5521 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-17 | 11 | 14.3801 | 5.3265 | 19.7066 | 0.67555 | 0.76558 | 0.1465 | 1.5876 | 8.056% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-17 | 12 | 14.739 | 5.4794 | 20.2184 | 0.71109 | 0.76558 | 0.15031 | 1.627 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-17 | 13 | 15.6291 | 5.8458 | 21.4749 | 0.80222 | 0.76558 | 0.15965 | 1.7274 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-17 | 14 | 16.629 | 6.118 | 22.747 | 0.90009 | 0.76558 | 0.1691 | 1.8348 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-17 | 15 | 18.4187 | 6.8234 | 25.242 | 1.1084 | 0.76558 | 0.18765 | 2.0616 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-10-17 | 16 | 20.1319 | 7.9219 | 28.0538 | 1.3691 | 0.76558 | 0.20856 | 2.3432 | 8.352% | 8.887% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-10-17 | 17 | 22.0453 | 9.0301 | 31.0754 | 1.6798 | 0.76558 | 0.23102 | 2.6764 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-10-17 | 18 | 23.8649 | 9.9585 | 33.8234 | 1.9901 | 0.76558 | 0.25145 | 3.0071 | 8.891% | 9.46% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-10-17 | 19 | 25.4408 | 10.4318 | 35.8726 | 2.2385 | 0.76558 | 0.26668 | 3.2708 | 9.118% | 9.701% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-10-17 | 20 | 25.8957 | 10.6531 | 36.5488 | 2.3237 | 0.76558 | 0.27171 | 3.361 | 9.196% | 9.784% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-10-17 | 21 | 26.7909 | 10.6586 | 37.4495 | 2.4396 | 0.76558 | 0.2784 | 3.4836 | 9.302% | 9.898% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-10-17 | 22 | 26.324 | 10.8119 | 37.1359 | 2.399 | 0.76558 | 0.27607 | 3.4406 | 9.265% | 9.858% | 6.661% | 1.1021 | 1.1094 | 1.0714
2010-10-17 | 23 | 25.7015 | 10.4062 | 36.1077 | 2.268 | 0.76558 | 0.26843 | 3.302 | 9.145% | 9.73% | 6.575% | 1.1007 | 1.1078 | 1.0704
2010-10-17 | 24 | 25.0434 | 10.1247 | 35.1681 | 2.1515 | 0.76558 | 0.26144 | 3.1785 | 9.038% | 9.616% | 6.498% | 1.0994 | 1.1064 | 1.0695
2010-10-17 | 25 | 23.8215 | 9.8416 | 33.6631 | 1.9713 | 0.76558 | 0.25026 | 2.9871 | 8.873% | 9.441% | 6.38% | 1.0974 | 1.1043 | 1.0681
2010-10-17 | 26 | 23.0138 | 9.276 | 32.2898 | 1.8137 | 0.76558 | 0.24005 | 2.8193 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-10-17 | 27 | 22.4958 | 9.2531 | 31.7489 | 1.7534 | 0.76558 | 0.23603 | 2.7551 | 8.678% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-10-17 | 28 | 21.9572 | 9.1798 | 31.1369 | 1.6865 | 0.76558 | 0.23148 | 2.6836 | 8.619% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-10-17 | 29 | 21.4249 | 8.7224 | 30.1472 | 1.581 | 0.76558 | 0.22412 | 2.5707 | 8.527% | 9.073% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-10-17 | 30 | 20.7079 | 8.3583 | 29.0662 | 1.4696 | 0.76558 | 0.21608 | 2.4513 | 8.434% | 8.973% | 6.064% | 1.0921 | 1.0986 | 1.0646
2010-10-17 | 31 | 20.9309 | 7.99 | 28.9208 | 1.455 | 0.76558 | 0.215 | 2.4356 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0645
2010-10-17 | 32 | 20.9746 | 8.1639 | 29.1385 | 1.477 | 0.76558 | 0.21662 | 2.4592 | 8.44% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-10-17 | 33 | 21.2713 | 8.934 | 30.2053 | 1.5871 | 0.76558 | 0.22455 | 2.5772 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2010-10-17 | 34 | 21.2504 | 9.3345 | 30.585 | 1.6272 | 0.76558 | 0.22737 | 2.6202 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-10-17 | 35 | 21.3445 | 9.9027 | 31.2472 | 1.6985 | 0.76558 | 0.2323 | 2.6963 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-10-17 | 36 | 22.146 | 10.2137 | 32.3597 | 1.8216 | 0.76558 | 0.24057 | 2.8277 | 8.738% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-10-17 | 37 | 23.1022 | 10.1435 | 33.2457 | 1.9227 | 0.76558 | 0.24715 | 2.9354 | 8.829% | 9.395% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-10-17 | 38 | 24.2395 | 9.9958 | 34.2353 | 2.0388 | 0.76558 | 0.25451 | 3.0589 | 8.935% | 9.507% | 6.424% | 1.0981 | 1.1051 | 1.0687
2010-10-17 | 39 | 24.8039 | 9.9382 | 34.7421 | 2.0996 | 0.76558 | 0.25828 | 3.1235 | 8.991% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-10-17 | 40 | 24.9785 | 9.6692 | 34.6477 | 2.0883 | 0.76558 | 0.25758 | 3.1114 | 8.98% | 9.555% | 6.457% | 1.0987 | 1.1056 | 1.069
2010-10-17 | 41 | 25.0412 | 9.4577 | 34.4989 | 2.0704 | 0.76558 | 0.25647 | 3.0924 | 8.964% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-10-17 | 42 | 25.1616 | 9.3019 | 34.4636 | 2.0661 | 0.76558 | 0.25621 | 3.0879 | 8.96% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2010-10-17 | 43 | 24.319 | 8.6741 | 32.9931 | 1.8936 | 0.76558 | 0.24527 | 2.9044 | 8.803% | 9.367% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-10-17 | 44 | 23.0889 | 8.3968 | 31.4856 | 1.7245 | 0.76558 | 0.23407 | 2.7241 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-10-17 | 45 | 21.5365 | 7.683 | 29.2196 | 1.4852 | 0.76558 | 0.21722 | 2.468 | 8.446% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-10-17 | 46 | 20.0454 | 7.1124 | 27.1578 | 1.283 | 0.76558 | 0.20189 | 2.2505 | 8.287% | 8.817% | 5.958% | 1.0904 | 1.0967 | 1.0634
2010-10-17 | 47 | 19.2255 | 7.0296 | 26.2551 | 1.1991 | 0.76558 | 0.19518 | 2.1599 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-10-17 | 48 | 18.9866 | 7.2238 | 26.2104 | 1.195 | 0.76558 | 0.19485 | 2.1555 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-10-18 | 1 | 17.537 | 6.3879 | 23.9249 | 0.99571 | 0.76558 | 0.17786 | 1.9392 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-10-18 | 2 | 16.4974 | 5.8121 | 22.3095 | 0.8658 | 0.76558 | 0.16585 | 1.7972 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-10-18 | 3 | 15.7214 | 5.6176 | 21.3389 | 0.7921 | 0.76558 | 0.15864 | 1.7163 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-18 | 4 | 15.0182 | 5.4052 | 20.4233 | 0.72558 | 0.76558 | 0.15183 | 1.643 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-18 | 5 | 14.4724 | 5.316 | 19.7884 | 0.68117 | 0.76558 | 0.14711 | 1.5939 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-10-18 | 6 | 14.1866 | 5.2414 | 19.428 | 0.65659 | 0.76558 | 0.14443 | 1.5666 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-10-18 | 7 | 13.8466 | 5.1049 | 18.9515 | 0.62477 | 0.76558 | 0.14089 | 1.5312 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-10-18 | 8 | 13.8848 | 4.971 | 18.8557 | 0.61847 | 0.76558 | 0.14018 | 1.5242 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-10-18 | 9 | 14.0592 | 4.9377 | 18.9969 | 0.62777 | 0.76558 | 0.14122 | 1.5346 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-10-18 | 10 | 13.9734 | 4.9278 | 18.9012 | 0.62146 | 0.76558 | 0.14051 | 1.5276 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-10-18 | 11 | 14.4478 | 5.0186 | 19.4664 | 0.65918 | 0.76558 | 0.14472 | 1.5695 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-18 | 12 | 14.8083 | 5.1585 | 19.9668 | 0.69351 | 0.76558 | 0.14844 | 1.6075 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-10-18 | 13 | 15.6547 | 5.2556 | 20.9103 | 0.7606 | 0.76558 | 0.15545 | 1.6816 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-18 | 14 | 16.2871 | 5.5106 | 21.7976 | 0.82652 | 0.76558 | 0.16205 | 1.7541 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-18 | 15 | 17.8281 | 6.2917 | 24.1198 | 1.012 | 0.76558 | 0.17931 | 1.9569 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-10-18 | 16 | 19.1523 | 7.1284 | 26.2806 | 1.2015 | 0.76558 | 0.19537 | 2.1624 | 8.228% | 8.755% | 5.916% | 1.0897 | 1.0959 | 1.0629
2010-10-18 | 17 | 20.8752 | 8.2141 | 29.0893 | 1.472 | 0.76558 | 0.21625 | 2.4538 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-10-18 | 18 | 22.8276 | 9.0094 | 31.8371 | 1.7632 | 0.76558 | 0.23668 | 2.7655 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-10-18 | 19 | 24.9877 | 9.8689 | 34.8566 | 2.1135 | 0.76558 | 0.25913 | 3.1382 | 9.003% | 9.579% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-10-18 | 20 | 25.7198 | 10.1569 | 35.8767 | 2.239 | 0.76558 | 0.26671 | 3.2713 | 9.118% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2010-10-18 | 21 | 27.0212 | 10.3799 | 37.401 | 2.4333 | 0.76558 | 0.27804 | 3.477 | 9.296% | 9.891% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-10-18 | 22 | 26.9116 | 10.6523 | 37.5638 | 2.4546 | 0.76558 | 0.27925 | 3.4994 | 9.316% | 9.912% | 6.698% | 1.1027 | 1.11 | 1.0718
2010-10-18 | 23 | 26.4141 | 10.3252 | 36.7393 | 2.348 | 0.76558 | 0.27312 | 3.3867 | 9.218% | 9.808% | 6.628% | 1.1015 | 1.1087 | 1.071
2010-10-18 | 24 | 25.6843 | 10.037 | 35.7213 | 2.2197 | 0.76558 | 0.26556 | 3.2508 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-10-18 | 25 | 24.7447 | 9.8252 | 34.57 | 2.0789 | 0.76558 | 0.257 | 3.1015 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-10-18 | 26 | 23.8165 | 9.3199 | 33.1364 | 1.9101 | 0.76558 | 0.24634 | 2.922 | 8.818% | 9.382% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-10-18 | 27 | 23.2399 | 9.2763 | 32.5162 | 1.8392 | 0.76558 | 0.24173 | 2.8465 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-10-18 | 28 | 22.5924 | 9.0791 | 31.6715 | 1.7449 | 0.76558 | 0.23545 | 2.7459 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-10-18 | 29 | 21.6216 | 8.7387 | 30.3603 | 1.6034 | 0.76558 | 0.2257 | 2.5947 | 8.546% | 9.093% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-10-18 | 30 | 21.0282 | 8.2768 | 29.305 | 1.4939 | 0.76558 | 0.21786 | 2.4773 | 8.454% | 8.995% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-10-18 | 31 | 21.1807 | 8.0935 | 29.2742 | 1.4907 | 0.76558 | 0.21763 | 2.474 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-10-18 | 32 | 20.8688 | 7.7921 | 28.6609 | 1.4289 | 0.76558 | 0.21307 | 2.4076 | 8.4% | 8.938% | 6.04% | 1.0917 | 1.0982 | 1.0643
2010-10-18 | 33 | 20.7333 | 7.7446 | 28.4779 | 1.4107 | 0.76558 | 0.21171 | 2.388 | 8.386% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-10-18 | 34 | 20.8823 | 7.8197 | 28.702 | 1.433 | 0.76558 | 0.21337 | 2.412 | 8.404% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2010-10-18 | 35 | 21.0068 | 8.3405 | 29.3474 | 1.4982 | 0.76558 | 0.21817 | 2.482 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-10-18 | 36 | 21.508 | 9.1029 | 30.6109 | 1.63 | 0.76558 | 0.22757 | 2.6231 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-10-18 | 37 | 22.3006 | 9.2449 | 31.5455 | 1.7311 | 0.76558 | 0.23451 | 2.7311 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-10-18 | 38 | 22.5605 | 9.2004 | 31.7609 | 1.7548 | 0.76558 | 0.23611 | 2.7565 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-10-18 | 39 | 23.1086 | 9.2374 | 32.346 | 1.82 | 0.76558 | 0.24046 | 2.8261 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-10-18 | 40 | 23.5058 | 9.0355 | 32.5413 | 1.8421 | 0.76558 | 0.24192 | 2.8496 | 8.757% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-10-18 | 41 | 24.6263 | 9.3008 | 33.9271 | 2.0023 | 0.76558 | 0.25222 | 3.0201 | 8.902% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-10-18 | 42 | 26.0632 | 9.6433 | 35.7065 | 2.2178 | 0.76558 | 0.26545 | 3.2489 | 9.099% | 9.681% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-10-18 | 43 | 25.6555 | 9.3797 | 35.0353 | 2.1352 | 0.76558 | 0.26046 | 3.1613 | 9.023% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-10-18 | 44 | 24.5075 | 8.8831 | 33.3906 | 1.9395 | 0.76558 | 0.24823 | 2.9533 | 8.845% | 9.411% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-10-18 | 45 | 22.6135 | 7.9407 | 30.5542 | 1.624 | 0.76558 | 0.22714 | 2.6167 | 8.564% | 9.112% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-10-18 | 46 | 20.6904 | 7.0269 | 27.7173 | 1.3364 | 0.76558 | 0.20605 | 2.308 | 8.327% | 8.86% | 5.987% | 1.0908 | 1.0972 | 1.0637
2010-10-18 | 47 | 19.2207 | 6.6533 | 25.874 | 1.1646 | 0.76558 | 0.19235 | 2.1225 | 8.203% | 8.728% | 5.898% | 1.0894 | 1.0956 | 1.0627
2010-10-18 | 48 | 18.8086 | 6.8035 | 25.612 | 1.1411 | 0.76558 | 0.1904 | 2.0971 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-10-19 | 1 | 17.3866 | 6.1479 | 23.5345 | 0.96348 | 0.76558 | 0.17496 | 1.904 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-10-19 | 2 | 16.1122 | 5.6048 | 21.717 | 0.82042 | 0.76558 | 0.16145 | 1.7474 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-19 | 3 | 15.6303 | 5.3428 | 20.973 | 0.76517 | 0.76558 | 0.15592 | 1.6867 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-19 | 4 | 15.2148 | 5.1389 | 20.3537 | 0.72065 | 0.76558 | 0.15131 | 1.6375 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-19 | 5 | 14.8069 | 5.0216 | 19.8285 | 0.68393 | 0.76558 | 0.14741 | 1.5969 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-10-19 | 6 | 14.7109 | 4.9529 | 19.6638 | 0.67262 | 0.76558 | 0.14618 | 1.5844 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-19 | 7 | 14.2315 | 5.069 | 19.3004 | 0.64799 | 0.76558 | 0.14348 | 1.557 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-10-19 | 8 | 14.31 | 5.0751 | 19.3851 | 0.65369 | 0.76558 | 0.14411 | 1.5634 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-19 | 9 | 14.5542 | 5.1176 | 19.6718 | 0.67317 | 0.76558 | 0.14624 | 1.585 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-19 | 10 | 14.8265 | 5.1553 | 19.9818 | 0.69455 | 0.76558 | 0.14855 | 1.6087 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-10-19 | 11 | 15.3449 | 5.2684 | 20.6132 | 0.73914 | 0.76558 | 0.15324 | 1.658 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-19 | 12 | 16.1268 | 5.7053 | 21.8321 | 0.82914 | 0.76558 | 0.1623 | 1.757 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-19 | 13 | 17.7886 | 6.5359 | 24.3245 | 1.0293 | 0.76558 | 0.18083 | 1.9757 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-10-19 | 14 | 20.2009 | 7.9983 | 28.1992 | 1.3833 | 0.76558 | 0.20964 | 2.3585 | 8.364% | 8.899% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-10-19 | 15 | 24.4171 | 10.1583 | 34.5753 | 2.0795 | 0.76558 | 0.25704 | 3.1022 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-10-19 | 16 | 27.2649 | 11.3824 | 38.6473 | 2.5982 | 0.76558 | 0.28731 | 3.6511 | 9.447% | 10.05% | 6.793% | 1.1043 | 1.1118 | 1.0729
2010-10-19 | 17 | 28.7648 | 12.3121 | 41.0769 | 2.9351 | 0.76558 | 0.30537 | 4.0061 | 9.753% | 10.38% | 7.012% | 1.1081 | 1.1158 | 1.0754
2010-10-19 | 18 | 29.0591 | 12.4762 | 41.5353 | 3.001 | 0.76558 | 0.30878 | 4.0754 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-10-19 | 19 | 28.8369 | 12.1618 | 40.9987 | 2.924 | 0.76558 | 0.30479 | 3.9943 | 9.743% | 10.37% | 7.005% | 1.1079 | 1.1156 | 1.0753
2010-10-19 | 20 | 27.7698 | 11.604 | 39.3737 | 2.6968 | 0.76558 | 0.29271 | 3.7551 | 9.537% | 10.15% | 6.857% | 1.1054 | 1.1129 | 1.0736
2010-10-19 | 21 | 27.8661 | 10.9325 | 38.7987 | 2.6186 | 0.76558 | 0.28843 | 3.6726 | 9.466% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-10-19 | 22 | 27.2406 | 10.7666 | 38.0071 | 2.5128 | 0.76558 | 0.28255 | 3.561 | 9.369% | 9.969% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-10-19 | 23 | 26.3007 | 10.3333 | 36.634 | 2.3345 | 0.76558 | 0.27234 | 3.3725 | 9.206% | 9.795% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-10-19 | 24 | 25.403 | 9.9975 | 35.4005 | 2.18 | 0.76558 | 0.26317 | 3.2087 | 9.064% | 9.644% | 6.517% | 1.0997 | 1.1067 | 1.0697
2010-10-19 | 25 | 24.1123 | 9.8799 | 33.9922 | 2.01 | 0.76558 | 0.2527 | 3.0283 | 8.909% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-10-19 | 26 | 22.7918 | 9.4582 | 32.25 | 1.8092 | 0.76558 | 0.23975 | 2.8146 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-10-19 | 27 | 22.7341 | 9.2847 | 32.0188 | 1.7834 | 0.76558 | 0.23803 | 2.787 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-10-19 | 28 | 23.0683 | 8.9155 | 31.9839 | 1.7795 | 0.76558 | 0.23777 | 2.7828 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-10-19 | 29 | 22.5213 | 8.6307 | 31.1519 | 1.6881 | 0.76558 | 0.23159 | 2.6853 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-10-19 | 30 | 21.8186 | 8.576 | 30.3946 | 1.607 | 0.76558 | 0.22596 | 2.5986 | 8.549% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-10-19 | 31 | 22.197 | 8.3608 | 30.5579 | 1.6244 | 0.76558 | 0.22717 | 2.6171 | 8.564% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-10-19 | 32 | 22.758 | 8.8694 | 31.6275 | 1.7401 | 0.76558 | 0.23512 | 2.7408 | 8.666% | 9.22% | 6.231% | 1.0949 | 1.1016 | 1.0664
2010-10-19 | 33 | 23.0271 | 9.2507 | 32.2779 | 1.8124 | 0.76558 | 0.23996 | 2.8179 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-10-19 | 34 | 22.8414 | 9.5047 | 32.3461 | 1.82 | 0.76558 | 0.24046 | 2.8261 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-10-19 | 35 | 22.7772 | 10.1185 | 32.8957 | 1.8824 | 0.76558 | 0.24455 | 2.8925 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2010-10-19 | 36 | 23.8697 | 10.7098 | 34.5796 | 2.0801 | 0.76558 | 0.25707 | 3.1027 | 8.973% | 9.547% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-10-19 | 37 | 25.511 | 10.8905 | 36.4014 | 2.305 | 0.76558 | 0.27061 | 3.3412 | 9.179% | 9.766% | 6.6% | 1.1011 | 1.1082 | 1.0707
2010-10-19 | 38 | 27.4182 | 10.7915 | 38.2098 | 2.5397 | 0.76558 | 0.28406 | 3.5893 | 9.394% | 9.995% | 6.754% | 1.1037 | 1.111 | 1.0724
2010-10-19 | 39 | 28.6944 | 10.8177 | 39.5121 | 2.7158 | 0.76558 | 0.29374 | 3.7751 | 9.554% | 10.17% | 6.87% | 1.1056 | 1.1132 | 1.0738
2010-10-19 | 40 | 29.6531 | 10.6823 | 40.3354 | 2.8301 | 0.76558 | 0.29986 | 3.8956 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-10-19 | 41 | 30.1992 | 10.4524 | 40.6516 | 2.8747 | 0.76558 | 0.30221 | 3.9425 | 9.698% | 10.32% | 6.973% | 1.1074 | 1.1151 | 1.075
2010-10-19 | 42 | 30.5212 | 10.4123 | 40.9335 | 2.9147 | 0.76558 | 0.3043 | 3.9846 | 9.734% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2010-10-19 | 43 | 29.4159 | 9.9483 | 39.3642 | 2.6955 | 0.76558 | 0.29264 | 3.7537 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2010-10-19 | 44 | 27.994 | 9.2556 | 37.2496 | 2.4137 | 0.76558 | 0.27692 | 3.4562 | 9.278% | 9.872% | 6.671% | 1.1023 | 1.1095 | 1.0715
2010-10-19 | 45 | 25.5524 | 8.2016 | 33.754 | 1.9819 | 0.76558 | 0.25093 | 2.9984 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-10-19 | 46 | 22.7867 | 7.1591 | 29.9458 | 1.5599 | 0.76558 | 0.22262 | 2.5481 | 8.509% | 9.054% | 6.118% | 1.093 | 1.0996 | 1.0652
2010-10-19 | 47 | 21.2851 | 6.7656 | 28.0507 | 1.3687 | 0.76558 | 0.20853 | 2.3429 | 8.352% | 8.887% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-10-19 | 48 | 20.7673 | 6.9438 | 27.7111 | 1.3358 | 0.76558 | 0.20601 | 2.3074 | 8.327% | 8.859% | 5.987% | 1.0908 | 1.0972 | 1.0637
2010-10-20 | 1 | 19.2433 | 6.1915 | 25.4348 | 1.1254 | 0.76558 | 0.18909 | 2.08 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-10-20 | 2 | 17.9072 | 5.6322 | 23.5394 | 0.96389 | 0.76558 | 0.175 | 1.9045 | 8.091% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-10-20 | 3 | 17.0392 | 5.4341 | 22.4733 | 0.87856 | 0.76558 | 0.16707 | 1.8112 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-10-20 | 4 | 16.5282 | 5.2038 | 21.7319 | 0.82154 | 0.76558 | 0.16156 | 1.7487 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 5 | 16.3222 | 5.1607 | 21.483 | 0.80283 | 0.76558 | 0.15971 | 1.7281 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 6 | 16.4222 | 5.069 | 21.4912 | 0.80344 | 0.76558 | 0.15977 | 1.7288 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 7 | 15.9475 | 5.0724 | 21.0199 | 0.76859 | 0.76558 | 0.15626 | 1.6904 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 8 | 15.9712 | 5.0907 | 21.0619 | 0.77167 | 0.76558 | 0.15658 | 1.6938 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 9 | 15.9592 | 5.2673 | 21.2266 | 0.78378 | 0.76558 | 0.1578 | 1.7072 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 10 | 16.2232 | 5.326 | 21.5492 | 0.80779 | 0.76558 | 0.1602 | 1.7336 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-20 | 11 | 16.9349 | 5.4114 | 22.3463 | 0.86865 | 0.76558 | 0.16613 | 1.8004 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-20 | 12 | 17.8269 | 5.8343 | 23.6612 | 0.97389 | 0.76558 | 0.1759 | 1.9154 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-10-20 | 13 | 19.6528 | 6.7216 | 26.3744 | 1.21 | 0.76558 | 0.19607 | 2.1717 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-10-20 | 14 | 22.4974 | 8.2045 | 30.7019 | 1.6397 | 0.76558 | 0.22824 | 2.6335 | 8.578% | 9.127% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-10-20 | 15 | 26.8041 | 10.3981 | 37.2022 | 2.4075 | 0.76558 | 0.27657 | 3.4497 | 9.273% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-10-20 | 16 | 28.9742 | 11.614 | 40.5883 | 2.8657 | 0.76558 | 0.30174 | 3.9331 | 9.69% | 10.31% | 6.967% | 1.1073 | 1.115 | 1.0749
2010-10-20 | 17 | 29.5344 | 11.6376 | 41.172 | 2.9488 | 0.76558 | 0.30608 | 4.0204 | 9.765% | 10.39% | 7.021% | 1.1082 | 1.1159 | 1.0755
2010-10-20 | 18 | 30.6788 | 11.7373 | 42.4161 | 3.1297 | 0.76558 | 0.31533 | 4.2106 | 9.927% | 10.56% | 7.137% | 1.1102 | 1.1181 | 1.0769
2010-10-20 | 19 | 30.5569 | 11.4776 | 42.0345 | 3.0736 | 0.76558 | 0.31249 | 4.1517 | 9.877% | 10.51% | 7.101% | 1.1096 | 1.1174 | 1.0764
2010-10-20 | 20 | 29.5243 | 10.9924 | 40.5167 | 2.8556 | 0.76558 | 0.30121 | 3.9224 | 9.681% | 10.3% | 6.961% | 1.1072 | 1.1148 | 1.0748
2010-10-20 | 21 | 29.0325 | 10.7657 | 39.7983 | 2.7553 | 0.76558 | 0.29587 | 3.8167 | 9.59% | 10.2% | 6.895% | 1.1061 | 1.1136 | 1.0741
2010-10-20 | 22 | 27.8884 | 10.4249 | 38.3133 | 2.5535 | 0.76558 | 0.28483 | 3.6039 | 9.406% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2010-10-20 | 23 | 26.5025 | 9.9958 | 36.4984 | 2.3173 | 0.76558 | 0.27133 | 3.3542 | 9.19% | 9.778% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-10-20 | 24 | 25.3592 | 10.0271 | 35.3863 | 2.1782 | 0.76558 | 0.26307 | 3.2069 | 9.062% | 9.642% | 6.516% | 1.0997 | 1.1067 | 1.0697
2010-10-20 | 25 | 24.2866 | 9.6234 | 33.91 | 2.0003 | 0.76558 | 0.25209 | 3.0179 | 8.9% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-10-20 | 26 | 23.215 | 8.9736 | 32.1885 | 1.8023 | 0.76558 | 0.23929 | 2.8072 | 8.721% | 9.279% | 6.271% | 1.0955 | 1.1023 | 1.0669
2010-10-20 | 27 | 22.9319 | 9.0292 | 31.9611 | 1.777 | 0.76558 | 0.2376 | 2.7801 | 8.699% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-10-20 | 28 | 22.9347 | 8.8999 | 31.8346 | 1.7629 | 0.76558 | 0.23666 | 2.7652 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-10-20 | 29 | 22.1895 | 8.4078 | 30.5973 | 1.6285 | 0.76558 | 0.22746 | 2.6216 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-10-20 | 30 | 21.7589 | 8.2589 | 30.0178 | 1.5674 | 0.76558 | 0.22316 | 2.5562 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-10-20 | 31 | 21.9203 | 8.0945 | 30.0149 | 1.5671 | 0.76558 | 0.22313 | 2.5559 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-10-20 | 32 | 21.7675 | 8.0176 | 29.7851 | 1.5432 | 0.76558 | 0.22143 | 2.5302 | 8.495% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2010-10-20 | 33 | 21.6956 | 8.3415 | 30.0371 | 1.5695 | 0.76558 | 0.2233 | 2.5583 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-10-20 | 34 | 21.4255 | 8.1954 | 29.6209 | 1.5263 | 0.76558 | 0.22021 | 2.512 | 8.481% | 9.023% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-10-20 | 35 | 21.674 | 8.6892 | 30.3632 | 1.6037 | 0.76558 | 0.22572 | 2.595 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-10-20 | 36 | 22.2759 | 9.2296 | 31.5056 | 1.7267 | 0.76558 | 0.23422 | 2.7265 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2010-10-20 | 37 | 23.4117 | 9.4578 | 32.8695 | 1.8794 | 0.76558 | 0.24436 | 2.8893 | 8.79% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-10-20 | 38 | 24.4348 | 9.6033 | 34.0381 | 2.0154 | 0.76558 | 0.25304 | 3.034 | 8.914% | 9.484% | 6.409% | 1.0979 | 1.1048 | 1.0685
2010-10-20 | 39 | 24.9835 | 9.7951 | 34.7786 | 2.1041 | 0.76558 | 0.25855 | 3.1282 | 8.995% | 9.57% | 6.467% | 1.0988 | 1.1058 | 1.0691
2010-10-20 | 40 | 25.2903 | 9.6917 | 34.982 | 2.1287 | 0.76558 | 0.26006 | 3.1544 | 9.017% | 9.594% | 6.483% | 1.0991 | 1.1061 | 1.0693
2010-10-20 | 41 | 26.563 | 9.8277 | 36.3907 | 2.3036 | 0.76558 | 0.27053 | 3.3398 | 9.177% | 9.765% | 6.599% | 1.101 | 1.1082 | 1.0706
2010-10-20 | 42 | 27.8409 | 10.0028 | 37.8437 | 2.4913 | 0.76558 | 0.28133 | 3.5382 | 9.349% | 9.948% | 6.722% | 1.1031 | 1.1105 | 1.0721
2010-10-20 | 43 | 27.5175 | 9.7708 | 37.2884 | 2.4187 | 0.76558 | 0.27721 | 3.4615 | 9.283% | 9.877% | 6.674% | 1.1023 | 1.1096 | 1.0715
2010-10-20 | 44 | 26.476 | 9.3421 | 35.8181 | 2.2317 | 0.76558 | 0.26628 | 3.2636 | 9.112% | 9.695% | 6.551% | 1.1002 | 1.1074 | 1.0701
2010-10-20 | 45 | 24.4103 | 8.2949 | 32.7052 | 1.8607 | 0.76558 | 0.24313 | 2.8694 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-10-20 | 46 | 22.0866 | 7.3425 | 29.4291 | 1.5066 | 0.76558 | 0.21878 | 2.4909 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-10-20 | 47 | 20.8268 | 6.9133 | 27.74 | 1.3386 | 0.76558 | 0.20622 | 2.3104 | 8.329% | 8.862% | 5.988% | 1.0909 | 1.0972 | 1.0637
2010-10-20 | 48 | 19.8712 | 7.058 | 26.9291 | 1.2615 | 0.76558 | 0.20019 | 2.2273 | 8.271% | 8.8% | 5.947% | 1.0902 | 1.0965 | 1.0632
2010-10-21 | 1 | 18.0898 | 6.1766 | 24.2664 | 1.0243 | 0.76558 | 0.1804 | 1.9703 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-10-21 | 2 | 16.6818 | 5.7013 | 22.3831 | 0.87152 | 0.76558 | 0.1664 | 1.8035 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-21 | 3 | 15.9281 | 5.4189 | 21.347 | 0.7927 | 0.76558 | 0.1587 | 1.717 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-21 | 4 | 15.4488 | 5.3753 | 20.8241 | 0.75434 | 0.76558 | 0.15481 | 1.6747 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-21 | 5 | 14.9027 | 5.1903 | 20.0929 | 0.7023 | 0.76558 | 0.14937 | 1.6172 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-21 | 6 | 14.8071 | 5.0211 | 19.8283 | 0.68392 | 0.76558 | 0.14741 | 1.5969 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-10-21 | 7 | 14.3077 | 4.9985 | 19.3062 | 0.64838 | 0.76558 | 0.14352 | 1.5575 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-10-21 | 8 | 14.413 | 5.0565 | 19.4695 | 0.65939 | 0.76558 | 0.14474 | 1.5697 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-21 | 9 | 14.532 | 5.0031 | 19.5352 | 0.66385 | 0.76558 | 0.14523 | 1.5747 | 8.061% | 8.576% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-10-21 | 10 | 15.0063 | 5.2389 | 20.2452 | 0.71298 | 0.76558 | 0.15051 | 1.6291 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-21 | 11 | 15.4266 | 5.4265 | 20.8531 | 0.75644 | 0.76558 | 0.15502 | 1.677 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-21 | 12 | 16.0784 | 5.7388 | 21.8171 | 0.828 | 0.76558 | 0.16219 | 1.7558 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-21 | 13 | 17.7887 | 6.4749 | 24.2635 | 1.0241 | 0.76558 | 0.18038 | 1.9701 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-10-21 | 14 | 20.5684 | 7.9839 | 28.5523 | 1.4181 | 0.76558 | 0.21226 | 2.396 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2010-10-21 | 15 | 24.1171 | 10.1379 | 34.255 | 2.0412 | 0.76558 | 0.25466 | 3.0614 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2010-10-21 | 16 | 26.5684 | 11.0842 | 37.6526 | 2.4662 | 0.76558 | 0.27991 | 3.5117 | 9.327% | 9.923% | 6.706% | 1.1029 | 1.1102 | 1.0719
2010-10-21 | 17 | 27.7926 | 11.3151 | 39.1076 | 2.6605 | 0.76558 | 0.29073 | 3.7168 | 9.504% | 10.11% | 6.833% | 1.105 | 1.1125 | 1.0733
2010-10-21 | 18 | 28.023 | 11.5272 | 39.5503 | 2.721 | 0.76558 | 0.29402 | 3.7806 | 9.559% | 10.17% | 6.873% | 1.1057 | 1.1132 | 1.0738
2010-10-21 | 19 | 27.6674 | 11.0139 | 38.6813 | 2.6028 | 0.76558 | 0.28756 | 3.6559 | 9.451% | 10.06% | 6.796% | 1.1044 | 1.1118 | 1.0729
2010-10-21 | 20 | 26.5145 | 10.4649 | 36.9794 | 2.3788 | 0.76558 | 0.27491 | 3.4193 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-10-21 | 21 | 26.0535 | 10.2012 | 36.2547 | 2.2865 | 0.76558 | 0.26952 | 3.3216 | 9.162% | 9.748% | 6.587% | 1.1009 | 1.108 | 1.0705
2010-10-21 | 22 | 24.9235 | 10.1526 | 35.0761 | 2.1402 | 0.76558 | 0.26076 | 3.1666 | 9.028% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-10-21 | 23 | 24.2011 | 9.7087 | 33.9099 | 2.0003 | 0.76558 | 0.25209 | 3.0179 | 8.9% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-10-21 | 24 | 23.5233 | 9.6199 | 33.1431 | 1.9108 | 0.76558 | 0.24639 | 2.9228 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2010-10-21 | 25 | 22.9555 | 9.2886 | 32.2441 | 1.8086 | 0.76558 | 0.23971 | 2.8139 | 8.727% | 9.285% | 6.275% | 1.0956 | 1.1024 | 1.0669
2010-10-21 | 26 | 22.4045 | 8.7556 | 31.1601 | 1.689 | 0.76558 | 0.23165 | 2.6862 | 8.621% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-10-21 | 27 | 22.374 | 9.0186 | 31.3926 | 1.7143 | 0.76558 | 0.23338 | 2.7133 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-10-21 | 28 | 22.0267 | 8.9916 | 31.0183 | 1.6737 | 0.76558 | 0.23059 | 2.6698 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-10-21 | 29 | 21.6623 | 8.532 | 30.1943 | 1.5859 | 0.76558 | 0.22447 | 2.576 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-10-21 | 30 | 21.1252 | 8.1981 | 29.3233 | 1.4958 | 0.76558 | 0.21799 | 2.4793 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2010-10-21 | 31 | 21.4523 | 8.2638 | 29.7161 | 1.5361 | 0.76558 | 0.22091 | 2.5226 | 8.489% | 9.032% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-10-21 | 32 | 21.7647 | 8.3685 | 30.1332 | 1.5795 | 0.76558 | 0.22401 | 2.5691 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-10-21 | 33 | 21.9064 | 8.6802 | 30.5866 | 1.6274 | 0.76558 | 0.22738 | 2.6204 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-10-21 | 34 | 22.1827 | 8.8484 | 31.0311 | 1.6751 | 0.76558 | 0.23069 | 2.6713 | 8.609% | 9.159% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-10-21 | 35 | 22.1569 | 9.2678 | 31.4247 | 1.7178 | 0.76558 | 0.23362 | 2.717 | 8.646% | 9.199% | 6.217% | 1.0946 | 1.1013 | 1.0663
2010-10-21 | 36 | 22.6791 | 9.6724 | 32.3515 | 1.8206 | 0.76558 | 0.2405 | 2.8267 | 8.738% | 9.297% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-10-21 | 37 | 24.0281 | 9.7129 | 33.741 | 1.9804 | 0.76558 | 0.25083 | 2.9968 | 8.882% | 9.45% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-10-21 | 38 | 24.9574 | 9.5767 | 34.5341 | 2.0746 | 0.76558 | 0.25673 | 3.0969 | 8.968% | 9.542% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-10-21 | 39 | 25.2213 | 9.3302 | 34.5515 | 2.0767 | 0.76558 | 0.25686 | 3.0991 | 8.97% | 9.544% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-10-21 | 40 | 25.8921 | 9.3503 | 35.2425 | 2.1606 | 0.76558 | 0.262 | 3.1881 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-10-21 | 41 | 26.4791 | 9.4942 | 35.9734 | 2.2511 | 0.76558 | 0.26743 | 3.2841 | 9.129% | 9.714% | 6.564% | 1.1005 | 1.1076 | 1.0703
2010-10-21 | 42 | 26.9841 | 9.8827 | 36.8668 | 2.3643 | 0.76558 | 0.27407 | 3.404 | 9.233% | 9.824% | 6.639% | 1.1017 | 1.1089 | 1.0711
2010-10-21 | 43 | 26.02 | 9.5205 | 35.5404 | 2.1973 | 0.76558 | 0.26421 | 3.227 | 9.08% | 9.661% | 6.528% | 1.0999 | 1.1069 | 1.0698
2010-10-21 | 44 | 25.0282 | 8.9932 | 34.0214 | 2.0134 | 0.76558 | 0.25292 | 3.0319 | 8.912% | 9.482% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-10-21 | 45 | 22.9143 | 8.0701 | 30.9844 | 1.67 | 0.76558 | 0.23034 | 2.6659 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-10-21 | 46 | 20.7236 | 7.1251 | 27.8488 | 1.3491 | 0.76558 | 0.20703 | 2.3217 | 8.337% | 8.87% | 5.994% | 1.091 | 1.0973 | 1.0638
2010-10-21 | 47 | 19.3215 | 6.8608 | 26.1823 | 1.1925 | 0.76558 | 0.19464 | 2.1527 | 8.222% | 8.748% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-10-21 | 48 | 18.7386 | 7.0506 | 25.7892 | 1.1569 | 0.76558 | 0.19172 | 2.1142 | 8.198% | 8.723% | 5.894% | 1.0893 | 1.0956 | 1.0626
2010-10-22 | 1 | 17.3396 | 6.3592 | 23.6988 | 0.97699 | 0.76558 | 0.17618 | 1.9187 | 8.096% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-10-22 | 2 | 16.1871 | 5.7957 | 21.9829 | 0.84063 | 0.76558 | 0.16342 | 1.7696 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-22 | 3 | 15.49 | 5.5589 | 21.0489 | 0.77071 | 0.76558 | 0.15648 | 1.6928 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-22 | 4 | 14.9834 | 5.2488 | 20.2322 | 0.71207 | 0.76558 | 0.15041 | 1.6281 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-22 | 5 | 14.4654 | 5.0862 | 19.5516 | 0.66496 | 0.76558 | 0.14535 | 1.5759 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-10-22 | 6 | 14.3521 | 5.052 | 19.4041 | 0.65497 | 0.76558 | 0.14425 | 1.5648 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-10-22 | 7 | 13.9789 | 5.0498 | 19.0288 | 0.62988 | 0.76558 | 0.14146 | 1.5369 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-10-22 | 8 | 14.151 | 5.07 | 19.221 | 0.64267 | 0.76558 | 0.14289 | 1.5511 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-22 | 9 | 13.9814 | 5.2524 | 19.2338 | 0.64352 | 0.76558 | 0.14299 | 1.5521 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-22 | 10 | 14.4419 | 5.2132 | 19.655 | 0.67202 | 0.76558 | 0.14612 | 1.5837 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-22 | 11 | 14.9618 | 5.3101 | 20.272 | 0.71487 | 0.76558 | 0.1507 | 1.6312 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-22 | 12 | 15.6943 | 5.7984 | 21.4927 | 0.80356 | 0.76558 | 0.15978 | 1.7289 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-22 | 13 | 17.4048 | 6.704 | 24.1089 | 1.0111 | 0.76558 | 0.17923 | 1.9559 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-10-22 | 14 | 19.8687 | 8.1086 | 27.9773 | 1.3616 | 0.76558 | 0.20799 | 2.3352 | 8.347% | 8.881% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-10-22 | 15 | 23.5532 | 9.8362 | 33.3894 | 1.9393 | 0.76558 | 0.24822 | 2.9531 | 8.845% | 9.411% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-10-22 | 16 | 25.9572 | 10.7229 | 36.6801 | 2.3404 | 0.76558 | 0.27268 | 3.3787 | 9.211% | 9.801% | 6.623% | 1.1015 | 1.1087 | 1.0709
2010-10-22 | 17 | 27.4037 | 11.3938 | 38.7975 | 2.6184 | 0.76558 | 0.28843 | 3.6724 | 9.466% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-10-22 | 18 | 27.3957 | 11.5578 | 38.9536 | 2.6395 | 0.76558 | 0.28959 | 3.6947 | 9.485% | 10.09% | 6.82% | 1.1048 | 1.1122 | 1.0732
2010-10-22 | 19 | 26.6284 | 11.3055 | 37.9338 | 2.5032 | 0.76558 | 0.282 | 3.5507 | 9.36% | 9.959% | 6.73% | 1.1033 | 1.1106 | 1.0722
2010-10-22 | 20 | 25.4843 | 10.8108 | 36.2951 | 2.2916 | 0.76558 | 0.26982 | 3.327 | 9.166% | 9.753% | 6.591% | 1.1009 | 1.1081 | 1.0706
2010-10-22 | 21 | 25.2731 | 10.4062 | 35.6793 | 2.2145 | 0.76558 | 0.26524 | 3.2453 | 9.096% | 9.678% | 6.54% | 1.1001 | 1.1071 | 1.07
2010-10-22 | 22 | 24.5161 | 9.9538 | 34.47 | 2.0669 | 0.76558 | 0.25625 | 3.0887 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-10-22 | 23 | 23.8491 | 9.3527 | 33.2017 | 1.9176 | 0.76558 | 0.24683 | 2.93 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-10-22 | 24 | 23.2316 | 9.1308 | 32.3624 | 1.8219 | 0.76558 | 0.24059 | 2.828 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-10-22 | 25 | 22.2325 | 9.0416 | 31.2741 | 1.7014 | 0.76558 | 0.2325 | 2.6995 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-10-22 | 26 | 21.5666 | 8.7038 | 30.2704 | 1.5939 | 0.76558 | 0.22503 | 2.5845 | 8.538% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-10-22 | 27 | 21.4459 | 8.9461 | 30.392 | 1.6068 | 0.76558 | 0.22594 | 2.5983 | 8.549% | 9.096% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-10-22 | 28 | 21.3111 | 8.7139 | 30.025 | 1.5682 | 0.76558 | 0.22321 | 2.557 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-10-22 | 29 | 20.8248 | 8.4298 | 29.2546 | 1.4888 | 0.76558 | 0.21748 | 2.4718 | 8.449% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-10-22 | 30 | 20.3631 | 8.3711 | 28.7343 | 1.4363 | 0.76558 | 0.21361 | 2.4155 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-10-22 | 31 | 21.005 | 8.4599 | 29.4649 | 1.5102 | 0.76558 | 0.21905 | 2.4949 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-10-22 | 32 | 21.1112 | 8.4163 | 29.5275 | 1.5167 | 0.76558 | 0.21951 | 2.5017 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-10-22 | 33 | 21.2504 | 8.5833 | 29.8337 | 1.5483 | 0.76558 | 0.22179 | 2.5356 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-10-22 | 34 | 21.8361 | 8.6654 | 30.5015 | 1.6184 | 0.76558 | 0.22675 | 2.6107 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-10-22 | 35 | 22.5506 | 9.0988 | 31.6494 | 1.7425 | 0.76558 | 0.23529 | 2.7433 | 8.668% | 9.223% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-22 | 36 | 23.5808 | 9.4823 | 33.0631 | 1.9016 | 0.76558 | 0.2458 | 2.913 | 8.81% | 9.374% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-10-22 | 37 | 25.3713 | 9.7391 | 35.1104 | 2.1444 | 0.76558 | 0.26102 | 3.171 | 9.032% | 9.61% | 6.494% | 1.0993 | 1.1063 | 1.0694
2010-10-22 | 38 | 25.878 | 9.7966 | 35.6746 | 2.2139 | 0.76558 | 0.26521 | 3.2447 | 9.095% | 9.677% | 6.539% | 1.1001 | 1.1071 | 1.07
2010-10-22 | 39 | 26.2011 | 9.7439 | 35.945 | 2.2476 | 0.76558 | 0.26722 | 3.2804 | 9.126% | 9.71% | 6.562% | 1.1004 | 1.1075 | 1.0702
2010-10-22 | 40 | 26.5457 | 9.488 | 36.0336 | 2.2587 | 0.76558 | 0.26788 | 3.2921 | 9.136% | 9.721% | 6.569% | 1.1005 | 1.1077 | 1.0703
2010-10-22 | 41 | 27.1598 | 9.719 | 36.8788 | 2.3659 | 0.76558 | 0.27416 | 3.4056 | 9.235% | 9.826% | 6.64% | 1.1017 | 1.109 | 1.0711
2010-10-22 | 42 | 28.5521 | 10.2764 | 38.8284 | 2.6226 | 0.76558 | 0.28866 | 3.6768 | 9.469% | 10.08% | 6.809% | 1.1046 | 1.112 | 1.0731
2010-10-22 | 43 | 27.5024 | 9.9431 | 37.4455 | 2.4391 | 0.76558 | 0.27837 | 3.4831 | 9.302% | 9.897% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-10-22 | 44 | 26.5744 | 9.5846 | 36.159 | 2.2744 | 0.76558 | 0.26881 | 3.3088 | 9.151% | 9.736% | 6.579% | 1.1007 | 1.1079 | 1.0704
2010-10-22 | 45 | 24.7371 | 8.6285 | 33.3656 | 1.9366 | 0.76558 | 0.24804 | 2.9502 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-10-22 | 46 | 22.3931 | 7.5738 | 29.9669 | 1.5621 | 0.76558 | 0.22278 | 2.5505 | 8.511% | 9.056% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-10-22 | 47 | 21.0496 | 7.2574 | 28.3071 | 1.3939 | 0.76558 | 0.21044 | 2.3699 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-10-22 | 48 | 20.3796 | 7.2847 | 27.6643 | 1.3313 | 0.76558 | 0.20566 | 2.3025 | 8.323% | 8.856% | 5.984% | 1.0908 | 1.0972 | 1.0637
2010-10-23 | 1 | 18.736 | 6.4339 | 25.1699 | 1.102 | 0.76558 | 0.18712 | 2.0547 | 8.163% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-10-23 | 2 | 17.6022 | 6.0902 | 23.6924 | 0.97645 | 0.76558 | 0.17613 | 1.9182 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-10-23 | 3 | 16.7123 | 6.3683 | 23.0807 | 0.92668 | 0.76558 | 0.17158 | 1.8638 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-10-23 | 4 | 16.2747 | 7.3882 | 23.663 | 0.97403 | 0.76558 | 0.17591 | 1.9155 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-10-23 | 5 | 15.8011 | 8.3884 | 24.1895 | 1.0179 | 0.76558 | 0.17983 | 1.9633 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-10-23 | 6 | 15.5708 | 8.6168 | 24.1875 | 1.0177 | 0.76558 | 0.17981 | 1.9631 | 8.116% | 8.636% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-10-23 | 7 | 15.3781 | 8.6672 | 24.0453 | 1.0058 | 0.76558 | 0.17876 | 1.9501 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-10-23 | 8 | 15.478 | 8.7403 | 24.2183 | 1.0203 | 0.76558 | 0.18004 | 1.9659 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-10-23 | 9 | 15.8285 | 8.8464 | 24.6749 | 1.0591 | 0.76558 | 0.18344 | 2.0081 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0622
2010-10-23 | 10 | 16.1502 | 8.9974 | 25.1476 | 1.1001 | 0.76558 | 0.18695 | 2.0526 | 8.162% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2010-10-23 | 11 | 16.8069 | 9.2143 | 26.0212 | 1.1778 | 0.76558 | 0.19344 | 2.1369 | 8.212% | 8.738% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-10-23 | 12 | 17.6548 | 9.7514 | 27.4062 | 1.3066 | 0.76558 | 0.20374 | 2.2759 | 8.304% | 8.836% | 5.971% | 1.0906 | 1.0969 | 1.0635
2010-10-23 | 13 | 19.3945 | 10.7787 | 30.1732 | 1.5837 | 0.76558 | 0.22431 | 2.5736 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2010-10-23 | 14 | 21.9871 | 12.3579 | 34.3451 | 2.0519 | 0.76558 | 0.25533 | 3.0728 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-10-23 | 15 | 26.037 | 14.5733 | 40.6104 | 2.8689 | 0.76558 | 0.3019 | 3.9363 | 9.693% | 10.31% | 6.969% | 1.1073 | 1.115 | 1.0749
2010-10-23 | 16 | 28.2844 | 15.3461 | 43.6305 | 3.3114 | 0.76558 | 0.32435 | 4.4014 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2010-10-23 | 17 | 29.372 | 14.4744 | 43.8463 | 3.3443 | 0.76558 | 0.32596 | 4.4358 | 10.12% | 10.76% | 7.274% | 1.1126 | 1.1206 | 1.0784
2010-10-23 | 18 | 29.2823 | 12.6935 | 41.9758 | 3.065 | 0.76558 | 0.31205 | 4.1426 | 9.869% | 10.5% | 7.096% | 1.1095 | 1.1173 | 1.0764
2010-10-23 | 19 | 28.3034 | 11.6398 | 39.9432 | 2.7754 | 0.76558 | 0.29694 | 3.8379 | 9.608% | 10.22% | 6.908% | 1.1063 | 1.1139 | 1.0742
2010-10-23 | 20 | 27.2174 | 11.0934 | 38.3108 | 2.5532 | 0.76558 | 0.28481 | 3.6035 | 9.406% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2010-10-23 | 21 | 26.9439 | 10.2906 | 37.2345 | 2.4117 | 0.76558 | 0.27681 | 3.4541 | 9.277% | 9.87% | 6.67% | 1.1023 | 1.1095 | 1.0715
2010-10-23 | 22 | 26.1761 | 9.9319 | 36.108 | 2.268 | 0.76558 | 0.26843 | 3.302 | 9.145% | 9.73% | 6.575% | 1.1007 | 1.1078 | 1.0704
2010-10-23 | 23 | 24.8199 | 9.4779 | 34.2978 | 2.0463 | 0.76558 | 0.25497 | 3.0668 | 8.942% | 9.514% | 6.429% | 1.0982 | 1.1051 | 1.0687
2010-10-23 | 24 | 23.8982 | 9.3142 | 33.2124 | 1.9188 | 0.76558 | 0.24691 | 2.9313 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-10-23 | 25 | 22.8398 | 9.0777 | 31.9175 | 1.7721 | 0.76558 | 0.23728 | 2.775 | 8.694% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-10-23 | 26 | 21.8678 | 8.8205 | 30.6884 | 1.6383 | 0.76558 | 0.22814 | 2.632 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-10-23 | 27 | 21.9934 | 9.0607 | 31.0541 | 1.6775 | 0.76558 | 0.23086 | 2.674 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-10-23 | 28 | 21.8367 | 8.9769 | 30.8136 | 1.6517 | 0.76558 | 0.22907 | 2.6463 | 8.588% | 9.138% | 6.175% | 1.0939 | 1.1006 | 1.0658
2010-10-23 | 29 | 21.5804 | 8.6646 | 30.2449 | 1.5913 | 0.76558 | 0.22484 | 2.5817 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-10-23 | 30 | 20.956 | 8.5693 | 29.5253 | 1.5164 | 0.76558 | 0.21949 | 2.5015 | 8.472% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-10-23 | 31 | 21.1872 | 8.4156 | 29.6028 | 1.5244 | 0.76558 | 0.22007 | 2.5101 | 8.479% | 9.022% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-10-23 | 32 | 21.2884 | 8.1781 | 29.4665 | 1.5104 | 0.76558 | 0.21906 | 2.495 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-10-23 | 33 | 21.1634 | 8.4231 | 29.5865 | 1.5227 | 0.76558 | 0.21995 | 2.5083 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-10-23 | 34 | 21.1453 | 8.4707 | 29.6161 | 1.5258 | 0.76558 | 0.22017 | 2.5115 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2010-10-23 | 35 | 20.7821 | 8.6496 | 29.4317 | 1.5068 | 0.76558 | 0.2188 | 2.4912 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-10-23 | 36 | 20.8508 | 8.9287 | 29.7794 | 1.5427 | 0.76558 | 0.22138 | 2.5296 | 8.494% | 9.038% | 6.108% | 1.0928 | 1.0994 | 1.065
2010-10-23 | 37 | 21.7097 | 9.0624 | 30.7721 | 1.6472 | 0.76558 | 0.22876 | 2.6415 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2010-10-23 | 38 | 22.2946 | 9.3954 | 31.6901 | 1.747 | 0.76558 | 0.23559 | 2.7481 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2010-10-23 | 39 | 22.6959 | 9.2788 | 31.9747 | 1.7785 | 0.76558 | 0.2377 | 2.7818 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-10-23 | 40 | 23.1594 | 9.388 | 32.5473 | 1.8427 | 0.76558 | 0.24196 | 2.8503 | 8.757% | 9.318% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-10-23 | 41 | 24.2301 | 9.592 | 33.8221 | 1.9899 | 0.76558 | 0.25144 | 3.0069 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-10-23 | 42 | 25.7611 | 9.8257 | 35.5868 | 2.203 | 0.76558 | 0.26456 | 3.2331 | 9.085% | 9.667% | 6.532% | 1.0999 | 1.107 | 1.0699
2010-10-23 | 43 | 25.4767 | 9.7495 | 35.2262 | 2.1586 | 0.76558 | 0.26188 | 3.186 | 9.044% | 9.623% | 6.503% | 1.0994 | 1.1065 | 1.0696
2010-10-23 | 44 | 24.4807 | 9.3675 | 33.8482 | 1.993 | 0.76558 | 0.25163 | 3.0102 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2010-10-23 | 45 | 23.211 | 8.6199 | 31.8309 | 1.7625 | 0.76558 | 0.23663 | 2.7647 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-10-23 | 46 | 21.493 | 8.0196 | 29.5127 | 1.5151 | 0.76558 | 0.2194 | 2.5001 | 8.471% | 9.013% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-10-23 | 47 | 20.6158 | 7.7489 | 28.3646 | 1.3996 | 0.76558 | 0.21087 | 2.376 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0978 | 1.0641
2010-10-23 | 48 | 19.942 | 7.7618 | 27.7037 | 1.3351 | 0.76558 | 0.20595 | 2.3066 | 8.326% | 8.859% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-10-24 | 1 | 18.4318 | 6.9725 | 25.4044 | 1.1227 | 0.76558 | 0.18886 | 2.0771 | 8.176% | 8.699% | 5.879% | 1.089 | 1.0953 | 1.0625
2010-10-24 | 2 | 17.1844 | 6.411 | 23.5953 | 0.96847 | 0.76558 | 0.17541 | 1.9095 | 8.093% | 8.61% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-10-24 | 3 | 16.0067 | 6.1815 | 22.1883 | 0.85641 | 0.76558 | 0.16495 | 1.7869 | 8.054% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-24 | 4 | 15.5632 | 5.9566 | 21.5198 | 0.80558 | 0.76558 | 0.15998 | 1.7311 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 5 | 15.1316 | 5.7041 | 20.8357 | 0.75518 | 0.76558 | 0.15489 | 1.6757 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 6 | 15.0319 | 5.5664 | 20.5984 | 0.73807 | 0.76558 | 0.15313 | 1.6568 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 7 | 14.652 | 5.5241 | 20.176 | 0.70812 | 0.76558 | 0.14999 | 1.6237 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 8 | 14.5889 | 5.4578 | 20.0466 | 0.69906 | 0.76558 | 0.14903 | 1.6137 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-24 | 9 | 14.6427 | 5.444 | 20.0867 | 0.70187 | 0.76558 | 0.14933 | 1.6168 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-24 | 10 | 14.8792 | 5.4683 | 20.3475 | 0.72021 | 0.76558 | 0.15127 | 1.637 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 11 | 15.3171 | 5.553 | 20.87 | 0.75767 | 0.76558 | 0.15515 | 1.6784 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 12 | 15.6893 | 5.7183 | 21.4076 | 0.79721 | 0.76558 | 0.15915 | 1.7219 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-24 | 13 | 16.7116 | 6.0801 | 22.7916 | 0.90362 | 0.76558 | 0.16944 | 1.8386 | 8.067% | 8.583% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-10-24 | 14 | 18.0035 | 6.6628 | 24.6663 | 1.0584 | 0.76558 | 0.18337 | 2.0073 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-10-24 | 15 | 19.9975 | 7.4863 | 27.4837 | 1.314 | 0.76558 | 0.20432 | 2.2839 | 8.31% | 8.842% | 5.975% | 1.0906 | 1.097 | 1.0635
2010-10-24 | 16 | 21.6235 | 8.3909 | 30.0144 | 1.5671 | 0.76558 | 0.22313 | 2.5558 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-10-24 | 17 | 23.7075 | 9.5557 | 33.2632 | 1.9247 | 0.76558 | 0.24728 | 2.9376 | 8.831% | 9.396% | 6.35% | 1.0969 | 1.1037 | 1.0678
2010-10-24 | 18 | 25.2912 | 9.9743 | 35.2656 | 2.1634 | 0.76558 | 0.26217 | 3.1911 | 9.049% | 9.628% | 6.506% | 1.0995 | 1.1065 | 1.0696
2010-10-24 | 19 | 26.369 | 10.2633 | 36.6323 | 2.3343 | 0.76558 | 0.27233 | 3.3722 | 9.206% | 9.795% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-10-24 | 20 | 26.1671 | 10.0701 | 36.2372 | 2.2843 | 0.76558 | 0.26939 | 3.3192 | 9.16% | 9.746% | 6.586% | 1.1008 | 1.108 | 1.0705
2010-10-24 | 21 | 26.5167 | 9.956 | 36.4727 | 2.314 | 0.76558 | 0.27114 | 3.3508 | 9.187% | 9.775% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-10-24 | 22 | 25.7593 | 9.6119 | 35.3712 | 2.1764 | 0.76558 | 0.26295 | 3.2049 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-10-24 | 23 | 24.8871 | 9.167 | 34.0541 | 2.0173 | 0.76558 | 0.25316 | 3.0361 | 8.915% | 9.486% | 6.41% | 1.0979 | 1.1048 | 1.0685
2010-10-24 | 24 | 24.1549 | 8.9301 | 33.0849 | 1.9041 | 0.76558 | 0.24596 | 2.9157 | 8.813% | 9.377% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-10-24 | 25 | 23.104 | 9.0366 | 32.1406 | 1.797 | 0.76558 | 0.23894 | 2.8015 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-10-24 | 26 | 22.0816 | 8.5109 | 30.5925 | 1.628 | 0.76558 | 0.22743 | 2.621 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-10-24 | 27 | 21.6176 | 8.4537 | 30.0713 | 1.573 | 0.76558 | 0.22355 | 2.5622 | 8.52% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-10-24 | 28 | 21.1301 | 8.4107 | 29.5408 | 1.518 | 0.76558 | 0.21961 | 2.5032 | 8.474% | 9.016% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-10-24 | 29 | 20.5632 | 7.905 | 28.4682 | 1.4098 | 0.76558 | 0.21164 | 2.387 | 8.385% | 8.921% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-10-24 | 30 | 19.9285 | 7.6393 | 27.5678 | 1.322 | 0.76558 | 0.20494 | 2.2925 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-10-24 | 31 | 20.0911 | 7.4724 | 27.5635 | 1.3216 | 0.76558 | 0.20491 | 2.2921 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-10-24 | 32 | 19.8185 | 7.3852 | 27.2037 | 1.2873 | 0.76558 | 0.20224 | 2.2551 | 8.29% | 8.82% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-10-24 | 33 | 19.9572 | 7.5649 | 27.522 | 1.3176 | 0.76558 | 0.2046 | 2.2878 | 8.313% | 8.845% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-10-24 | 34 | 20.2594 | 7.4154 | 27.6748 | 1.3323 | 0.76558 | 0.20574 | 2.3036 | 8.324% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2010-10-24 | 35 | 20.641 | 7.8808 | 28.5219 | 1.4151 | 0.76558 | 0.21203 | 2.3927 | 8.389% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-10-24 | 36 | 21.1653 | 8.4574 | 29.6227 | 1.5265 | 0.76558 | 0.22022 | 2.5122 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-10-24 | 37 | 22.027 | 8.8124 | 30.8394 | 1.6544 | 0.76558 | 0.22926 | 2.6493 | 8.591% | 9.14% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-10-24 | 38 | 22.4721 | 8.8003 | 31.2724 | 1.7012 | 0.76558 | 0.23248 | 2.6993 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-10-24 | 39 | 22.6708 | 8.6545 | 31.3253 | 1.707 | 0.76558 | 0.23288 | 2.7054 | 8.637% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-10-24 | 40 | 22.7492 | 8.5313 | 31.2805 | 1.7021 | 0.76558 | 0.23254 | 2.7002 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-10-24 | 41 | 23.2794 | 8.6317 | 31.9111 | 1.7714 | 0.76558 | 0.23723 | 2.7742 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-10-24 | 42 | 24.8702 | 8.9661 | 33.8363 | 1.9916 | 0.76558 | 0.25154 | 3.0087 | 8.892% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-10-24 | 43 | 24.7244 | 8.7033 | 33.4277 | 1.9438 | 0.76558 | 0.24851 | 2.9579 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-10-24 | 44 | 23.876 | 8.3312 | 32.2073 | 1.8044 | 0.76558 | 0.23943 | 2.8095 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-10-24 | 45 | 22.3707 | 7.835 | 30.2058 | 1.5871 | 0.76558 | 0.22455 | 2.5773 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2010-10-24 | 46 | 21.0176 | 7.1737 | 28.1913 | 1.3825 | 0.76558 | 0.20958 | 2.3577 | 8.363% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-10-24 | 47 | 20.0193 | 6.8446 | 26.8639 | 1.2554 | 0.76558 | 0.19971 | 2.2207 | 8.266% | 8.795% | 5.943% | 1.0901 | 1.0964 | 1.0632
2010-10-24 | 48 | 19.3273 | 7.0344 | 26.3617 | 1.2089 | 0.76558 | 0.19598 | 2.1704 | 8.233% | 8.76% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-10-25 | 1 | 17.6826 | 6.3507 | 24.0333 | 1.0048 | 0.76558 | 0.17867 | 1.949 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-10-25 | 2 | 16.6587 | 5.79 | 22.4487 | 0.87663 | 0.76558 | 0.16689 | 1.8091 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-10-25 | 3 | 16.1451 | 5.5514 | 21.6965 | 0.81887 | 0.76558 | 0.16129 | 1.7457 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-25 | 4 | 15.4703 | 5.2602 | 20.7305 | 0.74757 | 0.76558 | 0.15411 | 1.6673 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-25 | 5 | 15.11 | 5.0188 | 20.1288 | 0.70481 | 0.76558 | 0.14964 | 1.62 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-25 | 6 | 14.7166 | 4.9935 | 19.7101 | 0.67579 | 0.76558 | 0.14653 | 1.5879 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-10-25 | 7 | 14.6971 | 4.9285 | 19.6256 | 0.67001 | 0.76558 | 0.1459 | 1.5815 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-25 | 8 | 14.5112 | 4.8908 | 19.402 | 0.65483 | 0.76558 | 0.14424 | 1.5646 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-10-25 | 9 | 14.6434 | 4.9672 | 19.6106 | 0.66898 | 0.76558 | 0.14579 | 1.5803 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-25 | 10 | 14.8095 | 5.0727 | 19.8822 | 0.68765 | 0.76558 | 0.14781 | 1.601 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-25 | 11 | 14.874 | 5.1068 | 19.9808 | 0.69448 | 0.76558 | 0.14854 | 1.6086 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-10-25 | 12 | 15.3762 | 5.3062 | 20.6823 | 0.7441 | 0.76558 | 0.15375 | 1.6634 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-25 | 13 | 16.2607 | 5.6056 | 21.8663 | 0.83174 | 0.76558 | 0.16256 | 1.7599 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-25 | 14 | 17.2732 | 5.968 | 23.2412 | 0.93962 | 0.76558 | 0.17278 | 1.878 | 8.08% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-10-25 | 15 | 18.7476 | 6.4865 | 25.234 | 1.1077 | 0.76558 | 0.18759 | 2.0608 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-10-25 | 16 | 20.2439 | 7.3778 | 27.6218 | 1.3272 | 0.76558 | 0.20534 | 2.2981 | 8.32% | 8.852% | 5.982% | 1.0908 | 1.0971 | 1.0636
2010-10-25 | 17 | 22.3642 | 8.3959 | 30.7601 | 1.6459 | 0.76558 | 0.22867 | 2.6402 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-10-25 | 18 | 24.6157 | 9.0836 | 33.6993 | 1.9755 | 0.76558 | 0.25052 | 2.9916 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-10-25 | 19 | 26.5922 | 9.5454 | 36.1376 | 2.2717 | 0.76558 | 0.26865 | 3.3059 | 9.148% | 9.734% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-10-25 | 20 | 27.5462 | 9.9272 | 37.4735 | 2.4428 | 0.76558 | 0.27858 | 3.4869 | 9.305% | 9.901% | 6.69% | 1.1026 | 1.1099 | 1.0717
2010-10-25 | 21 | 28.9305 | 9.93 | 38.8605 | 2.627 | 0.76558 | 0.28889 | 3.6814 | 9.473% | 10.08% | 6.811% | 1.1046 | 1.1121 | 1.0731
2010-10-25 | 22 | 28.8141 | 9.6954 | 38.5095 | 2.5797 | 0.76558 | 0.28628 | 3.6316 | 9.43% | 10.03% | 6.78% | 1.1041 | 1.1115 | 1.0727
2010-10-25 | 23 | 27.9455 | 9.3761 | 37.3216 | 2.423 | 0.76558 | 0.27745 | 3.466 | 9.287% | 9.881% | 6.677% | 1.1024 | 1.1096 | 1.0716
2010-10-25 | 24 | 26.7053 | 9.1589 | 35.8642 | 2.2375 | 0.76558 | 0.26662 | 3.2697 | 9.117% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-10-25 | 25 | 25.37 | 9.0586 | 34.4286 | 2.0619 | 0.76558 | 0.25595 | 3.0835 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2010-10-25 | 26 | 24.4272 | 8.6626 | 33.0897 | 1.9047 | 0.76558 | 0.24599 | 2.9162 | 8.813% | 9.377% | 6.337% | 1.0966 | 1.1035 | 1.0677
2010-10-25 | 27 | 23.6333 | 8.7055 | 32.3388 | 1.8192 | 0.76558 | 0.24041 | 2.8252 | 8.736% | 9.295% | 6.281% | 1.0957 | 1.1025 | 1.067
2010-10-25 | 28 | 22.7873 | 8.8101 | 31.5974 | 1.7368 | 0.76558 | 0.2349 | 2.7372 | 8.663% | 9.217% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-10-25 | 29 | 21.8218 | 8.3945 | 30.2163 | 1.5882 | 0.76558 | 0.22463 | 2.5785 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-10-25 | 30 | 20.8514 | 8.1118 | 28.9632 | 1.4592 | 0.76558 | 0.21532 | 2.4401 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-10-25 | 31 | 20.8909 | 7.7657 | 28.6567 | 1.4285 | 0.76558 | 0.21304 | 2.4071 | 8.4% | 8.938% | 6.04% | 1.0917 | 1.0981 | 1.0643
2010-10-25 | 32 | 20.7225 | 7.6584 | 28.3809 | 1.4012 | 0.76558 | 0.21099 | 2.3777 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-10-25 | 33 | 20.2948 | 7.822 | 28.1167 | 1.3752 | 0.76558 | 0.20902 | 2.3498 | 8.357% | 8.892% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-10-25 | 34 | 20.2285 | 7.8215 | 28.0499 | 1.3687 | 0.76558 | 0.20853 | 2.3428 | 8.352% | 8.887% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-10-25 | 35 | 20.3739 | 8.3086 | 28.6825 | 1.4311 | 0.76558 | 0.21323 | 2.4099 | 8.402% | 8.94% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-10-25 | 36 | 21.3385 | 8.9412 | 30.2797 | 1.5949 | 0.76558 | 0.2251 | 2.5856 | 8.539% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-10-25 | 37 | 22.4594 | 9.1827 | 31.6421 | 1.7417 | 0.76558 | 0.23523 | 2.7425 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-25 | 38 | 22.9479 | 9.1538 | 32.1017 | 1.7926 | 0.76558 | 0.23865 | 2.7969 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-10-25 | 39 | 23.6161 | 9.3932 | 33.0093 | 1.8954 | 0.76558 | 0.2454 | 2.9064 | 8.805% | 9.368% | 6.331% | 1.0965 | 1.1034 | 1.0676
2010-10-25 | 40 | 24.2016 | 9.2739 | 33.4755 | 1.9493 | 0.76558 | 0.24886 | 2.9638 | 8.854% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-10-25 | 41 | 25.0192 | 9.5053 | 34.5244 | 2.0734 | 0.76558 | 0.25666 | 3.0957 | 8.967% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-10-25 | 42 | 26.1202 | 9.7429 | 35.8631 | 2.2373 | 0.76558 | 0.26661 | 3.2695 | 9.117% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2010-10-25 | 43 | 25.3324 | 9.4452 | 34.7776 | 2.1039 | 0.76558 | 0.25854 | 3.1281 | 8.994% | 9.57% | 6.467% | 1.0988 | 1.1058 | 1.0691
2010-10-25 | 44 | 24.067 | 9.0104 | 33.0774 | 1.9033 | 0.76558 | 0.2459 | 2.9147 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-10-25 | 45 | 22.3848 | 8.3586 | 30.7434 | 1.6441 | 0.76558 | 0.22855 | 2.6383 | 8.582% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-10-25 | 46 | 20.7548 | 7.522 | 28.2769 | 1.3909 | 0.76558 | 0.21021 | 2.3667 | 8.37% | 8.905% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-10-25 | 47 | 19.4404 | 7.3803 | 26.8206 | 1.2513 | 0.76558 | 0.19939 | 2.2163 | 8.263% | 8.792% | 5.941% | 1.0901 | 1.0964 | 1.0632
2010-10-25 | 48 | 18.9895 | 7.3679 | 26.3574 | 1.2085 | 0.76558 | 0.19594 | 2.17 | 8.233% | 8.76% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-10-26 | 1 | 17.3198 | 6.5801 | 23.8999 | 0.99363 | 0.76558 | 0.17767 | 1.9369 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-10-26 | 2 | 16.0338 | 5.9944 | 22.0281 | 0.84409 | 0.76558 | 0.16376 | 1.7734 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-10-26 | 3 | 15.1184 | 5.4758 | 20.5942 | 0.73778 | 0.76558 | 0.1531 | 1.6565 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-26 | 4 | 14.3768 | 5.3395 | 19.7164 | 0.67622 | 0.76558 | 0.14657 | 1.5884 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-10-26 | 5 | 13.9665 | 5.2658 | 19.2323 | 0.64343 | 0.76558 | 0.14298 | 1.552 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-26 | 6 | 13.7173 | 5.073 | 18.7903 | 0.61419 | 0.76558 | 0.13969 | 1.5195 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-10-26 | 7 | 13.6161 | 5.0841 | 18.7002 | 0.60831 | 0.76558 | 0.13902 | 1.5129 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-10-26 | 8 | 13.5599 | 5.0406 | 18.6005 | 0.60184 | 0.76558 | 0.13828 | 1.5057 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-10-26 | 9 | 13.694 | 4.9635 | 18.6575 | 0.60554 | 0.76558 | 0.1387 | 1.5098 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-10-26 | 10 | 13.9783 | 4.921 | 18.8994 | 0.62134 | 0.76558 | 0.1405 | 1.5274 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-10-26 | 11 | 14.2247 | 5.0293 | 19.254 | 0.64488 | 0.76558 | 0.14314 | 1.5536 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-10-26 | 12 | 14.6611 | 5.2158 | 19.8768 | 0.68727 | 0.76558 | 0.14777 | 1.6006 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-10-26 | 13 | 15.3952 | 5.4295 | 20.8247 | 0.75438 | 0.76558 | 0.15481 | 1.6748 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-26 | 14 | 15.944 | 5.7396 | 21.6836 | 0.81789 | 0.76558 | 0.1612 | 1.7447 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-26 | 15 | 17.118 | 6.4878 | 23.6058 | 0.96933 | 0.76558 | 0.17549 | 1.9104 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-10-26 | 16 | 19.0242 | 7.2184 | 26.2426 | 1.198 | 0.76558 | 0.19509 | 2.1586 | 8.226% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-10-26 | 17 | 21.3829 | 8.4189 | 29.8018 | 1.545 | 0.76558 | 0.22155 | 2.5321 | 8.496% | 9.04% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-10-26 | 18 | 23.5914 | 9.6521 | 33.2435 | 1.9224 | 0.76558 | 0.24714 | 2.9351 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-10-26 | 19 | 25.2257 | 10.4841 | 35.7098 | 2.2182 | 0.76558 | 0.26547 | 3.2493 | 9.099% | 9.682% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-10-26 | 20 | 26.1958 | 11.0027 | 37.1985 | 2.407 | 0.76558 | 0.27654 | 3.4492 | 9.272% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-10-26 | 21 | 27.8662 | 11.0367 | 38.9029 | 2.6327 | 0.76558 | 0.28921 | 3.6875 | 9.479% | 10.09% | 6.815% | 1.1047 | 1.1122 | 1.0731
2010-10-26 | 22 | 28.406 | 11.2796 | 39.6856 | 2.7397 | 0.76558 | 0.29503 | 3.8003 | 9.576% | 10.19% | 6.885% | 1.1059 | 1.1134 | 1.0739
2010-10-26 | 23 | 28.5591 | 11.186 | 39.7452 | 2.7479 | 0.76558 | 0.29547 | 3.809 | 9.583% | 10.2% | 6.891% | 1.106 | 1.1135 | 1.074
2010-10-26 | 24 | 29.013 | 11.1572 | 40.1702 | 2.807 | 0.76558 | 0.29863 | 3.8712 | 9.637% | 10.25% | 6.929% | 1.1066 | 1.1143 | 1.0744
2010-10-26 | 25 | 28.813 | 11.377 | 40.19 | 2.8098 | 0.76558 | 0.29878 | 3.8741 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2010-10-26 | 26 | 28.3337 | 10.9238 | 39.2575 | 2.6809 | 0.76558 | 0.29185 | 3.7383 | 9.523% | 10.13% | 6.847% | 1.1052 | 1.1127 | 1.0735
2010-10-26 | 27 | 27.91 | 10.8526 | 38.7626 | 2.6137 | 0.76558 | 0.28817 | 3.6675 | 9.461% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2010-10-26 | 28 | 27.5561 | 10.7858 | 38.3419 | 2.5573 | 0.76558 | 0.28504 | 3.6079 | 9.41% | 10.01% | 6.766% | 1.1039 | 1.1113 | 1.0726
2010-10-26 | 29 | 26.9956 | 10.4039 | 37.3995 | 2.4331 | 0.76558 | 0.27803 | 3.4767 | 9.296% | 9.891% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-10-26 | 30 | 26.4798 | 9.9314 | 36.4112 | 2.3062 | 0.76558 | 0.27069 | 3.3425 | 9.18% | 9.767% | 6.6% | 1.1011 | 1.1082 | 1.0707
2010-10-26 | 31 | 26.8318 | 9.7534 | 36.5852 | 2.3283 | 0.76558 | 0.27198 | 3.3659 | 9.2% | 9.789% | 6.615% | 1.1013 | 1.1085 | 1.0708
2010-10-26 | 32 | 26.7219 | 9.5874 | 36.3093 | 2.2934 | 0.76558 | 0.26993 | 3.3289 | 9.168% | 9.755% | 6.592% | 1.1009 | 1.1081 | 1.0706
2010-10-26 | 33 | 26.8914 | 9.8231 | 36.7145 | 2.3448 | 0.76558 | 0.27294 | 3.3833 | 9.215% | 9.805% | 6.626% | 1.1015 | 1.1087 | 1.071
2010-10-26 | 34 | 27.0339 | 10.0346 | 37.0685 | 2.3903 | 0.76558 | 0.27557 | 3.4314 | 9.257% | 9.849% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-10-26 | 35 | 27.7317 | 10.6378 | 38.3695 | 2.561 | 0.76558 | 0.28524 | 3.6118 | 9.413% | 10.02% | 6.768% | 1.1039 | 1.1113 | 1.0726
2010-10-26 | 36 | 28.5797 | 11.3256 | 39.9053 | 2.7701 | 0.76558 | 0.29666 | 3.8323 | 9.604% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-10-26 | 37 | 29.5398 | 11.2983 | 40.8381 | 2.9011 | 0.76558 | 0.3036 | 3.9703 | 9.722% | 10.34% | 6.99% | 1.1077 | 1.1154 | 1.0752
2010-10-26 | 38 | 29.9599 | 11.1948 | 41.1547 | 2.9463 | 0.76558 | 0.30595 | 4.0178 | 9.763% | 10.39% | 7.019% | 1.1082 | 1.1159 | 1.0755
2010-10-26 | 39 | 30.1337 | 10.8868 | 41.0205 | 2.9271 | 0.76558 | 0.30495 | 3.9976 | 9.745% | 10.37% | 7.007% | 1.108 | 1.1157 | 1.0753
2010-10-26 | 40 | 29.816 | 10.5225 | 40.3385 | 2.8306 | 0.76558 | 0.29988 | 3.896 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-10-26 | 41 | 29.7144 | 10.3594 | 40.0738 | 2.7935 | 0.76558 | 0.29791 | 3.857 | 9.625% | 10.24% | 6.92% | 1.1065 | 1.1141 | 1.0743
2010-10-26 | 42 | 30.2324 | 10.3568 | 40.5891 | 2.8659 | 0.76558 | 0.30174 | 3.9332 | 9.69% | 10.31% | 6.967% | 1.1073 | 1.115 | 1.0749
2010-10-26 | 43 | 29.2843 | 9.9071 | 39.1914 | 2.6719 | 0.76558 | 0.29135 | 3.7288 | 9.514% | 10.12% | 6.841% | 1.1051 | 1.1126 | 1.0734
2010-10-26 | 44 | 27.885 | 9.3198 | 37.2048 | 2.4079 | 0.76558 | 0.27659 | 3.45 | 9.273% | 9.867% | 6.667% | 1.1022 | 1.1095 | 1.0714
2010-10-26 | 45 | 25.4073 | 8.2903 | 33.6976 | 1.9753 | 0.76558 | 0.25051 | 2.9914 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-10-26 | 46 | 22.7848 | 7.2857 | 30.0706 | 1.573 | 0.76558 | 0.22355 | 2.5621 | 8.52% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-10-26 | 47 | 21.1903 | 6.7387 | 27.929 | 1.3569 | 0.76558 | 0.20763 | 2.3301 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-10-26 | 48 | 20.5205 | 6.8778 | 27.3983 | 1.3058 | 0.76558 | 0.20368 | 2.2751 | 8.304% | 8.835% | 5.97% | 1.0906 | 1.0969 | 1.0635
2010-10-27 | 1 | 19.0608 | 6.1843 | 25.2451 | 1.1086 | 0.76558 | 0.18768 | 2.0619 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-10-27 | 2 | 17.8414 | 5.7472 | 23.5886 | 0.96792 | 0.76558 | 0.17536 | 1.9089 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-10-27 | 3 | 17.2751 | 5.4457 | 22.7208 | 0.89801 | 0.76558 | 0.16891 | 1.8325 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-27 | 4 | 16.8073 | 5.2777 | 22.085 | 0.84846 | 0.76558 | 0.16418 | 1.7782 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-10-27 | 5 | 16.4135 | 5.1697 | 21.5831 | 0.81033 | 0.76558 | 0.16045 | 1.7364 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 6 | 16.1757 | 5.1392 | 21.3149 | 0.79032 | 0.76558 | 0.15846 | 1.7144 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 7 | 16.0756 | 5.1825 | 21.2581 | 0.78611 | 0.76558 | 0.15804 | 1.7097 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 8 | 15.9739 | 5.2449 | 21.2188 | 0.78321 | 0.76558 | 0.15774 | 1.7065 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 9 | 16.172 | 5.3121 | 21.4841 | 0.80292 | 0.76558 | 0.15972 | 1.7282 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 10 | 16.2721 | 5.3935 | 21.6656 | 0.81654 | 0.76558 | 0.16106 | 1.7432 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-27 | 11 | 16.6605 | 5.5341 | 22.1945 | 0.85689 | 0.76558 | 0.165 | 1.7875 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-10-27 | 12 | 17.3303 | 6.0295 | 23.3598 | 0.94923 | 0.76558 | 0.17366 | 1.8885 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-10-27 | 13 | 19.1202 | 7.007 | 26.1272 | 1.1875 | 0.76558 | 0.19423 | 2.1473 | 8.219% | 8.745% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-10-27 | 14 | 21.9523 | 8.428 | 30.3803 | 1.6055 | 0.76558 | 0.22585 | 2.597 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1001 | 1.0655
2010-10-27 | 15 | 26.0524 | 10.4987 | 36.5511 | 2.324 | 0.76558 | 0.27173 | 3.3613 | 9.196% | 9.785% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-10-27 | 16 | 28.2745 | 11.428 | 39.7026 | 2.742 | 0.76558 | 0.29515 | 3.8028 | 9.578% | 10.19% | 6.887% | 1.1059 | 1.1135 | 1.074
2010-10-27 | 17 | 29.0206 | 11.9356 | 40.9562 | 2.9179 | 0.76558 | 0.30447 | 3.988 | 9.737% | 10.36% | 7.001% | 1.1079 | 1.1156 | 1.0753
2010-10-27 | 18 | 28.6641 | 11.6745 | 40.3386 | 2.8306 | 0.76558 | 0.29988 | 3.896 | 9.658% | 10.28% | 6.944% | 1.1069 | 1.1145 | 1.0746
2010-10-27 | 19 | 27.8704 | 11.4139 | 39.2844 | 2.6846 | 0.76558 | 0.29204 | 3.7422 | 9.526% | 10.14% | 6.849% | 1.1053 | 1.1128 | 1.0735
2010-10-27 | 20 | 27.0724 | 10.9237 | 37.9961 | 2.5114 | 0.76558 | 0.28247 | 3.5594 | 9.368% | 9.967% | 6.736% | 1.1034 | 1.1107 | 1.0722
2010-10-27 | 21 | 26.8043 | 10.2375 | 37.0417 | 2.3868 | 0.76558 | 0.27537 | 3.4278 | 9.254% | 9.846% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-10-27 | 22 | 25.8599 | 9.9948 | 35.8547 | 2.2363 | 0.76558 | 0.26655 | 3.2684 | 9.116% | 9.699% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-10-27 | 23 | 24.416 | 9.4119 | 33.828 | 1.9906 | 0.76558 | 0.25148 | 3.0077 | 8.891% | 9.46% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-10-27 | 24 | 23.908 | 9.2472 | 33.1552 | 1.9122 | 0.76558 | 0.24648 | 2.9243 | 8.82% | 9.384% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-10-27 | 25 | 22.7293 | 8.9118 | 31.641 | 1.7416 | 0.76558 | 0.23522 | 2.7424 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-10-27 | 26 | 21.7306 | 8.3387 | 30.0693 | 1.5728 | 0.76558 | 0.22354 | 2.5619 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-10-27 | 27 | 21.814 | 8.5896 | 30.4037 | 1.608 | 0.76558 | 0.22602 | 2.5996 | 8.55% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-10-27 | 28 | 21.5544 | 8.5495 | 30.1039 | 1.5765 | 0.76558 | 0.2238 | 2.5658 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-10-27 | 29 | 21.47 | 8.2069 | 29.6769 | 1.532 | 0.76558 | 0.22062 | 2.5182 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-10-27 | 30 | 20.8293 | 7.984 | 28.8133 | 1.4442 | 0.76558 | 0.2142 | 2.424 | 8.413% | 8.951% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-10-27 | 31 | 20.6597 | 7.8316 | 28.4913 | 1.4121 | 0.76558 | 0.21181 | 2.3895 | 8.387% | 8.923% | 6.03% | 1.0915 | 1.098 | 1.0642
2010-10-27 | 32 | 20.8382 | 7.7916 | 28.6298 | 1.4258 | 0.76558 | 0.21284 | 2.4043 | 8.398% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2010-10-27 | 33 | 20.9889 | 8.1058 | 29.0946 | 1.4725 | 0.76558 | 0.21629 | 2.4544 | 8.436% | 8.976% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-10-27 | 34 | 21.0346 | 7.9536 | 28.9882 | 1.4618 | 0.76558 | 0.2155 | 2.4428 | 8.427% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2010-10-27 | 35 | 21.0207 | 8.4886 | 29.5093 | 1.5148 | 0.76558 | 0.21938 | 2.4997 | 8.471% | 9.013% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-10-27 | 36 | 21.3809 | 8.9768 | 30.3577 | 1.6031 | 0.76558 | 0.22568 | 2.5944 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2010-10-27 | 37 | 22.1928 | 9.1235 | 31.3163 | 1.706 | 0.76558 | 0.23281 | 2.7044 | 8.636% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-10-27 | 38 | 22.6396 | 9.0617 | 31.7014 | 1.7482 | 0.76558 | 0.23567 | 2.7494 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-10-27 | 39 | 22.8725 | 8.8972 | 31.7697 | 1.7557 | 0.76558 | 0.23618 | 2.7575 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2010-10-27 | 40 | 23.3539 | 8.6636 | 32.0175 | 1.7832 | 0.76558 | 0.23802 | 2.7868 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-10-27 | 41 | 24.4196 | 8.6982 | 33.1178 | 1.9079 | 0.76558 | 0.2462 | 2.9197 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-10-27 | 42 | 25.9187 | 9.232 | 35.1507 | 2.1493 | 0.76558 | 0.26131 | 3.1762 | 9.036% | 9.614% | 6.497% | 1.0993 | 1.1064 | 1.0695
2010-10-27 | 43 | 26.0312 | 9.2249 | 35.2561 | 2.1622 | 0.76558 | 0.2621 | 3.1899 | 9.048% | 9.627% | 6.505% | 1.0995 | 1.1065 | 1.0696
2010-10-27 | 44 | 25.4893 | 8.7902 | 34.2795 | 2.0441 | 0.76558 | 0.25484 | 3.0645 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2010-10-27 | 45 | 23.4794 | 7.9357 | 31.4151 | 1.7168 | 0.76558 | 0.23354 | 2.7159 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-10-27 | 46 | 21.382 | 6.9961 | 28.3781 | 1.4009 | 0.76558 | 0.21097 | 2.3774 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-10-27 | 47 | 20.104 | 6.5183 | 26.6223 | 1.2329 | 0.76558 | 0.19791 | 2.1964 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2010-10-27 | 48 | 19.2624 | 6.6244 | 25.8869 | 1.1657 | 0.76558 | 0.19245 | 2.1237 | 8.204% | 8.729% | 5.899% | 1.0894 | 1.0956 | 1.0627
2010-10-28 | 1 | 17.6365 | 5.911 | 23.5476 | 0.96455 | 0.76558 | 0.17506 | 1.9052 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-10-28 | 2 | 16.5412 | 5.4639 | 22.0051 | 0.84233 | 0.76558 | 0.16359 | 1.7715 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-10-28 | 3 | 15.6794 | 5.1986 | 20.8779 | 0.75825 | 0.76558 | 0.15521 | 1.679 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-10-28 | 4 | 15.1758 | 5.0178 | 20.1936 | 0.70935 | 0.76558 | 0.15012 | 1.6251 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-28 | 5 | 14.7323 | 4.897 | 19.6293 | 0.67026 | 0.76558 | 0.14593 | 1.5818 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-28 | 6 | 14.3867 | 4.9398 | 19.3265 | 0.64974 | 0.76558 | 0.14368 | 1.559 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-10-28 | 7 | 14.215 | 4.8561 | 19.0711 | 0.63268 | 0.76558 | 0.14178 | 1.54 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-10-28 | 8 | 14.2797 | 4.8153 | 19.0949 | 0.63427 | 0.76558 | 0.14195 | 1.5418 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-10-28 | 9 | 14.6199 | 5.0419 | 19.6617 | 0.67248 | 0.76558 | 0.14617 | 1.5842 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-28 | 10 | 14.5778 | 5.0679 | 19.6457 | 0.67138 | 0.76558 | 0.14605 | 1.583 | 8.058% | 8.573% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-28 | 11 | 14.9821 | 5.1393 | 20.1214 | 0.70429 | 0.76558 | 0.14958 | 1.6195 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-28 | 12 | 15.8359 | 5.5594 | 21.3952 | 0.79629 | 0.76558 | 0.15905 | 1.7209 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-28 | 13 | 17.3878 | 6.3506 | 23.7384 | 0.98025 | 0.76558 | 0.17647 | 1.9223 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-10-28 | 14 | 20.0959 | 7.7215 | 27.8174 | 1.3461 | 0.76558 | 0.2068 | 2.3184 | 8.335% | 8.868% | 5.993% | 1.0909 | 1.0973 | 1.0637
2010-10-28 | 15 | 23.7862 | 9.885 | 33.6712 | 1.9722 | 0.76558 | 0.25032 | 2.9881 | 8.874% | 9.442% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-10-28 | 16 | 26.3421 | 10.7629 | 37.105 | 2.395 | 0.76558 | 0.27584 | 3.4364 | 9.261% | 9.854% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-10-28 | 17 | 27.8104 | 11.2435 | 39.0539 | 2.6532 | 0.76558 | 0.29033 | 3.7091 | 9.497% | 10.11% | 6.829% | 1.1049 | 1.1124 | 1.0733
2010-10-28 | 18 | 27.7283 | 11.3205 | 39.0488 | 2.6525 | 0.76558 | 0.29029 | 3.7083 | 9.497% | 10.1% | 6.828% | 1.1049 | 1.1124 | 1.0733
2010-10-28 | 19 | 27.1026 | 11.1731 | 38.2757 | 2.5485 | 0.76558 | 0.28455 | 3.5986 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2010-10-28 | 20 | 26.0666 | 10.6724 | 36.739 | 2.348 | 0.76558 | 0.27312 | 3.3867 | 9.218% | 9.808% | 6.628% | 1.1015 | 1.1087 | 1.071
2010-10-28 | 21 | 25.4996 | 9.9752 | 35.4748 | 2.1891 | 0.76558 | 0.26372 | 3.2185 | 9.072% | 9.653% | 6.523% | 1.0998 | 1.1068 | 1.0698
2010-10-28 | 22 | 24.7459 | 9.8504 | 34.5963 | 2.0821 | 0.76558 | 0.25719 | 3.1048 | 8.974% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-10-28 | 23 | 24.1027 | 9.3708 | 33.4735 | 1.9491 | 0.76558 | 0.24885 | 2.9635 | 8.853% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-10-28 | 24 | 23.6379 | 9.2933 | 32.9312 | 1.8865 | 0.76558 | 0.24481 | 2.8969 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-10-28 | 25 | 23.0964 | 9.2194 | 32.3158 | 1.8166 | 0.76558 | 0.24024 | 2.8224 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2010-10-28 | 26 | 22.497 | 8.7024 | 31.1993 | 1.6933 | 0.76558 | 0.23194 | 2.6908 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-10-28 | 27 | 22.4867 | 9.1151 | 31.6018 | 1.7372 | 0.76558 | 0.23493 | 2.7377 | 8.663% | 9.218% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-10-28 | 28 | 22.1121 | 8.9736 | 31.0857 | 1.681 | 0.76558 | 0.2311 | 2.6776 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2010-10-28 | 29 | 21.5232 | 8.4334 | 29.9567 | 1.5611 | 0.76558 | 0.2227 | 2.5493 | 8.51% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-10-28 | 30 | 21.3104 | 8.2093 | 29.5197 | 1.5159 | 0.76558 | 0.21945 | 2.5009 | 8.472% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-10-28 | 31 | 21.878 | 8.3321 | 30.2101 | 1.5876 | 0.76558 | 0.22459 | 2.5778 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-10-28 | 32 | 21.8685 | 8.2745 | 30.143 | 1.5805 | 0.76558 | 0.22409 | 2.5702 | 8.527% | 9.072% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-10-28 | 33 | 22.0931 | 8.6463 | 30.7394 | 1.6437 | 0.76558 | 0.22852 | 2.6378 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-10-28 | 34 | 21.9189 | 8.8993 | 30.8182 | 1.6521 | 0.76558 | 0.22911 | 2.6468 | 8.589% | 9.138% | 6.175% | 1.094 | 1.1006 | 1.0658
2010-10-28 | 35 | 22.8144 | 9.3617 | 32.1761 | 1.8009 | 0.76558 | 0.2392 | 2.8057 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-10-28 | 36 | 25.5218 | 10.3448 | 35.8665 | 2.2378 | 0.76558 | 0.26664 | 3.27 | 9.117% | 9.701% | 6.555% | 1.1003 | 1.1074 | 1.0702
2010-10-28 | 37 | 26.3817 | 10.8363 | 37.2179 | 2.4096 | 0.76558 | 0.27668 | 3.4518 | 9.275% | 9.868% | 6.668% | 1.1022 | 1.1095 | 1.0714
2010-10-28 | 38 | 27.0357 | 11.055 | 38.0907 | 2.5239 | 0.76558 | 0.28317 | 3.5726 | 9.379% | 9.98% | 6.744% | 1.1035 | 1.1109 | 1.0723
2010-10-28 | 39 | 29.0693 | 10.8349 | 39.9041 | 2.7699 | 0.76558 | 0.29665 | 3.8322 | 9.603% | 10.22% | 6.905% | 1.1062 | 1.1138 | 1.0742
2010-10-28 | 40 | 29.5963 | 10.577 | 40.1732 | 2.8074 | 0.76558 | 0.29865 | 3.8717 | 9.637% | 10.25% | 6.929% | 1.1067 | 1.1143 | 1.0745
2010-10-28 | 41 | 30.1067 | 10.4746 | 40.5814 | 2.8648 | 0.76558 | 0.30169 | 3.932 | 9.689% | 10.31% | 6.967% | 1.1073 | 1.1149 | 1.0749
2010-10-28 | 42 | 30.9633 | 10.7324 | 41.6957 | 3.0242 | 0.76558 | 0.30997 | 4.0998 | 9.833% | 10.46% | 7.07% | 1.109 | 1.1168 | 1.0761
2010-10-28 | 43 | 30.4482 | 10.3927 | 40.8408 | 2.9015 | 0.76558 | 0.30362 | 3.9707 | 9.722% | 10.34% | 6.99% | 1.1077 | 1.1154 | 1.0752
2010-10-28 | 44 | 29.0865 | 9.6848 | 38.7713 | 2.6149 | 0.76558 | 0.28823 | 3.6687 | 9.462% | 10.07% | 6.803% | 1.1045 | 1.112 | 1.073
2010-10-28 | 45 | 26.5273 | 8.7427 | 35.27 | 2.1639 | 0.76558 | 0.2622 | 3.1917 | 9.049% | 9.629% | 6.507% | 1.0995 | 1.1065 | 1.0696
2010-10-28 | 46 | 23.8743 | 7.657 | 31.5313 | 1.7295 | 0.76558 | 0.23441 | 2.7295 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2010-10-28 | 47 | 22.515 | 7.1809 | 29.6959 | 1.534 | 0.76558 | 0.22076 | 2.5203 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-10-28 | 48 | 21.7104 | 7.3181 | 29.0286 | 1.4658 | 0.76558 | 0.2158 | 2.4472 | 8.43% | 8.97% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-10-29 | 1 | 19.8735 | 6.6107 | 26.4842 | 1.2201 | 0.76558 | 0.19689 | 2.1826 | 8.241% | 8.769% | 5.925% | 1.0898 | 1.0961 | 1.063
2010-10-29 | 2 | 18.4714 | 6.1017 | 24.5731 | 1.0504 | 0.76558 | 0.18268 | 1.9987 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-10-29 | 3 | 17.3618 | 5.7177 | 23.0795 | 0.92659 | 0.76558 | 0.17158 | 1.8637 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-10-29 | 4 | 16.8424 | 5.5553 | 22.3978 | 0.87266 | 0.76558 | 0.16651 | 1.8047 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-29 | 5 | 16.5706 | 5.4664 | 22.037 | 0.84477 | 0.76558 | 0.16383 | 1.7742 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-10-29 | 6 | 16.3324 | 5.4214 | 21.7538 | 0.8232 | 0.76558 | 0.16172 | 1.7505 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-29 | 7 | 16.3132 | 5.4573 | 21.7705 | 0.82447 | 0.76558 | 0.16184 | 1.7519 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-10-29 | 8 | 16.1238 | 5.3432 | 21.467 | 0.80163 | 0.76558 | 0.15959 | 1.7268 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-10-29 | 9 | 16.3403 | 5.3147 | 21.655 | 0.81574 | 0.76558 | 0.16099 | 1.7423 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-10-29 | 10 | 16.4627 | 5.4325 | 21.8952 | 0.83393 | 0.76558 | 0.16277 | 1.7623 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-10-29 | 11 | 17.0247 | 5.6138 | 22.6385 | 0.89152 | 0.76558 | 0.1683 | 1.8254 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-10-29 | 12 | 17.6422 | 5.9241 | 23.5663 | 0.96609 | 0.76558 | 0.17519 | 1.9069 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-10-29 | 13 | 19.3045 | 7.0002 | 26.3046 | 1.2036 | 0.76558 | 0.19555 | 2.1648 | 8.23% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-10-29 | 14 | 22.0804 | 8.3703 | 30.4507 | 1.613 | 0.76558 | 0.22637 | 2.6049 | 8.555% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2010-10-29 | 15 | 26.3602 | 10.8103 | 37.1705 | 2.4034 | 0.76558 | 0.27633 | 3.4453 | 9.269% | 9.862% | 6.664% | 1.1022 | 1.1094 | 1.0714
2010-10-29 | 16 | 27.4176 | 11.0949 | 38.5124 | 2.5801 | 0.76558 | 0.28631 | 3.632 | 9.431% | 10.03% | 6.781% | 1.1041 | 1.1115 | 1.0727
2010-10-29 | 17 | 26.6338 | 10.7652 | 37.399 | 2.4331 | 0.76558 | 0.27803 | 3.4767 | 9.296% | 9.891% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-10-29 | 18 | 30.1177 | 12.3239 | 42.4416 | 3.1334 | 0.76558 | 0.31552 | 4.2145 | 9.93% | 10.57% | 7.14% | 1.1102 | 1.1181 | 1.0769
2010-10-29 | 19 | 31.7739 | 12.8732 | 44.6471 | 3.4675 | 0.76558 | 0.33191 | 4.565 | 10.22% | 10.88% | 7.352% | 1.1139 | 1.1221 | 1.0793
2010-10-29 | 20 | 30.982 | 12.4734 | 43.4554 | 3.2849 | 0.76558 | 0.32305 | 4.3735 | 10.06% | 10.71% | 7.236% | 1.1119 | 1.1199 | 1.078
2010-10-29 | 21 | 29.7705 | 11.4624 | 41.2329 | 2.9575 | 0.76558 | 0.30653 | 4.0296 | 9.773% | 10.4% | 7.027% | 1.1083 | 1.116 | 1.0756
2010-10-29 | 22 | 28.4029 | 10.848 | 39.2508 | 2.68 | 0.76558 | 0.2918 | 3.7374 | 9.522% | 10.13% | 6.846% | 1.1052 | 1.1127 | 1.0735
2010-10-29 | 23 | 26.7897 | 10.226 | 37.0156 | 2.3834 | 0.76558 | 0.27518 | 3.4242 | 9.251% | 9.843% | 6.651% | 1.1019 | 1.1092 | 1.0713
2010-10-29 | 24 | 25.7217 | 9.9541 | 35.6758 | 2.214 | 0.76558 | 0.26522 | 3.2448 | 9.095% | 9.677% | 6.54% | 1.1001 | 1.1071 | 1.07
2010-10-29 | 25 | 24.7901 | 9.687 | 34.4771 | 2.0677 | 0.76558 | 0.25631 | 3.0896 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-10-29 | 26 | 23.9561 | 9.2846 | 33.2408 | 1.9221 | 0.76558 | 0.24712 | 2.9348 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-10-29 | 27 | 23.668 | 9.4061 | 33.0741 | 1.9029 | 0.76558 | 0.24588 | 2.9143 | 8.812% | 9.375% | 6.335% | 1.0966 | 1.1035 | 1.0676
2010-10-29 | 28 | 23.2912 | 9.3805 | 32.6717 | 1.8569 | 0.76558 | 0.24289 | 2.8653 | 8.77% | 9.331% | 6.306% | 1.0961 | 1.1029 | 1.0673
2010-10-29 | 29 | 22.779 | 8.8987 | 31.6777 | 1.7456 | 0.76558 | 0.2355 | 2.7467 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-10-29 | 30 | 22.3386 | 8.4889 | 30.8275 | 1.6531 | 0.76558 | 0.22918 | 2.6479 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-10-29 | 31 | 22.877 | 8.4025 | 31.2795 | 1.702 | 0.76558 | 0.23254 | 2.7001 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-10-29 | 32 | 23.2311 | 8.4566 | 31.6877 | 1.7467 | 0.76558 | 0.23557 | 2.7478 | 8.672% | 9.227% | 6.235% | 1.0949 | 1.1016 | 1.0665
2010-10-29 | 33 | 23.7755 | 8.7373 | 32.5128 | 1.8388 | 0.76558 | 0.2417 | 2.8461 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-10-29 | 34 | 23.9619 | 8.8786 | 32.8405 | 1.8761 | 0.76558 | 0.24414 | 2.8858 | 8.787% | 9.35% | 6.318% | 1.0963 | 1.1031 | 1.0674
2010-10-29 | 35 | 24.2563 | 9.4532 | 33.7095 | 1.9767 | 0.76558 | 0.2506 | 2.9929 | 8.878% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-10-29 | 36 | 25.2081 | 9.761 | 34.9691 | 2.1272 | 0.76558 | 0.25996 | 3.1527 | 9.016% | 9.593% | 6.482% | 1.0991 | 1.1061 | 1.0693
2010-10-29 | 37 | 26.6101 | 10.0179 | 36.628 | 2.3338 | 0.76558 | 0.2723 | 3.3717 | 9.205% | 9.794% | 6.618% | 1.1014 | 1.1086 | 1.0709
2010-10-29 | 38 | 27.0884 | 9.8621 | 36.9506 | 2.3751 | 0.76558 | 0.27469 | 3.4153 | 9.243% | 9.835% | 6.646% | 1.1018 | 1.1091 | 1.0712
2010-10-29 | 39 | 26.9539 | 9.9031 | 36.8571 | 2.3631 | 0.76558 | 0.274 | 3.4026 | 9.232% | 9.823% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-10-29 | 40 | 27.1158 | 9.7616 | 36.8774 | 2.3657 | 0.76558 | 0.27415 | 3.4054 | 9.234% | 9.825% | 6.64% | 1.1017 | 1.109 | 1.0711
2010-10-29 | 41 | 28.3279 | 9.5508 | 37.8787 | 2.4959 | 0.76558 | 0.28159 | 3.5431 | 9.354% | 9.952% | 6.725% | 1.1032 | 1.1105 | 1.0721
2010-10-29 | 42 | 29.0101 | 10.0091 | 39.0192 | 2.6485 | 0.76558 | 0.29007 | 3.7041 | 9.493% | 10.1% | 6.825% | 1.1049 | 1.1124 | 1.0733
2010-10-29 | 43 | 28.6785 | 9.9515 | 38.63 | 2.5959 | 0.76558 | 0.28718 | 3.6486 | 9.445% | 10.05% | 6.791% | 1.1043 | 1.1117 | 1.0729
2010-10-29 | 44 | 27.6046 | 9.4685 | 37.0731 | 2.3909 | 0.76558 | 0.27561 | 3.432 | 9.257% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2010-10-29 | 45 | 25.3407 | 8.5122 | 33.8529 | 1.9936 | 0.76558 | 0.25167 | 3.0108 | 8.894% | 9.463% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-10-29 | 46 | 22.9992 | 7.5378 | 30.537 | 1.6221 | 0.76558 | 0.22702 | 2.6147 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-10-29 | 47 | 21.5255 | 7.0649 | 28.5905 | 1.4219 | 0.76558 | 0.21254 | 2.4 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-10-29 | 48 | 20.8636 | 7.2812 | 28.1448 | 1.3779 | 0.76558 | 0.20923 | 2.3527 | 8.359% | 8.894% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-10-30 | 1 | 19.0901 | 6.4218 | 25.512 | 1.1322 | 0.76558 | 0.18966 | 2.0874 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-10-30 | 2 | 18.1693 | 6.0973 | 24.2666 | 1.0244 | 0.76558 | 0.1804 | 1.9703 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-10-30 | 3 | 17.3535 | 5.7064 | 23.0599 | 0.92502 | 0.76558 | 0.17143 | 1.862 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-10-30 | 4 | 16.6822 | 5.7594 | 22.4416 | 0.87607 | 0.76558 | 0.16683 | 1.8085 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-30 | 5 | 16.2188 | 6.1906 | 22.4094 | 0.87356 | 0.76558 | 0.16659 | 1.8057 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-10-30 | 6 | 16.0384 | 6.6951 | 22.7335 | 0.89902 | 0.76558 | 0.169 | 1.8336 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-10-30 | 7 | 15.9447 | 7.4636 | 23.4083 | 0.95318 | 0.76558 | 0.17402 | 1.8928 | 8.086% | 8.603% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-10-30 | 8 | 15.9152 | 8.1322 | 24.0475 | 1.0059 | 0.76558 | 0.17877 | 1.9503 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-10-30 | 9 | 16.0528 | 8.7775 | 24.8303 | 1.0725 | 0.76558 | 0.18459 | 2.0227 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-10-30 | 10 | 16.2306 | 8.9537 | 25.1843 | 1.1033 | 0.76558 | 0.18722 | 2.0561 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-10-30 | 11 | 16.7707 | 9.2715 | 26.0423 | 1.1798 | 0.76558 | 0.1936 | 2.1389 | 8.213% | 8.739% | 5.905% | 1.0895 | 1.0958 | 1.0628
2010-10-30 | 12 | 17.5125 | 9.8276 | 27.3401 | 1.3003 | 0.76558 | 0.20325 | 2.2691 | 8.3% | 8.831% | 5.967% | 1.0905 | 1.0969 | 1.0635
2010-10-30 | 13 | 19.355 | 10.5579 | 29.9129 | 1.5565 | 0.76558 | 0.22238 | 2.5445 | 8.506% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-10-30 | 14 | 22.0867 | 12.1262 | 34.2129 | 2.0362 | 0.76558 | 0.25434 | 3.0561 | 8.933% | 9.504% | 6.423% | 1.0981 | 1.105 | 1.0686
2010-10-30 | 15 | 25.7847 | 14.269 | 40.0536 | 2.7907 | 0.76558 | 0.29776 | 3.8541 | 9.622% | 10.24% | 6.918% | 1.1065 | 1.1141 | 1.0743
2010-10-30 | 16 | 27.8317 | 14.8165 | 42.6482 | 3.164 | 0.76558 | 0.31705 | 4.2466 | 9.957% | 10.59% | 7.159% | 1.1106 | 1.1185 | 1.0771
2010-10-30 | 17 | 28.2682 | 13.2688 | 41.537 | 3.0013 | 0.76558 | 0.30879 | 4.0756 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-10-30 | 18 | 27.9947 | 12.0051 | 39.9998 | 2.7832 | 0.76558 | 0.29736 | 3.8462 | 9.616% | 10.23% | 6.914% | 1.1064 | 1.114 | 1.0743
2010-10-30 | 19 | 27.3503 | 11.4472 | 38.7975 | 2.6184 | 0.76558 | 0.28843 | 3.6724 | 9.466% | 10.07% | 6.806% | 1.1046 | 1.112 | 1.073
2010-10-30 | 20 | 26.0299 | 10.7816 | 36.8116 | 2.3572 | 0.76558 | 0.27366 | 3.3965 | 9.227% | 9.817% | 6.634% | 1.1016 | 1.1089 | 1.0711
2010-10-30 | 21 | 25.5538 | 10.2348 | 35.7886 | 2.228 | 0.76558 | 0.26606 | 3.2597 | 9.108% | 9.691% | 6.549% | 1.1002 | 1.1073 | 1.0701
2010-10-30 | 22 | 24.3882 | 10.0867 | 34.4749 | 2.0675 | 0.76558 | 0.25629 | 3.0894 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-10-30 | 23 | 23.6178 | 9.2391 | 32.8569 | 1.878 | 0.76558 | 0.24426 | 2.8878 | 8.789% | 9.352% | 6.319% | 1.0964 | 1.1032 | 1.0675
2010-10-30 | 24 | 22.7018 | 9.0167 | 31.7184 | 1.7501 | 0.76558 | 0.2358 | 2.7515 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-10-30 | 25 | 21.8656 | 8.8457 | 30.7113 | 1.6407 | 0.76558 | 0.22831 | 2.6346 | 8.579% | 9.128% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-10-30 | 26 | 21.1791 | 8.4184 | 29.5975 | 1.5239 | 0.76558 | 0.22003 | 2.5095 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-10-30 | 27 | 20.9775 | 8.7007 | 29.6782 | 1.5322 | 0.76558 | 0.22063 | 2.5184 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-10-30 | 28 | 20.7396 | 8.6768 | 29.4165 | 1.5053 | 0.76558 | 0.21869 | 2.4895 | 8.463% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-10-30 | 29 | 20.5003 | 8.2936 | 28.7938 | 1.4422 | 0.76558 | 0.21406 | 2.4219 | 8.411% | 8.949% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-10-30 | 30 | 19.9931 | 8.2056 | 28.1987 | 1.3832 | 0.76558 | 0.20963 | 2.3584 | 8.364% | 8.899% | 6.013% | 1.0913 | 1.0977 | 1.064
2010-10-30 | 31 | 20.1862 | 8.2382 | 28.4244 | 1.4055 | 0.76558 | 0.21131 | 2.3823 | 8.381% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-10-30 | 32 | 20.3019 | 8.0685 | 28.3704 | 1.4001 | 0.76558 | 0.21091 | 2.3766 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-10-30 | 33 | 20.3788 | 8.2604 | 28.6392 | 1.4268 | 0.76558 | 0.21291 | 2.4053 | 8.399% | 8.936% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-10-30 | 34 | 20.2358 | 8.1344 | 28.3702 | 1.4001 | 0.76558 | 0.21091 | 2.3766 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-10-30 | 35 | 20.3903 | 8.1486 | 28.5389 | 1.4168 | 0.76558 | 0.21216 | 2.3945 | 8.39% | 8.927% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-10-30 | 36 | 20.4895 | 8.4736 | 28.963 | 1.4592 | 0.76558 | 0.21531 | 2.4401 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2010-10-30 | 37 | 21.1608 | 8.6372 | 29.798 | 1.5446 | 0.76558 | 0.22152 | 2.5317 | 8.496% | 9.04% | 6.109% | 1.0928 | 1.0994 | 1.0651
2010-10-30 | 38 | 21.7306 | 8.7178 | 30.4484 | 1.6127 | 0.76558 | 0.22636 | 2.6047 | 8.554% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2010-10-30 | 39 | 21.759 | 8.8077 | 30.5666 | 1.6253 | 0.76558 | 0.22724 | 2.6181 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-10-30 | 40 | 22.1253 | 8.6002 | 30.7255 | 1.6422 | 0.76558 | 0.22842 | 2.6362 | 8.58% | 9.129% | 6.169% | 1.0939 | 1.1005 | 1.0657
2010-10-30 | 41 | 22.9469 | 8.616 | 31.5629 | 1.733 | 0.76558 | 0.23464 | 2.7332 | 8.659% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-10-30 | 42 | 23.9566 | 9.1585 | 33.115 | 1.9076 | 0.76558 | 0.24618 | 2.9194 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-10-30 | 43 | 24.007 | 9.1259 | 33.1329 | 1.9096 | 0.76558 | 0.24631 | 2.9215 | 8.818% | 9.382% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-10-30 | 44 | 23.5774 | 8.9394 | 32.5168 | 1.8393 | 0.76558 | 0.24173 | 2.8466 | 8.754% | 9.315% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-10-30 | 45 | 22.23 | 8.241 | 30.471 | 1.6151 | 0.76558 | 0.22653 | 2.6072 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-10-30 | 46 | 20.7162 | 7.4492 | 28.1654 | 1.38 | 0.76558 | 0.20938 | 2.3549 | 8.361% | 8.896% | 6.012% | 1.0912 | 1.0976 | 1.064
2010-10-30 | 47 | 19.6288 | 7.1093 | 26.7381 | 1.2436 | 0.76558 | 0.19877 | 2.208 | 8.258% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-10-30 | 48 | 19.0031 | 7.3033 | 26.3064 | 1.2038 | 0.76558 | 0.19557 | 2.165 | 8.23% | 8.756% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-10-31 | 1 | 17.6552 | 6.5292 | 24.1844 | 1.0174 | 0.76558 | 0.17979 | 1.9628 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-10-31 | 2 | 16.5175 | 6.0384 | 22.5559 | 0.88503 | 0.76558 | 0.16768 | 1.8183 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-10-31 | 3 | 15.6497 | 5.596 | 21.2456 | 0.78519 | 0.76558 | 0.15794 | 1.7087 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-31 | 4 | 15.1458 | 5.462 | 20.6078 | 0.73875 | 0.76558 | 0.1532 | 1.6575 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-31 | 5 | 14.6838 | 5.2437 | 19.9275 | 0.69078 | 0.76558 | 0.14814 | 1.6045 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-10-31 | 6 | 14.4844 | 5.1966 | 19.681 | 0.6738 | 0.76558 | 0.14631 | 1.5857 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-10-31 | 7 | 14.1945 | 5.1214 | 19.3159 | 0.64903 | 0.76558 | 0.1436 | 1.5582 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-10-31 | 8 | 14.2792 | 5.153 | 19.4322 | 0.65687 | 0.76558 | 0.14446 | 1.5669 | 8.063% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-10-31 | 9 | 14.4796 | 5.2614 | 19.7411 | 0.67792 | 0.76558 | 0.14676 | 1.5903 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-10-31 | 10 | 14.468 | 5.4392 | 19.9073 | 0.68938 | 0.76558 | 0.14799 | 1.603 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-10-31 | 11 | 14.9365 | 5.8006 | 20.7371 | 0.74805 | 0.76558 | 0.15416 | 1.6678 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-10-31 | 12 | 15.4766 | 6.4697 | 21.9463 | 0.83784 | 0.76558 | 0.16315 | 1.7666 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-10-31 | 13 | 16.3253 | 7.3498 | 23.675 | 0.97503 | 0.76558 | 0.176 | 1.9166 | 8.095% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-10-31 | 14 | 17.7937 | 7.9454 | 25.7391 | 1.1524 | 0.76558 | 0.19135 | 2.1094 | 8.195% | 8.72% | 5.892% | 1.0893 | 1.0955 | 1.0626
2010-10-31 | 15 | 19.7158 | 8.4309 | 28.1467 | 1.3781 | 0.76558 | 0.20925 | 2.353 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.0639
2010-10-31 | 16 | 20.888 | 8.773 | 29.661 | 1.5304 | 0.76558 | 0.2205 | 2.5165 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-10-31 | 17 | 22.1821 | 9.1861 | 31.3682 | 1.7116 | 0.76558 | 0.23319 | 2.7104 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2010-10-31 | 18 | 23.3217 | 9.8354 | 33.1571 | 1.9124 | 0.76558 | 0.24649 | 2.9245 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-10-31 | 19 | 24.0956 | 10.2139 | 34.3095 | 2.0477 | 0.76558 | 0.25506 | 3.0683 | 8.943% | 9.515% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-10-31 | 20 | 23.9334 | 10.0455 | 33.9789 | 2.0084 | 0.76558 | 0.2526 | 3.0266 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-10-31 | 21 | 24.3734 | 9.8906 | 34.2641 | 2.0423 | 0.76558 | 0.25472 | 3.0626 | 8.938% | 9.51% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-10-31 | 22 | 23.733 | 9.7375 | 33.4705 | 1.9488 | 0.76558 | 0.24882 | 2.9632 | 8.853% | 9.42% | 6.365% | 1.0971 | 1.104 | 1.068
2010-10-31 | 23 | 22.7627 | 9.4312 | 32.1939 | 1.8029 | 0.76558 | 0.23933 | 2.8079 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-10-31 | 24 | 21.9047 | 9.1513 | 31.056 | 1.6777 | 0.76558 | 0.23087 | 2.6742 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-10-31 | 25 | 20.9088 | 8.9633 | 29.8721 | 1.5523 | 0.76558 | 0.22207 | 2.5399 | 8.503% | 9.047% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-10-31 | 26 | 19.961 | 8.5233 | 28.4843 | 1.4114 | 0.76558 | 0.21176 | 2.3887 | 8.386% | 8.923% | 6.03% | 1.0915 | 1.098 | 1.0642
2010-10-31 | 27 | 19.8745 | 8.4908 | 28.3653 | 1.3996 | 0.76558 | 0.21087 | 2.3761 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0978 | 1.0641
2010-10-31 | 28 | 19.7159 | 8.3457 | 28.0617 | 1.3698 | 0.76558 | 0.20861 | 2.344 | 8.353% | 8.888% | 6.006% | 1.0911 | 1.0975 | 1.0639
2010-10-31 | 29 | 19.2276 | 7.9446 | 27.1721 | 1.2843 | 0.76558 | 0.202 | 2.2519 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-10-31 | 30 | 18.694 | 7.7449 | 26.4389 | 1.216 | 0.76558 | 0.19655 | 2.1781 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-10-31 | 31 | 19.0269 | 7.6784 | 26.7053 | 1.2406 | 0.76558 | 0.19853 | 2.2047 | 8.256% | 8.784% | 5.936% | 1.09 | 1.0963 | 1.0631
2010-10-31 | 32 | 18.8027 | 7.694 | 26.4967 | 1.2213 | 0.76558 | 0.19698 | 2.1838 | 8.242% | 8.769% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-10-31 | 33 | 18.8018 | 7.882 | 26.6837 | 1.2386 | 0.76558 | 0.19837 | 2.2025 | 8.254% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-10-31 | 34 | 18.8053 | 7.8061 | 26.6114 | 1.2319 | 0.76558 | 0.19783 | 2.1953 | 8.249% | 8.777% | 5.931% | 1.0899 | 1.0962 | 1.0631
2010-10-31 | 35 | 19.4393 | 8.3008 | 27.7401 | 1.3386 | 0.76558 | 0.20622 | 2.3104 | 8.329% | 8.862% | 5.988% | 1.0909 | 1.0972 | 1.0637
2010-10-31 | 36 | 20.4617 | 8.8944 | 29.3561 | 1.4991 | 0.76558 | 0.21824 | 2.4829 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0648
2010-10-31 | 37 | 21.3809 | 9.2976 | 30.6785 | 1.6372 | 0.76558 | 0.22807 | 2.6308 | 8.576% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-10-31 | 38 | 21.5878 | 9.4467 | 31.0344 | 1.6754 | 0.76558 | 0.23071 | 2.6717 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-10-31 | 39 | 21.0196 | 9.221 | 30.2406 | 1.5908 | 0.76558 | 0.22481 | 2.5812 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-10-31 | 40 | 20.7973 | 8.9493 | 29.7466 | 1.5392 | 0.76558 | 0.22114 | 2.526 | 8.492% | 9.035% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-10-31 | 41 | 21.2243 | 8.4275 | 29.6518 | 1.5295 | 0.76558 | 0.22043 | 2.5155 | 8.483% | 9.026% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-10-31 | 42 | 22.0103 | 8.4955 | 30.5058 | 1.6188 | 0.76558 | 0.22678 | 2.6112 | 8.56% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-10-31 | 43 | 22.2526 | 8.4962 | 30.7488 | 1.6447 | 0.76558 | 0.22859 | 2.6389 | 8.582% | 9.131% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-10-31 | 44 | 21.5753 | 8.1001 | 29.6753 | 1.5319 | 0.76558 | 0.22061 | 2.5181 | 8.485% | 9.028% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-10-31 | 45 | 20.2777 | 7.6849 | 27.9626 | 1.3602 | 0.76558 | 0.20788 | 2.3336 | 8.345% | 8.88% | 6% | 1.0911 | 1.0974 | 1.0638
2010-10-31 | 46 | 19.2974 | 7.3982 | 26.6956 | 1.2397 | 0.76558 | 0.19846 | 2.2037 | 8.255% | 8.783% | 5.935% | 1.09 | 1.0963 | 1.0631
2010-10-31 | 47 | 18.4663 | 7.2173 | 25.6836 | 1.1475 | 0.76558 | 0.19093 | 2.104 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-10-31 | 48 | 17.8737 | 7.4033 | 25.277 | 1.1114 | 0.76558 | 0.18791 | 2.0649 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-11-01 | 1 | 16.2072 | 6.448 | 22.6552 | 0.89283 | 0.76558 | 0.16842 | 1.8268 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-11-01 | 2 | 14.9124 | 5.7911 | 20.7035 | 0.74563 | 0.76558 | 0.15391 | 1.6651 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-01 | 3 | 14.0865 | 5.4594 | 19.5459 | 0.66458 | 0.76558 | 0.14531 | 1.5755 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-01 | 4 | 13.5666 | 5.2743 | 18.8409 | 0.6175 | 0.76558 | 0.14007 | 1.5231 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-11-01 | 5 | 13.1476 | 5.0788 | 18.2264 | 0.57788 | 0.76558 | 0.1355 | 1.479 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-11-01 | 6 | 13.0398 | 4.9955 | 18.0353 | 0.56582 | 0.76558 | 0.13408 | 1.4655 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-11-01 | 7 | 12.7661 | 4.9022 | 17.6683 | 0.54303 | 0.76558 | 0.13135 | 1.44 | 8.15% | 8.672% | 5.86% | 1.0887 | 1.0949 | 1.0622
2010-11-01 | 8 | 12.6286 | 4.8885 | 17.5171 | 0.53377 | 0.76558 | 0.13022 | 1.4296 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-11-01 | 9 | 13.0134 | 4.9372 | 17.9506 | 0.56052 | 0.76558 | 0.13345 | 1.4595 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-01 | 10 | 13.0215 | 4.8857 | 17.9072 | 0.55781 | 0.76558 | 0.13312 | 1.4565 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-01 | 11 | 13.1337 | 5.058 | 18.1918 | 0.57569 | 0.76558 | 0.13524 | 1.4765 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-11-01 | 12 | 13.2777 | 5.0733 | 18.3509 | 0.5858 | 0.76558 | 0.13642 | 1.4878 | 8.108% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-11-01 | 13 | 13.4645 | 5.1432 | 18.6077 | 0.60231 | 0.76558 | 0.13833 | 1.5062 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-11-01 | 14 | 14.255 | 5.4231 | 19.6781 | 0.6736 | 0.76558 | 0.14629 | 1.5855 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-01 | 15 | 15.521 | 6.1413 | 21.6623 | 0.81629 | 0.76558 | 0.16104 | 1.7429 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-01 | 16 | 16.7814 | 6.8493 | 23.6307 | 0.97138 | 0.76558 | 0.17567 | 1.9126 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-11-01 | 17 | 17.9528 | 7.8381 | 25.7909 | 1.1571 | 0.76558 | 0.19173 | 2.1144 | 8.198% | 8.723% | 5.895% | 1.0893 | 1.0956 | 1.0626
2010-11-01 | 18 | 19.4866 | 8.3831 | 27.8697 | 1.3511 | 0.76558 | 0.20719 | 2.3239 | 8.338% | 8.872% | 5.995% | 1.091 | 1.0974 | 1.0638
2010-11-01 | 19 | 21.0213 | 8.7154 | 29.7367 | 1.5382 | 0.76558 | 0.22107 | 2.5249 | 8.491% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-11-01 | 20 | 21.7112 | 8.9646 | 30.6758 | 1.6369 | 0.76558 | 0.22805 | 2.6305 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-11-01 | 21 | 22.6383 | 9.2473 | 31.8856 | 1.7686 | 0.76558 | 0.23704 | 2.7712 | 8.691% | 9.247% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-11-01 | 22 | 22.4196 | 9.3643 | 31.784 | 1.7573 | 0.76558 | 0.23629 | 2.7592 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2010-11-01 | 23 | 21.8904 | 8.9178 | 30.8082 | 1.6511 | 0.76558 | 0.22903 | 2.6457 | 8.588% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-11-01 | 24 | 21.2396 | 8.6452 | 29.8848 | 1.5536 | 0.76558 | 0.22217 | 2.5413 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-11-01 | 25 | 20.5107 | 8.5478 | 29.0585 | 1.4689 | 0.76558 | 0.21602 | 2.4505 | 8.433% | 8.973% | 6.063% | 1.0921 | 1.0986 | 1.0645
2010-11-01 | 26 | 19.8128 | 8.2078 | 28.0207 | 1.3658 | 0.76558 | 0.20831 | 2.3397 | 8.35% | 8.884% | 6.004% | 1.0911 | 1.0975 | 1.0639
2010-11-01 | 27 | 19.6819 | 8.0881 | 27.77 | 1.3415 | 0.76558 | 0.20645 | 2.3135 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-11-01 | 28 | 19.4915 | 8.1584 | 27.6499 | 1.3299 | 0.76558 | 0.20555 | 2.301 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0971 | 1.0636
2010-11-01 | 29 | 19.2851 | 7.7669 | 27.052 | 1.273 | 0.76558 | 0.20111 | 2.2397 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-11-01 | 30 | 18.9813 | 7.6355 | 26.6168 | 1.2324 | 0.76558 | 0.19787 | 2.1958 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2010-11-01 | 31 | 19.2534 | 7.5703 | 26.8238 | 1.2516 | 0.76558 | 0.19941 | 2.2166 | 8.264% | 8.792% | 5.942% | 1.0901 | 1.0964 | 1.0632
2010-11-01 | 32 | 19.2141 | 7.5691 | 26.7832 | 1.2478 | 0.76558 | 0.19911 | 2.2125 | 8.261% | 8.79% | 5.94% | 1.09 | 1.0964 | 1.0631
2010-11-01 | 33 | 19.4348 | 7.7414 | 27.1763 | 1.2847 | 0.76558 | 0.20203 | 2.2523 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-11-01 | 34 | 19.6308 | 7.9416 | 27.5723 | 1.3225 | 0.76558 | 0.20498 | 2.293 | 8.316% | 8.849% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-11-01 | 35 | 20.0565 | 8.2944 | 28.351 | 1.3982 | 0.76558 | 0.21076 | 2.3745 | 8.376% | 8.912% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-11-01 | 36 | 20.6058 | 8.8261 | 29.4318 | 1.5068 | 0.76558 | 0.2188 | 2.4912 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-01 | 37 | 21.3148 | 9.0802 | 30.395 | 1.6071 | 0.76558 | 0.22596 | 2.5986 | 8.55% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-11-01 | 38 | 21.8363 | 9.1881 | 31.0244 | 1.6743 | 0.76558 | 0.23064 | 2.6706 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-11-01 | 39 | 21.7995 | 9.1802 | 30.9797 | 1.6695 | 0.76558 | 0.23031 | 2.6654 | 8.604% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-11-01 | 40 | 21.5758 | 9.1798 | 30.7556 | 1.6454 | 0.76558 | 0.22864 | 2.6397 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-11-01 | 41 | 21.6937 | 9.3662 | 31.0599 | 1.6782 | 0.76558 | 0.2309 | 2.6746 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-11-01 | 42 | 22.7532 | 9.1453 | 31.8986 | 1.77 | 0.76558 | 0.23714 | 2.7727 | 8.692% | 9.249% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-11-01 | 43 | 22.7774 | 8.7969 | 31.5743 | 1.7342 | 0.76558 | 0.23473 | 2.7345 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-11-01 | 44 | 21.8194 | 8.2364 | 30.0558 | 1.5714 | 0.76558 | 0.22344 | 2.5604 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2010-11-01 | 45 | 20.0768 | 7.5293 | 27.606 | 1.3257 | 0.76558 | 0.20523 | 2.2965 | 8.319% | 8.851% | 5.981% | 1.0907 | 1.0971 | 1.0636
2010-11-01 | 46 | 18.3918 | 6.887 | 25.2788 | 1.1116 | 0.76558 | 0.18793 | 2.0651 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-11-01 | 47 | 17.1115 | 6.58 | 23.6915 | 0.97638 | 0.76558 | 0.17613 | 1.9181 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-11-01 | 48 | 16.4533 | 6.5782 | 23.0315 | 0.92274 | 0.76558 | 0.17122 | 1.8595 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-11-02 | 1 | 14.7171 | 5.8739 | 20.591 | 0.73755 | 0.76558 | 0.15308 | 1.6562 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-02 | 2 | 13.6024 | 5.4275 | 19.0299 | 0.62996 | 0.76558 | 0.14147 | 1.537 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-11-02 | 3 | 12.8647 | 5.1496 | 18.0143 | 0.56451 | 0.76558 | 0.13392 | 1.464 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2010-11-02 | 4 | 12.451 | 5.0547 | 17.5057 | 0.53308 | 0.76558 | 0.13014 | 1.4288 | 8.162% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-11-02 | 5 | 12.3145 | 4.8685 | 17.183 | 0.51361 | 0.76558 | 0.12774 | 1.4069 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-11-02 | 6 | 12.2344 | 4.8736 | 17.1079 | 0.50913 | 0.76558 | 0.12718 | 1.4019 | 8.194% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2010-11-02 | 7 | 11.9511 | 4.912 | 16.8631 | 0.49466 | 0.76558 | 0.12536 | 1.3856 | 8.217% | 8.743% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-11-02 | 8 | 11.8879 | 4.7999 | 16.6878 | 0.48443 | 0.76558 | 0.12406 | 1.3741 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2010-11-02 | 9 | 12.067 | 4.8748 | 16.9418 | 0.49929 | 0.76558 | 0.12595 | 1.3908 | 8.209% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-11-02 | 10 | 12.2129 | 4.9749 | 17.1878 | 0.51389 | 0.76558 | 0.12778 | 1.4072 | 8.187% | 8.711% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-11-02 | 11 | 12.4186 | 5.0409 | 17.4595 | 0.53027 | 0.76558 | 0.1298 | 1.4256 | 8.165% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-11-02 | 12 | 13.1188 | 5.4584 | 18.5772 | 0.60034 | 0.76558 | 0.13811 | 1.504 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-11-02 | 13 | 14.7041 | 6.1774 | 20.8815 | 0.75851 | 0.76558 | 0.15524 | 1.6793 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-02 | 14 | 16.9188 | 7.2522 | 24.1711 | 1.0163 | 0.76558 | 0.17969 | 1.9616 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-11-02 | 15 | 20.3452 | 8.9248 | 29.2701 | 1.4903 | 0.76558 | 0.2176 | 2.4735 | 8.451% | 8.991% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-11-02 | 16 | 22.3409 | 9.5806 | 31.9215 | 1.7726 | 0.76558 | 0.23731 | 2.7754 | 8.695% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-11-02 | 17 | 23.3311 | 9.8382 | 33.1693 | 1.9138 | 0.76558 | 0.24658 | 2.926 | 8.821% | 9.386% | 6.343% | 1.0967 | 1.1036 | 1.0677
2010-11-02 | 18 | 23.1555 | 9.9157 | 33.0712 | 1.9025 | 0.76558 | 0.24586 | 2.914 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-11-02 | 19 | 22.6317 | 9.5293 | 32.161 | 1.7993 | 0.76558 | 0.23909 | 2.8039 | 8.718% | 9.276% | 6.269% | 1.0955 | 1.1022 | 1.0669
2010-11-02 | 20 | 22.0925 | 9.2869 | 31.3795 | 1.7129 | 0.76558 | 0.23328 | 2.7117 | 8.642% | 9.195% | 6.213% | 1.0946 | 1.1013 | 1.0663
2010-11-02 | 21 | 21.8753 | 9.1541 | 31.0294 | 1.6749 | 0.76558 | 0.23068 | 2.6711 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-11-02 | 22 | 21.3396 | 9.096 | 30.4356 | 1.6114 | 0.76558 | 0.22626 | 2.6032 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-11-02 | 23 | 20.8374 | 8.751 | 29.5884 | 1.5229 | 0.76558 | 0.21996 | 2.5085 | 8.478% | 9.02% | 6.096% | 1.0926 | 1.0991 | 1.0649
2010-11-02 | 24 | 20.2704 | 8.6676 | 28.938 | 1.4567 | 0.76558 | 0.21513 | 2.4374 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-11-02 | 25 | 19.8835 | 8.6723 | 28.5558 | 1.4185 | 0.76558 | 0.21229 | 2.3963 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2010-11-02 | 26 | 19.4535 | 8.2415 | 27.695 | 1.3342 | 0.76558 | 0.20589 | 2.3057 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2010-11-02 | 27 | 19.3946 | 8.4076 | 27.8023 | 1.3446 | 0.76558 | 0.20669 | 2.3169 | 8.333% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-11-02 | 28 | 19.1958 | 8.412 | 27.6078 | 1.3259 | 0.76558 | 0.20524 | 2.2967 | 8.319% | 8.851% | 5.981% | 1.0907 | 1.0971 | 1.0636
2010-11-02 | 29 | 19.0826 | 8.2102 | 27.2927 | 1.2958 | 0.76558 | 0.2029 | 2.2642 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-11-02 | 30 | 18.5471 | 7.9754 | 26.5225 | 1.2237 | 0.76558 | 0.19717 | 2.1864 | 8.244% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2010-11-02 | 31 | 18.8089 | 8.0838 | 26.8927 | 1.2581 | 0.76558 | 0.19992 | 2.2236 | 8.268% | 8.797% | 5.945% | 1.0901 | 1.0965 | 1.0632
2010-11-02 | 32 | 18.94 | 8.1726 | 27.1127 | 1.2787 | 0.76558 | 0.20156 | 2.2459 | 8.283% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-11-02 | 33 | 19.0093 | 8.6438 | 27.6531 | 1.3302 | 0.76558 | 0.20558 | 2.3014 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-11-02 | 34 | 19.2166 | 8.8715 | 28.0881 | 1.3724 | 0.76558 | 0.20881 | 2.3468 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-11-02 | 35 | 19.0529 | 9.1834 | 28.2363 | 1.3869 | 0.76558 | 0.20991 | 2.3624 | 8.367% | 8.902% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-11-02 | 36 | 19.6615 | 9.7328 | 29.3943 | 1.503 | 0.76558 | 0.21852 | 2.4871 | 8.461% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-11-02 | 37 | 20.4822 | 9.726 | 30.2083 | 1.5874 | 0.76558 | 0.22457 | 2.5775 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-11-02 | 38 | 20.8598 | 9.4716 | 30.3314 | 1.6004 | 0.76558 | 0.22549 | 2.5914 | 8.544% | 9.091% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-11-02 | 39 | 21.3015 | 9.1812 | 30.4826 | 1.6164 | 0.76558 | 0.22661 | 2.6086 | 8.558% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-11-02 | 40 | 21.0266 | 8.8781 | 29.9047 | 1.5557 | 0.76558 | 0.22232 | 2.5435 | 8.506% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-11-02 | 41 | 21.4811 | 8.7212 | 30.2023 | 1.5868 | 0.76558 | 0.22453 | 2.5769 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2010-11-02 | 42 | 22.4665 | 8.9972 | 31.4637 | 1.7221 | 0.76558 | 0.23391 | 2.7216 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-11-02 | 43 | 22.6858 | 9.0499 | 31.7357 | 1.752 | 0.76558 | 0.23593 | 2.7535 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-11-02 | 44 | 22.097 | 8.7071 | 30.8041 | 1.6506 | 0.76558 | 0.229 | 2.6452 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-11-02 | 45 | 20.8272 | 7.9273 | 28.7544 | 1.4383 | 0.76558 | 0.21376 | 2.4176 | 8.408% | 8.946% | 6.045% | 1.0918 | 1.0982 | 1.0643
2010-11-02 | 46 | 19.0729 | 7.2399 | 26.3127 | 1.2044 | 0.76558 | 0.19561 | 2.1656 | 8.23% | 8.757% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-11-02 | 47 | 17.6623 | 6.7749 | 24.4372 | 1.0388 | 0.76558 | 0.18167 | 1.9861 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2010-11-02 | 48 | 16.7276 | 6.8069 | 23.5345 | 0.96349 | 0.76558 | 0.17496 | 1.904 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-11-03 | 1 | 15.2183 | 6.0948 | 21.3131 | 0.79018 | 0.76558 | 0.15844 | 1.7142 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-03 | 2 | 14.0026 | 5.6007 | 19.6033 | 0.66849 | 0.76558 | 0.14573 | 1.5798 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-11-03 | 3 | 13.413 | 5.2904 | 18.7033 | 0.60852 | 0.76558 | 0.13904 | 1.5131 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-11-03 | 4 | 12.9573 | 5.2025 | 18.1598 | 0.57366 | 0.76558 | 0.135 | 1.4742 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-11-03 | 5 | 12.6404 | 5.117 | 17.7575 | 0.54852 | 0.76558 | 0.13201 | 1.4461 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-11-03 | 6 | 12.4892 | 5.1193 | 17.6086 | 0.53937 | 0.76558 | 0.1309 | 1.4358 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-11-03 | 7 | 12.145 | 4.9858 | 17.1308 | 0.51049 | 0.76558 | 0.12735 | 1.4034 | 8.192% | 8.717% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-11-03 | 8 | 12.1196 | 4.986 | 17.1056 | 0.50899 | 0.76558 | 0.12717 | 1.4017 | 8.195% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2010-11-03 | 9 | 12.3739 | 5.1127 | 17.4865 | 0.53192 | 0.76558 | 0.13 | 1.4275 | 8.163% | 8.686% | 5.869% | 1.0889 | 1.0951 | 1.0624
2010-11-03 | 10 | 12.6083 | 5.0692 | 17.6775 | 0.5436 | 0.76558 | 0.13142 | 1.4406 | 8.149% | 8.671% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-11-03 | 11 | 13.2435 | 5.268 | 18.5114 | 0.59609 | 0.76558 | 0.13762 | 1.4993 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-11-03 | 12 | 13.8297 | 6.1071 | 19.9368 | 0.69143 | 0.76558 | 0.14821 | 1.6052 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-03 | 13 | 15.3061 | 7.1721 | 22.4782 | 0.87894 | 0.76558 | 0.16711 | 1.8116 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-03 | 14 | 17.6062 | 8.5734 | 26.1797 | 1.1922 | 0.76558 | 0.19462 | 2.1524 | 8.222% | 8.748% | 5.911% | 1.0896 | 1.0959 | 1.0628
2010-11-03 | 15 | 21.1625 | 10.0162 | 31.1787 | 1.691 | 0.76558 | 0.23179 | 2.6884 | 8.623% | 9.174% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-11-03 | 16 | 23.295 | 10.2683 | 33.5633 | 1.9596 | 0.76558 | 0.24951 | 2.9747 | 8.863% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-11-03 | 17 | 24.165 | 10.7476 | 34.9126 | 2.1203 | 0.76558 | 0.25954 | 3.1454 | 9.009% | 9.586% | 6.478% | 1.099 | 1.106 | 1.0693
2010-11-03 | 18 | 23.9653 | 10.512 | 34.4773 | 2.0678 | 0.76558 | 0.25631 | 3.0897 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-11-03 | 19 | 23.2878 | 10.2504 | 33.5381 | 1.9566 | 0.76558 | 0.24933 | 2.9716 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-11-03 | 20 | 22.435 | 9.766 | 32.201 | 1.8037 | 0.76558 | 0.23939 | 2.8087 | 8.722% | 9.281% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-11-03 | 21 | 22.1934 | 9.3852 | 31.5787 | 1.7347 | 0.76558 | 0.23476 | 2.735 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-11-03 | 22 | 21.5084 | 9.4159 | 30.9243 | 1.6635 | 0.76558 | 0.2299 | 2.659 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-11-03 | 23 | 20.6735 | 9.0513 | 29.7248 | 1.537 | 0.76558 | 0.22098 | 2.5236 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-11-03 | 24 | 20.2405 | 8.9298 | 29.1703 | 1.4802 | 0.76558 | 0.21686 | 2.4626 | 8.442% | 8.983% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-11-03 | 25 | 19.7997 | 8.7397 | 28.5394 | 1.4169 | 0.76558 | 0.21217 | 2.3946 | 8.39% | 8.927% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-11-03 | 26 | 19.3771 | 8.5528 | 27.9299 | 1.357 | 0.76558 | 0.20763 | 2.3302 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-11-03 | 27 | 19.4964 | 8.6291 | 28.1256 | 1.3761 | 0.76558 | 0.20909 | 2.3507 | 8.358% | 8.893% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-11-03 | 28 | 19.2418 | 8.6371 | 27.8789 | 1.352 | 0.76558 | 0.20726 | 2.3249 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-11-03 | 29 | 19.0886 | 8.3609 | 27.4495 | 1.3107 | 0.76558 | 0.20406 | 2.2803 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-11-03 | 30 | 18.7398 | 8.311 | 27.0508 | 1.2729 | 0.76558 | 0.2011 | 2.2396 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-11-03 | 31 | 18.7144 | 8.2089 | 26.9233 | 1.2609 | 0.76558 | 0.20015 | 2.2267 | 8.27% | 8.8% | 5.946% | 1.0902 | 1.0965 | 1.0632
2010-11-03 | 32 | 18.9304 | 8.2376 | 27.168 | 1.284 | 0.76558 | 0.20197 | 2.2515 | 8.287% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-11-03 | 33 | 18.9865 | 8.74 | 27.7265 | 1.3373 | 0.76558 | 0.20612 | 2.309 | 8.328% | 8.861% | 5.988% | 1.0908 | 1.0972 | 1.0637
2010-11-03 | 34 | 19.1866 | 8.9213 | 28.1079 | 1.3743 | 0.76558 | 0.20896 | 2.3489 | 8.357% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-11-03 | 35 | 18.9662 | 9.125 | 28.0912 | 1.3727 | 0.76558 | 0.20883 | 2.3471 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-11-03 | 36 | 19.5896 | 9.5665 | 29.1561 | 1.4787 | 0.76558 | 0.21675 | 2.4611 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-11-03 | 37 | 20.2437 | 9.7944 | 30.0381 | 1.5696 | 0.76558 | 0.22331 | 2.5585 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-11-03 | 38 | 20.8229 | 9.7274 | 30.5503 | 1.6235 | 0.76558 | 0.22711 | 2.6162 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2010-11-03 | 39 | 20.8061 | 9.6554 | 30.4615 | 1.6141 | 0.76558 | 0.22645 | 2.6062 | 8.556% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2010-11-03 | 40 | 21.0337 | 9.1461 | 30.1798 | 1.5844 | 0.76558 | 0.22436 | 2.5743 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2010-11-03 | 41 | 21.3058 | 8.8627 | 30.1685 | 1.5832 | 0.76558 | 0.22428 | 2.5731 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-11-03 | 42 | 21.97 | 9.1414 | 31.1114 | 1.6837 | 0.76558 | 0.23129 | 2.6806 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-11-03 | 43 | 22.5176 | 9.3384 | 31.856 | 1.7653 | 0.76558 | 0.23682 | 2.7677 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-11-03 | 44 | 21.8485 | 8.9889 | 30.8374 | 1.6542 | 0.76558 | 0.22925 | 2.649 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-11-03 | 45 | 20.6817 | 8.0583 | 28.74 | 1.4368 | 0.76558 | 0.21366 | 2.4161 | 8.407% | 8.945% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-11-03 | 46 | 18.609 | 7.042 | 25.651 | 1.1446 | 0.76558 | 0.19069 | 2.1008 | 8.19% | 8.714% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-11-03 | 47 | 17.1951 | 6.7267 | 23.9218 | 0.99546 | 0.76558 | 0.17784 | 1.9389 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-11-03 | 48 | 16.1065 | 6.7763 | 22.8828 | 0.91086 | 0.76558 | 0.17011 | 1.8466 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-11-04 | 1 | 14.7445 | 5.9924 | 20.7369 | 0.74804 | 0.76558 | 0.15416 | 1.6678 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-04 | 2 | 13.6213 | 5.5856 | 19.2068 | 0.64172 | 0.76558 | 0.14279 | 1.5501 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-04 | 3 | 12.8592 | 5.2192 | 18.0784 | 0.56853 | 0.76558 | 0.1344 | 1.4685 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-11-04 | 4 | 12.3352 | 5.0853 | 17.4205 | 0.52791 | 0.76558 | 0.12951 | 1.423 | 8.168% | 8.691% | 5.873% | 1.089 | 1.0952 | 1.0624
2010-11-04 | 5 | 11.9538 | 4.9708 | 16.9246 | 0.49828 | 0.76558 | 0.12582 | 1.3897 | 8.211% | 8.736% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-11-04 | 6 | 11.845 | 4.9799 | 16.8249 | 0.49243 | 0.76558 | 0.12508 | 1.3831 | 8.22% | 8.747% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-11-04 | 7 | 11.9562 | 4.9205 | 16.8767 | 0.49546 | 0.76558 | 0.12546 | 1.3865 | 8.215% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-11-04 | 8 | 11.8661 | 4.8744 | 16.7405 | 0.4875 | 0.76558 | 0.12445 | 1.3775 | 8.229% | 8.755% | 5.916% | 1.0897 | 1.096 | 1.0629
2010-11-04 | 9 | 12.0907 | 4.8929 | 16.9836 | 0.50176 | 0.76558 | 0.12626 | 1.3936 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-11-04 | 10 | 12.2219 | 4.9652 | 17.1871 | 0.51386 | 0.76558 | 0.12777 | 1.4072 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-11-04 | 11 | 12.6689 | 5.2267 | 17.8956 | 0.55709 | 0.76558 | 0.13304 | 1.4557 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0948 | 1.0621
2010-11-04 | 12 | 13.1479 | 5.5895 | 18.7374 | 0.61074 | 0.76558 | 0.1393 | 1.5156 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-11-04 | 13 | 14.6132 | 6.2193 | 20.8325 | 0.75495 | 0.76558 | 0.15487 | 1.6754 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-04 | 14 | 17.0678 | 7.3206 | 24.3884 | 1.0347 | 0.76558 | 0.18131 | 1.9816 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-11-04 | 15 | 20.497 | 8.9206 | 29.4176 | 1.5054 | 0.76558 | 0.21869 | 2.4897 | 8.463% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-11-04 | 16 | 22.4439 | 9.8096 | 32.2535 | 1.8096 | 0.76558 | 0.23978 | 2.815 | 8.728% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-11-04 | 17 | 23.5835 | 9.7936 | 33.3771 | 1.9379 | 0.76558 | 0.24813 | 2.9516 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-11-04 | 18 | 23.1436 | 9.3846 | 32.5282 | 1.8406 | 0.76558 | 0.24182 | 2.848 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-04 | 19 | 22.735 | 9.3211 | 32.0561 | 1.7875 | 0.76558 | 0.23831 | 2.7914 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-11-04 | 20 | 21.7948 | 9.0139 | 30.8087 | 1.6511 | 0.76558 | 0.22904 | 2.6457 | 8.588% | 9.137% | 6.175% | 1.0939 | 1.1006 | 1.0658
2010-11-04 | 21 | 21.2598 | 8.5385 | 29.7983 | 1.5446 | 0.76558 | 0.22152 | 2.5317 | 8.496% | 9.04% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-11-04 | 22 | 20.8096 | 8.7045 | 29.5141 | 1.5153 | 0.76558 | 0.21941 | 2.5003 | 8.471% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-11-04 | 23 | 20.2305 | 8.4796 | 28.7101 | 1.4338 | 0.76558 | 0.21343 | 2.4129 | 8.404% | 8.942% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-11-04 | 24 | 19.827 | 8.4262 | 28.2533 | 1.3886 | 0.76558 | 0.21004 | 2.3642 | 8.368% | 8.903% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-11-04 | 25 | 19.6974 | 8.5324 | 28.2298 | 1.3863 | 0.76558 | 0.20986 | 2.3617 | 8.366% | 8.901% | 6.015% | 1.0913 | 1.0977 | 1.064
2010-11-04 | 26 | 19.3689 | 8.2361 | 27.605 | 1.3256 | 0.76558 | 0.20522 | 2.2964 | 8.319% | 8.851% | 5.981% | 1.0907 | 1.0971 | 1.0636
2010-11-04 | 27 | 19.3354 | 8.428 | 27.7634 | 1.3409 | 0.76558 | 0.2064 | 2.3128 | 8.33% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-11-04 | 28 | 18.8004 | 8.3022 | 27.1026 | 1.2778 | 0.76558 | 0.20148 | 2.2448 | 8.283% | 8.813% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-11-04 | 29 | 18.3816 | 8.005 | 26.3867 | 1.2112 | 0.76558 | 0.19616 | 2.1729 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-11-04 | 30 | 18.2738 | 7.9189 | 26.1926 | 1.1934 | 0.76558 | 0.19472 | 2.1537 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-11-04 | 31 | 18.9683 | 7.8329 | 26.8013 | 1.2495 | 0.76558 | 0.19924 | 2.2143 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2010-11-04 | 32 | 19.0862 | 7.9439 | 27.0301 | 1.271 | 0.76558 | 0.20095 | 2.2375 | 8.278% | 8.808% | 5.952% | 1.0902 | 1.0966 | 1.0633
2010-11-04 | 33 | 19.3716 | 8.2789 | 27.6505 | 1.33 | 0.76558 | 0.20556 | 2.3011 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0971 | 1.0636
2010-11-04 | 34 | 19.3916 | 8.6253 | 28.0169 | 1.3654 | 0.76558 | 0.20828 | 2.3393 | 8.35% | 8.884% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-11-04 | 35 | 19.5684 | 8.8381 | 28.4065 | 1.4037 | 0.76558 | 0.21118 | 2.3804 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-11-04 | 36 | 19.9715 | 9.1529 | 29.1244 | 1.4755 | 0.76558 | 0.21651 | 2.4576 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-11-04 | 37 | 20.5659 | 9.3661 | 29.932 | 1.5585 | 0.76558 | 0.22252 | 2.5466 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-11-04 | 38 | 21.1276 | 9.0733 | 30.2009 | 1.5866 | 0.76558 | 0.22452 | 2.5767 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-11-04 | 39 | 21.1849 | 8.8196 | 30.0045 | 1.5661 | 0.76558 | 0.22306 | 2.5547 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-11-04 | 40 | 21.0918 | 8.7852 | 29.877 | 1.5528 | 0.76558 | 0.22211 | 2.5405 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-11-04 | 41 | 21.1395 | 8.7233 | 29.8627 | 1.5513 | 0.76558 | 0.222 | 2.5389 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-11-04 | 42 | 21.5765 | 8.9198 | 30.4963 | 1.6178 | 0.76558 | 0.22671 | 2.6101 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-11-04 | 43 | 22.287 | 8.9709 | 31.2579 | 1.6996 | 0.76558 | 0.23237 | 2.6976 | 8.63% | 9.182% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-11-04 | 44 | 22.0406 | 8.5697 | 30.6103 | 1.6299 | 0.76558 | 0.22756 | 2.6231 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-11-04 | 45 | 20.2943 | 7.8229 | 28.1172 | 1.3752 | 0.76558 | 0.20903 | 2.3498 | 8.357% | 8.892% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-11-04 | 46 | 18.774 | 7.0731 | 25.8472 | 1.1621 | 0.76558 | 0.19215 | 2.1199 | 8.202% | 8.726% | 5.897% | 1.0893 | 1.0956 | 1.0627
2010-11-04 | 47 | 17.2571 | 6.7735 | 24.0306 | 1.0045 | 0.76558 | 0.17865 | 1.9488 | 8.109% | 8.628% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-11-04 | 48 | 16.4163 | 6.838 | 23.2542 | 0.94067 | 0.76558 | 0.17287 | 1.8791 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-11-05 | 1 | 14.8631 | 6.1058 | 20.9689 | 0.76487 | 0.76558 | 0.15589 | 1.6863 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-05 | 2 | 13.7576 | 5.6184 | 19.3761 | 0.65308 | 0.76558 | 0.14404 | 1.5627 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-11-05 | 3 | 13.1939 | 5.3215 | 18.5154 | 0.59635 | 0.76558 | 0.13765 | 1.4996 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-11-05 | 4 | 12.8028 | 5.1579 | 17.9607 | 0.56115 | 0.76558 | 0.13352 | 1.4603 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-05 | 5 | 12.5508 | 5.1792 | 17.7301 | 0.54683 | 0.76558 | 0.13181 | 1.4442 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-11-05 | 6 | 12.3534 | 5.0544 | 17.4078 | 0.52713 | 0.76558 | 0.12941 | 1.4221 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-11-05 | 7 | 12.1893 | 4.9829 | 17.1722 | 0.51296 | 0.76558 | 0.12766 | 1.4062 | 8.189% | 8.713% | 5.888% | 1.0892 | 1.0954 | 1.0626
2010-11-05 | 8 | 12.1565 | 4.9867 | 17.1432 | 0.51123 | 0.76558 | 0.12744 | 1.4043 | 8.191% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-11-05 | 9 | 12.3646 | 4.9121 | 17.2767 | 0.51923 | 0.76558 | 0.12844 | 1.4132 | 8.18% | 8.704% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-11-05 | 10 | 12.6543 | 5.0723 | 17.7266 | 0.54662 | 0.76558 | 0.13178 | 1.444 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-11-05 | 11 | 13.2343 | 5.379 | 18.6133 | 0.60268 | 0.76558 | 0.13837 | 1.5066 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-11-05 | 12 | 13.618 | 5.7117 | 19.3297 | 0.64996 | 0.76558 | 0.1437 | 1.5592 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-05 | 13 | 15.1458 | 6.2361 | 21.3819 | 0.79529 | 0.76558 | 0.15896 | 1.7198 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-05 | 14 | 17.8276 | 7.4211 | 25.2487 | 1.109 | 0.76558 | 0.1877 | 2.0622 | 8.168% | 8.69% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-11-05 | 15 | 21.2509 | 9.3329 | 30.5838 | 1.6271 | 0.76558 | 0.22736 | 2.62 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-11-05 | 16 | 23.3897 | 10.5631 | 33.9528 | 2.0053 | 0.76558 | 0.25241 | 3.0233 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2010-11-05 | 17 | 24.4339 | 10.9991 | 35.4331 | 2.184 | 0.76558 | 0.26341 | 3.213 | 9.068% | 9.648% | 6.52% | 1.0997 | 1.1068 | 1.0697
2010-11-05 | 18 | 24.3415 | 10.855 | 35.1966 | 2.1549 | 0.76558 | 0.26166 | 3.1822 | 9.041% | 9.62% | 6.501% | 1.0994 | 1.1064 | 1.0695
2010-11-05 | 19 | 23.6706 | 10.7712 | 34.4418 | 2.0635 | 0.76558 | 0.25604 | 3.0851 | 8.958% | 9.531% | 6.44% | 1.0984 | 1.1053 | 1.0688
2010-11-05 | 20 | 22.8884 | 10.1939 | 33.0822 | 1.9038 | 0.76558 | 0.24594 | 2.9153 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-11-05 | 21 | 22.3041 | 9.7175 | 32.0217 | 1.7837 | 0.76558 | 0.23805 | 2.7873 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2010-11-05 | 22 | 21.6719 | 9.514 | 31.1859 | 1.6918 | 0.76558 | 0.23184 | 2.6892 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-11-05 | 23 | 21.2175 | 9.2226 | 30.4401 | 1.6119 | 0.76558 | 0.2263 | 2.6037 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-11-05 | 24 | 20.7617 | 9.1203 | 29.882 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-11-05 | 25 | 20.2503 | 9.0246 | 29.2749 | 1.4908 | 0.76558 | 0.21763 | 2.474 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-11-05 | 26 | 19.5714 | 8.7747 | 28.3461 | 1.3977 | 0.76558 | 0.21073 | 2.374 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-11-05 | 27 | 19.0833 | 8.9209 | 28.0041 | 1.3642 | 0.76558 | 0.20819 | 2.338 | 8.349% | 8.883% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-11-05 | 28 | 19.0847 | 9.1188 | 28.2035 | 1.3837 | 0.76558 | 0.20967 | 2.3589 | 8.364% | 8.899% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-11-05 | 29 | 19.1792 | 9.1202 | 28.2993 | 1.3931 | 0.76558 | 0.21038 | 2.3691 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2010-11-05 | 30 | 18.9683 | 9.0382 | 28.0065 | 1.3644 | 0.76558 | 0.2082 | 2.3382 | 8.349% | 8.883% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-11-05 | 31 | 19.0725 | 9.0922 | 28.1647 | 1.3799 | 0.76558 | 0.20938 | 2.3548 | 8.361% | 8.896% | 6.012% | 1.0912 | 1.0976 | 1.064
2010-11-05 | 32 | 19.1037 | 8.9391 | 28.0429 | 1.368 | 0.76558 | 0.20847 | 2.342 | 8.352% | 8.886% | 6.005% | 1.0911 | 1.0975 | 1.0639
2010-11-05 | 33 | 19.3561 | 9.2486 | 28.6047 | 1.4233 | 0.76558 | 0.21265 | 2.4016 | 8.396% | 8.933% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-11-05 | 34 | 19.6258 | 9.2489 | 28.8747 | 1.4503 | 0.76558 | 0.21466 | 2.4306 | 8.418% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-11-05 | 35 | 19.7514 | 9.7438 | 29.4952 | 1.5133 | 0.76558 | 0.21927 | 2.4982 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-11-05 | 36 | 20.104 | 10.0956 | 30.1996 | 1.5865 | 0.76558 | 0.22451 | 2.5766 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-11-05 | 37 | 21.3149 | 10.3245 | 31.6394 | 1.7414 | 0.76558 | 0.23521 | 2.7422 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-11-05 | 38 | 22.6297 | 10.1525 | 32.7822 | 1.8694 | 0.76558 | 0.24371 | 2.8787 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-11-05 | 39 | 24.7761 | 10.2063 | 34.9825 | 2.1288 | 0.76558 | 0.26006 | 3.1544 | 9.017% | 9.594% | 6.483% | 1.0991 | 1.1061 | 1.0693
2010-11-05 | 40 | 24.6212 | 10.1282 | 34.7494 | 2.1005 | 0.76558 | 0.25833 | 3.1244 | 8.991% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-11-05 | 41 | 24.7517 | 10.1648 | 34.9165 | 2.1208 | 0.76558 | 0.25957 | 3.1459 | 9.01% | 9.587% | 6.478% | 1.099 | 1.106 | 1.0693
2010-11-05 | 42 | 25.0926 | 10.4122 | 35.5049 | 2.1929 | 0.76558 | 0.26395 | 3.2224 | 9.076% | 9.657% | 6.526% | 1.0998 | 1.1069 | 1.0698
2010-11-05 | 43 | 24.6171 | 10.2031 | 34.8202 | 2.1091 | 0.76558 | 0.25886 | 3.1335 | 8.999% | 9.575% | 6.47% | 1.0989 | 1.1059 | 1.0692
2010-11-05 | 44 | 23.5454 | 9.6902 | 33.2356 | 1.9215 | 0.76558 | 0.24708 | 2.9342 | 8.828% | 9.393% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-11-05 | 45 | 21.673 | 8.8823 | 30.5552 | 1.6241 | 0.76558 | 0.22715 | 2.6168 | 8.564% | 9.112% | 6.158% | 1.0937 | 1.1003 | 1.0656
2010-11-05 | 46 | 19.7836 | 8.2103 | 27.9939 | 1.3632 | 0.76558 | 0.20811 | 2.3369 | 8.348% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2010-11-05 | 47 | 18.2013 | 7.7669 | 25.9682 | 1.1731 | 0.76558 | 0.19305 | 2.1317 | 8.209% | 8.734% | 5.902% | 1.0894 | 1.0957 | 1.0627
2010-11-05 | 48 | 17.2833 | 7.7878 | 25.0711 | 1.0934 | 0.76558 | 0.18638 | 2.0454 | 8.158% | 8.68% | 5.866% | 1.0888 | 1.0951 | 1.0623
2010-11-06 | 1 | 15.9137 | 6.8844 | 22.798 | 0.90413 | 0.76558 | 0.16948 | 1.8392 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-11-06 | 2 | 14.894 | 6.3173 | 21.2113 | 0.78265 | 0.76558 | 0.15769 | 1.7059 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-06 | 3 | 13.9559 | 6.2337 | 20.1896 | 0.70907 | 0.76558 | 0.15009 | 1.6247 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-11-06 | 4 | 13.4287 | 6.0647 | 19.4935 | 0.66102 | 0.76558 | 0.14492 | 1.5715 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-11-06 | 5 | 13.1554 | 5.8388 | 18.9942 | 0.62759 | 0.76558 | 0.14121 | 1.5344 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-11-06 | 6 | 13.2097 | 5.6723 | 18.882 | 0.6202 | 0.76558 | 0.14037 | 1.5261 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-11-06 | 7 | 13.0878 | 5.6339 | 18.7216 | 0.60971 | 0.76558 | 0.13918 | 1.5145 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-11-06 | 8 | 12.8006 | 5.6244 | 18.4251 | 0.59054 | 0.76558 | 0.13697 | 1.4931 | 8.104% | 8.622% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-11-06 | 9 | 13.1246 | 6.0919 | 19.2165 | 0.64237 | 0.76558 | 0.14286 | 1.5508 | 8.07% | 8.587% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-11-06 | 10 | 13.2744 | 6.5829 | 19.8573 | 0.68592 | 0.76558 | 0.14762 | 1.5991 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-06 | 11 | 14.0104 | 7.1715 | 21.1819 | 0.78048 | 0.76558 | 0.15747 | 1.7035 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-06 | 12 | 14.2865 | 7.8444 | 22.131 | 0.85199 | 0.76558 | 0.16452 | 1.7821 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-06 | 13 | 15.8582 | 8.6528 | 24.5111 | 1.0451 | 0.76558 | 0.18222 | 1.9929 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-06 | 14 | 18.7984 | 10.0296 | 28.828 | 1.4457 | 0.76558 | 0.21431 | 2.4255 | 8.414% | 8.952% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-11-06 | 15 | 22.3767 | 11.5422 | 33.9189 | 2.0013 | 0.76558 | 0.25216 | 3.0191 | 8.901% | 9.47% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-06 | 16 | 24.4486 | 11.9057 | 36.3544 | 2.299 | 0.76558 | 0.27026 | 3.3349 | 9.173% | 9.76% | 6.596% | 1.101 | 1.1082 | 1.0706
2010-11-06 | 17 | 25.307 | 11.7509 | 37.0578 | 2.3889 | 0.76558 | 0.27549 | 3.43 | 9.256% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2010-11-06 | 18 | 25.1924 | 11.2952 | 36.4876 | 2.3159 | 0.76558 | 0.27125 | 3.3528 | 9.189% | 9.777% | 6.607% | 1.1012 | 1.1084 | 1.0707
2010-11-06 | 19 | 24.8366 | 10.8803 | 35.7169 | 2.2191 | 0.76558 | 0.26552 | 3.2502 | 9.1% | 9.682% | 6.543% | 1.1001 | 1.1072 | 1.07
2010-11-06 | 20 | 23.9427 | 10.4125 | 34.3552 | 2.0531 | 0.76558 | 0.2554 | 3.0741 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-11-06 | 21 | 23.8819 | 10.093 | 33.9749 | 2.0079 | 0.76558 | 0.25257 | 3.0261 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-11-06 | 22 | 22.9938 | 10.0424 | 33.0361 | 1.8985 | 0.76558 | 0.24559 | 2.9097 | 8.808% | 9.371% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-11-06 | 23 | 22.1338 | 9.7464 | 31.8802 | 1.768 | 0.76558 | 0.237 | 2.7706 | 8.691% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-11-06 | 24 | 21.1965 | 9.65 | 30.8465 | 1.6552 | 0.76558 | 0.22932 | 2.6501 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-11-06 | 25 | 20.4838 | 9.5333 | 30.0171 | 1.5674 | 0.76558 | 0.22315 | 2.5561 | 8.515% | 9.06% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-06 | 26 | 20.048 | 9.1163 | 29.1643 | 1.4796 | 0.76558 | 0.21681 | 2.462 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-11-06 | 27 | 20.022 | 9.2895 | 29.3116 | 1.4946 | 0.76558 | 0.21791 | 2.478 | 8.454% | 8.995% | 6.079% | 1.0923 | 1.0988 | 1.0647
2010-11-06 | 28 | 19.821 | 9.3708 | 29.1918 | 1.4824 | 0.76558 | 0.21702 | 2.465 | 8.444% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-11-06 | 29 | 19.7096 | 9.1817 | 28.8912 | 1.452 | 0.76558 | 0.21478 | 2.4324 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-11-06 | 30 | 19.2697 | 8.788 | 28.0576 | 1.3694 | 0.76558 | 0.20858 | 2.3436 | 8.353% | 8.887% | 6.006% | 1.0911 | 1.0975 | 1.0639
2010-11-06 | 31 | 19.2431 | 8.6421 | 27.8852 | 1.3526 | 0.76558 | 0.2073 | 2.3255 | 8.34% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-11-06 | 32 | 19.0488 | 8.7004 | 27.7492 | 1.3395 | 0.76558 | 0.20629 | 2.3113 | 8.329% | 8.863% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-11-06 | 33 | 19.6217 | 8.8873 | 28.5089 | 1.4138 | 0.76558 | 0.21194 | 2.3913 | 8.388% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2010-11-06 | 34 | 19.6641 | 8.9518 | 28.6159 | 1.4245 | 0.76558 | 0.21273 | 2.4028 | 8.397% | 8.934% | 6.037% | 1.0917 | 1.0981 | 1.0643
2010-11-06 | 35 | 19.4372 | 9.4444 | 28.8816 | 1.451 | 0.76558 | 0.21471 | 2.4313 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-11-06 | 36 | 19.7179 | 9.6826 | 29.4005 | 1.5036 | 0.76558 | 0.21857 | 2.4878 | 8.462% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-11-06 | 37 | 20.3145 | 9.6151 | 29.9297 | 1.5583 | 0.76558 | 0.2225 | 2.5463 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-11-06 | 38 | 20.8159 | 9.6128 | 30.4287 | 1.6107 | 0.76558 | 0.22621 | 2.6024 | 8.553% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-11-06 | 39 | 20.8325 | 9.4729 | 30.3053 | 1.5976 | 0.76558 | 0.22529 | 2.5885 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-11-06 | 40 | 20.8561 | 9.1698 | 30.0259 | 1.5683 | 0.76558 | 0.22322 | 2.5571 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-06 | 41 | 20.9785 | 9.1317 | 30.1103 | 1.5771 | 0.76558 | 0.22384 | 2.5665 | 8.524% | 9.069% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-11-06 | 42 | 21.6292 | 9.2893 | 30.9185 | 1.6629 | 0.76558 | 0.22985 | 2.6584 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-11-06 | 43 | 22.0331 | 9.3642 | 31.3973 | 1.7148 | 0.76558 | 0.23341 | 2.7138 | 8.643% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-11-06 | 44 | 21.6331 | 9.1531 | 30.7862 | 1.6487 | 0.76558 | 0.22887 | 2.6432 | 8.586% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-11-06 | 45 | 20.4453 | 8.7864 | 29.2317 | 1.4864 | 0.76558 | 0.21731 | 2.4693 | 8.447% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-11-06 | 46 | 19.1055 | 8.1081 | 27.2136 | 1.2883 | 0.76558 | 0.20231 | 2.2562 | 8.291% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2010-11-06 | 47 | 18.0405 | 7.8928 | 25.9333 | 1.1699 | 0.76558 | 0.19279 | 2.1283 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-11-06 | 48 | 17.0586 | 7.8529 | 24.9115 | 1.0795 | 0.76558 | 0.1852 | 2.0303 | 8.15% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0622
2010-11-07 | 1 | 15.2454 | 6.8299 | 22.0753 | 0.84771 | 0.76558 | 0.16411 | 1.7774 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-07 | 2 | 14.1518 | 6.3908 | 20.5427 | 0.73409 | 0.76558 | 0.15272 | 1.6524 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-07 | 3 | 13.4837 | 6.0625 | 19.5463 | 0.6646 | 0.76558 | 0.14531 | 1.5755 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-07 | 4 | 13.1022 | 5.9303 | 19.0325 | 0.63013 | 0.76558 | 0.14149 | 1.5372 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-11-07 | 5 | 12.7283 | 5.8441 | 18.5724 | 0.60002 | 0.76558 | 0.13807 | 1.5037 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-11-07 | 6 | 12.4505 | 5.8146 | 18.2651 | 0.58033 | 0.76558 | 0.13578 | 1.4817 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-11-07 | 7 | 12.183 | 5.6904 | 17.8735 | 0.55571 | 0.76558 | 0.13287 | 1.4542 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-11-07 | 8 | 12.15 | 5.5426 | 17.6927 | 0.54453 | 0.76558 | 0.13153 | 1.4416 | 8.148% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-11-07 | 9 | 12.3045 | 5.7352 | 18.0397 | 0.5661 | 0.76558 | 0.13411 | 1.4658 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-11-07 | 10 | 12.4306 | 5.8704 | 18.3009 | 0.58261 | 0.76558 | 0.13605 | 1.4842 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-11-07 | 11 | 12.6601 | 5.9345 | 18.5947 | 0.60147 | 0.76558 | 0.13823 | 1.5053 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2010-11-07 | 12 | 13.0498 | 5.9758 | 19.0256 | 0.62967 | 0.76558 | 0.14144 | 1.5367 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-11-07 | 13 | 13.7433 | 6.2072 | 19.9505 | 0.69238 | 0.76558 | 0.14831 | 1.6063 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-07 | 14 | 15.0562 | 6.6061 | 21.6623 | 0.81629 | 0.76558 | 0.16104 | 1.7429 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-07 | 15 | 16.7268 | 7.3229 | 24.0497 | 1.0061 | 0.76558 | 0.17879 | 1.9505 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-11-07 | 16 | 18.5707 | 8.0728 | 26.6435 | 1.2349 | 0.76558 | 0.19807 | 2.1985 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0962 | 1.0631
2010-11-07 | 17 | 20.2673 | 8.8766 | 29.1439 | 1.4775 | 0.76558 | 0.21666 | 2.4598 | 8.44% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-11-07 | 18 | 21.5282 | 9.3918 | 30.92 | 1.6631 | 0.76558 | 0.22986 | 2.6585 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-11-07 | 19 | 22.0582 | 10.2265 | 32.2847 | 1.8131 | 0.76558 | 0.24001 | 2.8187 | 8.731% | 9.29% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-11-07 | 20 | 22.3054 | 10.4335 | 32.7389 | 1.8645 | 0.76558 | 0.24339 | 2.8735 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-11-07 | 21 | 22.652 | 10.3527 | 33.0047 | 1.8949 | 0.76558 | 0.24536 | 2.9058 | 8.804% | 9.368% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-11-07 | 22 | 22.1636 | 10.2236 | 32.3872 | 1.8247 | 0.76558 | 0.24077 | 2.831 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-11-07 | 23 | 21.6984 | 9.9413 | 31.6397 | 1.7414 | 0.76558 | 0.23521 | 2.7422 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-11-07 | 24 | 21.1422 | 9.8154 | 30.9576 | 1.6671 | 0.76558 | 0.23014 | 2.6629 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-11-07 | 25 | 20.6966 | 9.7806 | 30.4772 | 1.6158 | 0.76558 | 0.22657 | 2.6079 | 8.557% | 9.105% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-11-07 | 26 | 19.8607 | 9.3734 | 29.2341 | 1.4867 | 0.76558 | 0.21733 | 2.4696 | 8.448% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-11-07 | 27 | 19.4647 | 9.4057 | 28.8704 | 1.4499 | 0.76558 | 0.21463 | 2.4301 | 8.417% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-11-07 | 28 | 19.3098 | 9.1437 | 28.4535 | 1.4083 | 0.76558 | 0.21153 | 2.3854 | 8.384% | 8.92% | 6.028% | 1.0915 | 1.0979 | 1.0641
2010-11-07 | 29 | 19.0863 | 8.825 | 27.9113 | 1.3552 | 0.76558 | 0.2075 | 2.3282 | 8.342% | 8.875% | 5.998% | 1.091 | 1.0974 | 1.0638
2010-11-07 | 30 | 18.6166 | 8.6314 | 27.248 | 1.2915 | 0.76558 | 0.20256 | 2.2597 | 8.293% | 8.824% | 5.963% | 1.0904 | 1.0968 | 1.0634
2010-11-07 | 31 | 18.6638 | 8.6638 | 27.3276 | 1.2991 | 0.76558 | 0.20316 | 2.2678 | 8.299% | 8.83% | 5.967% | 1.0905 | 1.0968 | 1.0635
2010-11-07 | 32 | 18.7595 | 8.4818 | 27.2413 | 1.2909 | 0.76558 | 0.20251 | 2.259 | 8.293% | 8.823% | 5.962% | 1.0904 | 1.0968 | 1.0634
2010-11-07 | 33 | 18.9672 | 8.6657 | 27.633 | 1.3283 | 0.76558 | 0.20543 | 2.2993 | 8.321% | 8.853% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-11-07 | 34 | 19.0445 | 8.7356 | 27.7801 | 1.3425 | 0.76558 | 0.20652 | 2.3146 | 8.332% | 8.865% | 5.991% | 1.0909 | 1.0973 | 1.0637
2010-11-07 | 35 | 19.4862 | 9.3999 | 28.8861 | 1.4515 | 0.76558 | 0.21474 | 2.4318 | 8.419% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-11-07 | 36 | 20.1038 | 9.9744 | 30.0782 | 1.5738 | 0.76558 | 0.22361 | 2.5629 | 8.521% | 9.066% | 6.127% | 1.0931 | 1.0997 | 1.0653
2010-11-07 | 37 | 20.6359 | 10.0064 | 30.6423 | 1.6333 | 0.76558 | 0.2278 | 2.6267 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-11-07 | 38 | 20.8284 | 9.7509 | 30.5793 | 1.6266 | 0.76558 | 0.22733 | 2.6195 | 8.566% | 9.115% | 6.159% | 1.0937 | 1.1003 | 1.0656
2010-11-07 | 39 | 20.599 | 9.5722 | 30.1712 | 1.5835 | 0.76558 | 0.2243 | 2.5734 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2010-11-07 | 40 | 20.4925 | 9.2641 | 29.7566 | 1.5403 | 0.76558 | 0.22121 | 2.5271 | 8.492% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-11-07 | 41 | 20.1014 | 9.1238 | 29.2251 | 1.4858 | 0.76558 | 0.21726 | 2.4686 | 8.447% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-11-07 | 42 | 20.3086 | 9.1044 | 29.413 | 1.5049 | 0.76558 | 0.21866 | 2.4892 | 8.463% | 9.004% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-11-07 | 43 | 20.9911 | 9.1017 | 30.0927 | 1.5753 | 0.76558 | 0.22371 | 2.5646 | 8.522% | 9.068% | 6.127% | 1.0932 | 1.0997 | 1.0653
2010-11-07 | 44 | 20.7641 | 8.6623 | 29.4264 | 1.5063 | 0.76558 | 0.21876 | 2.4906 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-07 | 45 | 19.4364 | 8.1173 | 27.5537 | 1.3207 | 0.76558 | 0.20484 | 2.2911 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2010-11-07 | 46 | 18.2158 | 7.7161 | 25.9319 | 1.1698 | 0.76558 | 0.19278 | 2.1281 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-11-07 | 47 | 17.2843 | 7.6443 | 24.9286 | 1.081 | 0.76558 | 0.18532 | 2.0319 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2010-11-07 | 48 | 16.5327 | 7.6573 | 24.1901 | 1.0179 | 0.76558 | 0.17983 | 1.9633 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-11-08 | 1 | 15.2505 | 6.7833 | 22.0338 | 0.84452 | 0.76558 | 0.1638 | 1.7739 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-08 | 2 | 14.2813 | 6.3183 | 20.5997 | 0.73817 | 0.76558 | 0.15314 | 1.6569 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-08 | 3 | 13.6435 | 6.0652 | 19.7087 | 0.67569 | 0.76558 | 0.14652 | 1.5878 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-11-08 | 4 | 13.0821 | 5.8729 | 18.955 | 0.625 | 0.76558 | 0.14091 | 1.5315 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-11-08 | 5 | 12.7723 | 5.7334 | 18.5057 | 0.59572 | 0.76558 | 0.13757 | 1.4989 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-11-08 | 6 | 12.5592 | 5.6557 | 18.2149 | 0.57715 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-11-08 | 7 | 12.3583 | 5.5381 | 17.8965 | 0.55715 | 0.76558 | 0.13304 | 1.4558 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0948 | 1.0621
2010-11-08 | 8 | 12.224 | 5.7165 | 17.9405 | 0.55989 | 0.76558 | 0.13337 | 1.4588 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-11-08 | 9 | 12.3464 | 5.7449 | 18.0914 | 0.56935 | 0.76558 | 0.13449 | 1.4694 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-11-08 | 10 | 12.5572 | 5.8111 | 18.3683 | 0.58691 | 0.76558 | 0.13655 | 1.489 | 8.107% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-11-08 | 11 | 13.0491 | 5.8433 | 18.8924 | 0.62088 | 0.76558 | 0.14045 | 1.5269 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-11-08 | 12 | 13.6796 | 6.2295 | 19.9092 | 0.68951 | 0.76558 | 0.14801 | 1.6031 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-11-08 | 13 | 14.7718 | 6.7316 | 21.5035 | 0.80436 | 0.76558 | 0.15986 | 1.7298 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-08 | 14 | 15.3705 | 6.9909 | 22.3614 | 0.86983 | 0.76558 | 0.16624 | 1.8016 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-08 | 15 | 16.892 | 7.4876 | 24.3796 | 1.0339 | 0.76558 | 0.18124 | 1.9807 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-11-08 | 16 | 17.7462 | 7.8944 | 25.6406 | 1.1436 | 0.76558 | 0.19062 | 2.0998 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-11-08 | 17 | 19.1921 | 8.9043 | 28.0964 | 1.3732 | 0.76558 | 0.20887 | 2.3477 | 8.356% | 8.89% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-11-08 | 18 | 20.5107 | 9.3372 | 29.8478 | 1.5497 | 0.76558 | 0.22189 | 2.5372 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2010-11-08 | 19 | 21.5946 | 9.7568 | 31.3513 | 1.7098 | 0.76558 | 0.23307 | 2.7085 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-11-08 | 20 | 21.8527 | 10.1548 | 32.0075 | 1.7821 | 0.76558 | 0.23795 | 2.7856 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-11-08 | 21 | 22.2384 | 9.8836 | 32.1219 | 1.7949 | 0.76558 | 0.2388 | 2.7993 | 8.715% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2010-11-08 | 22 | 21.7025 | 10.0342 | 31.7367 | 1.7521 | 0.76558 | 0.23593 | 2.7536 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-11-08 | 23 | 21.2281 | 9.7889 | 31.017 | 1.6735 | 0.76558 | 0.23058 | 2.6697 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-11-08 | 24 | 20.4669 | 9.5565 | 30.0234 | 1.568 | 0.76558 | 0.2232 | 2.5568 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-08 | 25 | 19.8839 | 9.5182 | 29.4021 | 1.5038 | 0.76558 | 0.21858 | 2.488 | 8.462% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-11-08 | 26 | 19.2809 | 9.1641 | 28.4451 | 1.4075 | 0.76558 | 0.21146 | 2.3845 | 8.383% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2010-11-08 | 27 | 18.9204 | 9.3522 | 28.2726 | 1.3905 | 0.76558 | 0.21018 | 2.3662 | 8.369% | 8.905% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-11-08 | 28 | 18.6582 | 9.2081 | 27.8663 | 1.3508 | 0.76558 | 0.20716 | 2.3235 | 8.338% | 8.872% | 5.995% | 1.091 | 1.0974 | 1.0638
2010-11-08 | 29 | 18.3231 | 8.7542 | 27.0773 | 1.2754 | 0.76558 | 0.2013 | 2.2423 | 8.281% | 8.811% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-11-08 | 30 | 17.5925 | 8.5631 | 26.1556 | 1.19 | 0.76558 | 0.19444 | 2.1501 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2010-11-08 | 31 | 17.6671 | 8.4261 | 26.0932 | 1.1844 | 0.76558 | 0.19398 | 2.1439 | 8.216% | 8.742% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-11-08 | 32 | 17.4429 | 8.3883 | 25.8312 | 1.1607 | 0.76558 | 0.19203 | 2.1183 | 8.201% | 8.725% | 5.896% | 1.0893 | 1.0956 | 1.0627
2010-11-08 | 33 | 17.6509 | 8.6049 | 26.2558 | 1.1992 | 0.76558 | 0.19519 | 2.1599 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-11-08 | 34 | 17.9436 | 8.3239 | 26.2676 | 1.2003 | 0.76558 | 0.19528 | 2.1611 | 8.227% | 8.754% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-11-08 | 35 | 18.1477 | 8.509 | 26.6567 | 1.2361 | 0.76558 | 0.19817 | 2.1998 | 8.252% | 8.781% | 5.934% | 1.0899 | 1.0963 | 1.0631
2010-11-08 | 36 | 19.04 | 9.1693 | 28.2093 | 1.3843 | 0.76558 | 0.20971 | 2.3596 | 8.364% | 8.9% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-11-08 | 37 | 19.8275 | 9.6603 | 29.4878 | 1.5126 | 0.76558 | 0.21922 | 2.4974 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-11-08 | 38 | 20.3669 | 9.635 | 30.0019 | 1.5658 | 0.76558 | 0.22304 | 2.5544 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-11-08 | 39 | 20.5083 | 9.5087 | 30.017 | 1.5674 | 0.76558 | 0.22315 | 2.5561 | 8.515% | 9.06% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-08 | 40 | 20.3664 | 9.3343 | 29.7007 | 1.5345 | 0.76558 | 0.2208 | 2.5209 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2010-11-08 | 41 | 20.8167 | 9.425 | 30.2417 | 1.5909 | 0.76558 | 0.22482 | 2.5813 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-11-08 | 42 | 21.3385 | 9.5585 | 30.8969 | 1.6606 | 0.76558 | 0.22969 | 2.6559 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-11-08 | 43 | 21.6169 | 9.4412 | 31.0581 | 1.678 | 0.76558 | 0.23089 | 2.6744 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-11-08 | 44 | 20.9108 | 8.8155 | 29.7262 | 1.5371 | 0.76558 | 0.22099 | 2.5237 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-11-08 | 45 | 19.5331 | 8.0116 | 27.5447 | 1.3198 | 0.76558 | 0.20477 | 2.2902 | 8.314% | 8.846% | 5.978% | 1.0907 | 1.097 | 1.0636
2010-11-08 | 46 | 17.8975 | 7.3551 | 25.2526 | 1.1093 | 0.76558 | 0.18773 | 2.0626 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-11-08 | 47 | 16.6764 | 7.0488 | 23.7252 | 0.97916 | 0.76558 | 0.17638 | 1.9211 | 8.097% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-11-08 | 48 | 15.4224 | 7.2797 | 22.7021 | 0.89654 | 0.76558 | 0.16877 | 1.8309 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-11-09 | 1 | 13.773 | 6.4631 | 20.2361 | 0.71234 | 0.76558 | 0.15044 | 1.6284 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-11-09 | 2 | 12.7768 | 6.0065 | 18.7833 | 0.61373 | 0.76558 | 0.13964 | 1.5189 | 8.087% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-11-09 | 3 | 12.1544 | 5.7848 | 17.9393 | 0.55981 | 0.76558 | 0.13336 | 1.4588 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-11-09 | 4 | 12.102 | 5.5357 | 17.6377 | 0.54115 | 0.76558 | 0.13112 | 1.4378 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2010-11-09 | 5 | 11.6833 | 5.5007 | 17.184 | 0.51367 | 0.76558 | 0.12775 | 1.407 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2010-11-09 | 6 | 11.4938 | 5.4614 | 16.9553 | 0.50008 | 0.76558 | 0.12605 | 1.3917 | 8.208% | 8.733% | 5.902% | 1.0894 | 1.0957 | 1.0627
2010-11-09 | 7 | 11.3893 | 5.3394 | 16.7287 | 0.48681 | 0.76558 | 0.12436 | 1.3768 | 8.23% | 8.757% | 5.917% | 1.0897 | 1.096 | 1.0629
2010-11-09 | 8 | 11.2815 | 5.3632 | 16.6447 | 0.48193 | 0.76558 | 0.12374 | 1.3712 | 8.238% | 8.766% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-11-09 | 9 | 11.3452 | 5.5758 | 16.9209 | 0.49806 | 0.76558 | 0.12579 | 1.3894 | 8.211% | 8.737% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-11-09 | 10 | 11.7407 | 5.6777 | 17.4185 | 0.52778 | 0.76558 | 0.12949 | 1.4229 | 8.169% | 8.691% | 5.873% | 1.089 | 1.0952 | 1.0624
2010-11-09 | 11 | 12.0828 | 5.684 | 17.7668 | 0.5491 | 0.76558 | 0.13208 | 1.4468 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2010-11-09 | 12 | 12.571 | 6.0232 | 18.5942 | 0.60144 | 0.76558 | 0.13823 | 1.5052 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2010-11-09 | 13 | 13.9225 | 6.6906 | 20.6131 | 0.73913 | 0.76558 | 0.15324 | 1.6579 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-09 | 14 | 16.1683 | 7.7391 | 23.9074 | 0.99426 | 0.76558 | 0.17773 | 1.9376 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-11-09 | 15 | 19.3349 | 9.369 | 28.7039 | 1.4332 | 0.76558 | 0.21339 | 2.4122 | 8.404% | 8.942% | 6.042% | 1.0917 | 1.0982 | 1.0643
2010-11-09 | 16 | 21.366 | 10.3074 | 31.6734 | 1.7451 | 0.76558 | 0.23546 | 2.7462 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-11-09 | 17 | 22.4322 | 10.7045 | 33.1367 | 1.9101 | 0.76558 | 0.24634 | 2.922 | 8.818% | 9.382% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-11-09 | 18 | 22.8682 | 10.6504 | 33.5186 | 1.9544 | 0.76558 | 0.24918 | 2.9691 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-11-09 | 19 | 22.6369 | 10.6179 | 33.2547 | 1.9237 | 0.76558 | 0.24722 | 2.9365 | 8.83% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2010-11-09 | 20 | 22.2506 | 10.1937 | 32.4443 | 1.8311 | 0.76558 | 0.24119 | 2.8379 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-11-09 | 21 | 22.2854 | 9.9561 | 32.2415 | 1.8083 | 0.76558 | 0.23969 | 2.8135 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2010-11-09 | 22 | 21.6683 | 10.1955 | 31.8638 | 1.7662 | 0.76558 | 0.23688 | 2.7686 | 8.689% | 9.245% | 6.247% | 1.0952 | 1.1019 | 1.0666
2010-11-09 | 23 | 21.2973 | 9.8061 | 31.1034 | 1.6829 | 0.76558 | 0.23123 | 2.6797 | 8.615% | 9.167% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-11-09 | 24 | 20.7226 | 9.6613 | 30.3839 | 1.6059 | 0.76558 | 0.22588 | 2.5974 | 8.549% | 9.096% | 6.146% | 1.0935 | 1.1001 | 1.0655
2010-11-09 | 25 | 20.1899 | 9.6437 | 29.8337 | 1.5483 | 0.76558 | 0.22179 | 2.5356 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-11-09 | 26 | 19.7444 | 9.1663 | 28.9107 | 1.454 | 0.76558 | 0.21493 | 2.4345 | 8.421% | 8.96% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-11-09 | 27 | 19.5567 | 9.2755 | 28.8322 | 1.4461 | 0.76558 | 0.21434 | 2.426 | 8.414% | 8.953% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-11-09 | 28 | 19.5529 | 9.4839 | 29.0368 | 1.4667 | 0.76558 | 0.21586 | 2.4481 | 8.431% | 8.971% | 6.062% | 1.0921 | 1.0985 | 1.0645
2010-11-09 | 29 | 19.188 | 9.3417 | 28.5297 | 1.4159 | 0.76558 | 0.21209 | 2.3936 | 8.39% | 8.927% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-11-09 | 30 | 18.7492 | 9.0214 | 27.7706 | 1.3415 | 0.76558 | 0.20645 | 2.3136 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-11-09 | 31 | 18.9827 | 8.9485 | 27.9312 | 1.3571 | 0.76558 | 0.20764 | 2.3303 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-11-09 | 32 | 18.9453 | 9.1564 | 28.1017 | 1.3737 | 0.76558 | 0.20891 | 2.3482 | 8.356% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-11-09 | 33 | 19.0434 | 9.6471 | 28.6904 | 1.4319 | 0.76558 | 0.21329 | 2.4108 | 8.403% | 8.94% | 6.041% | 1.0917 | 1.0982 | 1.0643
2010-11-09 | 34 | 19.3387 | 9.6654 | 29.0041 | 1.4634 | 0.76558 | 0.21562 | 2.4446 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-11-09 | 35 | 19.4486 | 9.9912 | 29.4398 | 1.5077 | 0.76558 | 0.21886 | 2.4921 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-09 | 36 | 19.8811 | 10.6612 | 30.5423 | 1.6227 | 0.76558 | 0.22706 | 2.6153 | 8.563% | 9.111% | 6.157% | 1.0936 | 1.1002 | 1.0656
2010-11-09 | 37 | 20.6853 | 10.9034 | 31.5887 | 1.7358 | 0.76558 | 0.23483 | 2.7362 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-11-09 | 38 | 21.3295 | 10.9275 | 32.257 | 1.81 | 0.76558 | 0.2398 | 2.8154 | 8.728% | 9.287% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-11-09 | 39 | 21.3919 | 10.8499 | 32.2418 | 1.8083 | 0.76558 | 0.23969 | 2.8136 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2010-11-09 | 40 | 21.3152 | 10.453 | 31.7682 | 1.7556 | 0.76558 | 0.23617 | 2.7573 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2010-11-09 | 41 | 21.8175 | 10.2445 | 32.062 | 1.7882 | 0.76558 | 0.23835 | 2.7921 | 8.709% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-11-09 | 42 | 22.1173 | 10.4093 | 32.5266 | 1.8404 | 0.76558 | 0.24181 | 2.8478 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-09 | 43 | 22.7663 | 10.6962 | 33.4626 | 1.9478 | 0.76558 | 0.24876 | 2.9622 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2010-11-09 | 44 | 22.202 | 10.5021 | 32.7041 | 1.8605 | 0.76558 | 0.24313 | 2.8692 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-11-09 | 45 | 20.9007 | 9.3935 | 30.2942 | 1.5964 | 0.76558 | 0.22521 | 2.5872 | 8.54% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-11-09 | 46 | 19.1024 | 8.6421 | 27.7445 | 1.339 | 0.76558 | 0.20626 | 2.3109 | 8.329% | 8.862% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-11-09 | 47 | 17.4538 | 8.2105 | 25.6643 | 1.1458 | 0.76558 | 0.19079 | 2.1021 | 8.191% | 8.715% | 5.889% | 1.0892 | 1.0955 | 1.0626
2010-11-09 | 48 | 16.4267 | 8.3038 | 24.7306 | 1.0639 | 0.76558 | 0.18385 | 2.0133 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-11-10 | 1 | 14.8588 | 7.4534 | 22.3123 | 0.86601 | 0.76558 | 0.16587 | 1.7975 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-11-10 | 2 | 13.7113 | 7.0604 | 20.7717 | 0.75055 | 0.76558 | 0.15442 | 1.6705 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-10 | 3 | 13.0902 | 6.7811 | 19.8712 | 0.68689 | 0.76558 | 0.14773 | 1.6002 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-10 | 4 | 12.8135 | 6.7273 | 19.5408 | 0.66423 | 0.76558 | 0.14527 | 1.5751 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-10 | 5 | 12.5075 | 6.8083 | 19.3158 | 0.64902 | 0.76558 | 0.1436 | 1.5582 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-10 | 6 | 12.2212 | 7.1066 | 19.3278 | 0.64983 | 0.76558 | 0.14369 | 1.5591 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-10 | 7 | 12.2739 | 7.2876 | 19.5615 | 0.66564 | 0.76558 | 0.14542 | 1.5766 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-10 | 8 | 12.2922 | 7.2638 | 19.556 | 0.66527 | 0.76558 | 0.14538 | 1.5762 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-10 | 9 | 12.2512 | 7.209 | 19.4603 | 0.65877 | 0.76558 | 0.14467 | 1.569 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-10 | 10 | 12.5691 | 7.3083 | 19.8774 | 0.68731 | 0.76558 | 0.14777 | 1.6007 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-10 | 11 | 12.8081 | 7.659 | 20.4671 | 0.7287 | 0.76558 | 0.15215 | 1.6464 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-10 | 12 | 13.4026 | 8.2648 | 21.6674 | 0.81667 | 0.76558 | 0.16108 | 1.7433 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-10 | 13 | 14.8063 | 8.5646 | 23.3709 | 0.95013 | 0.76558 | 0.17374 | 1.8895 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-11-10 | 14 | 17.4694 | 9.3429 | 26.8123 | 1.2506 | 0.76558 | 0.19933 | 2.2155 | 8.263% | 8.792% | 5.941% | 1.0901 | 1.0964 | 1.0632
2010-11-10 | 15 | 20.8934 | 10.7122 | 31.6055 | 1.7376 | 0.76558 | 0.23496 | 2.7382 | 8.664% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-11-10 | 16 | 22.7407 | 11.6683 | 34.409 | 2.0596 | 0.76558 | 0.2558 | 3.081 | 8.954% | 9.527% | 6.438% | 1.0983 | 1.1053 | 1.0688
2010-11-10 | 17 | 24.0944 | 12.1953 | 36.2897 | 2.2909 | 0.76558 | 0.26978 | 3.3262 | 9.166% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0706
2010-11-10 | 18 | 24.7262 | 12.4966 | 37.2228 | 2.4102 | 0.76558 | 0.27672 | 3.4525 | 9.275% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2010-11-10 | 19 | 24.6447 | 12.306 | 36.9507 | 2.3751 | 0.76558 | 0.2747 | 3.4154 | 9.243% | 9.835% | 6.646% | 1.1018 | 1.1091 | 1.0712
2010-11-10 | 20 | 24.1887 | 11.8738 | 36.0625 | 2.2623 | 0.76558 | 0.26809 | 3.296 | 9.14% | 9.724% | 6.571% | 1.1006 | 1.1077 | 1.0703
2010-11-10 | 21 | 24.0667 | 11.4835 | 35.5502 | 2.1985 | 0.76558 | 0.26428 | 3.2283 | 9.081% | 9.662% | 6.529% | 1.0999 | 1.107 | 1.0699
2010-11-10 | 22 | 23.3027 | 11.3299 | 34.6327 | 2.0864 | 0.76558 | 0.25746 | 3.1095 | 8.978% | 9.553% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-11-10 | 23 | 22.7228 | 11.2533 | 33.9761 | 2.0081 | 0.76558 | 0.25258 | 3.0262 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-11-10 | 24 | 22.1608 | 10.9125 | 33.0733 | 1.9028 | 0.76558 | 0.24587 | 2.9142 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1035 | 1.0676
2010-11-10 | 25 | 21.4167 | 10.9193 | 32.3361 | 1.8189 | 0.76558 | 0.24039 | 2.8249 | 8.736% | 9.295% | 6.281% | 1.0957 | 1.1025 | 1.067
2010-11-10 | 26 | 20.8046 | 10.2178 | 31.0224 | 1.6741 | 0.76558 | 0.23062 | 2.6703 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-11-10 | 27 | 20.1144 | 10.3398 | 30.4542 | 1.6134 | 0.76558 | 0.2264 | 2.6053 | 8.555% | 9.102% | 6.151% | 1.0936 | 1.1001 | 1.0655
2010-11-10 | 28 | 20.1423 | 10.1119 | 30.2542 | 1.5922 | 0.76558 | 0.22491 | 2.5827 | 8.537% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-11-10 | 29 | 19.7312 | 9.711 | 29.4422 | 1.5079 | 0.76558 | 0.21888 | 2.4924 | 8.465% | 9.007% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-11-10 | 30 | 19.2397 | 9.5477 | 28.7874 | 1.4416 | 0.76558 | 0.21401 | 2.4212 | 8.411% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-11-10 | 31 | 19.5016 | 9.3596 | 28.8611 | 1.449 | 0.76558 | 0.21456 | 2.4291 | 8.417% | 8.955% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-11-10 | 32 | 19.3815 | 9.4099 | 28.7914 | 1.442 | 0.76558 | 0.21404 | 2.4216 | 8.411% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-11-10 | 33 | 19.8395 | 9.8228 | 29.6623 | 1.5305 | 0.76558 | 0.22051 | 2.5166 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-11-10 | 34 | 19.9933 | 9.9572 | 29.9505 | 1.5604 | 0.76558 | 0.22266 | 2.5487 | 8.51% | 9.054% | 6.118% | 1.093 | 1.0996 | 1.0652
2010-11-10 | 35 | 20.0839 | 10.2815 | 30.3654 | 1.604 | 0.76558 | 0.22574 | 2.5953 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-11-10 | 36 | 20.6194 | 10.8683 | 31.4877 | 1.7247 | 0.76558 | 0.23408 | 2.7244 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-11-10 | 37 | 20.9513 | 11.0099 | 31.9612 | 1.777 | 0.76558 | 0.2376 | 2.7802 | 8.699% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-11-10 | 38 | 21.5036 | 10.8822 | 32.3858 | 1.8245 | 0.76558 | 0.24076 | 2.8308 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-11-10 | 39 | 21.5891 | 10.6255 | 32.2147 | 1.8053 | 0.76558 | 0.23949 | 2.8103 | 8.724% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-11-10 | 40 | 21.392 | 10.2852 | 31.6772 | 1.7455 | 0.76558 | 0.23549 | 2.7466 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-11-10 | 41 | 21.2626 | 10.0018 | 31.2644 | 1.7003 | 0.76558 | 0.23242 | 2.6983 | 8.631% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-11-10 | 42 | 21.9225 | 10.1674 | 32.0899 | 1.7913 | 0.76558 | 0.23856 | 2.7954 | 8.711% | 9.269% | 6.263% | 1.0954 | 1.1022 | 1.0668
2010-11-10 | 43 | 22.3661 | 10.5821 | 32.9482 | 1.8884 | 0.76558 | 0.24494 | 2.8989 | 8.798% | 9.362% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-11-10 | 44 | 21.7557 | 10.4417 | 32.1974 | 1.8033 | 0.76558 | 0.23936 | 2.8083 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-11-10 | 45 | 20.4486 | 9.5431 | 29.9917 | 1.5647 | 0.76558 | 0.22296 | 2.5533 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-11-10 | 46 | 18.5268 | 8.5522 | 27.079 | 1.2756 | 0.76558 | 0.20131 | 2.2424 | 8.281% | 8.811% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-11-10 | 47 | 17.2213 | 8.1537 | 25.375 | 1.1201 | 0.76558 | 0.18864 | 2.0743 | 8.175% | 8.698% | 5.878% | 1.089 | 1.0953 | 1.0624
2010-11-10 | 48 | 16.137 | 8.1902 | 24.3272 | 1.0295 | 0.76558 | 0.18085 | 1.9759 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-11-11 | 1 | 14.8842 | 7.2591 | 22.1433 | 0.85294 | 0.76558 | 0.16462 | 1.7831 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-11 | 2 | 13.694 | 6.7933 | 20.4873 | 0.73014 | 0.76558 | 0.15231 | 1.648 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-11 | 3 | 13.1028 | 6.641 | 19.7438 | 0.6781 | 0.76558 | 0.14678 | 1.5905 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-11-11 | 4 | 12.2306 | 6.5402 | 18.7707 | 0.61291 | 0.76558 | 0.13954 | 1.518 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2010-11-11 | 5 | 12.0284 | 6.3432 | 18.3716 | 0.58712 | 0.76558 | 0.13658 | 1.4893 | 8.106% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-11-11 | 6 | 11.8342 | 6.0565 | 17.8907 | 0.55678 | 0.76558 | 0.133 | 1.4554 | 8.135% | 8.655% | 5.849% | 1.0886 | 1.0948 | 1.0621
2010-11-11 | 7 | 11.5522 | 5.9751 | 17.5273 | 0.5344 | 0.76558 | 0.1303 | 1.4303 | 8.16% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-11-11 | 8 | 11.5444 | 5.9375 | 17.4819 | 0.53164 | 0.76558 | 0.12996 | 1.4272 | 8.164% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-11-11 | 9 | 11.9748 | 6.103 | 18.0779 | 0.5685 | 0.76558 | 0.13439 | 1.4685 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-11-11 | 10 | 12.708 | 6.1936 | 18.9016 | 0.62149 | 0.76558 | 0.14052 | 1.5276 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-11-11 | 11 | 13.2785 | 6.3705 | 19.6489 | 0.6716 | 0.76558 | 0.14607 | 1.5833 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-11 | 12 | 14.0502 | 6.8034 | 20.8535 | 0.75647 | 0.76558 | 0.15503 | 1.6771 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-11 | 13 | 15.3486 | 7.2943 | 22.6429 | 0.89186 | 0.76558 | 0.16833 | 1.8258 | 8.063% | 8.579% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-11-11 | 14 | 17.7573 | 8.4301 | 26.1874 | 1.1929 | 0.76558 | 0.19468 | 2.1532 | 8.222% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-11-11 | 15 | 21.1598 | 9.9092 | 31.0691 | 1.6792 | 0.76558 | 0.23097 | 2.6757 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-11-11 | 16 | 23.239 | 10.7857 | 34.0248 | 2.0138 | 0.76558 | 0.25294 | 3.0324 | 8.912% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-11-11 | 17 | 24.1989 | 11.4062 | 35.605 | 2.2052 | 0.76558 | 0.26469 | 3.2355 | 9.087% | 9.669% | 6.534% | 1.1 | 1.107 | 1.0699
2010-11-11 | 18 | 24.0069 | 11.6183 | 35.6252 | 2.2077 | 0.76558 | 0.26484 | 3.2382 | 9.09% | 9.671% | 6.535% | 1.1 | 1.1071 | 1.0699
2010-11-11 | 19 | 23.7852 | 11.7419 | 35.5271 | 2.1956 | 0.76558 | 0.26411 | 3.2253 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-11-11 | 20 | 22.9095 | 11.2194 | 34.1289 | 2.0262 | 0.76558 | 0.25372 | 3.0455 | 8.923% | 9.495% | 6.416% | 1.098 | 1.1049 | 1.0686
2010-11-11 | 21 | 22.9035 | 10.8551 | 33.7587 | 1.9825 | 0.76558 | 0.25097 | 2.999 | 8.884% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2010-11-11 | 22 | 21.8122 | 10.6235 | 32.4357 | 1.8301 | 0.76558 | 0.24113 | 2.8368 | 8.746% | 9.306% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-11-11 | 23 | 21.424 | 10.7573 | 32.1813 | 1.8015 | 0.76558 | 0.23924 | 2.8064 | 8.72% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-11-11 | 24 | 21.6875 | 10.7153 | 32.4027 | 1.8264 | 0.76558 | 0.24089 | 2.8329 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-11-11 | 25 | 20.9445 | 10.4645 | 31.409 | 1.7161 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-11-11 | 26 | 20.3977 | 10.3446 | 30.7424 | 1.644 | 0.76558 | 0.22854 | 2.6381 | 8.581% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-11-11 | 27 | 20.0845 | 10.4642 | 30.5487 | 1.6234 | 0.76558 | 0.2271 | 2.6161 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2010-11-11 | 28 | 19.9694 | 10.374 | 30.3434 | 1.6016 | 0.76558 | 0.22558 | 2.5928 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-11-11 | 29 | 19.8535 | 9.9599 | 29.8134 | 1.5462 | 0.76558 | 0.22164 | 2.5334 | 8.497% | 9.041% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-11-11 | 30 | 19.6887 | 9.5729 | 29.2616 | 1.4895 | 0.76558 | 0.21753 | 2.4726 | 8.45% | 8.991% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-11-11 | 31 | 20.0266 | 9.4017 | 29.4283 | 1.5065 | 0.76558 | 0.21877 | 2.4908 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-11 | 32 | 19.9711 | 9.4661 | 29.4372 | 1.5074 | 0.76558 | 0.21884 | 2.4918 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-11 | 33 | 20.2444 | 9.7394 | 29.9838 | 1.5639 | 0.76558 | 0.2229 | 2.5524 | 8.513% | 9.057% | 6.121% | 1.093 | 1.0996 | 1.0652
2010-11-11 | 34 | 20.3529 | 9.8156 | 30.1686 | 1.5832 | 0.76558 | 0.22428 | 2.5731 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-11-11 | 35 | 20.6557 | 10.2515 | 30.9071 | 1.6617 | 0.76558 | 0.22977 | 2.657 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-11-11 | 36 | 21.0138 | 10.6928 | 31.7066 | 1.7488 | 0.76558 | 0.23571 | 2.7501 | 8.673% | 9.229% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-11-11 | 37 | 21.7906 | 10.7065 | 32.4971 | 1.8371 | 0.76558 | 0.24159 | 2.8442 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-11-11 | 38 | 21.9882 | 10.4446 | 32.4328 | 1.8298 | 0.76558 | 0.24111 | 2.8365 | 8.746% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2010-11-11 | 39 | 22.2311 | 10.1418 | 32.373 | 1.8231 | 0.76558 | 0.24066 | 2.8293 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2010-11-11 | 40 | 22.3007 | 10.1418 | 32.4425 | 1.8309 | 0.76558 | 0.24118 | 2.8377 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-11-11 | 41 | 22.5806 | 9.9158 | 32.4963 | 1.837 | 0.76558 | 0.24158 | 2.8441 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-11-11 | 42 | 23.4244 | 10.2723 | 33.6967 | 1.9752 | 0.76558 | 0.25051 | 2.9913 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-11-11 | 43 | 24.1671 | 10.6212 | 34.7883 | 2.1052 | 0.76558 | 0.25862 | 3.1294 | 8.996% | 9.571% | 6.468% | 1.0988 | 1.1058 | 1.0692
2010-11-11 | 44 | 24.2447 | 10.317 | 34.5617 | 2.0779 | 0.76558 | 0.25694 | 3.1004 | 8.971% | 9.545% | 6.45% | 1.0985 | 1.1055 | 1.0689
2010-11-11 | 45 | 22.6446 | 9.5239 | 32.1685 | 1.8001 | 0.76558 | 0.23914 | 2.8048 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-11-11 | 46 | 20.6467 | 8.4731 | 29.1199 | 1.4751 | 0.76558 | 0.21648 | 2.4571 | 8.438% | 8.978% | 6.067% | 1.0922 | 1.0986 | 1.0646
2010-11-11 | 47 | 19.0066 | 7.9635 | 26.9701 | 1.2653 | 0.76558 | 0.2005 | 2.2314 | 8.274% | 8.803% | 5.949% | 1.0902 | 1.0965 | 1.0632
2010-11-11 | 48 | 18.0206 | 7.9802 | 26.0008 | 1.176 | 0.76558 | 0.19329 | 2.1349 | 8.211% | 8.736% | 5.904% | 1.0895 | 1.0957 | 1.0627
2010-11-12 | 1 | 16.4945 | 6.9897 | 23.4842 | 0.95937 | 0.76558 | 0.17458 | 1.8995 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-11-12 | 2 | 15.1334 | 6.4239 | 21.5573 | 0.8084 | 0.76558 | 0.16026 | 1.7342 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-12 | 3 | 14.5066 | 6.243 | 20.7497 | 0.74896 | 0.76558 | 0.15426 | 1.6688 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-12 | 4 | 13.838 | 6.0809 | 19.9189 | 0.69018 | 0.76558 | 0.14808 | 1.6038 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-11-12 | 5 | 13.5979 | 5.9999 | 19.5978 | 0.66811 | 0.76558 | 0.14569 | 1.5794 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-11-12 | 6 | 13.4321 | 5.8729 | 19.305 | 0.6483 | 0.76558 | 0.14352 | 1.5574 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-11-12 | 7 | 13.4806 | 5.8588 | 19.3394 | 0.65061 | 0.76558 | 0.14377 | 1.56 | 8.066% | 8.582% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-12 | 8 | 13.5723 | 6.2353 | 19.8076 | 0.68249 | 0.76558 | 0.14725 | 1.5953 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-12 | 9 | 13.7267 | 6.2463 | 19.973 | 0.69394 | 0.76558 | 0.14848 | 1.608 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-12 | 10 | 13.9652 | 6.5505 | 20.5156 | 0.73216 | 0.76558 | 0.15252 | 1.6503 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-12 | 11 | 14.4301 | 6.8965 | 21.3266 | 0.79118 | 0.76558 | 0.15854 | 1.7153 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-12 | 12 | 15.2068 | 7.8787 | 23.0854 | 0.92707 | 0.76558 | 0.17162 | 1.8643 | 8.076% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-11-12 | 13 | 16.6427 | 8.8688 | 25.5115 | 1.1322 | 0.76558 | 0.18966 | 2.0874 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2010-11-12 | 14 | 19.0442 | 10.3406 | 29.3847 | 1.502 | 0.76558 | 0.21845 | 2.4861 | 8.46% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2010-11-12 | 15 | 22.6071 | 11.8413 | 34.4485 | 2.0643 | 0.76558 | 0.25609 | 3.086 | 8.958% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-11-12 | 16 | 24.7156 | 12.4003 | 37.1159 | 2.3964 | 0.76558 | 0.27592 | 3.4379 | 9.263% | 9.855% | 6.66% | 1.1021 | 1.1093 | 1.0713
2010-11-12 | 17 | 25.6737 | 12.4469 | 38.1207 | 2.5279 | 0.76558 | 0.28339 | 3.5768 | 9.383% | 9.983% | 6.746% | 1.1035 | 1.1109 | 1.0723
2010-11-12 | 18 | 25.2751 | 12.1865 | 37.4616 | 2.4412 | 0.76558 | 0.27849 | 3.4853 | 9.304% | 9.899% | 6.689% | 1.1026 | 1.1099 | 1.0717
2010-11-12 | 19 | 24.8297 | 11.8792 | 36.7089 | 2.3441 | 0.76558 | 0.2729 | 3.3826 | 9.215% | 9.804% | 6.625% | 1.1015 | 1.1087 | 1.071
2010-11-12 | 20 | 24.1137 | 11.4119 | 35.5256 | 2.1954 | 0.76558 | 0.2641 | 3.2251 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-11-12 | 21 | 23.95 | 10.8929 | 34.8428 | 2.1118 | 0.76558 | 0.25903 | 3.1364 | 9.002% | 9.578% | 6.472% | 1.0989 | 1.1059 | 1.0692
2010-11-12 | 22 | 23.4587 | 11.0257 | 34.4844 | 2.0686 | 0.76558 | 0.25636 | 3.0906 | 8.962% | 9.536% | 6.444% | 1.0984 | 1.1054 | 1.0689
2010-11-12 | 23 | 22.406 | 10.4132 | 32.8191 | 1.8737 | 0.76558 | 0.24398 | 2.8832 | 8.785% | 9.347% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-11-12 | 24 | 22.2465 | 10.6147 | 32.8612 | 1.8785 | 0.76558 | 0.24429 | 2.8883 | 8.789% | 9.352% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-11-12 | 25 | 22.1615 | 10.622 | 32.7835 | 1.8696 | 0.76558 | 0.24372 | 2.8789 | 8.781% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-11-12 | 26 | 21.7146 | 10.099 | 31.8136 | 1.7606 | 0.76558 | 0.23651 | 2.7627 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-11-12 | 27 | 21.4091 | 10.2048 | 31.614 | 1.7386 | 0.76558 | 0.23502 | 2.7392 | 8.664% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-11-12 | 28 | 21.0983 | 10.1188 | 31.2171 | 1.6952 | 0.76558 | 0.23207 | 2.6928 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-11-12 | 29 | 20.7509 | 10.0757 | 30.8266 | 1.6531 | 0.76558 | 0.22917 | 2.6478 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-11-12 | 30 | 19.9803 | 10.0183 | 29.9986 | 1.5654 | 0.76558 | 0.22301 | 2.554 | 8.514% | 9.059% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-11-12 | 31 | 20.2081 | 9.8079 | 30.016 | 1.5673 | 0.76558 | 0.22314 | 2.556 | 8.515% | 9.06% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-12 | 32 | 20.1171 | 9.7062 | 29.8234 | 1.5472 | 0.76558 | 0.22171 | 2.5345 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-11-12 | 33 | 20.4804 | 9.9304 | 30.4109 | 1.6088 | 0.76558 | 0.22608 | 2.6004 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-11-12 | 34 | 20.7981 | 10.1766 | 30.9747 | 1.669 | 0.76558 | 0.23027 | 2.6648 | 8.603% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-11-12 | 35 | 21.0772 | 10.734 | 31.8112 | 1.7603 | 0.76558 | 0.23649 | 2.7624 | 8.684% | 9.239% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-11-12 | 36 | 21.4987 | 11.2009 | 32.6996 | 1.86 | 0.76558 | 0.24309 | 2.8687 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-11-12 | 37 | 22.2713 | 11.3183 | 33.5896 | 1.9627 | 0.76558 | 0.24971 | 2.9779 | 8.866% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2010-11-12 | 38 | 22.7249 | 11.1968 | 33.9217 | 2.0017 | 0.76558 | 0.25218 | 3.0194 | 8.901% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-12 | 39 | 22.8327 | 10.9916 | 33.8242 | 1.9902 | 0.76558 | 0.25145 | 3.0072 | 8.891% | 9.46% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-11-12 | 40 | 22.9056 | 10.6829 | 33.5885 | 1.9625 | 0.76558 | 0.2497 | 2.9778 | 8.866% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2010-11-12 | 41 | 23.2745 | 10.6058 | 33.8803 | 1.9968 | 0.76558 | 0.25187 | 3.0142 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-11-12 | 42 | 23.4957 | 10.5895 | 34.0852 | 2.021 | 0.76558 | 0.25339 | 3.04 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1048 | 1.0685
2010-11-12 | 43 | 23.9749 | 10.734 | 34.709 | 2.0956 | 0.76558 | 0.25803 | 3.1193 | 8.987% | 9.562% | 6.462% | 1.0987 | 1.1057 | 1.0691
2010-11-12 | 44 | 23.4297 | 10.3371 | 33.7668 | 1.9834 | 0.76558 | 0.25103 | 3 | 8.885% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-11-12 | 45 | 21.6978 | 9.371 | 31.0689 | 1.6791 | 0.76558 | 0.23097 | 2.6757 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-11-12 | 46 | 20.1249 | 8.4155 | 28.5404 | 1.417 | 0.76558 | 0.21217 | 2.3947 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2010-11-12 | 47 | 18.6777 | 8.0284 | 26.7061 | 1.2407 | 0.76558 | 0.19854 | 2.2048 | 8.256% | 8.784% | 5.936% | 1.09 | 1.0963 | 1.0631
2010-11-12 | 48 | 17.4777 | 7.9764 | 25.4541 | 1.1271 | 0.76558 | 0.18923 | 2.0819 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-11-13 | 1 | 16.0493 | 7.2143 | 23.2636 | 0.94143 | 0.76558 | 0.17294 | 1.88 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-11-13 | 2 | 14.9923 | 6.7107 | 21.703 | 0.81936 | 0.76558 | 0.16134 | 1.7463 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-13 | 3 | 14.186 | 6.411 | 20.597 | 0.73798 | 0.76558 | 0.15312 | 1.6567 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-13 | 4 | 13.558 | 6.2619 | 19.8199 | 0.68334 | 0.76558 | 0.14734 | 1.5963 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-13 | 5 | 13.0496 | 6.219 | 19.2685 | 0.64585 | 0.76558 | 0.14324 | 1.5547 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-11-13 | 6 | 12.8207 | 6.2227 | 19.0434 | 0.63085 | 0.76558 | 0.14157 | 1.538 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2010-11-13 | 7 | 12.8093 | 6.3699 | 19.1792 | 0.63987 | 0.76558 | 0.14258 | 1.548 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-13 | 8 | 12.3946 | 6.4637 | 18.8583 | 0.61864 | 0.76558 | 0.14019 | 1.5244 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-11-13 | 9 | 12.5195 | 6.3678 | 18.8873 | 0.62055 | 0.76558 | 0.14041 | 1.5265 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-11-13 | 10 | 12.6774 | 6.3692 | 19.0466 | 0.63106 | 0.76558 | 0.14159 | 1.5382 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2010-11-13 | 11 | 13.2347 | 6.639 | 19.8737 | 0.68706 | 0.76558 | 0.14774 | 1.6004 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-13 | 12 | 13.9257 | 6.9466 | 20.8723 | 0.75784 | 0.76558 | 0.15517 | 1.6786 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-13 | 13 | 15.3883 | 7.6425 | 23.0307 | 0.92268 | 0.76558 | 0.17121 | 1.8595 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-11-13 | 14 | 17.6281 | 9.1025 | 26.7306 | 1.2429 | 0.76558 | 0.19872 | 2.2072 | 8.257% | 8.786% | 5.937% | 1.09 | 1.0963 | 1.0631
2010-11-13 | 15 | 20.5951 | 10.7503 | 31.3454 | 1.7092 | 0.76558 | 0.23303 | 2.7078 | 8.638% | 9.191% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-11-13 | 16 | 21.4536 | 11.1493 | 32.6029 | 1.849 | 0.76558 | 0.24237 | 2.857 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-11-13 | 17 | 23.9031 | 12.5171 | 36.4202 | 2.3074 | 0.76558 | 0.27075 | 3.3437 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-11-13 | 18 | 22.0267 | 11.6487 | 33.6754 | 1.9727 | 0.76558 | 0.25035 | 2.9886 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-11-13 | 19 | 24.616 | 12.4287 | 37.0446 | 2.3872 | 0.76558 | 0.27539 | 3.4282 | 9.254% | 9.846% | 6.654% | 1.102 | 1.1092 | 1.0713
2010-11-13 | 20 | 24.9962 | 12.406 | 37.4022 | 2.4335 | 0.76558 | 0.27805 | 3.4771 | 9.297% | 9.892% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-11-13 | 21 | 24.6766 | 11.7662 | 36.4428 | 2.3102 | 0.76558 | 0.27092 | 3.3467 | 9.184% | 9.771% | 6.603% | 1.1011 | 1.1083 | 1.0707
2010-11-13 | 22 | 24.1085 | 11.6567 | 35.7653 | 2.2251 | 0.76558 | 0.26588 | 3.2566 | 9.105% | 9.688% | 6.547% | 1.1002 | 1.1073 | 1.0701
2010-11-13 | 23 | 22.6397 | 11.2443 | 33.8839 | 1.9972 | 0.76558 | 0.2519 | 3.0147 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-11-13 | 24 | 22.5922 | 11.1781 | 33.7703 | 1.9838 | 0.76558 | 0.25105 | 3.0005 | 8.885% | 9.454% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-11-13 | 25 | 21.8187 | 10.8433 | 32.662 | 1.8557 | 0.76558 | 0.24281 | 2.8641 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-11-13 | 26 | 21.2138 | 10.0459 | 31.2597 | 1.6998 | 0.76558 | 0.23239 | 2.6978 | 8.63% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-11-13 | 27 | 21.0252 | 9.9579 | 30.9831 | 1.6699 | 0.76558 | 0.23033 | 2.6658 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-11-13 | 28 | 20.8054 | 9.8645 | 30.67 | 1.6363 | 0.76558 | 0.228 | 2.6299 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-11-13 | 29 | 20.4959 | 9.3922 | 29.8881 | 1.5539 | 0.76558 | 0.22219 | 2.5417 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-11-13 | 30 | 19.9083 | 9.3286 | 29.2368 | 1.4869 | 0.76558 | 0.21735 | 2.4699 | 8.448% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-11-13 | 31 | 19.9984 | 9.2967 | 29.2951 | 1.4929 | 0.76558 | 0.21778 | 2.4762 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-11-13 | 32 | 20.0435 | 9.3794 | 29.4229 | 1.5059 | 0.76558 | 0.21873 | 2.4902 | 8.464% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-11-13 | 33 | 19.9871 | 9.4128 | 29.3999 | 1.5036 | 0.76558 | 0.21856 | 2.4877 | 8.462% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-11-13 | 34 | 20.1605 | 9.1635 | 29.324 | 1.4958 | 0.76558 | 0.218 | 2.4794 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2010-11-13 | 35 | 20.2298 | 9.5091 | 29.7389 | 1.5385 | 0.76558 | 0.22108 | 2.5251 | 8.491% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-11-13 | 36 | 20.5642 | 9.8001 | 30.3642 | 1.6038 | 0.76558 | 0.22573 | 2.5951 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-11-13 | 37 | 21.0553 | 10.0134 | 31.0687 | 1.6791 | 0.76558 | 0.23097 | 2.6757 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-11-13 | 38 | 21.5478 | 9.9318 | 31.4796 | 1.7238 | 0.76558 | 0.23402 | 2.7234 | 8.651% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-11-13 | 39 | 21.8353 | 9.6399 | 31.4752 | 1.7233 | 0.76558 | 0.23399 | 2.7229 | 8.651% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2010-11-13 | 40 | 21.7515 | 9.5228 | 31.2743 | 1.7014 | 0.76558 | 0.2325 | 2.6995 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-11-13 | 41 | 21.9834 | 9.5787 | 31.562 | 1.7329 | 0.76558 | 0.23464 | 2.7331 | 8.659% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-11-13 | 42 | 22.2681 | 9.8533 | 32.1214 | 1.7948 | 0.76558 | 0.23879 | 2.7992 | 8.714% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2010-11-13 | 43 | 23.0705 | 10.0469 | 33.1174 | 1.9079 | 0.76558 | 0.2462 | 2.9196 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-11-13 | 44 | 23.2745 | 9.8146 | 33.0892 | 1.9046 | 0.76558 | 0.24599 | 2.9162 | 8.813% | 9.377% | 6.337% | 1.0966 | 1.1035 | 1.0677
2010-11-13 | 45 | 22.2047 | 9.3086 | 31.5133 | 1.7275 | 0.76558 | 0.23427 | 2.7274 | 8.655% | 9.209% | 6.223% | 1.0947 | 1.1014 | 1.0664
2010-11-13 | 46 | 20.7015 | 8.4711 | 29.1727 | 1.4804 | 0.76558 | 0.21687 | 2.4629 | 8.442% | 8.983% | 6.07% | 1.0922 | 1.0987 | 1.0646
2010-11-13 | 47 | 19.3797 | 8.1452 | 27.5249 | 1.3179 | 0.76558 | 0.20462 | 2.2881 | 8.313% | 8.845% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-11-13 | 48 | 18.4398 | 8.2141 | 26.6539 | 1.2358 | 0.76558 | 0.19815 | 2.1996 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0963 | 1.0631
2010-11-14 | 1 | 16.7917 | 7.4567 | 24.2484 | 1.0228 | 0.76558 | 0.18027 | 1.9687 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0946 | 1.062
2010-11-14 | 2 | 15.6681 | 7.1022 | 22.7703 | 0.90193 | 0.76558 | 0.16928 | 1.8368 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-14 | 3 | 14.8273 | 7.0929 | 21.9202 | 0.83584 | 0.76558 | 0.16296 | 1.7644 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-14 | 4 | 14.2299 | 7.1726 | 21.4025 | 0.79683 | 0.76558 | 0.15911 | 1.7215 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-14 | 5 | 13.9919 | 7.1756 | 21.1676 | 0.77943 | 0.76558 | 0.15736 | 1.7024 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-14 | 6 | 13.8845 | 7.8038 | 21.6883 | 0.81825 | 0.76558 | 0.16123 | 1.7451 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-14 | 7 | 13.5363 | 9.1903 | 22.7266 | 0.89847 | 0.76558 | 0.16895 | 1.833 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-11-14 | 8 | 13.5043 | 10.5388 | 24.0431 | 1.0056 | 0.76558 | 0.17874 | 1.9499 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-11-14 | 9 | 13.6633 | 10.9169 | 24.5802 | 1.051 | 0.76558 | 0.18273 | 1.9993 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-14 | 10 | 14.1255 | 11.0971 | 25.2226 | 1.1067 | 0.76558 | 0.18751 | 2.0597 | 8.166% | 8.689% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-11-14 | 11 | 14.3897 | 11.5528 | 25.9424 | 1.1707 | 0.76558 | 0.19286 | 2.1292 | 8.207% | 8.733% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-11-14 | 12 | 14.7254 | 11.7827 | 26.5081 | 1.2223 | 0.76558 | 0.19706 | 2.185 | 8.243% | 8.77% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-11-14 | 13 | 15.5414 | 12.0375 | 27.5789 | 1.3231 | 0.76558 | 0.20503 | 2.2937 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2010-11-14 | 14 | 16.6357 | 12.2955 | 28.9312 | 1.456 | 0.76558 | 0.21508 | 2.4367 | 8.422% | 8.961% | 6.056% | 1.092 | 1.0984 | 1.0645
2010-11-14 | 15 | 18.3962 | 11.7979 | 30.1941 | 1.5859 | 0.76558 | 0.22447 | 2.576 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-11-14 | 16 | 20.066 | 11.6123 | 31.6783 | 1.7457 | 0.76558 | 0.2355 | 2.7467 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-11-14 | 17 | 22.1019 | 11.5256 | 33.6275 | 1.9671 | 0.76558 | 0.24999 | 2.9827 | 8.87% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-11-14 | 18 | 23.1982 | 11.5073 | 34.7054 | 2.0952 | 0.76558 | 0.258 | 3.1188 | 8.986% | 9.562% | 6.461% | 1.0987 | 1.1057 | 1.0691
2010-11-14 | 19 | 24.5051 | 11.5153 | 36.0204 | 2.257 | 0.76558 | 0.26778 | 3.2904 | 9.135% | 9.719% | 6.568% | 1.1005 | 1.1077 | 1.0703
2010-11-14 | 20 | 24.9868 | 11.5793 | 36.5661 | 2.3259 | 0.76558 | 0.27184 | 3.3633 | 9.198% | 9.787% | 6.613% | 1.1013 | 1.1085 | 1.0708
2010-11-14 | 21 | 25.4648 | 11.5663 | 37.0311 | 2.3854 | 0.76558 | 0.27529 | 3.4263 | 9.253% | 9.845% | 6.653% | 1.102 | 1.1092 | 1.0713
2010-11-14 | 22 | 24.5668 | 11.7812 | 36.3479 | 2.2982 | 0.76558 | 0.27022 | 3.334 | 9.173% | 9.76% | 6.595% | 1.101 | 1.1082 | 1.0706
2010-11-14 | 23 | 23.557 | 11.6091 | 35.1661 | 2.1512 | 0.76558 | 0.26143 | 3.1782 | 9.038% | 9.616% | 6.498% | 1.0994 | 1.1064 | 1.0695
2010-11-14 | 24 | 22.6578 | 11.7041 | 34.3619 | 2.0539 | 0.76558 | 0.25545 | 3.075 | 8.949% | 9.522% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-11-14 | 25 | 21.4576 | 11.3585 | 32.8161 | 1.8733 | 0.76558 | 0.24396 | 2.8828 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-11-14 | 26 | 20.7638 | 10.805 | 31.5688 | 1.7336 | 0.76558 | 0.23469 | 2.7339 | 8.66% | 9.214% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-11-14 | 27 | 21.0111 | 10.6723 | 31.6835 | 1.7462 | 0.76558 | 0.23554 | 2.7473 | 8.671% | 9.226% | 6.235% | 1.0949 | 1.1016 | 1.0665
2010-11-14 | 28 | 20.7587 | 10.4287 | 31.1874 | 1.692 | 0.76558 | 0.23185 | 2.6894 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-11-14 | 29 | 20.1499 | 9.9629 | 30.1127 | 1.5774 | 0.76558 | 0.22386 | 2.5668 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-11-14 | 30 | 19.4545 | 9.6293 | 29.0838 | 1.4714 | 0.76558 | 0.21621 | 2.4532 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-11-14 | 31 | 19.6492 | 9.3547 | 29.0039 | 1.4634 | 0.76558 | 0.21562 | 2.4445 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2010-11-14 | 32 | 19.5443 | 9.103 | 28.6473 | 1.4276 | 0.76558 | 0.21297 | 2.4061 | 8.399% | 8.937% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-11-14 | 33 | 19.4097 | 9.2627 | 28.6724 | 1.4301 | 0.76558 | 0.21315 | 2.4088 | 8.401% | 8.939% | 6.04% | 1.0917 | 1.0982 | 1.0643
2010-11-14 | 34 | 19.499 | 9.3256 | 28.8247 | 1.4453 | 0.76558 | 0.21429 | 2.4252 | 8.414% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2010-11-14 | 35 | 19.8319 | 9.8673 | 29.6993 | 1.5344 | 0.76558 | 0.22079 | 2.5207 | 8.487% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2010-11-14 | 36 | 20.3749 | 10.2755 | 30.6504 | 1.6342 | 0.76558 | 0.22786 | 2.6276 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-11-14 | 37 | 20.801 | 10.0792 | 30.8801 | 1.6588 | 0.76558 | 0.22957 | 2.6539 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-11-14 | 38 | 20.3788 | 9.7758 | 30.1546 | 1.5818 | 0.76558 | 0.22417 | 2.5715 | 8.528% | 9.074% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-11-14 | 39 | 21.2821 | 9.556 | 30.8381 | 1.6543 | 0.76558 | 0.22925 | 2.6491 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-11-14 | 40 | 21.6306 | 9.3557 | 30.9863 | 1.6702 | 0.76558 | 0.23036 | 2.6662 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-11-14 | 41 | 21.3659 | 9.1424 | 30.5083 | 1.6191 | 0.76558 | 0.2268 | 2.6115 | 8.56% | 9.108% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-11-14 | 42 | 21.7863 | 9.0167 | 30.803 | 1.6505 | 0.76558 | 0.22899 | 2.6451 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-11-14 | 43 | 22.0229 | 9.2555 | 31.2785 | 1.7019 | 0.76558 | 0.23253 | 2.7 | 8.632% | 9.185% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-11-14 | 44 | 21.3874 | 9.2439 | 30.6313 | 1.6322 | 0.76558 | 0.22772 | 2.6255 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2010-11-14 | 45 | 20.4576 | 8.982 | 29.4396 | 1.5076 | 0.76558 | 0.21886 | 2.4921 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-14 | 46 | 19.2447 | 8.4073 | 27.652 | 1.3301 | 0.76558 | 0.20557 | 2.3013 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-11-14 | 47 | 18.3652 | 8.1709 | 26.5361 | 1.2249 | 0.76558 | 0.19727 | 2.1878 | 8.245% | 8.772% | 5.928% | 1.0899 | 1.0962 | 1.063
2010-11-14 | 48 | 17.4894 | 8.1959 | 25.6854 | 1.1476 | 0.76558 | 0.19095 | 2.1042 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-11-15 | 1 | 15.8442 | 7.3643 | 23.2085 | 0.93697 | 0.76558 | 0.17253 | 1.8751 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-11-15 | 2 | 14.8288 | 6.9116 | 21.7404 | 0.82218 | 0.76558 | 0.16162 | 1.7494 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-11-15 | 3 | 14.0695 | 6.5822 | 20.6518 | 0.74191 | 0.76558 | 0.15353 | 1.661 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-15 | 4 | 13.3761 | 6.3304 | 19.7066 | 0.67555 | 0.76558 | 0.1465 | 1.5876 | 8.056% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-15 | 5 | 12.9968 | 6.1477 | 19.1445 | 0.63757 | 0.76558 | 0.14232 | 1.5455 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-11-15 | 6 | 12.6979 | 6.3089 | 19.0068 | 0.62842 | 0.76558 | 0.1413 | 1.5353 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-11-15 | 7 | 12.598 | 6.1203 | 18.7182 | 0.60949 | 0.76558 | 0.13915 | 1.5142 | 8.09% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-11-15 | 8 | 12.6198 | 6.0593 | 18.679 | 0.60694 | 0.76558 | 0.13886 | 1.5114 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-11-15 | 9 | 12.543 | 5.9357 | 18.4787 | 0.59399 | 0.76558 | 0.13737 | 1.4969 | 8.101% | 8.619% | 5.825% | 1.0881 | 1.0943 | 1.0618
2010-11-15 | 10 | 12.7464 | 5.7411 | 18.4875 | 0.59456 | 0.76558 | 0.13744 | 1.4976 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-11-15 | 11 | 12.7455 | 5.7489 | 18.4944 | 0.59499 | 0.76558 | 0.13749 | 1.4981 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-11-15 | 12 | 13.0667 | 5.84 | 18.9067 | 0.62182 | 0.76558 | 0.14055 | 1.528 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-11-15 | 13 | 13.6888 | 6.14 | 19.8289 | 0.68396 | 0.76558 | 0.14741 | 1.5969 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-15 | 14 | 14.634 | 6.4516 | 21.0856 | 0.7734 | 0.76558 | 0.15675 | 1.6957 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-15 | 15 | 16.0606 | 6.901 | 22.9617 | 0.91715 | 0.76558 | 0.1707 | 1.8534 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-11-15 | 16 | 17.1944 | 7.69 | 24.8844 | 1.0772 | 0.76558 | 0.18499 | 2.0278 | 8.149% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-11-15 | 17 | 19.055 | 8.6001 | 27.6551 | 1.3304 | 0.76558 | 0.20559 | 2.3016 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-11-15 | 18 | 20.4547 | 9.2731 | 29.7279 | 1.5373 | 0.76558 | 0.221 | 2.5239 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2010-11-15 | 19 | 21.9387 | 9.8736 | 31.8123 | 1.7605 | 0.76558 | 0.2365 | 2.7625 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-11-15 | 20 | 22.511 | 10.3037 | 32.8147 | 1.8731 | 0.76558 | 0.24395 | 2.8827 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-11-15 | 21 | 22.9111 | 10.0535 | 32.9646 | 1.8903 | 0.76558 | 0.24506 | 2.9009 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-11-15 | 22 | 22.6227 | 9.9586 | 32.5813 | 1.8466 | 0.76558 | 0.24221 | 2.8544 | 8.761% | 9.322% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-11-15 | 23 | 22.1065 | 9.7471 | 31.8536 | 1.765 | 0.76558 | 0.2368 | 2.7674 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-11-15 | 24 | 21.6028 | 9.5865 | 31.1893 | 1.6922 | 0.76558 | 0.23187 | 2.6896 | 8.624% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-11-15 | 25 | 21.0759 | 9.6297 | 30.7056 | 1.6401 | 0.76558 | 0.22827 | 2.6339 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-11-15 | 26 | 20.6798 | 9.2932 | 29.973 | 1.5628 | 0.76558 | 0.22282 | 2.5512 | 8.512% | 9.056% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-11-15 | 27 | 20.2297 | 9.2623 | 29.4921 | 1.513 | 0.76558 | 0.21925 | 2.4978 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-11-15 | 28 | 20.1285 | 8.9332 | 29.0616 | 1.4692 | 0.76558 | 0.21605 | 2.4508 | 8.433% | 8.973% | 6.063% | 1.0921 | 1.0986 | 1.0645
2010-11-15 | 29 | 19.7292 | 8.6762 | 28.4054 | 1.4036 | 0.76558 | 0.21117 | 2.3803 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-11-15 | 30 | 19.374 | 8.6094 | 27.9834 | 1.3622 | 0.76558 | 0.20803 | 2.3358 | 8.347% | 8.881% | 6.002% | 1.0911 | 1.0975 | 1.0638
2010-11-15 | 31 | 19.6657 | 8.4933 | 28.159 | 1.3793 | 0.76558 | 0.20934 | 2.3543 | 8.361% | 8.896% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-11-15 | 32 | 19.6675 | 8.2544 | 27.9219 | 1.3562 | 0.76558 | 0.20757 | 2.3294 | 8.342% | 8.876% | 5.998% | 1.091 | 1.0974 | 1.0638
2010-11-15 | 33 | 20.0927 | 8.5295 | 28.6222 | 1.4251 | 0.76558 | 0.21278 | 2.4034 | 8.397% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2010-11-15 | 34 | 20.2379 | 8.6494 | 28.8873 | 1.4516 | 0.76558 | 0.21475 | 2.4319 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-11-15 | 35 | 20.691 | 9.1178 | 29.8088 | 1.5457 | 0.76558 | 0.2216 | 2.5329 | 8.497% | 9.041% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-11-15 | 36 | 21.2076 | 9.7929 | 31.0005 | 1.6718 | 0.76558 | 0.23046 | 2.6678 | 8.606% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2010-11-15 | 37 | 22.1223 | 10.2396 | 32.3619 | 1.8218 | 0.76558 | 0.24058 | 2.828 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-11-15 | 38 | 22.5415 | 10.2821 | 32.8236 | 1.8742 | 0.76558 | 0.24401 | 2.8837 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-11-15 | 39 | 22.9123 | 10.2657 | 33.178 | 1.9149 | 0.76558 | 0.24665 | 2.9271 | 8.822% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-11-15 | 40 | 23.229 | 10.1546 | 33.3836 | 1.9387 | 0.76558 | 0.24818 | 2.9524 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-11-15 | 41 | 23.4178 | 9.8685 | 33.2863 | 1.9274 | 0.76558 | 0.24745 | 2.9404 | 8.834% | 9.399% | 6.351% | 1.0969 | 1.1037 | 1.0678
2010-11-15 | 42 | 23.9372 | 9.7276 | 33.6648 | 1.9715 | 0.76558 | 0.25027 | 2.9873 | 8.874% | 9.442% | 6.38% | 1.0974 | 1.1043 | 1.0681
2010-11-15 | 43 | 24.2478 | 9.6304 | 33.8782 | 1.9965 | 0.76558 | 0.25185 | 3.014 | 8.896% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-11-15 | 44 | 23.845 | 9.2722 | 33.1172 | 1.9078 | 0.76558 | 0.2462 | 2.9196 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-11-15 | 45 | 22.3717 | 8.5984 | 30.9701 | 1.6685 | 0.76558 | 0.23024 | 2.6643 | 8.603% | 9.153% | 6.185% | 1.0941 | 1.1008 | 1.0659
2010-11-15 | 46 | 20.0358 | 7.8531 | 27.8889 | 1.353 | 0.76558 | 0.20733 | 2.3259 | 8.34% | 8.874% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-11-15 | 47 | 18.6431 | 7.4807 | 26.1238 | 1.1872 | 0.76558 | 0.19421 | 2.1469 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-11-15 | 48 | 17.6529 | 7.6006 | 25.2535 | 1.1094 | 0.76558 | 0.18774 | 2.0627 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2010-11-16 | 1 | 16.0175 | 6.7851 | 22.8026 | 0.90449 | 0.76558 | 0.16952 | 1.8396 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-11-16 | 2 | 15.0857 | 6.3375 | 21.4232 | 0.79837 | 0.76558 | 0.15926 | 1.7232 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-16 | 3 | 14.4279 | 6.0031 | 20.431 | 0.72613 | 0.76558 | 0.15189 | 1.6436 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-16 | 4 | 14.0936 | 5.951 | 20.0446 | 0.69892 | 0.76558 | 0.14901 | 1.6135 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-11-16 | 5 | 13.7377 | 6.1675 | 19.9052 | 0.68924 | 0.76558 | 0.14798 | 1.6028 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-11-16 | 6 | 13.2659 | 6.2773 | 19.5433 | 0.6644 | 0.76558 | 0.14529 | 1.5753 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-16 | 7 | 13.1764 | 6.3668 | 19.5433 | 0.6644 | 0.76558 | 0.14529 | 1.5753 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-16 | 8 | 13.1724 | 6.6233 | 19.7957 | 0.68167 | 0.76558 | 0.14716 | 1.5944 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-16 | 9 | 13.567 | 6.6019 | 20.1689 | 0.70762 | 0.76558 | 0.14994 | 1.6231 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-11-16 | 10 | 13.7252 | 6.6184 | 20.3436 | 0.71993 | 0.76558 | 0.15124 | 1.6367 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-16 | 11 | 14.1095 | 6.9012 | 21.0107 | 0.76792 | 0.76558 | 0.1562 | 1.6897 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-16 | 12 | 14.7621 | 7.3068 | 22.069 | 0.84722 | 0.76558 | 0.16406 | 1.7769 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-16 | 13 | 16.3023 | 7.9436 | 24.2459 | 1.0226 | 0.76558 | 0.18025 | 1.9684 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-11-16 | 14 | 18.8856 | 9.1783 | 28.0639 | 1.37 | 0.76558 | 0.20863 | 2.3442 | 8.353% | 8.888% | 6.006% | 1.0911 | 1.0975 | 1.0639
2010-11-16 | 15 | 22.5612 | 10.3741 | 32.9353 | 1.8869 | 0.76558 | 0.24485 | 2.8974 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-11-16 | 16 | 24.4202 | 10.5845 | 35.0048 | 2.1315 | 0.76558 | 0.26023 | 3.1573 | 9.02% | 9.597% | 6.485% | 1.0991 | 1.1062 | 1.0693
2010-11-16 | 17 | 24.5482 | 10.756 | 35.3041 | 2.1681 | 0.76558 | 0.26246 | 3.1962 | 9.053% | 9.633% | 6.509% | 1.0995 | 1.1066 | 1.0696
2010-11-16 | 18 | 23.0441 | 10.288 | 33.3321 | 1.9327 | 0.76558 | 0.24779 | 2.946 | 8.838% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-11-16 | 19 | 22.9799 | 10.6691 | 33.649 | 1.9696 | 0.76558 | 0.25015 | 2.9853 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-11-16 | 20 | 21.6865 | 10.112 | 31.7985 | 1.7589 | 0.76558 | 0.23639 | 2.7609 | 8.682% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-11-16 | 21 | 22.4652 | 10.4199 | 32.8851 | 1.8812 | 0.76558 | 0.24447 | 2.8912 | 8.792% | 9.355% | 6.321% | 1.0964 | 1.1032 | 1.0675
2010-11-16 | 22 | 27.0149 | 12.7068 | 39.7217 | 2.7447 | 0.76558 | 0.2953 | 3.8055 | 9.581% | 10.19% | 6.888% | 1.106 | 1.1135 | 1.074
2010-11-16 | 23 | 24.8151 | 11.7626 | 36.5777 | 2.3274 | 0.76558 | 0.27192 | 3.3649 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-11-16 | 24 | 24.9741 | 12.5353 | 37.5094 | 2.4475 | 0.76558 | 0.27885 | 3.4919 | 9.309% | 9.905% | 6.693% | 1.1026 | 1.1099 | 1.0717
2010-11-16 | 25 | 23.9093 | 11.8367 | 35.7461 | 2.2228 | 0.76558 | 0.26574 | 3.2541 | 9.103% | 9.686% | 6.545% | 1.1001 | 1.1072 | 1.07
2010-11-16 | 26 | 22.67 | 11.2017 | 33.8717 | 1.9958 | 0.76558 | 0.25181 | 3.0131 | 8.896% | 9.465% | 6.396% | 1.0976 | 1.1045 | 1.0683
2010-11-16 | 27 | 22.1969 | 11.0982 | 33.2951 | 1.9284 | 0.76558 | 0.24752 | 2.9415 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-11-16 | 28 | 21.6885 | 10.8949 | 32.5834 | 1.8468 | 0.76558 | 0.24223 | 2.8546 | 8.761% | 9.322% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-11-16 | 29 | 21.2678 | 10.2785 | 31.5464 | 1.7311 | 0.76558 | 0.23452 | 2.7312 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-11-16 | 30 | 20.6132 | 9.8347 | 30.4479 | 1.6127 | 0.76558 | 0.22635 | 2.6046 | 8.554% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2010-11-16 | 31 | 20.777 | 9.8585 | 30.6356 | 1.6326 | 0.76558 | 0.22775 | 2.626 | 8.572% | 9.12% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-11-16 | 32 | 20.6702 | 9.8366 | 30.5068 | 1.6189 | 0.76558 | 0.22679 | 2.6113 | 8.56% | 9.108% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-11-16 | 33 | 21.043 | 10.0527 | 31.0957 | 1.682 | 0.76558 | 0.23117 | 2.6788 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-11-16 | 34 | 21.3128 | 10.1534 | 31.4662 | 1.7224 | 0.76558 | 0.23392 | 2.7219 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-11-16 | 35 | 21.966 | 10.6914 | 32.6574 | 1.8552 | 0.76558 | 0.24278 | 2.8636 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-11-16 | 36 | 23.0608 | 11.3319 | 34.3926 | 2.0576 | 0.76558 | 0.25568 | 3.0789 | 8.952% | 9.525% | 6.437% | 1.0983 | 1.1053 | 1.0688
2010-11-16 | 37 | 24.3391 | 11.6205 | 35.9596 | 2.2494 | 0.76558 | 0.26733 | 3.2823 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2010-11-16 | 38 | 25.0455 | 11.2904 | 36.3359 | 2.2967 | 0.76558 | 0.27013 | 3.3324 | 9.171% | 9.758% | 6.594% | 1.101 | 1.1081 | 1.0706
2010-11-16 | 39 | 25.319 | 10.7591 | 36.0782 | 2.2642 | 0.76558 | 0.26821 | 3.298 | 9.141% | 9.726% | 6.573% | 1.1006 | 1.1077 | 1.0704
2010-11-16 | 40 | 25.3656 | 10.4526 | 35.8182 | 2.2317 | 0.76558 | 0.26628 | 3.2636 | 9.112% | 9.695% | 6.551% | 1.1002 | 1.1074 | 1.0701
2010-11-16 | 41 | 25.6306 | 10.5016 | 36.1322 | 2.271 | 0.76558 | 0.26861 | 3.3052 | 9.148% | 9.733% | 6.577% | 1.1007 | 1.1078 | 1.0704
2010-11-16 | 42 | 26.0966 | 10.4807 | 36.5773 | 2.3273 | 0.76558 | 0.27192 | 3.3648 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2010-11-16 | 43 | 25.9528 | 10.5575 | 36.5102 | 2.3188 | 0.76558 | 0.27142 | 3.3558 | 9.191% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2010-11-16 | 44 | 25.3026 | 10.3598 | 35.6624 | 2.2124 | 0.76558 | 0.26512 | 3.2431 | 9.094% | 9.676% | 6.538% | 1.1 | 1.1071 | 1.07
2010-11-16 | 45 | 23.4867 | 9.6302 | 33.1169 | 1.9078 | 0.76558 | 0.2462 | 2.9196 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-11-16 | 46 | 21.5429 | 8.7727 | 30.3156 | 1.5987 | 0.76558 | 0.22537 | 2.5897 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-11-16 | 47 | 19.9235 | 8.3147 | 28.2381 | 1.3871 | 0.76558 | 0.20993 | 2.3626 | 8.367% | 8.902% | 6.016% | 1.0913 | 1.0977 | 1.064
2010-11-16 | 48 | 18.8458 | 8.2147 | 27.0605 | 1.2738 | 0.76558 | 0.20117 | 2.2406 | 8.28% | 8.81% | 5.953% | 1.0903 | 1.0966 | 1.0633
2010-11-17 | 1 | 17.0953 | 7.4923 | 24.5876 | 1.0516 | 0.76558 | 0.18279 | 2 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-17 | 2 | 16.0735 | 6.9567 | 23.0302 | 0.92264 | 0.76558 | 0.17121 | 1.8594 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-11-17 | 3 | 15.47 | 6.9009 | 22.3709 | 0.87057 | 0.76558 | 0.16631 | 1.8025 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-17 | 4 | 14.9744 | 7.0918 | 22.0662 | 0.84701 | 0.76558 | 0.16404 | 1.7766 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-17 | 5 | 14.4732 | 6.9025 | 21.3756 | 0.79483 | 0.76558 | 0.15891 | 1.7193 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-17 | 6 | 14.0092 | 7.1543 | 21.1635 | 0.77913 | 0.76558 | 0.15733 | 1.702 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-17 | 7 | 13.5613 | 7.6616 | 21.2229 | 0.78351 | 0.76558 | 0.15777 | 1.7069 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-17 | 8 | 13.456 | 8.6008 | 22.0569 | 0.8463 | 0.76558 | 0.16397 | 1.7758 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-17 | 9 | 13.8639 | 9.5498 | 23.4138 | 0.95362 | 0.76558 | 0.17406 | 1.8933 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-11-17 | 10 | 14.1438 | 10.0055 | 24.1493 | 1.0145 | 0.76558 | 0.17953 | 1.9596 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-11-17 | 11 | 14.7931 | 10.3139 | 25.107 | 1.0965 | 0.76558 | 0.18665 | 2.0488 | 8.16% | 8.682% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-11-17 | 12 | 15.6052 | 10.9736 | 26.5788 | 1.2289 | 0.76558 | 0.19759 | 2.192 | 8.247% | 8.775% | 5.93% | 1.0899 | 1.0962 | 1.063
2010-11-17 | 13 | 17.3631 | 11.7934 | 29.1564 | 1.4788 | 0.76558 | 0.21675 | 2.4611 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-11-17 | 14 | 19.903 | 12.6277 | 32.5307 | 1.8409 | 0.76558 | 0.24184 | 2.8483 | 8.756% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-17 | 15 | 23.4333 | 13.0474 | 36.4807 | 2.3151 | 0.76558 | 0.2712 | 3.3518 | 9.188% | 9.776% | 6.606% | 1.1012 | 1.1084 | 1.0707
2010-11-17 | 16 | 24.6844 | 12.1758 | 36.8602 | 2.3635 | 0.76558 | 0.27402 | 3.4031 | 9.232% | 9.823% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-11-17 | 17 | 24.3244 | 11.0799 | 35.4043 | 2.1805 | 0.76558 | 0.2632 | 3.2092 | 9.065% | 9.645% | 6.517% | 1.0997 | 1.1067 | 1.0697
2010-11-17 | 18 | 23.411 | 11.0541 | 34.4651 | 2.0663 | 0.76558 | 0.25622 | 3.0881 | 8.96% | 9.534% | 6.442% | 1.0984 | 1.1054 | 1.0689
2010-11-17 | 19 | 24.8295 | 11.4141 | 36.2437 | 2.2851 | 0.76558 | 0.26944 | 3.3201 | 9.16% | 9.747% | 6.586% | 1.1008 | 1.108 | 1.0705
2010-11-17 | 20 | 25.8298 | 12.2 | 38.0298 | 2.5158 | 0.76558 | 0.28272 | 3.5641 | 9.372% | 9.972% | 6.738% | 1.1034 | 1.1108 | 1.0723
2010-11-17 | 21 | 24.998 | 11.2768 | 36.2749 | 2.289 | 0.76558 | 0.26967 | 3.3243 | 9.164% | 9.751% | 6.589% | 1.1009 | 1.108 | 1.0705
2010-11-17 | 22 | 23.294 | 10.7899 | 34.084 | 2.0209 | 0.76558 | 0.25338 | 3.0398 | 8.919% | 9.489% | 6.412% | 1.0979 | 1.1048 | 1.0685
2010-11-17 | 23 | 21.9919 | 10.1615 | 32.1534 | 1.7984 | 0.76558 | 0.23903 | 2.803 | 8.718% | 9.276% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-11-17 | 24 | 23.032 | 10.4714 | 33.5034 | 1.9526 | 0.76558 | 0.24907 | 2.9672 | 8.857% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2010-11-17 | 25 | 22.1345 | 10.172 | 32.3065 | 1.8156 | 0.76558 | 0.24017 | 2.8213 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-11-17 | 26 | 21.2976 | 9.8323 | 31.1299 | 1.6857 | 0.76558 | 0.23142 | 2.6827 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.101 | 1.0661
2010-11-17 | 27 | 21.0666 | 9.9527 | 31.0194 | 1.6738 | 0.76558 | 0.2306 | 2.67 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-11-17 | 28 | 20.7908 | 10.0904 | 30.8812 | 1.6589 | 0.76558 | 0.22957 | 2.6541 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-11-17 | 29 | 20.3723 | 9.6604 | 30.0327 | 1.569 | 0.76558 | 0.22327 | 2.5578 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0996 | 1.0652
2010-11-17 | 30 | 19.9813 | 9.6397 | 29.621 | 1.5263 | 0.76558 | 0.22021 | 2.5121 | 8.481% | 9.023% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-11-17 | 31 | 19.942 | 9.5345 | 29.4765 | 1.5114 | 0.76558 | 0.21913 | 2.4961 | 8.468% | 9.01% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-11-17 | 32 | 19.8855 | 9.6873 | 29.5728 | 1.5213 | 0.76558 | 0.21985 | 2.5067 | 8.477% | 9.019% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-11-17 | 33 | 20.2541 | 10.0467 | 30.3008 | 1.5971 | 0.76558 | 0.22526 | 2.588 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-11-17 | 34 | 20.2846 | 9.9183 | 30.2029 | 1.5868 | 0.76558 | 0.22453 | 2.5769 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2010-11-17 | 35 | 20.4789 | 10.3907 | 30.8696 | 1.6577 | 0.76558 | 0.22949 | 2.6527 | 8.593% | 9.143% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-11-17 | 36 | 21.1589 | 10.9876 | 32.1465 | 1.7976 | 0.76558 | 0.23898 | 2.8022 | 8.717% | 9.275% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-11-17 | 37 | 22.0143 | 11.2052 | 33.2195 | 1.9196 | 0.76558 | 0.24696 | 2.9322 | 8.827% | 9.392% | 6.346% | 1.0968 | 1.1037 | 1.0678
2010-11-17 | 38 | 22.9691 | 11.1234 | 34.0924 | 2.0219 | 0.76558 | 0.25345 | 3.0409 | 8.92% | 9.49% | 6.413% | 1.0979 | 1.1049 | 1.0685
2010-11-17 | 39 | 23.2465 | 10.764 | 34.0105 | 2.0121 | 0.76558 | 0.25284 | 3.0306 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2010-11-17 | 40 | 23.4217 | 10.5047 | 33.9263 | 2.0022 | 0.76558 | 0.25221 | 3.02 | 8.902% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-17 | 41 | 23.4873 | 10.5828 | 34.0701 | 2.0192 | 0.76558 | 0.25328 | 3.0381 | 8.917% | 9.488% | 6.411% | 1.0979 | 1.1048 | 1.0685
2010-11-17 | 42 | 23.9171 | 10.5848 | 34.5019 | 2.0707 | 0.76558 | 0.25649 | 3.0928 | 8.964% | 9.538% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-11-17 | 43 | 24.3143 | 10.3411 | 34.6554 | 2.0892 | 0.76558 | 0.25763 | 3.1124 | 8.981% | 9.556% | 6.457% | 1.0987 | 1.1057 | 1.069
2010-11-17 | 44 | 24.4453 | 10.1877 | 34.6329 | 2.0865 | 0.76558 | 0.25747 | 3.1095 | 8.979% | 9.553% | 6.456% | 1.0986 | 1.1056 | 1.069
2010-11-17 | 45 | 23.0591 | 9.3589 | 32.418 | 1.8281 | 0.76558 | 0.241 | 2.8347 | 8.744% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-11-17 | 46 | 20.9607 | 8.4672 | 29.4279 | 1.5064 | 0.76558 | 0.21877 | 2.4908 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2010-11-17 | 47 | 19.4403 | 8.111 | 27.5513 | 1.3204 | 0.76558 | 0.20482 | 2.2908 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2010-11-17 | 48 | 18.3868 | 7.881 | 26.2678 | 1.2003 | 0.76558 | 0.19528 | 2.1611 | 8.227% | 8.754% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-11-18 | 1 | 16.8132 | 7.079 | 23.8922 | 0.99299 | 0.76558 | 0.17762 | 1.9362 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-11-18 | 2 | 15.6152 | 6.6247 | 22.24 | 0.86041 | 0.76558 | 0.16533 | 1.7913 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-18 | 3 | 14.9263 | 6.3625 | 21.2889 | 0.78839 | 0.76558 | 0.15826 | 1.7122 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-18 | 4 | 14.2443 | 6.2766 | 20.521 | 0.73254 | 0.76558 | 0.15256 | 1.6507 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-18 | 5 | 13.9386 | 6.1129 | 20.0515 | 0.69941 | 0.76558 | 0.14907 | 1.614 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-11-18 | 6 | 13.9672 | 6.0553 | 20.0225 | 0.69739 | 0.76558 | 0.14885 | 1.6118 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-11-18 | 7 | 13.8733 | 6.1002 | 19.9735 | 0.69398 | 0.76558 | 0.14849 | 1.608 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-18 | 8 | 13.8156 | 5.9635 | 19.779 | 0.68053 | 0.76558 | 0.14704 | 1.5931 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-18 | 9 | 14.0822 | 6.0586 | 20.1408 | 0.70565 | 0.76558 | 0.14973 | 1.621 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-18 | 10 | 14.2604 | 5.9952 | 20.2556 | 0.71372 | 0.76558 | 0.15058 | 1.6299 | 8.047% | 8.562% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-18 | 11 | 14.8506 | 6.3064 | 21.157 | 0.77865 | 0.76558 | 0.15728 | 1.7015 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-18 | 12 | 15.487 | 6.7626 | 22.2496 | 0.86115 | 0.76558 | 0.16541 | 1.7921 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-18 | 13 | 17.1846 | 7.5114 | 24.6961 | 1.0609 | 0.76558 | 0.18359 | 2.0101 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2010-11-18 | 14 | 19.7809 | 8.8079 | 28.5887 | 1.4218 | 0.76558 | 0.21253 | 2.3999 | 8.394% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-11-18 | 15 | 22.9605 | 10.2538 | 33.2143 | 1.919 | 0.76558 | 0.24692 | 2.9315 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-11-18 | 16 | 23.9384 | 10.5883 | 34.5267 | 2.0737 | 0.76558 | 0.25668 | 3.096 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-11-18 | 17 | 25.6044 | 11.4833 | 37.0877 | 2.3927 | 0.76558 | 0.27571 | 3.434 | 9.259% | 9.852% | 6.657% | 1.102 | 1.1093 | 1.0713
2010-11-18 | 18 | 25.6479 | 11.8014 | 37.4493 | 2.4396 | 0.76558 | 0.2784 | 3.4836 | 9.302% | 9.898% | 6.688% | 1.1026 | 1.1098 | 1.0717
2010-11-18 | 19 | 25.1801 | 11.4593 | 36.6395 | 2.3352 | 0.76558 | 0.27238 | 3.3732 | 9.206% | 9.796% | 6.619% | 1.1014 | 1.1086 | 1.0709
2010-11-18 | 20 | 24.3384 | 11.1602 | 35.4986 | 2.1921 | 0.76558 | 0.2639 | 3.2216 | 9.075% | 9.656% | 6.525% | 1.0998 | 1.1069 | 1.0698
2010-11-18 | 21 | 23.816 | 10.8245 | 34.6406 | 2.0874 | 0.76558 | 0.25752 | 3.1105 | 8.979% | 9.554% | 6.456% | 1.0987 | 1.1056 | 1.069
2010-11-18 | 22 | 23.2213 | 10.7984 | 34.0197 | 2.0132 | 0.76558 | 0.25291 | 3.0317 | 8.912% | 9.482% | 6.407% | 1.0978 | 1.1048 | 1.0685
2010-11-18 | 23 | 22.2362 | 10.6101 | 32.8463 | 1.8768 | 0.76558 | 0.24418 | 2.8865 | 8.788% | 9.35% | 6.319% | 1.0963 | 1.1031 | 1.0674
2010-11-18 | 24 | 21.685 | 10.5115 | 32.1965 | 1.8032 | 0.76558 | 0.23935 | 2.8082 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-11-18 | 25 | 21.2405 | 10.4646 | 31.7051 | 1.7486 | 0.76558 | 0.2357 | 2.7499 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-11-18 | 26 | 20.5286 | 9.911 | 30.4397 | 1.6118 | 0.76558 | 0.22629 | 2.6037 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-11-18 | 27 | 20.4281 | 9.899 | 30.3271 | 1.5999 | 0.76558 | 0.22546 | 2.5909 | 8.543% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-11-18 | 28 | 20.2458 | 9.8572 | 30.103 | 1.5764 | 0.76558 | 0.22379 | 2.5657 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-11-18 | 29 | 19.9572 | 9.539 | 29.4962 | 1.5134 | 0.76558 | 0.21928 | 2.4983 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-11-18 | 30 | 19.55 | 9.3475 | 28.8976 | 1.4526 | 0.76558 | 0.21483 | 2.433 | 8.42% | 8.958% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-11-18 | 31 | 19.6134 | 9.2862 | 28.8997 | 1.4528 | 0.76558 | 0.21484 | 2.4333 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-11-18 | 32 | 19.4304 | 9.3322 | 28.7626 | 1.4391 | 0.76558 | 0.21382 | 2.4185 | 8.408% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0643
2010-11-18 | 33 | 19.5557 | 9.6585 | 29.2142 | 1.4846 | 0.76558 | 0.21718 | 2.4674 | 8.446% | 8.986% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-11-18 | 34 | 19.9568 | 9.8524 | 29.8092 | 1.5457 | 0.76558 | 0.22161 | 2.5329 | 8.497% | 9.041% | 6.109% | 1.0929 | 1.0994 | 1.0651
2010-11-18 | 35 | 20.4738 | 10.5634 | 31.0372 | 1.6757 | 0.76558 | 0.23073 | 2.672 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2010-11-18 | 36 | 21.132 | 11.087 | 32.219 | 1.8058 | 0.76558 | 0.23952 | 2.8109 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-11-18 | 37 | 21.58 | 11.0275 | 32.6075 | 1.8496 | 0.76558 | 0.24241 | 2.8576 | 8.763% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-11-18 | 38 | 22.0392 | 11.0692 | 33.1084 | 1.9068 | 0.76558 | 0.24613 | 2.9185 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-11-18 | 39 | 22.5849 | 11.2193 | 33.8042 | 1.9878 | 0.76558 | 0.2513 | 3.0047 | 8.889% | 9.457% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-11-18 | 40 | 22.4957 | 10.8589 | 33.3547 | 1.9353 | 0.76558 | 0.24796 | 2.9488 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-11-18 | 41 | 22.8745 | 10.629 | 33.5035 | 1.9526 | 0.76558 | 0.24907 | 2.9673 | 8.857% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2010-11-18 | 42 | 23.1837 | 10.5543 | 33.738 | 1.98 | 0.76558 | 0.25081 | 2.9964 | 8.881% | 9.45% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-11-18 | 43 | 23.3712 | 10.472 | 33.8432 | 1.9924 | 0.76558 | 0.25159 | 3.0096 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2010-11-18 | 44 | 23.1648 | 10.3877 | 33.5525 | 1.9583 | 0.76558 | 0.24943 | 2.9733 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-11-18 | 45 | 21.9851 | 9.6995 | 31.6846 | 1.7463 | 0.76558 | 0.23555 | 2.7475 | 8.671% | 9.226% | 6.235% | 1.0949 | 1.1016 | 1.0665
2010-11-18 | 46 | 20.2496 | 8.6782 | 28.9277 | 1.4557 | 0.76558 | 0.21505 | 2.4363 | 8.422% | 8.961% | 6.055% | 1.092 | 1.0984 | 1.0645
2010-11-18 | 47 | 18.7802 | 8.1041 | 26.8843 | 1.2573 | 0.76558 | 0.19986 | 2.2227 | 8.268% | 8.797% | 5.944% | 1.0901 | 1.0965 | 1.0632
2010-11-18 | 48 | 17.4098 | 8.136 | 25.5458 | 1.1352 | 0.76558 | 0.18991 | 2.0907 | 8.184% | 8.708% | 5.884% | 1.0891 | 1.0954 | 1.0625
2010-11-19 | 1 | 15.737 | 7.3185 | 23.0555 | 0.92466 | 0.76558 | 0.1714 | 1.8616 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-11-19 | 2 | 14.4109 | 6.9912 | 21.4021 | 0.7968 | 0.76558 | 0.15911 | 1.7215 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-19 | 3 | 13.6312 | 6.6229 | 20.2541 | 0.71361 | 0.76558 | 0.15057 | 1.6298 | 8.047% | 8.562% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-19 | 4 | 13.2677 | 6.48 | 19.7478 | 0.67838 | 0.76558 | 0.14681 | 1.5908 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-11-19 | 5 | 13.0038 | 6.2 | 19.2038 | 0.64152 | 0.76558 | 0.14276 | 1.5499 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-19 | 6 | 12.8539 | 6.0202 | 18.8741 | 0.61968 | 0.76558 | 0.14031 | 1.5256 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-11-19 | 7 | 12.3422 | 6.0059 | 18.3482 | 0.58563 | 0.76558 | 0.1364 | 1.4876 | 8.108% | 8.627% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-11-19 | 8 | 12.1589 | 5.9766 | 18.1355 | 0.57213 | 0.76558 | 0.13482 | 1.4725 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-11-19 | 9 | 12.3201 | 6.2346 | 18.5547 | 0.59888 | 0.76558 | 0.13794 | 1.5024 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-11-19 | 10 | 12.6198 | 6.3912 | 19.011 | 0.6287 | 0.76558 | 0.14133 | 1.5356 | 8.077% | 8.594% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-11-19 | 11 | 13.0462 | 6.6819 | 19.7281 | 0.67703 | 0.76558 | 0.14666 | 1.5893 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-11-19 | 12 | 13.7054 | 6.9152 | 20.6206 | 0.73967 | 0.76558 | 0.1533 | 1.6585 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-19 | 13 | 15.1116 | 7.4767 | 22.5883 | 0.88757 | 0.76558 | 0.16792 | 1.8211 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-19 | 14 | 17.4842 | 8.7473 | 26.2315 | 1.197 | 0.76558 | 0.19501 | 2.1576 | 8.225% | 8.751% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-11-19 | 15 | 20.8906 | 10.3143 | 31.2049 | 1.6939 | 0.76558 | 0.23198 | 2.6914 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-11-19 | 16 | 23.1388 | 11.1751 | 34.3139 | 2.0482 | 0.76558 | 0.25509 | 3.0689 | 8.944% | 9.516% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-11-19 | 17 | 24.2355 | 11.6939 | 35.9294 | 2.2456 | 0.76558 | 0.2671 | 3.2783 | 9.124% | 9.708% | 6.56% | 1.1004 | 1.1075 | 1.0702
2010-11-19 | 18 | 24.3037 | 11.7405 | 36.0442 | 2.26 | 0.76558 | 0.26796 | 3.2935 | 9.137% | 9.722% | 6.57% | 1.1006 | 1.1077 | 1.0703
2010-11-19 | 19 | 23.9703 | 11.383 | 35.3532 | 2.1742 | 0.76558 | 0.26282 | 3.2026 | 9.059% | 9.639% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-11-19 | 20 | 23.1098 | 10.879 | 33.9888 | 2.0096 | 0.76558 | 0.25268 | 3.0278 | 8.908% | 9.478% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-11-19 | 21 | 22.8387 | 10.4574 | 33.2961 | 1.9285 | 0.76558 | 0.24753 | 2.9416 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-11-19 | 22 | 22.2543 | 10.4608 | 32.7151 | 1.8618 | 0.76558 | 0.24321 | 2.8706 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-11-19 | 23 | 21.683 | 10.3931 | 32.0761 | 1.7898 | 0.76558 | 0.23846 | 2.7938 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-11-19 | 24 | 21.1131 | 10.4186 | 31.5317 | 1.7295 | 0.76558 | 0.23441 | 2.7295 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2010-11-19 | 25 | 20.6478 | 10.2819 | 30.9298 | 1.6641 | 0.76558 | 0.22994 | 2.6596 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-11-19 | 26 | 20.2031 | 9.8974 | 30.1005 | 1.5761 | 0.76558 | 0.22377 | 2.5654 | 8.523% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-11-19 | 27 | 19.8938 | 10.0925 | 29.9863 | 1.5642 | 0.76558 | 0.22292 | 2.5527 | 8.513% | 9.058% | 6.121% | 1.093 | 1.0996 | 1.0652
2010-11-19 | 28 | 19.9748 | 10.2699 | 30.2447 | 1.5912 | 0.76558 | 0.22484 | 2.5817 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-11-19 | 29 | 19.9103 | 10.0917 | 30.002 | 1.5658 | 0.76558 | 0.22304 | 2.5544 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-11-19 | 30 | 19.7049 | 9.8508 | 29.5557 | 1.5196 | 0.76558 | 0.21972 | 2.5049 | 8.475% | 9.017% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-11-19 | 31 | 19.6436 | 9.819 | 29.4626 | 1.51 | 0.76558 | 0.21903 | 2.4946 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2010-11-19 | 32 | 19.5366 | 10.0042 | 29.5408 | 1.518 | 0.76558 | 0.21961 | 2.5032 | 8.474% | 9.016% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-11-19 | 33 | 19.6833 | 10.2434 | 29.9267 | 1.5579 | 0.76558 | 0.22248 | 2.546 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-11-19 | 34 | 20.1034 | 10.3043 | 30.4076 | 1.6084 | 0.76558 | 0.22605 | 2.6001 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-11-19 | 35 | 20.4457 | 10.6175 | 31.0632 | 1.6785 | 0.76558 | 0.23093 | 2.675 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-11-19 | 36 | 21.3845 | 10.8763 | 32.2608 | 1.8104 | 0.76558 | 0.23983 | 2.8159 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-11-19 | 37 | 22.8803 | 11.2051 | 34.0854 | 2.021 | 0.76558 | 0.2534 | 3.04 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1048 | 1.0685
2010-11-19 | 38 | 23.8231 | 11.2754 | 35.0985 | 2.143 | 0.76558 | 0.26093 | 3.1695 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-11-19 | 39 | 24.2167 | 11.2471 | 35.4638 | 2.1878 | 0.76558 | 0.26364 | 3.217 | 9.071% | 9.652% | 6.522% | 1.0998 | 1.1068 | 1.0698
2010-11-19 | 40 | 23.9775 | 11.0059 | 34.9835 | 2.1289 | 0.76558 | 0.26007 | 3.1546 | 9.017% | 9.594% | 6.483% | 1.0991 | 1.1061 | 1.0693
2010-11-19 | 41 | 23.7249 | 10.8755 | 34.6005 | 2.0826 | 0.76558 | 0.25722 | 3.1054 | 8.975% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-11-19 | 42 | 23.4646 | 10.8838 | 34.3484 | 2.0523 | 0.76558 | 0.25535 | 3.0733 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-11-19 | 43 | 23.2625 | 10.6335 | 33.8961 | 1.9986 | 0.76558 | 0.25199 | 3.0162 | 8.898% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2010-11-19 | 44 | 22.7736 | 10.2599 | 33.0335 | 1.8982 | 0.76558 | 0.24557 | 2.9094 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-11-19 | 45 | 21.4012 | 9.5093 | 30.9105 | 1.6621 | 0.76558 | 0.22979 | 2.6574 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-11-19 | 46 | 19.5064 | 8.518 | 28.0244 | 1.3662 | 0.76558 | 0.20834 | 2.3401 | 8.35% | 8.885% | 6.004% | 1.0911 | 1.0975 | 1.0639
2010-11-19 | 47 | 18.2245 | 7.999 | 26.2235 | 1.1962 | 0.76558 | 0.19495 | 2.1568 | 8.225% | 8.751% | 5.913% | 1.0896 | 1.0959 | 1.0629
2010-11-19 | 48 | 16.9834 | 8.0085 | 24.9919 | 1.0865 | 0.76558 | 0.18579 | 2.0379 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-11-20 | 1 | 15.39 | 7.2914 | 22.6814 | 0.8949 | 0.76558 | 0.16862 | 1.8291 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-11-20 | 2 | 14.2346 | 6.6628 | 20.8974 | 0.75966 | 0.76558 | 0.15535 | 1.6806 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-20 | 3 | 13.4814 | 6.4127 | 19.8941 | 0.68846 | 0.76558 | 0.14789 | 1.6019 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-20 | 4 | 13.0217 | 6.2608 | 19.2825 | 0.64679 | 0.76558 | 0.14335 | 1.5557 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-11-20 | 5 | 12.6269 | 6.1744 | 18.8013 | 0.61491 | 0.76558 | 0.13977 | 1.5203 | 8.086% | 8.603% | 5.814% | 1.088 | 1.0941 | 1.0617
2010-11-20 | 6 | 12.4884 | 6.0585 | 18.5469 | 0.59838 | 0.76558 | 0.13788 | 1.5018 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-11-20 | 7 | 12.353 | 6.1242 | 18.4772 | 0.59389 | 0.76558 | 0.13736 | 1.4968 | 8.101% | 8.619% | 5.825% | 1.0882 | 1.0943 | 1.0618
2010-11-20 | 8 | 12.0218 | 6.2836 | 18.3055 | 0.5829 | 0.76558 | 0.13609 | 1.4846 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-11-20 | 9 | 11.9831 | 6.4788 | 18.4619 | 0.59291 | 0.76558 | 0.13725 | 1.4957 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-11-20 | 10 | 12.1964 | 6.3426 | 18.539 | 0.59787 | 0.76558 | 0.13782 | 1.5013 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-11-20 | 11 | 12.4624 | 6.4763 | 18.9387 | 0.62393 | 0.76558 | 0.14079 | 1.5303 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-11-20 | 12 | 12.954 | 6.577 | 19.531 | 0.66356 | 0.76558 | 0.1452 | 1.5743 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-11-20 | 13 | 14.1015 | 7.178 | 21.2795 | 0.78769 | 0.76558 | 0.15819 | 1.7115 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-20 | 14 | 16.6294 | 8.742 | 25.3714 | 1.1198 | 0.76558 | 0.18861 | 2.074 | 8.174% | 8.698% | 5.877% | 1.089 | 1.0953 | 1.0624
2010-11-20 | 15 | 19.9571 | 9.9121 | 29.8692 | 1.552 | 0.76558 | 0.22205 | 2.5396 | 8.502% | 9.047% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-11-20 | 16 | 22.1889 | 10.7954 | 32.9843 | 1.8926 | 0.76558 | 0.24521 | 2.9033 | 8.802% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2010-11-20 | 17 | 23.3017 | 11.1977 | 34.4994 | 2.0704 | 0.76558 | 0.25647 | 3.0925 | 8.964% | 9.538% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-11-20 | 18 | 23.5549 | 11.3023 | 34.8572 | 2.1136 | 0.76558 | 0.25913 | 3.1383 | 9.003% | 9.58% | 6.473% | 1.0989 | 1.1059 | 1.0692
2010-11-20 | 19 | 23.352 | 11.1925 | 34.5445 | 2.0758 | 0.76558 | 0.25681 | 3.0982 | 8.969% | 9.543% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-11-20 | 20 | 22.8167 | 11.048 | 33.8647 | 1.9949 | 0.76558 | 0.25175 | 3.0123 | 8.895% | 9.464% | 6.396% | 1.0976 | 1.1045 | 1.0683
2010-11-20 | 21 | 22.4419 | 10.6991 | 33.141 | 1.9106 | 0.76558 | 0.24637 | 2.9225 | 8.818% | 9.383% | 6.34% | 1.0967 | 1.1035 | 1.0677
2010-11-20 | 22 | 22.0452 | 10.5592 | 32.6044 | 1.8492 | 0.76558 | 0.24239 | 2.8572 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-11-20 | 23 | 21.6972 | 10.309 | 32.0062 | 1.782 | 0.76558 | 0.23794 | 2.7855 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0668
2010-11-20 | 24 | 21.2844 | 10.2922 | 31.5766 | 1.7345 | 0.76558 | 0.23474 | 2.7348 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-11-20 | 25 | 21.0673 | 10.4174 | 31.4847 | 1.7244 | 0.76558 | 0.23406 | 2.724 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-11-20 | 26 | 20.6529 | 10.2603 | 30.9132 | 1.6624 | 0.76558 | 0.22981 | 2.6577 | 8.597% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-11-20 | 27 | 20.4084 | 10.2357 | 30.6441 | 1.6335 | 0.76558 | 0.22781 | 2.6269 | 8.572% | 9.121% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-11-20 | 28 | 20.5831 | 10.0426 | 30.6257 | 1.6316 | 0.76558 | 0.22768 | 2.6248 | 8.571% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2010-11-20 | 29 | 20.2005 | 9.7985 | 29.999 | 1.5655 | 0.76558 | 0.22302 | 2.5541 | 8.514% | 9.059% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-11-20 | 30 | 19.8823 | 9.6772 | 29.5595 | 1.52 | 0.76558 | 0.21975 | 2.5053 | 8.475% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-11-20 | 31 | 19.7613 | 9.7192 | 29.4805 | 1.5118 | 0.76558 | 0.21916 | 2.4966 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-11-20 | 32 | 20.0194 | 9.9012 | 29.9206 | 1.5573 | 0.76558 | 0.22243 | 2.5453 | 8.507% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-11-20 | 33 | 20.1322 | 10.19 | 30.3222 | 1.5994 | 0.76558 | 0.22542 | 2.5904 | 8.543% | 9.09% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-11-20 | 34 | 20.4378 | 10.106 | 30.5438 | 1.6229 | 0.76558 | 0.22707 | 2.6155 | 8.563% | 9.111% | 6.157% | 1.0937 | 1.1002 | 1.0656
2010-11-20 | 35 | 20.0884 | 10.309 | 30.3974 | 1.6073 | 0.76558 | 0.22598 | 2.5989 | 8.55% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2010-11-20 | 36 | 20.1221 | 10.6027 | 30.7248 | 1.6422 | 0.76558 | 0.22841 | 2.6361 | 8.58% | 9.129% | 6.169% | 1.0939 | 1.1005 | 1.0657
2010-11-20 | 37 | 20.5334 | 10.7702 | 31.3037 | 1.7046 | 0.76558 | 0.23272 | 2.7029 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-11-20 | 38 | 20.9158 | 10.5983 | 31.5141 | 1.7276 | 0.76558 | 0.23428 | 2.7275 | 8.655% | 9.209% | 6.223% | 1.0947 | 1.1014 | 1.0664
2010-11-20 | 39 | 20.8486 | 10.5456 | 31.3942 | 1.7145 | 0.76558 | 0.23339 | 2.7135 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-11-20 | 40 | 20.7367 | 10.3384 | 31.0752 | 1.6798 | 0.76558 | 0.23102 | 2.6764 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-11-20 | 41 | 20.4865 | 10.1318 | 30.6184 | 1.6308 | 0.76558 | 0.22762 | 2.624 | 8.57% | 9.118% | 6.162% | 1.0937 | 1.1003 | 1.0657
2010-11-20 | 42 | 20.9624 | 10.1951 | 31.1575 | 1.6887 | 0.76558 | 0.23163 | 2.6859 | 8.621% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-11-20 | 43 | 21.0316 | 10.2184 | 31.2499 | 1.6988 | 0.76558 | 0.23232 | 2.6967 | 8.629% | 9.182% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-11-20 | 44 | 20.9251 | 9.9715 | 30.8967 | 1.6606 | 0.76558 | 0.22969 | 2.6558 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-11-20 | 45 | 20.1641 | 9.5786 | 29.7427 | 1.5388 | 0.76558 | 0.22111 | 2.5255 | 8.491% | 9.035% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-11-20 | 46 | 18.836 | 9.1747 | 28.0107 | 1.3648 | 0.76558 | 0.20824 | 2.3387 | 8.349% | 8.883% | 6.003% | 1.0911 | 1.0975 | 1.0639
2010-11-20 | 47 | 17.9204 | 8.8936 | 26.814 | 1.2507 | 0.76558 | 0.19934 | 2.2156 | 8.263% | 8.792% | 5.941% | 1.0901 | 1.0964 | 1.0632
2010-11-20 | 48 | 16.5895 | 8.7105 | 25.3 | 1.1135 | 0.76558 | 0.18808 | 2.0671 | 8.17% | 8.693% | 5.875% | 1.089 | 1.0952 | 1.0624
2010-11-21 | 1 | 14.9175 | 7.7182 | 22.6357 | 0.8913 | 0.76558 | 0.16828 | 1.8252 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-21 | 2 | 13.9164 | 7.0797 | 20.9961 | 0.76685 | 0.76558 | 0.15609 | 1.6885 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-21 | 3 | 13.0329 | 6.7388 | 19.7717 | 0.68002 | 0.76558 | 0.14699 | 1.5926 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-21 | 4 | 12.6739 | 6.4695 | 19.1433 | 0.63749 | 0.76558 | 0.14231 | 1.5454 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-11-21 | 5 | 12.3198 | 6.5108 | 18.8305 | 0.61682 | 0.76558 | 0.13999 | 1.5224 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-11-21 | 6 | 12.0129 | 6.4399 | 18.4528 | 0.59232 | 0.76558 | 0.13718 | 1.4951 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-11-21 | 7 | 11.735 | 6.3138 | 18.0489 | 0.56668 | 0.76558 | 0.13418 | 1.4664 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-11-21 | 8 | 11.4102 | 6.3721 | 17.7822 | 0.55006 | 0.76558 | 0.1322 | 1.4478 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2010-11-21 | 9 | 11.4024 | 6.5157 | 17.9181 | 0.55849 | 0.76558 | 0.13321 | 1.4573 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-21 | 10 | 11.2598 | 6.3763 | 17.6361 | 0.54105 | 0.76558 | 0.13111 | 1.4377 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2010-11-21 | 11 | 11.502 | 6.4727 | 17.9747 | 0.56203 | 0.76558 | 0.13363 | 1.4612 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-11-21 | 12 | 11.9691 | 6.5285 | 18.4976 | 0.5952 | 0.76558 | 0.13751 | 1.4983 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-11-21 | 13 | 12.8165 | 6.5953 | 19.4117 | 0.65548 | 0.76558 | 0.14431 | 1.5654 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2010-11-21 | 14 | 13.7994 | 6.9998 | 20.7992 | 0.75254 | 0.76558 | 0.15462 | 1.6727 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-21 | 15 | 15.3421 | 7.7478 | 23.0899 | 0.92743 | 0.76558 | 0.17165 | 1.8647 | 8.076% | 8.592% | 5.806% | 1.0879 | 1.094 | 1.0616
2010-11-21 | 16 | 16.9804 | 8.4724 | 25.4528 | 1.1269 | 0.76558 | 0.18922 | 2.0817 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2010-11-21 | 17 | 18.4368 | 9.379 | 27.8158 | 1.3459 | 0.76558 | 0.20679 | 2.3183 | 8.334% | 8.868% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-11-21 | 18 | 20.1466 | 10.0311 | 30.1778 | 1.5842 | 0.76558 | 0.22435 | 2.5741 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2010-11-21 | 19 | 21.5312 | 10.4739 | 32.0051 | 1.7819 | 0.76558 | 0.23793 | 2.7854 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0668
2010-11-21 | 20 | 22.1141 | 10.6444 | 32.7585 | 1.8667 | 0.76558 | 0.24353 | 2.8758 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-11-21 | 21 | 22.4069 | 10.4257 | 32.8326 | 1.8752 | 0.76558 | 0.24408 | 2.8849 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2010-11-21 | 22 | 22.3167 | 10.8986 | 33.2153 | 1.9192 | 0.76558 | 0.24693 | 2.9317 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-11-21 | 23 | 21.7606 | 10.4274 | 32.1881 | 1.8023 | 0.76558 | 0.23929 | 2.8072 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-11-21 | 24 | 21.2868 | 10.202 | 31.4888 | 1.7248 | 0.76558 | 0.23409 | 2.7245 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-11-21 | 25 | 20.961 | 10.0003 | 30.9612 | 1.6675 | 0.76558 | 0.23017 | 2.6633 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-11-21 | 26 | 20.2366 | 9.7285 | 29.9651 | 1.5619 | 0.76558 | 0.22276 | 2.5503 | 8.511% | 9.056% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-11-21 | 27 | 19.8425 | 9.7561 | 29.5986 | 1.524 | 0.76558 | 0.22004 | 2.5096 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-11-21 | 28 | 19.5504 | 9.5511 | 29.1016 | 1.4732 | 0.76558 | 0.21634 | 2.4551 | 8.436% | 8.976% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-11-21 | 29 | 19.4157 | 8.9569 | 28.3726 | 1.4003 | 0.76558 | 0.21093 | 2.3768 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-11-21 | 30 | 19.1106 | 8.7627 | 27.8733 | 1.3515 | 0.76558 | 0.20721 | 2.3243 | 8.339% | 8.872% | 5.996% | 1.091 | 1.0974 | 1.0638
2010-11-21 | 31 | 19.2642 | 8.8633 | 28.1275 | 1.3762 | 0.76558 | 0.2091 | 2.3509 | 8.358% | 8.893% | 6.009% | 1.0912 | 1.0976 | 1.0639
2010-11-21 | 32 | 19.0662 | 8.8796 | 27.9458 | 1.3585 | 0.76558 | 0.20775 | 2.3319 | 8.344% | 8.878% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-11-21 | 33 | 19.1844 | 9.1029 | 28.2873 | 1.3919 | 0.76558 | 0.21029 | 2.3678 | 8.371% | 8.906% | 6.018% | 1.0914 | 1.0978 | 1.064
2010-11-21 | 34 | 19.3796 | 9.0479 | 28.4275 | 1.4058 | 0.76558 | 0.21133 | 2.3827 | 8.382% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-11-21 | 35 | 19.8823 | 9.3858 | 29.2681 | 1.4901 | 0.76558 | 0.21758 | 2.4733 | 8.45% | 8.991% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-11-21 | 36 | 20.6606 | 10.1122 | 30.7728 | 1.6473 | 0.76558 | 0.22877 | 2.6416 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2010-11-21 | 37 | 21.2659 | 10.1668 | 31.4327 | 1.7187 | 0.76558 | 0.23367 | 2.7179 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2010-11-21 | 38 | 21.6238 | 9.9792 | 31.603 | 1.7374 | 0.76558 | 0.23494 | 2.7379 | 8.663% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-11-21 | 39 | 21.5903 | 9.6526 | 31.2429 | 1.698 | 0.76558 | 0.23226 | 2.6958 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-11-21 | 40 | 21.5473 | 9.6969 | 31.2442 | 1.6981 | 0.76558 | 0.23227 | 2.696 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-11-21 | 41 | 21.2196 | 9.6834 | 30.9031 | 1.6613 | 0.76558 | 0.22974 | 2.6566 | 8.596% | 9.147% | 6.181% | 1.094 | 1.1007 | 1.0659
2010-11-21 | 42 | 21.0784 | 9.563 | 30.6414 | 1.6332 | 0.76558 | 0.22779 | 2.6266 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-11-21 | 43 | 20.956 | 9.514 | 30.47 | 1.615 | 0.76558 | 0.22652 | 2.6071 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-11-21 | 44 | 20.9696 | 9.3428 | 30.3124 | 1.5984 | 0.76558 | 0.22535 | 2.5893 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-11-21 | 45 | 19.9462 | 8.8831 | 28.8293 | 1.4458 | 0.76558 | 0.21432 | 2.4257 | 8.414% | 8.952% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-11-21 | 46 | 18.7793 | 8.3764 | 27.1556 | 1.2828 | 0.76558 | 0.20188 | 2.2502 | 8.286% | 8.817% | 5.958% | 1.0904 | 1.0967 | 1.0634
2010-11-21 | 47 | 17.7262 | 8.2719 | 25.9981 | 1.1758 | 0.76558 | 0.19327 | 2.1346 | 8.211% | 8.736% | 5.903% | 1.0895 | 1.0957 | 1.0627
2010-11-21 | 48 | 16.8026 | 8.4167 | 25.2194 | 1.1064 | 0.76558 | 0.18748 | 2.0594 | 8.166% | 8.689% | 5.871% | 1.0889 | 1.0952 | 1.0624
2010-11-22 | 1 | 15.419 | 7.4219 | 22.8409 | 0.90753 | 0.76558 | 0.1698 | 1.8429 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-11-22 | 2 | 14.4363 | 7.1188 | 21.5551 | 0.80823 | 0.76558 | 0.16024 | 1.734 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-22 | 3 | 13.7042 | 6.914 | 20.6182 | 0.7395 | 0.76558 | 0.15328 | 1.6584 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-22 | 4 | 13.2642 | 6.752 | 20.0162 | 0.69695 | 0.76558 | 0.1488 | 1.6113 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-11-22 | 5 | 12.8742 | 6.6373 | 19.5115 | 0.66224 | 0.76558 | 0.14505 | 1.5729 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-11-22 | 6 | 12.5243 | 6.4691 | 18.9933 | 0.62753 | 0.76558 | 0.1412 | 1.5343 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-11-22 | 7 | 12.4557 | 6.6371 | 19.0928 | 0.63412 | 0.76558 | 0.14194 | 1.5416 | 8.074% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-11-22 | 8 | 12.4186 | 6.6665 | 19.0851 | 0.63361 | 0.76558 | 0.14188 | 1.5411 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-11-22 | 9 | 12.4409 | 6.6832 | 19.1241 | 0.63621 | 0.76558 | 0.14217 | 1.544 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-11-22 | 10 | 12.6178 | 6.8292 | 19.447 | 0.65787 | 0.76558 | 0.14457 | 1.568 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-22 | 11 | 12.839 | 6.8256 | 19.6645 | 0.67267 | 0.76558 | 0.14619 | 1.5844 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-22 | 12 | 13.2327 | 6.8814 | 20.1141 | 0.70378 | 0.76558 | 0.14953 | 1.6189 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-22 | 13 | 13.751 | 6.9955 | 20.7465 | 0.74873 | 0.76558 | 0.15423 | 1.6685 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-22 | 14 | 14.8932 | 7.4419 | 22.335 | 0.86778 | 0.76558 | 0.16604 | 1.7994 | 8.056% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-22 | 15 | 16.4809 | 8.1027 | 24.5836 | 1.0513 | 0.76558 | 0.18276 | 1.9996 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-22 | 16 | 17.8211 | 8.7706 | 26.5917 | 1.2301 | 0.76558 | 0.19769 | 2.1933 | 8.248% | 8.776% | 5.93% | 1.0899 | 1.0962 | 1.063
2010-11-22 | 17 | 19.1765 | 9.4307 | 28.6072 | 1.4236 | 0.76558 | 0.21267 | 2.4018 | 8.396% | 8.933% | 6.037% | 1.0917 | 1.0981 | 1.0642
2010-11-22 | 18 | 20.3779 | 9.9204 | 30.2983 | 1.5969 | 0.76558 | 0.22524 | 2.5877 | 8.541% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-11-22 | 19 | 21.6194 | 10.4668 | 32.0861 | 1.7909 | 0.76558 | 0.23853 | 2.795 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1022 | 1.0668
2010-11-22 | 20 | 21.8937 | 10.9784 | 32.872 | 1.8797 | 0.76558 | 0.24437 | 2.8896 | 8.791% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2010-11-22 | 21 | 22.599 | 11.3286 | 33.9276 | 2.0023 | 0.76558 | 0.25222 | 3.0201 | 8.902% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-22 | 22 | 22.0957 | 11.4028 | 33.4984 | 1.952 | 0.76558 | 0.24903 | 2.9666 | 8.856% | 9.423% | 6.367% | 1.0972 | 1.104 | 1.068
2010-11-22 | 23 | 21.61 | 10.9919 | 32.6019 | 1.8489 | 0.76558 | 0.24237 | 2.8569 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-11-22 | 24 | 21.0203 | 10.9447 | 31.965 | 1.7774 | 0.76558 | 0.23763 | 2.7806 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-11-22 | 25 | 20.4399 | 10.917 | 31.357 | 1.7104 | 0.76558 | 0.23311 | 2.7091 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-11-22 | 26 | 20.067 | 10.4656 | 30.5326 | 1.6217 | 0.76558 | 0.22698 | 2.6142 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-11-22 | 27 | 19.4742 | 10.2206 | 29.6948 | 1.5339 | 0.76558 | 0.22075 | 2.5202 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-11-22 | 28 | 19.2388 | 9.9567 | 29.1955 | 1.4827 | 0.76558 | 0.21704 | 2.4654 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-11-22 | 29 | 18.6139 | 9.7793 | 28.3932 | 1.4024 | 0.76558 | 0.21108 | 2.379 | 8.379% | 8.915% | 6.024% | 1.0915 | 1.0979 | 1.0641
2010-11-22 | 30 | 18.3235 | 9.6059 | 27.9294 | 1.3569 | 0.76558 | 0.20763 | 2.3301 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-11-22 | 31 | 18.2642 | 9.3741 | 27.6383 | 1.3288 | 0.76558 | 0.20547 | 2.2998 | 8.321% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-11-22 | 32 | 18.1461 | 8.9939 | 27.14 | 1.2813 | 0.76558 | 0.20176 | 2.2487 | 8.285% | 8.816% | 5.957% | 1.0903 | 1.0967 | 1.0633
2010-11-22 | 33 | 18.0734 | 9.2854 | 27.3588 | 1.302 | 0.76558 | 0.20339 | 2.271 | 8.301% | 8.832% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-11-22 | 34 | 18.2934 | 9.541 | 27.8344 | 1.3477 | 0.76558 | 0.20692 | 2.3202 | 8.336% | 8.869% | 5.993% | 1.0909 | 1.0973 | 1.0638
2010-11-22 | 35 | 18.4307 | 10.0716 | 28.5023 | 1.4132 | 0.76558 | 0.21189 | 2.3906 | 8.388% | 8.924% | 6.031% | 1.0916 | 1.098 | 1.0642
2010-11-22 | 36 | 18.783 | 10.5929 | 29.376 | 1.5011 | 0.76558 | 0.21838 | 2.4851 | 8.46% | 9.001% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-11-22 | 37 | 19.3776 | 10.837 | 30.2145 | 1.5881 | 0.76558 | 0.22462 | 2.5783 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-11-22 | 38 | 19.9143 | 10.7772 | 30.6915 | 1.6386 | 0.76558 | 0.22816 | 2.6323 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-11-22 | 39 | 20.0654 | 10.6923 | 30.7577 | 1.6457 | 0.76558 | 0.22866 | 2.6399 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-11-22 | 40 | 20.1052 | 10.3351 | 30.4403 | 1.6119 | 0.76558 | 0.2263 | 2.6038 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-11-22 | 41 | 20.3149 | 10.2887 | 30.6035 | 1.6292 | 0.76558 | 0.22751 | 2.6223 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-11-22 | 42 | 20.4281 | 10.3987 | 30.8267 | 1.6531 | 0.76558 | 0.22917 | 2.6478 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-11-22 | 43 | 21.0008 | 10.5103 | 31.5111 | 1.7273 | 0.76558 | 0.23426 | 2.7271 | 8.654% | 9.208% | 6.223% | 1.0947 | 1.1014 | 1.0664
2010-11-22 | 44 | 21.0617 | 10.3216 | 31.3833 | 1.7133 | 0.76558 | 0.23331 | 2.7122 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-11-22 | 45 | 19.8724 | 9.8248 | 29.6972 | 1.5341 | 0.76558 | 0.22077 | 2.5205 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-11-22 | 46 | 18.4061 | 9.0652 | 27.4712 | 1.3128 | 0.76558 | 0.20422 | 2.2826 | 8.309% | 8.841% | 5.974% | 1.0906 | 1.097 | 1.0635
2010-11-22 | 47 | 16.9865 | 8.4338 | 25.4202 | 1.1241 | 0.76558 | 0.18898 | 2.0786 | 8.177% | 8.7% | 5.879% | 1.0891 | 1.0953 | 1.0625
2010-11-22 | 48 | 15.8623 | 8.3688 | 24.2311 | 1.0214 | 0.76558 | 0.18014 | 1.9671 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-11-23 | 1 | 14.373 | 7.5482 | 21.9212 | 0.83592 | 0.76558 | 0.16296 | 1.7645 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-23 | 2 | 13.265 | 7.1048 | 20.3698 | 0.72179 | 0.76558 | 0.15143 | 1.6388 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-23 | 3 | 12.6856 | 6.8876 | 19.5732 | 0.66644 | 0.76558 | 0.14551 | 1.5775 | 8.06% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-23 | 4 | 12.1397 | 6.7728 | 18.9125 | 0.6222 | 0.76558 | 0.1406 | 1.5284 | 8.081% | 8.599% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-11-23 | 5 | 11.919 | 6.6522 | 18.5712 | 0.59995 | 0.76558 | 0.13806 | 1.5036 | 8.096% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-11-23 | 6 | 11.5664 | 6.6746 | 18.241 | 0.5788 | 0.76558 | 0.13561 | 1.48 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-11-23 | 7 | 11.3582 | 6.5868 | 17.945 | 0.56017 | 0.76558 | 0.13341 | 1.4592 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-23 | 8 | 11.0139 | 6.4029 | 17.4168 | 0.52768 | 0.76558 | 0.12948 | 1.4227 | 8.169% | 8.692% | 5.873% | 1.089 | 1.0952 | 1.0624
2010-11-23 | 9 | 11.2273 | 6.5128 | 17.7401 | 0.54745 | 0.76558 | 0.13188 | 1.4449 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2010-11-23 | 10 | 11.3907 | 6.5158 | 17.9065 | 0.55777 | 0.76558 | 0.13312 | 1.4565 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-11-23 | 11 | 11.8335 | 6.6851 | 18.5186 | 0.59656 | 0.76558 | 0.13767 | 1.4998 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-11-23 | 12 | 12.2172 | 6.7429 | 18.9601 | 0.62534 | 0.76558 | 0.14095 | 1.5319 | 8.079% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-11-23 | 13 | 13.4994 | 7.1909 | 20.6903 | 0.74468 | 0.76558 | 0.15381 | 1.6641 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-23 | 14 | 15.6263 | 8.3486 | 23.9749 | 0.99988 | 0.76558 | 0.17823 | 1.9437 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-11-23 | 15 | 18.7684 | 9.6538 | 28.4222 | 1.4052 | 0.76558 | 0.21129 | 2.3821 | 8.381% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-11-23 | 16 | 21.0872 | 10.5355 | 31.6228 | 1.7395 | 0.76558 | 0.23509 | 2.7402 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2010-11-23 | 17 | 22.2969 | 10.9096 | 33.2065 | 1.9181 | 0.76558 | 0.24686 | 2.9306 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0678
2010-11-23 | 18 | 22.5704 | 11.0716 | 33.642 | 1.9688 | 0.76558 | 0.2501 | 2.9845 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2010-11-23 | 19 | 21.883 | 11.2103 | 33.0933 | 1.9051 | 0.76558 | 0.24602 | 2.9167 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2010-11-23 | 20 | 21.6981 | 11.1364 | 32.8345 | 1.8754 | 0.76558 | 0.2441 | 2.8851 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2010-11-23 | 21 | 21.7552 | 10.7472 | 32.5024 | 1.8377 | 0.76558 | 0.24163 | 2.8449 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-11-23 | 22 | 21.2718 | 10.9874 | 32.2592 | 1.8103 | 0.76558 | 0.23982 | 2.8157 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-11-23 | 23 | 20.8772 | 10.5575 | 31.4348 | 1.7189 | 0.76558 | 0.23369 | 2.7182 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2010-11-23 | 24 | 20.4651 | 10.643 | 31.1081 | 1.6834 | 0.76558 | 0.23126 | 2.6802 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-11-23 | 25 | 20.4947 | 10.6604 | 31.1551 | 1.6885 | 0.76558 | 0.23161 | 2.6857 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-11-23 | 26 | 20.2212 | 10.4077 | 30.6289 | 1.6319 | 0.76558 | 0.2277 | 2.6252 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2010-11-23 | 27 | 20.298 | 10.7602 | 31.0582 | 1.678 | 0.76558 | 0.23089 | 2.6745 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2010-11-23 | 28 | 20.2651 | 10.8443 | 31.1094 | 1.6835 | 0.76558 | 0.23127 | 2.6804 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-11-23 | 29 | 20.0627 | 10.6327 | 30.6955 | 1.639 | 0.76558 | 0.22819 | 2.6328 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-11-23 | 30 | 19.9395 | 10.4723 | 30.4117 | 1.6089 | 0.76558 | 0.22608 | 2.6005 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-11-23 | 31 | 19.7448 | 10.4299 | 30.1747 | 1.5839 | 0.76558 | 0.22432 | 2.5738 | 8.53% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2010-11-23 | 32 | 19.7766 | 10.7075 | 30.4841 | 1.6165 | 0.76558 | 0.22662 | 2.6087 | 8.558% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-11-23 | 33 | 19.9897 | 10.9383 | 30.928 | 1.6639 | 0.76558 | 0.22992 | 2.6594 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-11-23 | 34 | 20.2644 | 10.9832 | 31.2477 | 1.6985 | 0.76558 | 0.2323 | 2.6964 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-11-23 | 35 | 20.481 | 11.3676 | 31.8486 | 1.7645 | 0.76558 | 0.23677 | 2.7668 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2010-11-23 | 36 | 20.5082 | 11.8323 | 32.3405 | 1.8194 | 0.76558 | 0.24042 | 2.8254 | 8.736% | 9.296% | 6.281% | 1.0957 | 1.1025 | 1.067
2010-11-23 | 37 | 21.5011 | 12.0543 | 33.5554 | 1.9587 | 0.76558 | 0.24945 | 2.9737 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-11-23 | 38 | 21.9974 | 11.943 | 33.9405 | 2.0039 | 0.76558 | 0.25232 | 3.0218 | 8.903% | 9.473% | 6.401% | 1.0977 | 1.1046 | 1.0684
2010-11-23 | 39 | 21.7002 | 11.8558 | 33.556 | 1.9587 | 0.76558 | 0.24946 | 2.9738 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-11-23 | 40 | 21.4895 | 11.5373 | 33.0268 | 1.8974 | 0.76558 | 0.24552 | 2.9085 | 8.807% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-11-23 | 41 | 21.251 | 11.2759 | 32.5269 | 1.8404 | 0.76558 | 0.24181 | 2.8478 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-23 | 42 | 20.9665 | 11.234 | 32.2005 | 1.8037 | 0.76558 | 0.23938 | 2.8086 | 8.722% | 9.281% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-11-23 | 43 | 20.8539 | 11.3839 | 32.2378 | 1.8079 | 0.76558 | 0.23966 | 2.8131 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1023 | 1.0669
2010-11-23 | 44 | 20.8939 | 11.2756 | 32.1695 | 1.8002 | 0.76558 | 0.23915 | 2.8049 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-11-23 | 45 | 20.0777 | 10.402 | 30.4797 | 1.6161 | 0.76558 | 0.22659 | 2.6082 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-11-23 | 46 | 18.4596 | 9.6744 | 28.134 | 1.3769 | 0.76558 | 0.20915 | 2.3516 | 8.359% | 8.894% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-11-23 | 47 | 17.0288 | 9.2129 | 26.2417 | 1.1979 | 0.76558 | 0.19508 | 2.1586 | 8.226% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-11-23 | 48 | 15.8308 | 9.1403 | 24.9711 | 1.0847 | 0.76558 | 0.18564 | 2.0359 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-11-24 | 1 | 14.2929 | 8.0864 | 22.3793 | 0.87122 | 0.76558 | 0.16637 | 1.8032 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-24 | 2 | 13.24 | 7.4755 | 20.7155 | 0.74649 | 0.76558 | 0.154 | 1.6661 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-24 | 3 | 12.5605 | 7.2768 | 19.8373 | 0.68454 | 0.76558 | 0.14747 | 1.5976 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-11-24 | 4 | 12.2479 | 7.0049 | 19.2527 | 0.64479 | 0.76558 | 0.14313 | 1.5535 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-11-24 | 5 | 11.8519 | 6.9043 | 18.7563 | 0.61197 | 0.76558 | 0.13944 | 1.517 | 8.088% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-11-24 | 6 | 11.5216 | 6.6098 | 18.1314 | 0.57187 | 0.76558 | 0.13479 | 1.4722 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-11-24 | 7 | 11.2215 | 6.4721 | 17.6936 | 0.54459 | 0.76558 | 0.13154 | 1.4417 | 8.148% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-11-24 | 8 | 11.0608 | 6.6346 | 17.6954 | 0.5447 | 0.76558 | 0.13155 | 1.4418 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-11-24 | 9 | 11.0183 | 6.7487 | 17.767 | 0.54911 | 0.76558 | 0.13208 | 1.4468 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2010-11-24 | 10 | 11.1833 | 6.7874 | 17.9706 | 0.56177 | 0.76558 | 0.1336 | 1.4609 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-11-24 | 11 | 11.5831 | 7.0657 | 18.6488 | 0.60497 | 0.76558 | 0.13864 | 1.5092 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-11-24 | 12 | 12.1448 | 7.024 | 19.1688 | 0.63918 | 0.76558 | 0.1425 | 1.5473 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-11-24 | 13 | 13.4015 | 7.538 | 20.9395 | 0.76272 | 0.76558 | 0.15567 | 1.684 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-24 | 14 | 15.4926 | 8.81 | 24.3026 | 1.0274 | 0.76558 | 0.18067 | 1.9736 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-11-24 | 15 | 18.8399 | 9.93 | 28.7699 | 1.4398 | 0.76558 | 0.21388 | 2.4193 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2010-11-24 | 16 | 20.9449 | 10.9929 | 31.9379 | 1.7744 | 0.76558 | 0.23743 | 2.7774 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-11-24 | 17 | 22.1326 | 11.5797 | 33.7123 | 1.977 | 0.76558 | 0.25062 | 2.9932 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-11-24 | 18 | 22.3665 | 11.4805 | 33.847 | 1.9929 | 0.76558 | 0.25162 | 3.0101 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2010-11-24 | 19 | 22.1914 | 11.1558 | 33.3472 | 1.9344 | 0.76558 | 0.24791 | 2.9479 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2010-11-24 | 20 | 21.7535 | 11.1515 | 32.9051 | 1.8835 | 0.76558 | 0.24462 | 2.8937 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2010-11-24 | 21 | 21.756 | 10.7895 | 32.5456 | 1.8425 | 0.76558 | 0.24195 | 2.8501 | 8.757% | 9.318% | 6.296% | 1.096 | 1.1028 | 1.0672
2010-11-24 | 22 | 21.1011 | 10.974 | 32.0751 | 1.7897 | 0.76558 | 0.23845 | 2.7937 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-11-24 | 23 | 20.672 | 10.5928 | 31.2647 | 1.7004 | 0.76558 | 0.23243 | 2.6984 | 8.631% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-11-24 | 24 | 20.494 | 10.3927 | 30.8867 | 1.6595 | 0.76558 | 0.22962 | 2.6547 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-11-24 | 25 | 20.1334 | 10.2869 | 30.4203 | 1.6098 | 0.76558 | 0.22615 | 2.6015 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-11-24 | 26 | 19.76 | 10.1043 | 29.8643 | 1.5515 | 0.76558 | 0.22202 | 2.5391 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-11-24 | 27 | 19.96 | 10.3855 | 30.3456 | 1.6019 | 0.76558 | 0.22559 | 2.593 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-11-24 | 28 | 19.766 | 10.3076 | 30.0736 | 1.5733 | 0.76558 | 0.22357 | 2.5624 | 8.521% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-11-24 | 29 | 19.3683 | 10.0855 | 29.4538 | 1.5091 | 0.76558 | 0.21896 | 2.4936 | 8.466% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-11-24 | 30 | 19.1279 | 9.7756 | 28.9035 | 1.4532 | 0.76558 | 0.21487 | 2.4337 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-11-24 | 31 | 19.4017 | 9.7572 | 29.159 | 1.479 | 0.76558 | 0.21677 | 2.4614 | 8.441% | 8.982% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-11-24 | 32 | 19.2239 | 9.925 | 29.1489 | 1.478 | 0.76558 | 0.2167 | 2.4603 | 8.44% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-11-24 | 33 | 19.2619 | 10.1937 | 29.4556 | 1.5093 | 0.76558 | 0.21898 | 2.4938 | 8.466% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2010-11-24 | 34 | 19.5026 | 10.1156 | 29.6182 | 1.526 | 0.76558 | 0.22019 | 2.5118 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2010-11-24 | 35 | 19.7668 | 10.6983 | 30.4651 | 1.6145 | 0.76558 | 0.22648 | 2.6066 | 8.556% | 9.103% | 6.152% | 1.0936 | 1.1002 | 1.0655
2010-11-24 | 36 | 20.0776 | 11.3299 | 31.4074 | 1.7159 | 0.76558 | 0.23349 | 2.715 | 8.644% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-11-24 | 37 | 20.6566 | 11.5676 | 32.2242 | 1.8063 | 0.76558 | 0.23956 | 2.8115 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-11-24 | 38 | 21.4128 | 11.6212 | 33.034 | 1.8983 | 0.76558 | 0.24558 | 2.9094 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2010-11-24 | 39 | 21.3331 | 11.4803 | 32.8134 | 1.873 | 0.76558 | 0.24394 | 2.8825 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-11-24 | 40 | 21.1188 | 11.3891 | 32.5079 | 1.8383 | 0.76558 | 0.24167 | 2.8455 | 8.753% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-11-24 | 41 | 21.149 | 11.0571 | 32.2062 | 1.8043 | 0.76558 | 0.23942 | 2.8093 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-11-24 | 42 | 21.0935 | 11.1157 | 32.2092 | 1.8047 | 0.76558 | 0.23945 | 2.8097 | 8.723% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2010-11-24 | 43 | 21.4766 | 11.0732 | 32.5498 | 1.843 | 0.76558 | 0.24198 | 2.8506 | 8.758% | 9.318% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-11-24 | 44 | 21.7621 | 11.1491 | 32.9112 | 1.8842 | 0.76558 | 0.24467 | 2.8944 | 8.795% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2010-11-24 | 45 | 20.75 | 10.2115 | 30.9615 | 1.6676 | 0.76558 | 0.23017 | 2.6633 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-11-24 | 46 | 18.8243 | 9.5604 | 28.3847 | 1.4015 | 0.76558 | 0.21102 | 2.3781 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-11-24 | 47 | 17.3004 | 9.0325 | 26.3329 | 1.2062 | 0.76558 | 0.19576 | 2.1676 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2010-11-24 | 48 | 16.0607 | 8.6735 | 24.7342 | 1.0642 | 0.76558 | 0.18388 | 2.0137 | 8.141% | 8.662% | 5.854% | 1.0886 | 1.0948 | 1.0622
2010-11-25 | 1 | 14.5334 | 7.8882 | 22.4216 | 0.87452 | 0.76558 | 0.16669 | 1.8068 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-11-25 | 2 | 13.3291 | 7.2707 | 20.5998 | 0.73817 | 0.76558 | 0.15314 | 1.6569 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-25 | 3 | 12.5584 | 6.9544 | 19.5128 | 0.66233 | 0.76558 | 0.14506 | 1.573 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-11-25 | 4 | 12.1481 | 6.894 | 19.0421 | 0.63076 | 0.76558 | 0.14156 | 1.5379 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2010-11-25 | 5 | 11.8768 | 6.7939 | 18.6706 | 0.60639 | 0.76558 | 0.1388 | 1.5108 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-11-25 | 6 | 11.6276 | 6.6165 | 18.2441 | 0.579 | 0.76558 | 0.13563 | 1.4802 | 8.113% | 8.633% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-11-25 | 7 | 11.5913 | 6.6112 | 18.2025 | 0.57636 | 0.76558 | 0.13532 | 1.4773 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-11-25 | 8 | 11.3389 | 6.6043 | 17.9432 | 0.56006 | 0.76558 | 0.13339 | 1.459 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-25 | 9 | 11.4294 | 6.6407 | 18.0701 | 0.56801 | 0.76558 | 0.13434 | 1.4679 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-11-25 | 10 | 11.7076 | 6.7375 | 18.4451 | 0.59183 | 0.76558 | 0.13712 | 1.4945 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-11-25 | 11 | 11.871 | 6.8586 | 18.7296 | 0.61023 | 0.76558 | 0.13924 | 1.515 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-11-25 | 12 | 12.1533 | 7.0439 | 19.1972 | 0.64108 | 0.76558 | 0.14271 | 1.5494 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-25 | 13 | 13.7366 | 7.6899 | 21.4265 | 0.79861 | 0.76558 | 0.15929 | 1.7235 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-25 | 14 | 15.7511 | 8.7141 | 24.4652 | 1.0412 | 0.76558 | 0.18188 | 1.9886 | 8.128% | 8.649% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-11-25 | 15 | 18.7359 | 10.1453 | 28.8812 | 1.451 | 0.76558 | 0.21471 | 2.4313 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-11-25 | 16 | 21.1873 | 10.8976 | 32.085 | 1.7908 | 0.76558 | 0.23852 | 2.7949 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1022 | 1.0668
2010-11-25 | 17 | 22.5199 | 11.4004 | 33.9203 | 2.0015 | 0.76558 | 0.25217 | 3.0192 | 8.901% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-25 | 18 | 22.5138 | 11.3425 | 33.8563 | 1.9939 | 0.76558 | 0.25169 | 3.0112 | 8.894% | 9.463% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-11-25 | 19 | 22.1628 | 11.1994 | 33.3622 | 1.9362 | 0.76558 | 0.24802 | 2.9498 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-11-25 | 20 | 21.5688 | 11.2284 | 32.7973 | 1.8712 | 0.76558 | 0.24382 | 2.8806 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-11-25 | 21 | 21.473 | 11.0542 | 32.5272 | 1.8405 | 0.76558 | 0.24181 | 2.8479 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-25 | 22 | 21.2423 | 11.2191 | 32.4614 | 1.833 | 0.76558 | 0.24132 | 2.8399 | 8.749% | 9.309% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-11-25 | 23 | 20.6324 | 10.9689 | 31.6013 | 1.7372 | 0.76558 | 0.23493 | 2.7377 | 8.663% | 9.218% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-11-25 | 24 | 20.6758 | 10.9644 | 31.6403 | 1.7415 | 0.76558 | 0.23522 | 2.7423 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-11-25 | 25 | 20.5275 | 11.1928 | 31.7203 | 1.7503 | 0.76558 | 0.23581 | 2.7517 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-11-25 | 26 | 20.1037 | 10.8145 | 30.9182 | 1.6629 | 0.76558 | 0.22985 | 2.6583 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-11-25 | 27 | 19.8123 | 10.8294 | 30.6417 | 1.6333 | 0.76558 | 0.22779 | 2.6267 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-11-25 | 28 | 19.5098 | 10.7016 | 30.2114 | 1.5877 | 0.76558 | 0.2246 | 2.5779 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-11-25 | 29 | 19.5584 | 10.444 | 30.0024 | 1.5658 | 0.76558 | 0.22304 | 2.5545 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-11-25 | 30 | 19.2962 | 10.2566 | 29.5527 | 1.5193 | 0.76558 | 0.2197 | 2.5045 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-11-25 | 31 | 19.5282 | 10.4268 | 29.955 | 1.5609 | 0.76558 | 0.22269 | 2.5492 | 8.51% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-11-25 | 32 | 19.5122 | 10.5173 | 30.0294 | 1.5687 | 0.76558 | 0.22324 | 2.5575 | 8.517% | 9.062% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-11-25 | 33 | 19.8769 | 11.0077 | 30.8847 | 1.6593 | 0.76558 | 0.2296 | 2.6545 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-11-25 | 34 | 19.9737 | 11.3264 | 31.3001 | 1.7042 | 0.76558 | 0.23269 | 2.7025 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-11-25 | 35 | 20.4156 | 11.7551 | 32.1707 | 1.8003 | 0.76558 | 0.23916 | 2.8051 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-11-25 | 36 | 21.2907 | 12.0981 | 33.3889 | 1.9393 | 0.76558 | 0.24822 | 2.9531 | 8.844% | 9.411% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-11-25 | 37 | 22.5605 | 12.1727 | 34.7332 | 2.0986 | 0.76558 | 0.25821 | 3.1224 | 8.99% | 9.565% | 6.463% | 1.0988 | 1.1058 | 1.0691
2010-11-25 | 38 | 23.3679 | 11.7135 | 35.0814 | 2.1409 | 0.76558 | 0.2608 | 3.1672 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-11-25 | 39 | 22.9315 | 11.5142 | 34.4457 | 2.064 | 0.76558 | 0.25607 | 3.0856 | 8.958% | 9.531% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-11-25 | 40 | 22.8608 | 11.1667 | 34.0275 | 2.0142 | 0.76558 | 0.25296 | 3.0327 | 8.913% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-11-25 | 41 | 22.7676 | 10.742 | 33.5096 | 1.9533 | 0.76558 | 0.24911 | 2.968 | 8.857% | 9.424% | 6.368% | 1.0972 | 1.104 | 1.068
2010-11-25 | 42 | 22.4516 | 10.4555 | 32.9071 | 1.8837 | 0.76558 | 0.24464 | 2.8939 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2010-11-25 | 43 | 21.9892 | 10.3695 | 32.3587 | 1.8215 | 0.76558 | 0.24056 | 2.8276 | 8.738% | 9.298% | 6.283% | 1.0957 | 1.1025 | 1.067
2010-11-25 | 44 | 21.6098 | 10.3225 | 31.9324 | 1.7738 | 0.76558 | 0.23739 | 2.7767 | 8.696% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-11-25 | 45 | 20.4497 | 9.8613 | 30.311 | 1.5982 | 0.76558 | 0.22534 | 2.5891 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-11-25 | 46 | 18.6259 | 9.0362 | 27.6622 | 1.3311 | 0.76558 | 0.20564 | 2.3023 | 8.323% | 8.856% | 5.984% | 1.0908 | 1.0972 | 1.0637
2010-11-25 | 47 | 17.0472 | 8.6411 | 25.6883 | 1.1479 | 0.76558 | 0.19097 | 2.1044 | 8.192% | 8.717% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-11-25 | 48 | 15.69 | 8.599 | 24.2889 | 1.0262 | 0.76558 | 0.18057 | 1.9724 | 8.121% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-11-26 | 1 | 14.5242 | 7.8252 | 22.3493 | 0.86889 | 0.76558 | 0.16615 | 1.8006 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-26 | 2 | 13.3591 | 7.2248 | 20.584 | 0.73704 | 0.76558 | 0.15302 | 1.6556 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-26 | 3 | 12.6369 | 6.9311 | 19.568 | 0.66608 | 0.76558 | 0.14547 | 1.5771 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-26 | 4 | 12.3216 | 6.8559 | 19.1775 | 0.63977 | 0.76558 | 0.14257 | 1.5479 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-26 | 5 | 11.7631 | 6.7694 | 18.5325 | 0.59745 | 0.76558 | 0.13777 | 1.5008 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-11-26 | 6 | 11.3454 | 6.52 | 17.8654 | 0.55521 | 0.76558 | 0.13281 | 1.4536 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-11-26 | 7 | 11.2396 | 6.4577 | 17.6973 | 0.54481 | 0.76558 | 0.13156 | 1.442 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-11-26 | 8 | 11.3599 | 6.5969 | 17.9568 | 0.56091 | 0.76558 | 0.13349 | 1.46 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-11-26 | 9 | 11.4239 | 6.7357 | 18.1596 | 0.57365 | 0.76558 | 0.135 | 1.4742 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2010-11-26 | 10 | 11.6652 | 6.8953 | 18.5605 | 0.59926 | 0.76558 | 0.13798 | 1.5028 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-11-26 | 11 | 12.1624 | 7.0798 | 19.2421 | 0.64408 | 0.76558 | 0.14305 | 1.5527 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-11-26 | 12 | 12.422 | 7.3355 | 19.7575 | 0.67905 | 0.76558 | 0.14688 | 1.5915 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-11-26 | 13 | 13.9299 | 7.9964 | 21.9263 | 0.83631 | 0.76558 | 0.163 | 1.7649 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-26 | 14 | 16.4884 | 9.1548 | 25.6432 | 1.1439 | 0.76558 | 0.19063 | 2.1001 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-11-26 | 15 | 19.7158 | 10.6347 | 30.3505 | 1.6024 | 0.76558 | 0.22563 | 2.5936 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-11-26 | 16 | 22.0872 | 11.6924 | 33.7795 | 1.9849 | 0.76558 | 0.25112 | 3.0016 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2010-11-26 | 17 | 23.0234 | 12.179 | 35.2023 | 2.1556 | 0.76558 | 0.2617 | 3.1829 | 9.042% | 9.62% | 6.501% | 1.0994 | 1.1064 | 1.0695
2010-11-26 | 18 | 22.8344 | 12.2238 | 35.0582 | 2.138 | 0.76558 | 0.26063 | 3.1642 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2010-11-26 | 19 | 22.6062 | 11.9877 | 34.5939 | 2.0818 | 0.76558 | 0.25718 | 3.1045 | 8.974% | 9.549% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-11-26 | 20 | 22.244 | 11.9056 | 34.1496 | 2.0286 | 0.76558 | 0.25387 | 3.0481 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-11-26 | 21 | 22.2759 | 11.5847 | 33.8606 | 1.9944 | 0.76558 | 0.25172 | 3.0118 | 8.895% | 9.464% | 6.395% | 1.0976 | 1.1045 | 1.0683
2010-11-26 | 22 | 21.8084 | 11.5673 | 33.3757 | 1.9377 | 0.76558 | 0.24812 | 2.9514 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-11-26 | 23 | 21.2684 | 11.1543 | 32.4228 | 1.8287 | 0.76558 | 0.24103 | 2.8353 | 8.745% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2010-11-26 | 24 | 20.9347 | 10.9987 | 31.9334 | 1.7739 | 0.76558 | 0.2374 | 2.7769 | 8.696% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-11-26 | 25 | 20.7621 | 10.8189 | 31.581 | 1.7349 | 0.76558 | 0.23478 | 2.7353 | 8.661% | 9.216% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-11-26 | 26 | 20.389 | 10.0917 | 30.4807 | 1.6162 | 0.76558 | 0.2266 | 2.6083 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2010-11-26 | 27 | 20.1759 | 10.1889 | 30.3648 | 1.6039 | 0.76558 | 0.22574 | 2.5952 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-11-26 | 28 | 20.1118 | 10.2361 | 30.3479 | 1.6021 | 0.76558 | 0.22561 | 2.5933 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-11-26 | 29 | 19.9371 | 10.0059 | 29.9429 | 1.5596 | 0.76558 | 0.2226 | 2.5478 | 8.509% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2010-11-26 | 30 | 19.7732 | 9.9874 | 29.7606 | 1.5407 | 0.76558 | 0.22124 | 2.5275 | 8.493% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-11-26 | 31 | 19.8885 | 10.2087 | 30.0972 | 1.5757 | 0.76558 | 0.22375 | 2.5651 | 8.523% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-11-26 | 32 | 19.75 | 10.2846 | 30.0346 | 1.5692 | 0.76558 | 0.22328 | 2.5581 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-11-26 | 33 | 19.9655 | 10.4438 | 30.4093 | 1.6086 | 0.76558 | 0.22607 | 2.6002 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-11-26 | 34 | 19.9938 | 10.424 | 30.4178 | 1.6095 | 0.76558 | 0.22613 | 2.6012 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-11-26 | 35 | 20.0725 | 10.8552 | 30.9277 | 1.6639 | 0.76558 | 0.22992 | 2.6594 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-11-26 | 36 | 20.8062 | 11.3414 | 32.1477 | 1.7978 | 0.76558 | 0.23899 | 2.8023 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-11-26 | 37 | 21.517 | 11.5641 | 33.0811 | 1.9037 | 0.76558 | 0.24593 | 2.9152 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-11-26 | 38 | 21.9656 | 11.322 | 33.2876 | 1.9275 | 0.76558 | 0.24746 | 2.9406 | 8.834% | 9.399% | 6.352% | 1.0969 | 1.1037 | 1.0678
2010-11-26 | 39 | 22.0815 | 11.4958 | 33.5773 | 1.9612 | 0.76558 | 0.24962 | 2.9764 | 8.864% | 9.432% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-11-26 | 40 | 21.9506 | 11.3528 | 33.3034 | 1.9294 | 0.76558 | 0.24758 | 2.9425 | 8.835% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2010-11-26 | 41 | 21.6466 | 11.1478 | 32.7944 | 1.8708 | 0.76558 | 0.2438 | 2.8802 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-11-26 | 42 | 21.5966 | 11.3755 | 32.9722 | 1.8912 | 0.76558 | 0.24512 | 2.9019 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2010-11-26 | 43 | 21.7429 | 11.6564 | 33.3993 | 1.9405 | 0.76558 | 0.24829 | 2.9544 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-11-26 | 44 | 22.2577 | 11.7353 | 33.9929 | 2.0101 | 0.76558 | 0.25271 | 3.0284 | 8.909% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-11-26 | 45 | 21.2062 | 11.2535 | 32.4597 | 1.8328 | 0.76558 | 0.24131 | 2.8397 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-11-26 | 46 | 20.0154 | 10.8744 | 30.8898 | 1.6598 | 0.76558 | 0.22964 | 2.6551 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-11-26 | 47 | 18.1501 | 10.6186 | 28.7687 | 1.4397 | 0.76558 | 0.21387 | 2.4192 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2010-11-26 | 48 | 17.0566 | 10.3026 | 27.3592 | 1.3021 | 0.76558 | 0.20339 | 2.2711 | 8.301% | 8.832% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-11-27 | 1 | 15.1112 | 9.3412 | 24.4524 | 1.0401 | 0.76558 | 0.18178 | 1.9875 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-11-27 | 2 | 14.1339 | 8.7839 | 22.9178 | 0.91365 | 0.76558 | 0.17037 | 1.8496 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-27 | 3 | 13.4376 | 8.4875 | 21.9251 | 0.83622 | 0.76558 | 0.16299 | 1.7648 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-27 | 4 | 12.6788 | 8.2261 | 20.905 | 0.76021 | 0.76558 | 0.15541 | 1.6812 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-27 | 5 | 12.4168 | 8.0535 | 20.4703 | 0.72893 | 0.76558 | 0.15218 | 1.6467 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-27 | 6 | 12.2727 | 7.779 | 20.0517 | 0.69942 | 0.76558 | 0.14907 | 1.6141 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-11-27 | 7 | 12.0047 | 7.6945 | 19.6993 | 0.67505 | 0.76558 | 0.14645 | 1.5871 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-27 | 8 | 11.8905 | 7.592 | 19.4825 | 0.66027 | 0.76558 | 0.14483 | 1.5707 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-27 | 9 | 12.0809 | 7.7272 | 19.8082 | 0.68253 | 0.76558 | 0.14726 | 1.5954 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-27 | 10 | 12.1685 | 7.7996 | 19.9681 | 0.6936 | 0.76558 | 0.14845 | 1.6076 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-11-27 | 11 | 12.6523 | 7.9967 | 20.649 | 0.74171 | 0.76558 | 0.15351 | 1.6608 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-27 | 12 | 12.9574 | 8.1494 | 21.1068 | 0.77496 | 0.76558 | 0.15691 | 1.6975 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-27 | 13 | 14.4386 | 9.0032 | 23.4418 | 0.95591 | 0.76558 | 0.17427 | 1.8958 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2010-11-27 | 14 | 16.3723 | 9.882 | 26.2543 | 1.199 | 0.76558 | 0.19518 | 2.1598 | 8.226% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-11-27 | 15 | 19.7561 | 11.0561 | 30.8122 | 1.6515 | 0.76558 | 0.22906 | 2.6461 | 8.588% | 9.138% | 6.175% | 1.0939 | 1.1006 | 1.0658
2010-11-27 | 16 | 21.8284 | 12.0755 | 33.9039 | 1.9996 | 0.76558 | 0.25205 | 3.0172 | 8.899% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2010-11-27 | 17 | 23.137 | 12.711 | 35.848 | 2.2354 | 0.76558 | 0.2665 | 3.2675 | 9.115% | 9.698% | 6.554% | 1.1003 | 1.1074 | 1.0701
2010-11-27 | 18 | 23.3621 | 12.621 | 35.9831 | 2.2523 | 0.76558 | 0.2675 | 3.2854 | 9.13% | 9.715% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-11-27 | 19 | 22.6218 | 12.2772 | 34.899 | 2.1187 | 0.76558 | 0.25944 | 3.1437 | 9.008% | 9.584% | 6.477% | 1.099 | 1.106 | 1.0693
2010-11-27 | 20 | 22.9844 | 12.6899 | 35.6743 | 2.2138 | 0.76558 | 0.26521 | 3.2446 | 9.095% | 9.677% | 6.539% | 1.1001 | 1.1071 | 1.07
2010-11-27 | 21 | 22.7934 | 12.1118 | 34.9052 | 2.1194 | 0.76558 | 0.25949 | 3.1445 | 9.009% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2010-11-27 | 22 | 22.1334 | 12.126 | 34.2594 | 2.0417 | 0.76558 | 0.25469 | 3.062 | 8.938% | 9.51% | 6.426% | 1.0981 | 1.1051 | 1.0687
2010-11-27 | 23 | 21.6912 | 11.6147 | 33.3058 | 1.9296 | 0.76558 | 0.2476 | 2.9428 | 8.836% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2010-11-27 | 24 | 21.4154 | 11.37 | 32.7855 | 1.8698 | 0.76558 | 0.24373 | 2.8791 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-11-27 | 25 | 21.081 | 11.2827 | 32.3637 | 1.822 | 0.76558 | 0.2406 | 2.8282 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-11-27 | 26 | 20.5079 | 11.038 | 31.5459 | 1.7311 | 0.76558 | 0.23452 | 2.7312 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-11-27 | 27 | 20.4863 | 11.2245 | 31.7109 | 1.7492 | 0.76558 | 0.23574 | 2.7506 | 8.674% | 9.229% | 6.237% | 1.095 | 1.1017 | 1.0665
2010-11-27 | 28 | 20.3233 | 10.9548 | 31.2781 | 1.7018 | 0.76558 | 0.23253 | 2.6999 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-11-27 | 29 | 20.0209 | 10.4 | 30.4209 | 1.6098 | 0.76558 | 0.22615 | 2.6016 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-11-27 | 30 | 19.9704 | 10.1989 | 30.1693 | 1.5833 | 0.76558 | 0.22428 | 2.5732 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-11-27 | 31 | 19.8756 | 10.0673 | 29.9429 | 1.5596 | 0.76558 | 0.2226 | 2.5478 | 8.509% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2010-11-27 | 32 | 20.0359 | 9.7976 | 29.8335 | 1.5483 | 0.76558 | 0.22179 | 2.5356 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-11-27 | 33 | 20.3435 | 9.3578 | 29.7013 | 1.5346 | 0.76558 | 0.2208 | 2.5209 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2010-11-27 | 34 | 21.318 | 9.9044 | 31.2224 | 1.6958 | 0.76558 | 0.23211 | 2.6935 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-11-27 | 35 | 22.0959 | 10.3877 | 32.4836 | 1.8355 | 0.76558 | 0.24149 | 2.8426 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-11-27 | 36 | 23.4644 | 11.0725 | 34.5369 | 2.0749 | 0.76558 | 0.25675 | 3.0972 | 8.968% | 9.542% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-11-27 | 37 | 24.0759 | 11.0656 | 35.1414 | 2.1482 | 0.76558 | 0.26125 | 3.175 | 9.035% | 9.613% | 6.496% | 1.0993 | 1.1064 | 1.0695
2010-11-27 | 38 | 24.2236 | 11.0148 | 35.2384 | 2.1601 | 0.76558 | 0.26197 | 3.1876 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-11-27 | 39 | 22.8987 | 10.9076 | 33.8062 | 1.9881 | 0.76558 | 0.25132 | 3.005 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-11-27 | 40 | 22.3997 | 10.7438 | 33.1435 | 1.9109 | 0.76558 | 0.24639 | 2.9228 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2010-11-27 | 41 | 22.3507 | 10.6065 | 32.9572 | 1.8895 | 0.76558 | 0.24501 | 2.9 | 8.799% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-11-27 | 42 | 22.8984 | 10.4816 | 33.3799 | 1.9382 | 0.76558 | 0.24815 | 2.952 | 8.844% | 9.41% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-11-27 | 43 | 21.8725 | 10.3529 | 32.2254 | 1.8065 | 0.76558 | 0.23957 | 2.8116 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-11-27 | 44 | 21.481 | 10.4802 | 31.9612 | 1.777 | 0.76558 | 0.2376 | 2.7802 | 8.699% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-11-27 | 45 | 20.5334 | 10.0142 | 30.5476 | 1.6233 | 0.76558 | 0.22709 | 2.6159 | 8.563% | 9.112% | 6.157% | 1.0937 | 1.1002 | 1.0656
2010-11-27 | 46 | 19.3267 | 9.3973 | 28.724 | 1.4352 | 0.76558 | 0.21354 | 2.4144 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-11-27 | 47 | 18.2194 | 9.1306 | 27.35 | 1.3012 | 0.76558 | 0.20332 | 2.2701 | 8.3% | 8.831% | 5.968% | 1.0905 | 1.0969 | 1.0635
2010-11-27 | 48 | 16.9969 | 9.0984 | 26.0953 | 1.1846 | 0.76558 | 0.194 | 2.1441 | 8.217% | 8.742% | 5.908% | 1.0895 | 1.0958 | 1.0628
2010-11-28 | 1 | 15.6956 | 8.2383 | 23.9339 | 0.99646 | 0.76558 | 0.17793 | 1.94 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-11-28 | 2 | 14.6134 | 7.6623 | 22.2756 | 0.86317 | 0.76558 | 0.1656 | 1.7943 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-11-28 | 3 | 13.7699 | 7.3036 | 21.0736 | 0.77252 | 0.76558 | 0.15666 | 1.6948 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-28 | 4 | 13.2402 | 7.0838 | 20.3239 | 0.71854 | 0.76558 | 0.15109 | 1.6352 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-11-28 | 5 | 12.768 | 7.0571 | 19.8251 | 0.6837 | 0.76558 | 0.14738 | 1.5967 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-11-28 | 6 | 12.386 | 7.0278 | 19.4138 | 0.65563 | 0.76558 | 0.14432 | 1.5655 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2010-11-28 | 7 | 12.3932 | 7.033 | 19.4262 | 0.65646 | 0.76558 | 0.14442 | 1.5665 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-11-28 | 8 | 12.4641 | 7.0163 | 19.4804 | 0.66013 | 0.76558 | 0.14482 | 1.5705 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-11-28 | 9 | 12.5446 | 7.0616 | 19.6061 | 0.66868 | 0.76558 | 0.14575 | 1.58 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-11-28 | 10 | 12.7041 | 6.9282 | 19.6323 | 0.67047 | 0.76558 | 0.14595 | 1.582 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-11-28 | 11 | 13.0599 | 7.051 | 20.1109 | 0.70355 | 0.76558 | 0.14951 | 1.6186 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-28 | 12 | 13.2973 | 7.2003 | 20.4976 | 0.73087 | 0.76558 | 0.15238 | 1.6488 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-28 | 13 | 14.2975 | 7.608 | 21.9055 | 0.83472 | 0.76558 | 0.16285 | 1.7631 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-28 | 14 | 15.4944 | 7.8497 | 23.3441 | 0.94796 | 0.76558 | 0.17354 | 1.8871 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-11-28 | 15 | 17.3131 | 8.2396 | 25.5527 | 1.1358 | 0.76558 | 0.18996 | 2.0914 | 8.184% | 8.708% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-11-28 | 16 | 19.0566 | 9.2128 | 28.2694 | 1.3902 | 0.76558 | 0.21016 | 2.3659 | 8.369% | 8.905% | 6.017% | 1.0913 | 1.0978 | 1.064
2010-11-28 | 17 | 20.8853 | 10.1016 | 30.9869 | 1.6703 | 0.76558 | 0.23036 | 2.6662 | 8.604% | 9.155% | 6.187% | 1.0941 | 1.1008 | 1.0659
2010-11-28 | 18 | 22.1312 | 10.816 | 32.9472 | 1.8883 | 0.76558 | 0.24493 | 2.8988 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-11-28 | 19 | 23.0943 | 11.2354 | 34.3297 | 2.0501 | 0.76558 | 0.25521 | 3.0709 | 8.945% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2010-11-28 | 20 | 22.9139 | 11.5354 | 34.4493 | 2.0644 | 0.76558 | 0.2561 | 3.0861 | 8.958% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-11-28 | 21 | 23.0204 | 11.3378 | 34.3582 | 2.0535 | 0.76558 | 0.25542 | 3.0745 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2010-11-28 | 22 | 22.5397 | 11.3886 | 33.9283 | 2.0024 | 0.76558 | 0.25223 | 3.0202 | 8.902% | 9.472% | 6.4% | 1.0977 | 1.1046 | 1.0684
2010-11-28 | 23 | 21.6965 | 10.9483 | 32.6448 | 1.8538 | 0.76558 | 0.24269 | 2.8621 | 8.767% | 9.328% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-11-28 | 24 | 21.2045 | 10.8315 | 32.036 | 1.7853 | 0.76558 | 0.23816 | 2.789 | 8.706% | 9.263% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-11-28 | 25 | 20.1768 | 10.8262 | 31.0031 | 1.672 | 0.76558 | 0.23048 | 2.6681 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-11-28 | 26 | 19.4806 | 10.347 | 29.8276 | 1.5476 | 0.76558 | 0.22174 | 2.535 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-11-28 | 27 | 19.4933 | 10.2099 | 29.7032 | 1.5348 | 0.76558 | 0.22082 | 2.5212 | 8.488% | 9.031% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-11-28 | 28 | 19.3965 | 10.101 | 29.4975 | 1.5136 | 0.76558 | 0.21929 | 2.4984 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2010-11-28 | 29 | 18.7391 | 9.7599 | 28.499 | 1.4128 | 0.76558 | 0.21186 | 2.3903 | 8.387% | 8.924% | 6.03% | 1.0916 | 1.098 | 1.0642
2010-11-28 | 30 | 18.3114 | 9.4075 | 27.7189 | 1.3366 | 0.76558 | 0.20607 | 2.3082 | 8.327% | 8.86% | 5.987% | 1.0908 | 1.0972 | 1.0637
2010-11-28 | 31 | 18.3073 | 9.2179 | 27.5253 | 1.3179 | 0.76558 | 0.20463 | 2.2881 | 8.313% | 8.845% | 5.977% | 1.0907 | 1.097 | 1.0636
2010-11-28 | 32 | 18.1207 | 9.0835 | 27.2042 | 1.2874 | 0.76558 | 0.20224 | 2.2552 | 8.29% | 8.82% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-11-28 | 33 | 18.3696 | 9.2867 | 27.6562 | 1.3305 | 0.76558 | 0.2056 | 2.3017 | 8.323% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-11-28 | 34 | 18.3146 | 9.4322 | 27.7468 | 1.3392 | 0.76558 | 0.20627 | 2.3111 | 8.329% | 8.862% | 5.989% | 1.0909 | 1.0972 | 1.0637
2010-11-28 | 35 | 18.4601 | 9.8027 | 28.2629 | 1.3895 | 0.76558 | 0.21011 | 2.3652 | 8.369% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-11-28 | 36 | 19.0245 | 10.1611 | 29.1855 | 1.4817 | 0.76558 | 0.21697 | 2.4643 | 8.443% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-11-28 | 37 | 19.5855 | 10.4037 | 29.9891 | 1.5645 | 0.76558 | 0.22294 | 2.553 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-11-28 | 38 | 20.014 | 10.3064 | 30.3204 | 1.5992 | 0.76558 | 0.22541 | 2.5902 | 8.543% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-11-28 | 39 | 20.0588 | 10.2919 | 30.3507 | 1.6024 | 0.76558 | 0.22563 | 2.5936 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-11-28 | 40 | 19.9643 | 10.1458 | 30.1101 | 1.5771 | 0.76558 | 0.22384 | 2.5665 | 8.524% | 9.069% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-11-28 | 41 | 19.9066 | 9.7771 | 29.6837 | 1.5328 | 0.76558 | 0.22067 | 2.519 | 8.486% | 9.029% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-11-28 | 42 | 19.8594 | 9.8056 | 29.665 | 1.5308 | 0.76558 | 0.22053 | 2.5169 | 8.485% | 9.028% | 6.1% | 1.0927 | 1.0992 | 1.065
2010-11-28 | 43 | 20.1005 | 10.0179 | 30.1184 | 1.578 | 0.76558 | 0.2239 | 2.5674 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-11-28 | 44 | 20.472 | 10.0691 | 30.5411 | 1.6226 | 0.76558 | 0.22705 | 2.6152 | 8.563% | 9.111% | 6.157% | 1.0936 | 1.1002 | 1.0656
2010-11-28 | 45 | 19.7907 | 9.7946 | 29.5852 | 1.5226 | 0.76558 | 0.21994 | 2.5081 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-11-28 | 46 | 18.9093 | 9.2432 | 28.1525 | 1.3787 | 0.76558 | 0.20929 | 2.3536 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-11-28 | 47 | 17.8813 | 9.0141 | 26.8954 | 1.2583 | 0.76558 | 0.19994 | 2.2238 | 8.268% | 8.798% | 5.945% | 1.0901 | 1.0965 | 1.0632
2010-11-28 | 48 | 16.805 | 9.2672 | 26.0722 | 1.1825 | 0.76558 | 0.19382 | 2.1419 | 8.215% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-11-29 | 1 | 15.3277 | 8.5066 | 23.8343 | 0.98819 | 0.76558 | 0.17719 | 1.931 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-11-29 | 2 | 14.0844 | 7.9179 | 22.0023 | 0.84211 | 0.76558 | 0.16357 | 1.7713 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-11-29 | 3 | 13.348 | 7.5897 | 20.9377 | 0.76259 | 0.76558 | 0.15565 | 1.6838 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-29 | 4 | 12.8676 | 7.2647 | 20.1322 | 0.70505 | 0.76558 | 0.14967 | 1.6203 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-11-29 | 5 | 12.5779 | 7.1085 | 19.6864 | 0.67417 | 0.76558 | 0.14635 | 1.5861 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-11-29 | 6 | 12.0542 | 7.0572 | 19.1114 | 0.63536 | 0.76558 | 0.14208 | 1.543 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-11-29 | 7 | 11.8026 | 7.1277 | 18.9303 | 0.62337 | 0.76558 | 0.14073 | 1.5297 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-11-29 | 8 | 11.8022 | 7.1573 | 18.9594 | 0.6253 | 0.76558 | 0.14095 | 1.5318 | 8.079% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-11-29 | 9 | 11.8297 | 7.2158 | 19.0455 | 0.63099 | 0.76558 | 0.14159 | 1.5382 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2010-11-29 | 10 | 11.8986 | 7.6256 | 19.5243 | 0.66311 | 0.76558 | 0.14515 | 1.5738 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-11-29 | 11 | 12.3045 | 8.1719 | 20.4764 | 0.72936 | 0.76558 | 0.15222 | 1.6472 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-29 | 12 | 12.2671 | 8.4859 | 20.753 | 0.7492 | 0.76558 | 0.15428 | 1.6691 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-11-29 | 13 | 12.8072 | 8.6832 | 21.4903 | 0.80338 | 0.76558 | 0.15976 | 1.7287 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-11-29 | 14 | 13.8171 | 8.6468 | 22.4639 | 0.87782 | 0.76558 | 0.167 | 1.8104 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-11-29 | 15 | 15.3194 | 8.6048 | 23.9242 | 0.99565 | 0.76558 | 0.17786 | 1.9391 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-11-29 | 16 | 16.8875 | 9.5556 | 26.4431 | 1.2164 | 0.76558 | 0.19658 | 2.1785 | 8.238% | 8.766% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-11-29 | 17 | 18.9827 | 10.423 | 29.4056 | 1.5042 | 0.76558 | 0.21861 | 2.4883 | 8.462% | 9.004% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-11-29 | 18 | 20.5083 | 10.7934 | 31.3018 | 1.7044 | 0.76558 | 0.2327 | 2.7027 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-11-29 | 19 | 21.2353 | 10.8791 | 32.1144 | 1.794 | 0.76558 | 0.23874 | 2.7984 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-11-29 | 20 | 21.3807 | 11.1487 | 32.5294 | 1.8407 | 0.76558 | 0.24183 | 2.8481 | 8.756% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-11-29 | 21 | 21.2921 | 10.6587 | 31.9507 | 1.7758 | 0.76558 | 0.23753 | 2.7789 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-11-29 | 22 | 21.5325 | 10.6967 | 32.2292 | 1.8069 | 0.76558 | 0.2396 | 2.8121 | 8.725% | 9.284% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-11-29 | 23 | 21.0669 | 10.6345 | 31.7014 | 1.7482 | 0.76558 | 0.23567 | 2.7495 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2010-11-29 | 24 | 20.5164 | 10.6788 | 31.1952 | 1.6928 | 0.76558 | 0.23191 | 2.6903 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-11-29 | 25 | 19.7722 | 10.4868 | 30.259 | 1.5927 | 0.76558 | 0.22495 | 2.5833 | 8.537% | 9.084% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-11-29 | 26 | 19.1242 | 10.1831 | 29.3074 | 1.4941 | 0.76558 | 0.21787 | 2.4776 | 8.454% | 8.995% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-11-29 | 27 | 18.7776 | 10.1828 | 28.9603 | 1.459 | 0.76558 | 0.21529 | 2.4398 | 8.425% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2010-11-29 | 28 | 18.423 | 10.0632 | 28.4862 | 1.4116 | 0.76558 | 0.21177 | 2.3889 | 8.386% | 8.923% | 6.03% | 1.0915 | 1.098 | 1.0642
2010-11-29 | 29 | 18.0332 | 9.7679 | 27.8011 | 1.3445 | 0.76558 | 0.20668 | 2.3168 | 8.333% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-11-29 | 30 | 17.8199 | 9.4795 | 27.2994 | 1.2964 | 0.76558 | 0.20295 | 2.2649 | 8.297% | 8.828% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-11-29 | 31 | 18.0844 | 9.2283 | 27.3127 | 1.2977 | 0.76558 | 0.20305 | 2.2663 | 8.298% | 8.829% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-11-29 | 32 | 17.6981 | 9.0657 | 26.7639 | 1.246 | 0.76558 | 0.19897 | 2.2106 | 8.26% | 8.788% | 5.939% | 1.09 | 1.0963 | 1.0631
2010-11-29 | 33 | 17.8564 | 9.4494 | 27.3058 | 1.297 | 0.76558 | 0.20299 | 2.2656 | 8.297% | 8.828% | 5.966% | 1.0905 | 1.0968 | 1.0634
2010-11-29 | 34 | 17.9459 | 9.4638 | 27.4097 | 1.3069 | 0.76558 | 0.20377 | 2.2762 | 8.305% | 8.836% | 5.971% | 1.0906 | 1.0969 | 1.0635
2010-11-29 | 35 | 18.5896 | 9.9645 | 28.5541 | 1.4183 | 0.76558 | 0.21227 | 2.3962 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2010-11-29 | 36 | 19.2393 | 10.372 | 29.6113 | 1.5253 | 0.76558 | 0.22013 | 2.511 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2010-11-29 | 37 | 20.127 | 10.712 | 30.8389 | 1.6544 | 0.76558 | 0.22926 | 2.6492 | 8.59% | 9.14% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-11-29 | 38 | 20.5537 | 10.9322 | 31.4859 | 1.7245 | 0.76558 | 0.23407 | 2.7242 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-11-29 | 39 | 21.0515 | 10.9195 | 31.971 | 1.7781 | 0.76558 | 0.23768 | 2.7813 | 8.7% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-11-29 | 40 | 20.9178 | 10.4732 | 31.391 | 1.7141 | 0.76558 | 0.23336 | 2.7131 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-11-29 | 41 | 21.2323 | 10.4395 | 31.6718 | 1.7449 | 0.76558 | 0.23545 | 2.746 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2010-11-29 | 42 | 21.5968 | 10.5008 | 32.0976 | 1.7922 | 0.76558 | 0.23862 | 2.7964 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-11-29 | 43 | 21.4256 | 10.4902 | 31.9157 | 1.7719 | 0.76558 | 0.23727 | 2.7748 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2010-11-29 | 44 | 21.5188 | 10.2959 | 31.8147 | 1.7607 | 0.76558 | 0.23651 | 2.7628 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-11-29 | 45 | 20.1599 | 9.4868 | 29.6467 | 1.5289 | 0.76558 | 0.2204 | 2.5149 | 8.483% | 9.026% | 6.099% | 1.0927 | 1.0992 | 1.065
2010-11-29 | 46 | 18.872 | 8.7539 | 27.6259 | 1.3276 | 0.76558 | 0.20537 | 2.2986 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2010-11-29 | 47 | 17.3986 | 8.3634 | 25.762 | 1.1545 | 0.76558 | 0.19152 | 2.1116 | 8.197% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-11-29 | 48 | 16.4048 | 8.516 | 24.9209 | 1.0803 | 0.76558 | 0.18526 | 2.0312 | 8.151% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0623
2010-11-30 | 1 | 14.9788 | 7.7768 | 22.7556 | 0.90076 | 0.76558 | 0.16917 | 1.8355 | 8.066% | 8.582% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-11-30 | 2 | 13.9163 | 7.2357 | 21.152 | 0.77828 | 0.76558 | 0.15725 | 1.7011 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-11-30 | 3 | 13.0776 | 6.9076 | 19.9851 | 0.69478 | 0.76558 | 0.14857 | 1.6089 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-11-30 | 4 | 12.486 | 6.7246 | 19.2107 | 0.64198 | 0.76558 | 0.14281 | 1.5504 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-11-30 | 5 | 12.1921 | 6.52 | 18.7122 | 0.60909 | 0.76558 | 0.13911 | 1.5138 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-11-30 | 6 | 12.0769 | 6.5338 | 18.6107 | 0.6025 | 0.76558 | 0.13835 | 1.5064 | 8.094% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-11-30 | 7 | 12.0757 | 6.6491 | 18.7248 | 0.60992 | 0.76558 | 0.1392 | 1.5147 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-11-30 | 8 | 11.9045 | 6.544 | 18.4485 | 0.59205 | 0.76558 | 0.13715 | 1.4948 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-11-30 | 9 | 12.0471 | 6.5685 | 18.6156 | 0.60282 | 0.76558 | 0.13839 | 1.5068 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-11-30 | 10 | 12.1841 | 6.7732 | 18.9573 | 0.62516 | 0.76558 | 0.14093 | 1.5317 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2010-11-30 | 11 | 12.5865 | 6.8108 | 19.3973 | 0.65451 | 0.76558 | 0.1442 | 1.5643 | 8.064% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-11-30 | 12 | 13.1867 | 7.0288 | 20.2154 | 0.71089 | 0.76558 | 0.15028 | 1.6267 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-11-30 | 13 | 14.599 | 7.8447 | 22.4437 | 0.87624 | 0.76558 | 0.16685 | 1.8087 | 8.059% | 8.574% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-11-30 | 14 | 16.7578 | 8.9368 | 25.6945 | 1.1485 | 0.76558 | 0.19102 | 2.1051 | 8.193% | 8.717% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-11-30 | 15 | 20.2418 | 10.4982 | 30.74 | 1.6438 | 0.76558 | 0.22852 | 2.6379 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2010-11-30 | 16 | 22.7437 | 11.7194 | 34.4631 | 2.0661 | 0.76558 | 0.2562 | 3.0878 | 8.96% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2010-11-30 | 17 | 21.6051 | 11.0677 | 32.6728 | 1.857 | 0.76558 | 0.24289 | 2.8655 | 8.77% | 9.331% | 6.306% | 1.0961 | 1.1029 | 1.0673
2010-11-30 | 18 | 21.9245 | 11.0536 | 32.9781 | 1.8918 | 0.76558 | 0.24516 | 2.9026 | 8.802% | 9.365% | 6.328% | 1.0965 | 1.1033 | 1.0676
2010-11-30 | 19 | 24.0679 | 11.9984 | 36.0663 | 2.2628 | 0.76558 | 0.26812 | 3.2965 | 9.14% | 9.725% | 6.572% | 1.1006 | 1.1077 | 1.0703
2010-11-30 | 20 | 23.8267 | 12.1375 | 35.9642 | 2.25 | 0.76558 | 0.26736 | 3.2829 | 9.128% | 9.712% | 6.563% | 1.1005 | 1.1076 | 1.0702
2010-11-30 | 21 | 25.1602 | 12.659 | 37.8192 | 2.488 | 0.76558 | 0.28115 | 3.5348 | 9.347% | 9.945% | 6.72% | 1.1031 | 1.1104 | 1.072
2010-11-30 | 22 | 24.9699 | 12.7316 | 37.7015 | 2.4726 | 0.76558 | 0.28028 | 3.5184 | 9.332% | 9.93% | 6.71% | 1.1029 | 1.1102 | 1.0719
2010-11-30 | 23 | 25.1822 | 12.8666 | 38.0488 | 2.5184 | 0.76558 | 0.28286 | 3.5668 | 9.374% | 9.974% | 6.74% | 1.1034 | 1.1108 | 1.0723
2010-11-30 | 24 | 23.6159 | 12.1789 | 35.7948 | 2.2288 | 0.76558 | 0.2661 | 3.2605 | 9.109% | 9.692% | 6.549% | 1.1002 | 1.1073 | 1.0701
2010-11-30 | 25 | 22.6583 | 11.8717 | 34.53 | 2.0741 | 0.76558 | 0.2567 | 3.0964 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-11-30 | 26 | 22.0475 | 11.3537 | 33.4012 | 1.9407 | 0.76558 | 0.24831 | 2.9546 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-11-30 | 27 | 21.6885 | 11.3677 | 33.0562 | 1.9008 | 0.76558 | 0.24574 | 2.9121 | 8.81% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-11-30 | 28 | 21.5532 | 11.004 | 32.5573 | 1.8439 | 0.76558 | 0.24203 | 2.8515 | 8.758% | 9.319% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-11-30 | 29 | 20.7275 | 10.7355 | 31.463 | 1.722 | 0.76558 | 0.2339 | 2.7215 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-11-30 | 30 | 20.3645 | 10.5628 | 30.9273 | 1.6639 | 0.76558 | 0.22992 | 2.6594 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-11-30 | 31 | 20.2884 | 10.3536 | 30.642 | 1.6333 | 0.76558 | 0.2278 | 2.6267 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2010-11-30 | 32 | 20.2631 | 10.6062 | 30.8693 | 1.6576 | 0.76558 | 0.22949 | 2.6527 | 8.593% | 9.143% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-11-30 | 33 | 20.5489 | 11.0062 | 31.555 | 1.7321 | 0.76558 | 0.23458 | 2.7323 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-11-30 | 34 | 20.5934 | 10.9598 | 31.5532 | 1.7319 | 0.76558 | 0.23457 | 2.732 | 8.659% | 9.213% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-11-30 | 35 | 20.735 | 11.1722 | 31.9072 | 1.771 | 0.76558 | 0.2372 | 2.7738 | 8.693% | 9.25% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-11-30 | 36 | 21.8777 | 11.833 | 33.7107 | 1.9768 | 0.76558 | 0.25061 | 2.993 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-11-30 | 37 | 22.8676 | 12.232 | 35.0996 | 2.1431 | 0.76558 | 0.26093 | 3.1696 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-11-30 | 38 | 23.2273 | 12.1913 | 35.4186 | 2.1822 | 0.76558 | 0.26331 | 3.2111 | 9.066% | 9.646% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-11-30 | 39 | 23.2538 | 11.956 | 35.2098 | 2.1566 | 0.76558 | 0.26175 | 3.1839 | 9.043% | 9.621% | 6.502% | 1.0994 | 1.1065 | 1.0695
2010-11-30 | 40 | 23.1997 | 11.7321 | 34.9318 | 2.1226 | 0.76558 | 0.25969 | 3.1479 | 9.012% | 9.588% | 6.479% | 1.099 | 1.1061 | 1.0693
2010-11-30 | 41 | 23.5134 | 11.7767 | 35.2901 | 2.1664 | 0.76558 | 0.26235 | 3.1943 | 9.052% | 9.631% | 6.508% | 1.0995 | 1.1066 | 1.0696
2010-11-30 | 42 | 23.733 | 11.7089 | 35.4418 | 2.1851 | 0.76558 | 0.26348 | 3.2141 | 9.069% | 9.649% | 6.52% | 1.0997 | 1.1068 | 1.0698
2010-11-30 | 43 | 23.4626 | 11.609 | 35.0716 | 2.1397 | 0.76558 | 0.26073 | 3.166 | 9.027% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-11-30 | 44 | 23.3681 | 11.2156 | 34.5837 | 2.0805 | 0.76558 | 0.2571 | 3.1032 | 8.973% | 9.547% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-11-30 | 45 | 21.832 | 10.3574 | 32.1894 | 1.8024 | 0.76558 | 0.2393 | 2.8073 | 8.721% | 9.279% | 6.271% | 1.0955 | 1.1023 | 1.0669
2010-11-30 | 46 | 20.1434 | 9.3844 | 29.5279 | 1.5167 | 0.76558 | 0.21951 | 2.5018 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2010-11-30 | 47 | 18.3168 | 8.9332 | 27.2499 | 1.2917 | 0.76558 | 0.20258 | 2.2599 | 8.293% | 8.824% | 5.963% | 1.0904 | 1.0968 | 1.0634
2010-11-30 | 48 | 17.0552 | 8.9955 | 26.0507 | 1.1805 | 0.76558 | 0.19366 | 2.1398 | 8.214% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2010-12-01 | 1 | 15.5022 | 8.1807 | 23.6829 | 0.97568 | 0.76558 | 0.17606 | 1.9173 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-12-01 | 2 | 14.3732 | 7.5481 | 21.9213 | 0.83593 | 0.76558 | 0.16297 | 1.7645 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-01 | 3 | 13.6871 | 7.2242 | 20.9114 | 0.76068 | 0.76558 | 0.15546 | 1.6817 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-01 | 4 | 13.1611 | 6.9753 | 20.1365 | 0.70535 | 0.76558 | 0.1497 | 1.6206 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-01 | 5 | 12.8196 | 6.9695 | 19.7891 | 0.68122 | 0.76558 | 0.14711 | 1.5939 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-01 | 6 | 12.4433 | 6.8649 | 19.3083 | 0.64852 | 0.76558 | 0.14354 | 1.5576 | 8.067% | 8.583% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-12-01 | 7 | 12.2119 | 6.9336 | 19.1454 | 0.63762 | 0.76558 | 0.14233 | 1.5455 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-01 | 8 | 12.2096 | 6.8753 | 19.0849 | 0.6336 | 0.76558 | 0.14188 | 1.5411 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-01 | 9 | 12.3813 | 6.7093 | 19.0906 | 0.63398 | 0.76558 | 0.14192 | 1.5415 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-01 | 10 | 12.5798 | 6.6637 | 19.2435 | 0.64417 | 0.76558 | 0.14306 | 1.5528 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-01 | 11 | 12.9328 | 6.9765 | 19.9093 | 0.68952 | 0.76558 | 0.14801 | 1.6031 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-12-01 | 12 | 13.1873 | 7.2727 | 20.46 | 0.72819 | 0.76558 | 0.1521 | 1.6459 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-01 | 13 | 14.9543 | 7.9198 | 22.8741 | 0.91017 | 0.76558 | 0.17005 | 1.8458 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-01 | 14 | 17.1746 | 9.263 | 26.4377 | 1.2159 | 0.76558 | 0.19654 | 2.178 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2010-12-01 | 15 | 20.269 | 10.6916 | 30.9606 | 1.6675 | 0.76558 | 0.23016 | 2.6632 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-12-01 | 16 | 22.5904 | 11.5447 | 34.1351 | 2.0269 | 0.76558 | 0.25376 | 3.0463 | 8.924% | 9.495% | 6.416% | 1.098 | 1.1049 | 1.0686
2010-12-01 | 17 | 22.5355 | 11.4936 | 34.0291 | 2.0144 | 0.76558 | 0.25298 | 3.0329 | 8.913% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2010-12-01 | 18 | 23.7649 | 11.9443 | 35.7091 | 2.2182 | 0.76558 | 0.26547 | 3.2492 | 9.099% | 9.681% | 6.542% | 1.1001 | 1.1072 | 1.07
2010-12-01 | 19 | 23.5251 | 11.5566 | 35.0817 | 2.1409 | 0.76558 | 0.2608 | 3.1673 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-12-01 | 20 | 22.8306 | 11.2088 | 34.0394 | 2.0156 | 0.76558 | 0.25305 | 3.0342 | 8.914% | 9.484% | 6.409% | 1.0979 | 1.1048 | 1.0685
2010-12-01 | 21 | 22.77 | 10.9182 | 33.6882 | 1.9742 | 0.76558 | 0.25044 | 2.9902 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2010-12-01 | 22 | 21.9518 | 10.8214 | 32.7732 | 1.8684 | 0.76558 | 0.24364 | 2.8776 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.1031 | 1.0674
2010-12-01 | 23 | 21.3264 | 10.5013 | 31.8277 | 1.7622 | 0.76558 | 0.23661 | 2.7643 | 8.685% | 9.241% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-12-01 | 24 | 20.8387 | 10.3333 | 31.172 | 1.6903 | 0.76558 | 0.23174 | 2.6876 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2010-12-01 | 25 | 20.2756 | 10.5159 | 30.7915 | 1.6493 | 0.76558 | 0.22891 | 2.6438 | 8.586% | 9.136% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-12-01 | 26 | 19.9175 | 10.2028 | 30.1204 | 1.5782 | 0.76558 | 0.22392 | 2.5677 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-12-01 | 27 | 19.8622 | 10.2665 | 30.1287 | 1.579 | 0.76558 | 0.22398 | 2.5686 | 8.525% | 9.071% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-12-01 | 28 | 20.0159 | 10.2834 | 30.2994 | 1.597 | 0.76558 | 0.22525 | 2.5878 | 8.541% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-12-01 | 29 | 19.5556 | 9.9946 | 29.5502 | 1.519 | 0.76558 | 0.21968 | 2.5042 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-12-01 | 30 | 19.3396 | 9.9679 | 29.3075 | 1.4941 | 0.76558 | 0.21788 | 2.4776 | 8.454% | 8.995% | 6.078% | 1.0923 | 1.0988 | 1.0647
2010-12-01 | 31 | 19.2553 | 10.0303 | 29.2855 | 1.4919 | 0.76558 | 0.21771 | 2.4752 | 8.452% | 8.993% | 6.077% | 1.0923 | 1.0988 | 1.0647
2010-12-01 | 32 | 19.315 | 10.0054 | 29.3204 | 1.4955 | 0.76558 | 0.21797 | 2.479 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2010-12-01 | 33 | 19.7398 | 10.2887 | 30.0285 | 1.5686 | 0.76558 | 0.22324 | 2.5574 | 8.516% | 9.062% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-12-01 | 34 | 20.2341 | 10.447 | 30.6812 | 1.6375 | 0.76558 | 0.22809 | 2.6312 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-12-01 | 35 | 20.8501 | 11.03 | 31.8801 | 1.768 | 0.76558 | 0.237 | 2.7705 | 8.691% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-12-01 | 36 | 21.5441 | 11.919 | 33.4631 | 1.9479 | 0.76558 | 0.24877 | 2.9622 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2010-12-01 | 37 | 22.1106 | 12.3738 | 34.4844 | 2.0686 | 0.76558 | 0.25636 | 3.0906 | 8.962% | 9.536% | 6.444% | 1.0984 | 1.1054 | 1.0689
2010-12-01 | 38 | 22.1619 | 12.3146 | 34.4766 | 2.0677 | 0.76558 | 0.2563 | 3.0896 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2010-12-01 | 39 | 22.1201 | 12.0392 | 34.1593 | 2.0298 | 0.76558 | 0.25394 | 3.0493 | 8.927% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-12-01 | 40 | 22.1204 | 11.7153 | 33.8357 | 1.9915 | 0.76558 | 0.25154 | 3.0086 | 8.892% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-12-01 | 41 | 22.2457 | 11.23 | 33.4757 | 1.9494 | 0.76558 | 0.24886 | 2.9638 | 8.854% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2010-12-01 | 42 | 22.804 | 11.0794 | 33.8834 | 1.9971 | 0.76558 | 0.25189 | 3.0146 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-12-01 | 43 | 22.766 | 10.9057 | 33.6718 | 1.9723 | 0.76558 | 0.25032 | 2.9882 | 8.874% | 9.442% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-12-01 | 44 | 22.7754 | 10.6458 | 33.4212 | 1.943 | 0.76558 | 0.24846 | 2.9571 | 8.848% | 9.414% | 6.362% | 1.0971 | 1.1039 | 1.0679
2010-12-01 | 45 | 21.3392 | 9.9255 | 31.2648 | 1.7004 | 0.76558 | 0.23243 | 2.6984 | 8.631% | 9.183% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-12-01 | 46 | 19.7259 | 9.111 | 28.8369 | 1.4465 | 0.76558 | 0.21438 | 2.4265 | 8.415% | 8.953% | 6.05% | 1.0919 | 1.0983 | 1.0644
2010-12-01 | 47 | 18.1019 | 8.5457 | 26.6476 | 1.2352 | 0.76558 | 0.1981 | 2.1989 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0963 | 1.0631
2010-12-01 | 48 | 16.762 | 8.5455 | 25.3075 | 1.1141 | 0.76558 | 0.18814 | 2.0678 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2010-12-02 | 1 | 15.1542 | 7.5635 | 22.7177 | 0.89776 | 0.76558 | 0.16889 | 1.8322 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-02 | 2 | 13.9488 | 7.0981 | 21.0469 | 0.77057 | 0.76558 | 0.15647 | 1.6926 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-02 | 3 | 13.1912 | 6.8318 | 20.023 | 0.69742 | 0.76558 | 0.14885 | 1.6118 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-02 | 4 | 12.8063 | 6.7318 | 19.5381 | 0.66405 | 0.76558 | 0.14525 | 1.5749 | 8.061% | 8.576% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-02 | 5 | 12.4798 | 6.5806 | 19.0604 | 0.63197 | 0.76558 | 0.1417 | 1.5393 | 8.076% | 8.592% | 5.806% | 1.0879 | 1.094 | 1.0616
2010-12-02 | 6 | 12.4104 | 6.664 | 19.0744 | 0.6329 | 0.76558 | 0.1418 | 1.5403 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-02 | 7 | 12.1201 | 6.609 | 18.7291 | 0.61019 | 0.76558 | 0.13923 | 1.515 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-12-02 | 8 | 12.0123 | 6.5445 | 18.5568 | 0.59902 | 0.76558 | 0.13795 | 1.5026 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-12-02 | 9 | 12.3104 | 6.5638 | 18.8742 | 0.61969 | 0.76558 | 0.14031 | 1.5256 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-12-02 | 10 | 12.3369 | 6.553 | 18.8899 | 0.62072 | 0.76558 | 0.14043 | 1.5267 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-02 | 11 | 12.7369 | 6.8653 | 19.6022 | 0.66841 | 0.76558 | 0.14573 | 1.5797 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-12-02 | 12 | 13.1234 | 7.0623 | 20.1857 | 0.7088 | 0.76558 | 0.15006 | 1.6244 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-02 | 13 | 14.9083 | 7.8168 | 22.7251 | 0.89835 | 0.76558 | 0.16894 | 1.8329 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-02 | 14 | 17.2483 | 9.0056 | 26.2539 | 1.199 | 0.76558 | 0.19517 | 2.1598 | 8.226% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2010-12-02 | 15 | 20.8595 | 10.6833 | 31.5428 | 1.7308 | 0.76558 | 0.23449 | 2.7308 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-12-02 | 16 | 23.5977 | 11.5367 | 35.1344 | 2.1473 | 0.76558 | 0.26119 | 3.1741 | 9.034% | 9.612% | 6.496% | 1.0993 | 1.1063 | 1.0695
2010-12-02 | 17 | 25.2899 | 12.2815 | 37.5714 | 2.4556 | 0.76558 | 0.27931 | 3.5004 | 9.317% | 9.913% | 6.699% | 1.1027 | 1.11 | 1.0718
2010-12-02 | 18 | 25.6484 | 12.4355 | 38.0839 | 2.523 | 0.76558 | 0.28312 | 3.5717 | 9.379% | 9.979% | 6.743% | 1.1035 | 1.1108 | 1.0723
2010-12-02 | 19 | 25.4291 | 12.2356 | 37.6647 | 2.4678 | 0.76558 | 0.28 | 3.5133 | 9.328% | 9.925% | 6.707% | 1.1029 | 1.1102 | 1.0719
2010-12-02 | 20 | 24.7497 | 12.0579 | 36.8076 | 2.3567 | 0.76558 | 0.27363 | 3.3959 | 9.226% | 9.817% | 6.634% | 1.1016 | 1.1089 | 1.071
2010-12-02 | 21 | 24.7573 | 11.8554 | 36.6127 | 2.3318 | 0.76558 | 0.27218 | 3.3696 | 9.203% | 9.792% | 6.617% | 1.1014 | 1.1086 | 1.0709
2010-12-02 | 22 | 23.3571 | 11.9866 | 35.3437 | 2.173 | 0.76558 | 0.26275 | 3.2013 | 9.058% | 9.637% | 6.512% | 1.0996 | 1.1067 | 1.0697
2010-12-02 | 23 | 24.6559 | 12.209 | 36.8649 | 2.3641 | 0.76558 | 0.27406 | 3.4037 | 9.233% | 9.824% | 6.638% | 1.1017 | 1.1089 | 1.0711
2010-12-02 | 24 | 24.4916 | 11.7248 | 36.2164 | 2.2816 | 0.76558 | 0.26924 | 3.3164 | 9.157% | 9.743% | 6.584% | 1.1008 | 1.108 | 1.0705
2010-12-02 | 25 | 23.7938 | 11.7657 | 35.5595 | 2.1996 | 0.76558 | 0.26435 | 3.2295 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-12-02 | 26 | 23.0959 | 11.3006 | 34.3965 | 2.0581 | 0.76558 | 0.25571 | 3.0794 | 8.953% | 9.526% | 6.437% | 1.0983 | 1.1053 | 1.0688
2010-12-02 | 27 | 22.6822 | 11.4101 | 34.0923 | 2.0218 | 0.76558 | 0.25345 | 3.0409 | 8.92% | 9.49% | 6.413% | 1.0979 | 1.1049 | 1.0685
2010-12-02 | 28 | 22.2451 | 11.3526 | 33.5977 | 1.9636 | 0.76558 | 0.24977 | 2.9789 | 8.867% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-12-02 | 29 | 21.6882 | 10.9139 | 32.6021 | 1.849 | 0.76558 | 0.24237 | 2.8569 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-12-02 | 30 | 21.2826 | 10.7635 | 32.0461 | 1.7864 | 0.76558 | 0.23823 | 2.7902 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-12-02 | 31 | 21.2793 | 10.659 | 31.9383 | 1.7744 | 0.76558 | 0.23743 | 2.7774 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-12-02 | 32 | 21.3833 | 10.7569 | 32.1401 | 1.7969 | 0.76558 | 0.23893 | 2.8014 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-12-02 | 33 | 21.7925 | 10.9499 | 32.7424 | 1.8649 | 0.76558 | 0.24341 | 2.8739 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-12-02 | 34 | 22.2656 | 11.1205 | 33.3861 | 1.9389 | 0.76558 | 0.2482 | 2.9527 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-12-02 | 35 | 22.4975 | 11.5456 | 34.043 | 2.016 | 0.76558 | 0.25308 | 3.0347 | 8.914% | 9.485% | 6.409% | 1.0979 | 1.1048 | 1.0685
2010-12-02 | 36 | 22.9496 | 12.4318 | 35.3814 | 2.1776 | 0.76558 | 0.26303 | 3.2062 | 9.062% | 9.642% | 6.516% | 1.0996 | 1.1067 | 1.0697
2010-12-02 | 37 | 23.9647 | 12.4597 | 36.4243 | 2.3079 | 0.76558 | 0.27078 | 3.3443 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-12-02 | 38 | 24.8211 | 12.1976 | 37.0187 | 2.3838 | 0.76558 | 0.2752 | 3.4246 | 9.251% | 9.843% | 6.652% | 1.1019 | 1.1092 | 1.0713
2010-12-02 | 39 | 24.9052 | 12.0753 | 36.9805 | 2.3789 | 0.76558 | 0.27492 | 3.4194 | 9.247% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2010-12-02 | 40 | 24.3688 | 11.7279 | 36.0967 | 2.2666 | 0.76558 | 0.26835 | 3.3005 | 9.143% | 9.729% | 6.574% | 1.1006 | 1.1078 | 1.0704
2010-12-02 | 41 | 23.8058 | 11.4329 | 35.2388 | 2.1601 | 0.76558 | 0.26197 | 3.1877 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2010-12-02 | 42 | 23.8418 | 11.2604 | 35.1022 | 2.1434 | 0.76558 | 0.26095 | 3.1699 | 9.031% | 9.609% | 6.493% | 1.0993 | 1.1063 | 1.0694
2010-12-02 | 43 | 23.7711 | 11.0626 | 34.8337 | 2.1107 | 0.76558 | 0.25896 | 3.1353 | 9.001% | 9.577% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-12-02 | 44 | 23.8419 | 10.756 | 34.5979 | 2.0823 | 0.76558 | 0.2572 | 3.105 | 8.975% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2010-12-02 | 45 | 22.4927 | 9.8989 | 32.3916 | 1.8252 | 0.76558 | 0.2408 | 2.8315 | 8.742% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-12-02 | 46 | 20.6727 | 8.9497 | 29.6223 | 1.5264 | 0.76558 | 0.22022 | 2.5122 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-12-02 | 47 | 18.651 | 8.4385 | 27.0895 | 1.2765 | 0.76558 | 0.20139 | 2.2435 | 8.282% | 8.812% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-12-02 | 48 | 17.467 | 8.4533 | 25.9203 | 1.1687 | 0.76558 | 0.19269 | 2.127 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-12-03 | 1 | 16.0373 | 7.6798 | 23.717 | 0.97849 | 0.76558 | 0.17632 | 1.9204 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-12-03 | 2 | 14.8613 | 7.1627 | 22.024 | 0.84378 | 0.76558 | 0.16373 | 1.7731 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-12-03 | 3 | 13.9136 | 6.8622 | 20.7758 | 0.75084 | 0.76558 | 0.15445 | 1.6709 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-03 | 4 | 13.3188 | 6.8019 | 20.1207 | 0.70424 | 0.76558 | 0.14958 | 1.6194 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-03 | 5 | 13.073 | 6.6569 | 19.7299 | 0.67715 | 0.76558 | 0.14667 | 1.5894 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-03 | 6 | 13.0055 | 6.5211 | 19.5266 | 0.66326 | 0.76558 | 0.14516 | 1.574 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-03 | 7 | 12.8388 | 6.4845 | 19.3233 | 0.64953 | 0.76558 | 0.14365 | 1.5588 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-12-03 | 8 | 12.7812 | 6.6515 | 19.4327 | 0.6569 | 0.76558 | 0.14446 | 1.5669 | 8.063% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-12-03 | 9 | 13.0889 | 6.7455 | 19.8344 | 0.68434 | 0.76558 | 0.14745 | 1.5974 | 8.054% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-03 | 10 | 13.2531 | 6.8828 | 20.1359 | 0.7053 | 0.76558 | 0.14969 | 1.6206 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-03 | 11 | 13.7407 | 7.0733 | 20.814 | 0.75361 | 0.76558 | 0.15473 | 1.6739 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-03 | 12 | 14.1517 | 7.319 | 21.4707 | 0.80191 | 0.76558 | 0.15962 | 1.7271 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-03 | 13 | 15.6805 | 7.8992 | 23.5797 | 0.96719 | 0.76558 | 0.17529 | 1.9081 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-12-03 | 14 | 18.1402 | 9.052 | 27.1921 | 1.2862 | 0.76558 | 0.20215 | 2.254 | 8.289% | 8.82% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-12-03 | 15 | 21.2388 | 10.6442 | 31.8829 | 1.7683 | 0.76558 | 0.23702 | 2.7709 | 8.691% | 9.247% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-12-03 | 16 | 23.347 | 11.4366 | 34.7836 | 2.1047 | 0.76558 | 0.25859 | 3.1288 | 8.995% | 9.571% | 6.468% | 1.0988 | 1.1058 | 1.0691
2010-12-03 | 17 | 22.4217 | 10.8065 | 33.2282 | 1.9207 | 0.76558 | 0.24702 | 2.9333 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2010-12-03 | 18 | 25.1377 | 12.2796 | 37.4173 | 2.4355 | 0.76558 | 0.27816 | 3.4792 | 9.298% | 9.893% | 6.686% | 1.1025 | 1.1098 | 1.0716
2010-12-03 | 19 | 24.6818 | 11.7921 | 36.4738 | 2.3142 | 0.76558 | 0.27115 | 3.3509 | 9.187% | 9.775% | 6.606% | 1.1012 | 1.1083 | 1.0707
2010-12-03 | 20 | 23.3158 | 11.2331 | 34.5489 | 2.0764 | 0.76558 | 0.25684 | 3.0988 | 8.969% | 9.543% | 6.449% | 1.0985 | 1.1055 | 1.0689
2010-12-03 | 21 | 22.8941 | 10.6421 | 33.5362 | 1.9564 | 0.76558 | 0.24931 | 2.9713 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2010-12-03 | 22 | 22.0454 | 10.4695 | 32.5149 | 1.8391 | 0.76558 | 0.24172 | 2.8464 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2010-12-03 | 23 | 21.5091 | 10.3172 | 31.8263 | 1.762 | 0.76558 | 0.2366 | 2.7642 | 8.685% | 9.241% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-12-03 | 24 | 20.9332 | 10.2565 | 31.1897 | 1.6922 | 0.76558 | 0.23187 | 2.6897 | 8.624% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-12-03 | 25 | 20.4434 | 10.1503 | 30.5937 | 1.6282 | 0.76558 | 0.22744 | 2.6212 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-12-03 | 26 | 19.9771 | 10.0949 | 30.072 | 1.5731 | 0.76558 | 0.22356 | 2.5622 | 8.52% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-12-03 | 27 | 19.9122 | 10.0536 | 29.9658 | 1.562 | 0.76558 | 0.22277 | 2.5504 | 8.511% | 9.056% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-12-03 | 28 | 19.8557 | 9.9083 | 29.764 | 1.541 | 0.76558 | 0.22127 | 2.5279 | 8.493% | 9.037% | 6.107% | 1.0928 | 1.0993 | 1.065
2010-12-03 | 29 | 19.4309 | 9.7772 | 29.2081 | 1.484 | 0.76558 | 0.21714 | 2.4667 | 8.445% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-12-03 | 30 | 18.8905 | 9.7026 | 28.5931 | 1.4222 | 0.76558 | 0.21256 | 2.4003 | 8.395% | 8.932% | 6.036% | 1.0916 | 1.0981 | 1.0642
2010-12-03 | 31 | 19.1507 | 9.6571 | 28.8079 | 1.4436 | 0.76558 | 0.21416 | 2.4234 | 8.412% | 8.951% | 6.048% | 1.0918 | 1.0983 | 1.0644
2010-12-03 | 32 | 19.0476 | 9.8019 | 28.8495 | 1.4478 | 0.76558 | 0.21447 | 2.4279 | 8.416% | 8.954% | 6.051% | 1.0919 | 1.0983 | 1.0644
2010-12-03 | 33 | 19.1742 | 10.1729 | 29.3471 | 1.4982 | 0.76558 | 0.21817 | 2.4819 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-12-03 | 34 | 19.3785 | 10.1247 | 29.5033 | 1.5142 | 0.76558 | 0.21933 | 2.4991 | 8.471% | 9.013% | 6.09% | 1.0925 | 1.0991 | 1.0649
2010-12-03 | 35 | 19.4311 | 10.401 | 29.8321 | 1.5481 | 0.76558 | 0.22178 | 2.5355 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-12-03 | 36 | 19.7712 | 10.606 | 30.3772 | 1.6052 | 0.76558 | 0.22583 | 2.5966 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2010-12-03 | 37 | 20.1586 | 10.8179 | 30.9766 | 1.6692 | 0.76558 | 0.23028 | 2.665 | 8.603% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-12-03 | 38 | 20.5709 | 10.8813 | 31.4522 | 1.7208 | 0.76558 | 0.23382 | 2.7202 | 8.649% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-03 | 39 | 21.0661 | 10.862 | 31.9281 | 1.7733 | 0.76558 | 0.23736 | 2.7762 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.1019 | 1.0667
2010-12-03 | 40 | 21.1467 | 10.6007 | 31.7474 | 1.7533 | 0.76558 | 0.23601 | 2.7549 | 8.677% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-12-03 | 41 | 20.9791 | 10.4021 | 31.3812 | 1.7131 | 0.76558 | 0.23329 | 2.7119 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-12-03 | 42 | 20.9882 | 10.5967 | 31.585 | 1.7354 | 0.76558 | 0.23481 | 2.7358 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-12-03 | 43 | 20.9218 | 10.6767 | 31.5984 | 1.7369 | 0.76558 | 0.23491 | 2.7373 | 8.663% | 9.217% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-12-03 | 44 | 21.6053 | 10.9799 | 32.5853 | 1.847 | 0.76558 | 0.24224 | 2.8549 | 8.761% | 9.322% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-12-03 | 45 | 20.6956 | 10.5354 | 31.231 | 1.6967 | 0.76558 | 0.23218 | 2.6945 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-12-03 | 46 | 19.5049 | 9.8696 | 29.3744 | 1.501 | 0.76558 | 0.21837 | 2.4849 | 8.459% | 9.001% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-12-03 | 47 | 17.7365 | 9.2404 | 26.9769 | 1.266 | 0.76558 | 0.20055 | 2.2321 | 8.274% | 8.804% | 5.949% | 1.0902 | 1.0965 | 1.0633
2010-12-03 | 48 | 16.4758 | 9.2768 | 25.7525 | 1.1537 | 0.76558 | 0.19145 | 2.1107 | 8.196% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-12-04 | 1 | 15.0262 | 8.2887 | 23.3149 | 0.94559 | 0.76558 | 0.17333 | 1.8845 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-12-04 | 2 | 13.8625 | 7.6938 | 21.5564 | 0.80832 | 0.76558 | 0.16025 | 1.7342 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-04 | 3 | 13.2543 | 7.5552 | 20.8095 | 0.75328 | 0.76558 | 0.1547 | 1.6736 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-04 | 4 | 12.5895 | 7.3506 | 19.94 | 0.69165 | 0.76558 | 0.14824 | 1.6055 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-04 | 5 | 12.3693 | 7.386 | 19.7554 | 0.6789 | 0.76558 | 0.14686 | 1.5913 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-04 | 6 | 12.1163 | 7.3717 | 19.4881 | 0.66065 | 0.76558 | 0.14488 | 1.5711 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-04 | 7 | 11.9004 | 7.312 | 19.2124 | 0.64209 | 0.76558 | 0.14283 | 1.5505 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-12-04 | 8 | 11.9916 | 7.1529 | 19.1444 | 0.63756 | 0.76558 | 0.14232 | 1.5455 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-04 | 9 | 12.1555 | 7.1034 | 19.2589 | 0.6452 | 0.76558 | 0.14317 | 1.554 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-04 | 10 | 12.2863 | 7.2153 | 19.5016 | 0.66157 | 0.76558 | 0.14498 | 1.5721 | 8.062% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-04 | 11 | 12.5905 | 7.4732 | 20.0637 | 0.70026 | 0.76558 | 0.14916 | 1.615 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-04 | 12 | 13.1097 | 8.0015 | 21.1112 | 0.77528 | 0.76558 | 0.15694 | 1.6978 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-04 | 13 | 14.3987 | 8.5667 | 22.9654 | 0.91745 | 0.76558 | 0.17073 | 1.8538 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-04 | 14 | 16.5966 | 9.4666 | 26.0631 | 1.1816 | 0.76558 | 0.19376 | 2.141 | 8.215% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2010-12-04 | 15 | 19.4981 | 10.8506 | 30.3487 | 1.6022 | 0.76558 | 0.22562 | 2.5934 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-12-04 | 16 | 21.7703 | 11.4808 | 33.2512 | 1.9233 | 0.76558 | 0.24719 | 2.9361 | 8.83% | 9.395% | 6.349% | 1.0969 | 1.1037 | 1.0678
2010-12-04 | 17 | 22.8104 | 11.7128 | 34.5232 | 2.0733 | 0.76558 | 0.25665 | 3.0955 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-12-04 | 18 | 23.208 | 11.8811 | 35.0891 | 2.1418 | 0.76558 | 0.26086 | 3.1682 | 9.029% | 9.607% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-12-04 | 19 | 22.788 | 11.7104 | 34.4985 | 2.0703 | 0.76558 | 0.25647 | 3.0923 | 8.964% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2010-12-04 | 20 | 22.5467 | 11.4242 | 33.971 | 2.0075 | 0.76558 | 0.25254 | 3.0256 | 8.906% | 9.476% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-12-04 | 21 | 22.3854 | 10.9111 | 33.2965 | 1.9286 | 0.76558 | 0.24753 | 2.9417 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2010-12-04 | 22 | 21.6337 | 10.9969 | 32.6306 | 1.8522 | 0.76558 | 0.24258 | 2.8603 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-12-04 | 23 | 20.9641 | 10.9426 | 31.9068 | 1.7709 | 0.76558 | 0.2372 | 2.7737 | 8.693% | 9.25% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-12-04 | 24 | 20.4579 | 10.9601 | 31.418 | 1.7171 | 0.76558 | 0.23357 | 2.7162 | 8.645% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-12-04 | 25 | 20.0334 | 10.8049 | 30.8383 | 1.6543 | 0.76558 | 0.22926 | 2.6491 | 8.59% | 9.14% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-12-04 | 26 | 19.3498 | 10.4119 | 29.7617 | 1.5408 | 0.76558 | 0.22125 | 2.5276 | 8.493% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-12-04 | 27 | 19.7049 | 10.625 | 30.3299 | 1.6002 | 0.76558 | 0.22548 | 2.5913 | 8.544% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2010-12-04 | 28 | 19.7802 | 10.6594 | 30.4396 | 1.6118 | 0.76558 | 0.22629 | 2.6037 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-12-04 | 29 | 19.8833 | 10.4664 | 30.3497 | 1.6023 | 0.76558 | 0.22562 | 2.5935 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-12-04 | 30 | 19.6063 | 10.2593 | 29.8656 | 1.5516 | 0.76558 | 0.22202 | 2.5392 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-12-04 | 31 | 19.6357 | 10.1117 | 29.7474 | 1.5393 | 0.76558 | 0.22115 | 2.5261 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-12-04 | 32 | 19.7083 | 10.159 | 29.8673 | 1.5518 | 0.76558 | 0.22204 | 2.5394 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-12-04 | 33 | 19.7213 | 10.4348 | 30.156 | 1.5819 | 0.76558 | 0.22418 | 2.5717 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-12-04 | 34 | 19.7755 | 10.7688 | 30.5443 | 1.6229 | 0.76558 | 0.22707 | 2.6156 | 8.563% | 9.111% | 6.157% | 1.0937 | 1.1002 | 1.0656
2010-12-04 | 35 | 19.8564 | 10.8291 | 30.6856 | 1.638 | 0.76558 | 0.22812 | 2.6317 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-12-04 | 36 | 19.8257 | 11.1864 | 31.0121 | 1.673 | 0.76558 | 0.23055 | 2.6691 | 8.607% | 9.158% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-12-04 | 37 | 19.8956 | 11.2618 | 31.1574 | 1.6887 | 0.76558 | 0.23163 | 2.6859 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-12-04 | 38 | 20.2227 | 11.3872 | 31.6099 | 1.7381 | 0.76558 | 0.23499 | 2.7387 | 8.664% | 9.219% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-12-04 | 39 | 19.8048 | 11.4025 | 31.2072 | 1.6941 | 0.76558 | 0.232 | 2.6917 | 8.625% | 9.177% | 6.202% | 1.0944 | 1.101 | 1.0661
2010-12-04 | 40 | 19.8042 | 11.2671 | 31.0713 | 1.6794 | 0.76558 | 0.23099 | 2.676 | 8.612% | 9.164% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-12-04 | 41 | 19.7946 | 11.0071 | 30.8017 | 1.6504 | 0.76558 | 0.22898 | 2.6449 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-04 | 42 | 19.7015 | 10.7963 | 30.4978 | 1.618 | 0.76558 | 0.22672 | 2.6103 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-12-04 | 43 | 19.6961 | 11.164 | 30.8601 | 1.6566 | 0.76558 | 0.22942 | 2.6516 | 8.592% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2010-12-04 | 44 | 20.3789 | 11.4524 | 31.8313 | 1.7626 | 0.76558 | 0.23664 | 2.7648 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-12-04 | 45 | 19.7453 | 11.1365 | 30.8818 | 1.659 | 0.76558 | 0.22958 | 2.6541 | 8.594% | 9.145% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-12-04 | 46 | 18.7807 | 10.4268 | 29.2074 | 1.484 | 0.76558 | 0.21713 | 2.4667 | 8.445% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0646
2010-12-04 | 47 | 17.5896 | 10.0569 | 27.6465 | 1.3296 | 0.76558 | 0.20553 | 2.3007 | 8.322% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-12-04 | 48 | 16.3654 | 10.1257 | 26.4911 | 1.2208 | 0.76558 | 0.19694 | 2.1833 | 8.242% | 8.769% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-12-05 | 1 | 14.7349 | 9.305 | 24.0399 | 1.0053 | 0.76558 | 0.17872 | 1.9496 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-12-05 | 2 | 13.6806 | 8.7636 | 22.4442 | 0.87628 | 0.76558 | 0.16685 | 1.8087 | 8.059% | 8.574% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-12-05 | 3 | 12.8736 | 8.1498 | 21.0234 | 0.76885 | 0.76558 | 0.15629 | 1.6907 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-05 | 4 | 12.2134 | 7.8868 | 20.1002 | 0.70281 | 0.76558 | 0.14943 | 1.6178 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-05 | 5 | 11.8777 | 7.7735 | 19.6512 | 0.67176 | 0.76558 | 0.14609 | 1.5834 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-12-05 | 6 | 11.6088 | 7.7134 | 19.3223 | 0.64946 | 0.76558 | 0.14364 | 1.5587 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-12-05 | 7 | 11.4315 | 7.7455 | 19.177 | 0.63973 | 0.76558 | 0.14256 | 1.5479 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-12-05 | 8 | 11.2133 | 7.7647 | 18.978 | 0.62652 | 0.76558 | 0.14109 | 1.5332 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-12-05 | 9 | 11.1344 | 7.7178 | 18.8522 | 0.61824 | 0.76558 | 0.14015 | 1.524 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-12-05 | 10 | 11.2192 | 7.6984 | 18.9176 | 0.62254 | 0.76558 | 0.14064 | 1.5288 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-05 | 11 | 11.6187 | 7.781 | 19.3997 | 0.65467 | 0.76558 | 0.14422 | 1.5645 | 8.064% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-12-05 | 12 | 11.7662 | 7.7741 | 19.5403 | 0.6642 | 0.76558 | 0.14526 | 1.575 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-05 | 13 | 12.5956 | 7.8453 | 20.4409 | 0.72683 | 0.76558 | 0.15196 | 1.6444 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-05 | 14 | 13.6189 | 7.9684 | 21.5873 | 0.81065 | 0.76558 | 0.16048 | 1.7367 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-05 | 15 | 15.1993 | 8.1958 | 23.3951 | 0.95211 | 0.76558 | 0.17392 | 1.8916 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-12-05 | 16 | 16.6629 | 8.9817 | 25.6446 | 1.144 | 0.76558 | 0.19065 | 2.1002 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2010-12-05 | 17 | 18.1455 | 9.7824 | 27.928 | 1.3568 | 0.76558 | 0.20762 | 2.33 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-12-05 | 18 | 19.3765 | 10.3775 | 29.754 | 1.54 | 0.76558 | 0.2212 | 2.5268 | 8.492% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-12-05 | 19 | 20.5229 | 10.9118 | 31.4348 | 1.7189 | 0.76558 | 0.23369 | 2.7182 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2010-12-05 | 20 | 20.6285 | 11.3171 | 31.9456 | 1.7752 | 0.76558 | 0.23749 | 2.7783 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-12-05 | 21 | 20.944 | 11.1773 | 32.1213 | 1.7948 | 0.76558 | 0.23879 | 2.7992 | 8.714% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2010-12-05 | 22 | 20.9188 | 10.8807 | 31.7995 | 1.759 | 0.76558 | 0.2364 | 2.761 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-12-05 | 23 | 20.5678 | 10.5279 | 31.0957 | 1.682 | 0.76558 | 0.23117 | 2.6788 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-12-05 | 24 | 20.2724 | 10.5318 | 30.8042 | 1.6506 | 0.76558 | 0.229 | 2.6452 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-05 | 25 | 19.908 | 10.6227 | 30.5307 | 1.6215 | 0.76558 | 0.22697 | 2.614 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-12-05 | 26 | 19.572 | 10.3354 | 29.9074 | 1.5559 | 0.76558 | 0.22234 | 2.5439 | 8.506% | 9.05% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-12-05 | 27 | 19.7889 | 10.4512 | 30.24 | 1.5907 | 0.76558 | 0.22481 | 2.5811 | 8.535% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-12-05 | 28 | 19.0719 | 10.3075 | 29.3794 | 1.5015 | 0.76558 | 0.21841 | 2.4855 | 8.46% | 9.001% | 6.083% | 1.0924 | 1.0989 | 1.0648
2010-12-05 | 29 | 18.883 | 9.9952 | 28.8782 | 1.4507 | 0.76558 | 0.21468 | 2.431 | 8.418% | 8.957% | 6.053% | 1.0919 | 1.0984 | 1.0644
2010-12-05 | 30 | 18.5344 | 9.8936 | 28.428 | 1.4058 | 0.76558 | 0.21134 | 2.3827 | 8.382% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2010-12-05 | 31 | 18.5257 | 9.7987 | 28.3244 | 1.3956 | 0.76558 | 0.21057 | 2.3717 | 8.373% | 8.909% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-12-05 | 32 | 18.6379 | 9.7538 | 28.3917 | 1.4022 | 0.76558 | 0.21107 | 2.3789 | 8.379% | 8.915% | 6.024% | 1.0914 | 1.0979 | 1.0641
2010-12-05 | 33 | 18.7061 | 9.9361 | 28.6422 | 1.4271 | 0.76558 | 0.21293 | 2.4056 | 8.399% | 8.936% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-12-05 | 34 | 18.8637 | 9.8755 | 28.7392 | 1.4368 | 0.76558 | 0.21365 | 2.416 | 8.407% | 8.945% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-12-05 | 35 | 19.2115 | 10.2043 | 29.4158 | 1.5052 | 0.76558 | 0.21868 | 2.4895 | 8.463% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-12-05 | 36 | 19.5999 | 10.5899 | 30.1898 | 1.5855 | 0.76558 | 0.22443 | 2.5755 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-12-05 | 37 | 20.2672 | 10.6696 | 30.9368 | 1.6649 | 0.76558 | 0.22999 | 2.6605 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-12-05 | 38 | 20.4375 | 10.6518 | 31.0893 | 1.6813 | 0.76558 | 0.23112 | 2.678 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2010-12-05 | 39 | 20.1978 | 10.57 | 30.7678 | 1.6468 | 0.76558 | 0.22873 | 2.6411 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2010-12-05 | 40 | 19.8245 | 10.3166 | 30.1411 | 1.5803 | 0.76558 | 0.22407 | 2.57 | 8.527% | 9.072% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-12-05 | 41 | 19.45 | 9.8214 | 29.2714 | 1.4905 | 0.76558 | 0.21761 | 2.4736 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-12-05 | 42 | 19.702 | 9.6675 | 29.3695 | 1.5005 | 0.76558 | 0.21834 | 2.4844 | 8.459% | 9% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-12-05 | 43 | 19.883 | 9.8993 | 29.7823 | 1.5429 | 0.76558 | 0.22141 | 2.5299 | 8.495% | 9.038% | 6.108% | 1.0928 | 1.0994 | 1.0651
2010-12-05 | 44 | 20.1346 | 9.9857 | 30.1203 | 1.5782 | 0.76558 | 0.22392 | 2.5677 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-12-05 | 45 | 19.0258 | 9.8422 | 28.868 | 1.4497 | 0.76558 | 0.21461 | 2.4299 | 8.417% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2010-12-05 | 46 | 17.8807 | 9.2949 | 27.1756 | 1.2847 | 0.76558 | 0.20203 | 2.2523 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-12-05 | 47 | 17.0412 | 9.1757 | 26.2169 | 1.1956 | 0.76558 | 0.1949 | 2.1561 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2010-12-05 | 48 | 16.002 | 9.177 | 25.1789 | 1.1028 | 0.76558 | 0.18718 | 2.0556 | 8.164% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-12-06 | 1 | 14.7853 | 8.5063 | 23.2915 | 0.94369 | 0.76558 | 0.17315 | 1.8824 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-06 | 2 | 13.5485 | 8.1237 | 21.6722 | 0.81704 | 0.76558 | 0.16111 | 1.7437 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-06 | 3 | 12.717 | 7.6616 | 20.3786 | 0.72241 | 0.76558 | 0.1515 | 1.6395 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-06 | 4 | 12.1863 | 7.3848 | 19.5711 | 0.66629 | 0.76558 | 0.14549 | 1.5774 | 8.06% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-06 | 5 | 12.0182 | 7.1801 | 19.1983 | 0.64115 | 0.76558 | 0.14272 | 1.5494 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-12-06 | 6 | 11.8515 | 7.1198 | 18.9714 | 0.62608 | 0.76558 | 0.14104 | 1.5327 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-12-06 | 7 | 11.4939 | 7.1421 | 18.636 | 0.60414 | 0.76558 | 0.13854 | 1.5083 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-06 | 8 | 11.2676 | 7.2174 | 18.4849 | 0.59439 | 0.76558 | 0.13742 | 1.4974 | 8.101% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-12-06 | 9 | 11.2728 | 7.2122 | 18.485 | 0.59439 | 0.76558 | 0.13742 | 1.4974 | 8.101% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-12-06 | 10 | 11.4277 | 7.0379 | 18.4656 | 0.59314 | 0.76558 | 0.13728 | 1.496 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2010-12-06 | 11 | 11.5743 | 7.0451 | 18.6194 | 0.60307 | 0.76558 | 0.13842 | 1.5071 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-06 | 12 | 11.7153 | 7.0063 | 18.7216 | 0.60971 | 0.76558 | 0.13918 | 1.5145 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-12-06 | 13 | 12.2299 | 7.1418 | 19.3716 | 0.65278 | 0.76558 | 0.14401 | 1.5624 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-06 | 14 | 13.0577 | 7.1387 | 20.1964 | 0.70955 | 0.76558 | 0.15014 | 1.6253 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-06 | 15 | 14.4707 | 7.654 | 22.1246 | 0.8515 | 0.76558 | 0.16448 | 1.7816 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-06 | 16 | 15.4112 | 8.0479 | 23.4591 | 0.95732 | 0.76558 | 0.1744 | 1.8973 | 8.088% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-12-06 | 17 | 17.1926 | 8.7992 | 25.9918 | 1.1752 | 0.76558 | 0.19323 | 2.134 | 8.21% | 8.736% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-12-06 | 18 | 18.7089 | 9.6245 | 28.3334 | 1.3965 | 0.76558 | 0.21063 | 2.3727 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2010-12-06 | 19 | 20.0941 | 10.1821 | 30.2763 | 1.5946 | 0.76558 | 0.22508 | 2.5852 | 8.539% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-12-06 | 20 | 21.0511 | 10.6398 | 31.6909 | 1.747 | 0.76558 | 0.23559 | 2.7482 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2010-12-06 | 21 | 21.6354 | 10.829 | 32.4644 | 1.8334 | 0.76558 | 0.24134 | 2.8403 | 8.749% | 9.309% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-12-06 | 22 | 21.6398 | 10.8868 | 32.5266 | 1.8404 | 0.76558 | 0.24181 | 2.8478 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-12-06 | 23 | 21.1304 | 10.6279 | 31.7583 | 1.7545 | 0.76558 | 0.2361 | 2.7562 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-12-06 | 24 | 20.7843 | 10.8124 | 31.5967 | 1.7367 | 0.76558 | 0.23489 | 2.7371 | 8.663% | 9.217% | 6.229% | 1.0948 | 1.1015 | 1.0664
2010-12-06 | 25 | 20.2801 | 10.9421 | 31.2222 | 1.6957 | 0.76558 | 0.23211 | 2.6934 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-12-06 | 26 | 19.8201 | 10.7523 | 30.5724 | 1.6259 | 0.76558 | 0.22728 | 2.6188 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2010-12-06 | 27 | 19.51 | 10.4688 | 29.9789 | 1.5634 | 0.76558 | 0.22287 | 2.5518 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-12-06 | 28 | 19.1768 | 10.1382 | 29.315 | 1.4949 | 0.76558 | 0.21793 | 2.4784 | 8.454% | 8.996% | 6.079% | 1.0924 | 1.0988 | 1.0647
2010-12-06 | 29 | 18.9653 | 9.8013 | 28.7666 | 1.4395 | 0.76558 | 0.21385 | 2.4189 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2010-12-06 | 30 | 18.6231 | 9.5364 | 28.1596 | 1.3794 | 0.76558 | 0.20934 | 2.3543 | 8.361% | 8.896% | 6.011% | 1.0912 | 1.0976 | 1.064
2010-12-06 | 31 | 18.5386 | 9.3832 | 27.9218 | 1.3562 | 0.76558 | 0.20757 | 2.3293 | 8.342% | 8.876% | 5.998% | 1.091 | 1.0974 | 1.0638
2010-12-06 | 32 | 18.3645 | 9.2005 | 27.5649 | 1.3217 | 0.76558 | 0.20492 | 2.2922 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-12-06 | 33 | 18.4203 | 9.4389 | 27.8592 | 1.3501 | 0.76558 | 0.20711 | 2.3228 | 8.338% | 8.871% | 5.995% | 1.091 | 1.0973 | 1.0638
2010-12-06 | 34 | 18.6103 | 9.5938 | 28.204 | 1.3837 | 0.76558 | 0.20967 | 2.359 | 8.364% | 8.899% | 6.014% | 1.0913 | 1.0977 | 1.064
2010-12-06 | 35 | 18.766 | 9.7616 | 28.5276 | 1.4157 | 0.76558 | 0.21208 | 2.3933 | 8.39% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-12-06 | 36 | 19.3391 | 10.2175 | 29.5566 | 1.5196 | 0.76558 | 0.21973 | 2.505 | 8.475% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-12-06 | 37 | 19.779 | 10.5125 | 30.2914 | 1.5962 | 0.76558 | 0.22519 | 2.5869 | 8.54% | 9.087% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-12-06 | 38 | 20.2861 | 10.4944 | 30.7805 | 1.6481 | 0.76558 | 0.22883 | 2.6425 | 8.585% | 9.134% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-12-06 | 39 | 20.297 | 10.5315 | 30.8284 | 1.6532 | 0.76558 | 0.22918 | 2.648 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-12-06 | 40 | 19.9921 | 10.2029 | 30.1951 | 1.586 | 0.76558 | 0.22447 | 2.5761 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-12-06 | 41 | 19.9057 | 9.9613 | 29.867 | 1.5517 | 0.76558 | 0.22203 | 2.5393 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-12-06 | 42 | 19.5838 | 9.8403 | 29.4241 | 1.5061 | 0.76558 | 0.21874 | 2.4904 | 8.464% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2010-12-06 | 43 | 19.8016 | 10.0307 | 29.8323 | 1.5481 | 0.76558 | 0.22178 | 2.5355 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-12-06 | 44 | 20.2619 | 10.1892 | 30.4511 | 1.613 | 0.76558 | 0.22638 | 2.605 | 8.555% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2010-12-06 | 45 | 19.5291 | 9.666 | 29.1952 | 1.4827 | 0.76558 | 0.21704 | 2.4653 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-12-06 | 46 | 18.411 | 8.8316 | 27.2426 | 1.291 | 0.76558 | 0.20252 | 2.2591 | 8.293% | 8.823% | 5.962% | 1.0904 | 1.0968 | 1.0634
2010-12-06 | 47 | 16.8405 | 8.3148 | 25.1554 | 1.1008 | 0.76558 | 0.18701 | 2.0534 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2010-12-06 | 48 | 15.7816 | 8.2424 | 24.024 | 1.004 | 0.76558 | 0.1786 | 1.9482 | 8.109% | 8.628% | 5.831% | 1.0882 | 1.0944 | 1.0619
2010-12-07 | 1 | 13.9733 | 7.5449 | 21.5182 | 0.80546 | 0.76558 | 0.15997 | 1.731 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-07 | 2 | 13.0139 | 7.0613 | 20.0752 | 0.70106 | 0.76558 | 0.14924 | 1.6159 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-07 | 3 | 12.467 | 6.7004 | 19.1674 | 0.63909 | 0.76558 | 0.14249 | 1.5472 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-07 | 4 | 11.9621 | 6.5651 | 18.5272 | 0.59711 | 0.76558 | 0.13773 | 1.5004 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-12-07 | 5 | 11.6101 | 6.4708 | 18.0809 | 0.56869 | 0.76558 | 0.13442 | 1.4687 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-12-07 | 6 | 11.3443 | 6.5171 | 17.8614 | 0.55497 | 0.76558 | 0.13278 | 1.4533 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-12-07 | 7 | 11.0984 | 6.5795 | 17.6778 | 0.54362 | 0.76558 | 0.13142 | 1.4406 | 8.149% | 8.671% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-12-07 | 8 | 11.1315 | 6.5846 | 17.7161 | 0.54597 | 0.76558 | 0.1317 | 1.4433 | 8.147% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-12-07 | 9 | 11.2663 | 6.6616 | 17.9279 | 0.5591 | 0.76558 | 0.13328 | 1.458 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-12-07 | 10 | 11.4764 | 6.6294 | 18.1058 | 0.57025 | 0.76558 | 0.1346 | 1.4704 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-12-07 | 11 | 12.0255 | 6.7248 | 18.7503 | 0.61157 | 0.76558 | 0.13939 | 1.5165 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-12-07 | 12 | 12.5362 | 7.0516 | 19.5878 | 0.66743 | 0.76558 | 0.14562 | 1.5786 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-07 | 13 | 13.3445 | 7.7714 | 21.1159 | 0.77563 | 0.76558 | 0.15698 | 1.6982 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-07 | 14 | 15.375 | 8.7661 | 24.1411 | 1.0138 | 0.76558 | 0.17947 | 1.9588 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-12-07 | 15 | 18.4293 | 10.0916 | 28.5209 | 1.415 | 0.76558 | 0.21203 | 2.3926 | 8.389% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-12-07 | 16 | 20.5502 | 10.6842 | 31.2344 | 1.6971 | 0.76558 | 0.2322 | 2.6948 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2010-12-07 | 17 | 21.8805 | 11.2022 | 33.0827 | 1.9039 | 0.76558 | 0.24594 | 2.9154 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2010-12-07 | 18 | 22.2928 | 11.2263 | 33.5191 | 1.9544 | 0.76558 | 0.24919 | 2.9692 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-12-07 | 19 | 22.3156 | 11.1261 | 33.4416 | 1.9454 | 0.76558 | 0.24861 | 2.9596 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.104 | 1.068
2010-12-07 | 20 | 21.6085 | 10.8827 | 32.4911 | 1.8364 | 0.76558 | 0.24154 | 2.8435 | 8.752% | 9.312% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-12-07 | 21 | 21.5936 | 10.5979 | 32.1915 | 1.8027 | 0.76558 | 0.23932 | 2.8076 | 8.721% | 9.28% | 6.271% | 1.0955 | 1.1023 | 1.0669
2010-12-07 | 22 | 21.14 | 10.5967 | 31.7367 | 1.7521 | 0.76558 | 0.23593 | 2.7536 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-12-07 | 23 | 20.8587 | 10.2594 | 31.1181 | 1.6845 | 0.76558 | 0.23134 | 2.6814 | 8.617% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-07 | 24 | 20.483 | 10.3865 | 30.8695 | 1.6577 | 0.76558 | 0.22949 | 2.6527 | 8.593% | 9.143% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-12-07 | 25 | 20.4245 | 10.4099 | 30.8345 | 1.6539 | 0.76558 | 0.22923 | 2.6487 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-12-07 | 26 | 19.8683 | 9.9974 | 29.8657 | 1.5516 | 0.76558 | 0.22203 | 2.5392 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2010-12-07 | 27 | 19.8523 | 10.2032 | 30.0555 | 1.5714 | 0.76558 | 0.22344 | 2.5604 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2010-12-07 | 28 | 19.8884 | 10.2973 | 30.1857 | 1.585 | 0.76558 | 0.2244 | 2.575 | 8.531% | 9.077% | 6.133% | 1.0933 | 1.0998 | 1.0653
2010-12-07 | 29 | 19.5462 | 10.2125 | 29.7588 | 1.5405 | 0.76558 | 0.22123 | 2.5273 | 8.493% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-12-07 | 30 | 19.2465 | 10.2664 | 29.5129 | 1.5152 | 0.76558 | 0.2194 | 2.5001 | 8.471% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-12-07 | 31 | 19.0397 | 10.1185 | 29.1582 | 1.479 | 0.76558 | 0.21677 | 2.4613 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-12-07 | 32 | 19.2303 | 10.1171 | 29.3475 | 1.4982 | 0.76558 | 0.21817 | 2.482 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-12-07 | 33 | 19.7987 | 10.5039 | 30.3026 | 1.5973 | 0.76558 | 0.22527 | 2.5882 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2010-12-07 | 34 | 19.8464 | 10.6299 | 30.4764 | 1.6157 | 0.76558 | 0.22656 | 2.6078 | 8.557% | 9.105% | 6.152% | 1.0936 | 1.1002 | 1.0656
2010-12-07 | 35 | 19.7804 | 11.138 | 30.9184 | 1.6629 | 0.76558 | 0.22985 | 2.6583 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-12-07 | 36 | 20.2556 | 11.5007 | 31.7563 | 1.7543 | 0.76558 | 0.23608 | 2.7559 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0665
2010-12-07 | 37 | 20.8924 | 11.4479 | 32.3403 | 1.8194 | 0.76558 | 0.24042 | 2.8254 | 8.736% | 9.296% | 6.281% | 1.0957 | 1.1025 | 1.067
2010-12-07 | 38 | 21.1014 | 11.243 | 32.3444 | 1.8198 | 0.76558 | 0.24045 | 2.8259 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2010-12-07 | 39 | 21.1766 | 11.4318 | 32.6084 | 1.8497 | 0.76558 | 0.24241 | 2.8577 | 8.764% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-12-07 | 40 | 21.1677 | 11.2763 | 32.444 | 1.8311 | 0.76558 | 0.24119 | 2.8378 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-12-07 | 41 | 20.9331 | 10.8599 | 31.793 | 1.7583 | 0.76558 | 0.23635 | 2.7602 | 8.682% | 9.238% | 6.242% | 1.0951 | 1.1018 | 1.0666
2010-12-07 | 42 | 20.8899 | 10.6922 | 31.5821 | 1.7351 | 0.76558 | 0.23479 | 2.7354 | 8.661% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-12-07 | 43 | 20.7642 | 10.6466 | 31.4109 | 1.7163 | 0.76558 | 0.23351 | 2.7154 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-12-07 | 44 | 21.0925 | 10.7386 | 31.8311 | 1.7625 | 0.76558 | 0.23664 | 2.7648 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2010-12-07 | 45 | 20.1316 | 10.1364 | 30.268 | 1.5937 | 0.76558 | 0.22502 | 2.5843 | 8.538% | 9.084% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-12-07 | 46 | 18.7785 | 9.1802 | 27.9587 | 1.3598 | 0.76558 | 0.20785 | 2.3332 | 8.345% | 8.879% | 6% | 1.0911 | 1.0974 | 1.0638
2010-12-07 | 47 | 17.263 | 8.6977 | 25.9607 | 1.1724 | 0.76558 | 0.19299 | 2.1309 | 8.208% | 8.734% | 5.902% | 1.0894 | 1.0957 | 1.0627
2010-12-07 | 48 | 15.784 | 8.5638 | 24.3478 | 1.0312 | 0.76558 | 0.181 | 1.9778 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-12-08 | 1 | 14.2561 | 7.7246 | 21.9807 | 0.84046 | 0.76558 | 0.16341 | 1.7694 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-08 | 2 | 12.9115 | 7.3303 | 20.2418 | 0.71274 | 0.76558 | 0.15048 | 1.6288 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-08 | 3 | 12.5512 | 7.0753 | 19.6264 | 0.67007 | 0.76558 | 0.14591 | 1.5815 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-08 | 4 | 12.0392 | 6.9045 | 18.9437 | 0.62426 | 0.76558 | 0.14083 | 1.5307 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-08 | 5 | 11.5752 | 6.6837 | 18.2589 | 0.57994 | 0.76558 | 0.13574 | 1.4813 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-12-08 | 6 | 11.3148 | 6.6224 | 17.9372 | 0.55968 | 0.76558 | 0.13335 | 1.4586 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-12-08 | 7 | 11.0392 | 6.473 | 17.5122 | 0.53348 | 0.76558 | 0.13019 | 1.4292 | 8.161% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-12-08 | 8 | 10.9513 | 6.5754 | 17.5268 | 0.53436 | 0.76558 | 0.1303 | 1.4302 | 8.16% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-12-08 | 9 | 10.9108 | 6.6859 | 17.5967 | 0.53864 | 0.76558 | 0.13082 | 1.435 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-12-08 | 10 | 11.1042 | 6.6597 | 17.764 | 0.54893 | 0.76558 | 0.13206 | 1.4466 | 8.143% | 8.664% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-12-08 | 11 | 11.3628 | 6.7731 | 18.1359 | 0.57215 | 0.76558 | 0.13482 | 1.4726 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-12-08 | 12 | 11.675 | 6.9701 | 18.6451 | 0.60473 | 0.76558 | 0.13861 | 1.5089 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-08 | 13 | 12.9751 | 7.6641 | 20.6392 | 0.741 | 0.76558 | 0.15343 | 1.66 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-08 | 14 | 15.0038 | 8.8116 | 23.8154 | 0.98662 | 0.76558 | 0.17705 | 1.9292 | 8.101% | 8.619% | 5.825% | 1.0881 | 1.0943 | 1.0618
2010-12-08 | 15 | 18.0139 | 10.2403 | 28.2542 | 1.3887 | 0.76558 | 0.21005 | 2.3643 | 8.368% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-12-08 | 16 | 20.1733 | 10.897 | 31.0703 | 1.6793 | 0.76558 | 0.23098 | 2.6758 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-12-08 | 17 | 21.6252 | 11.2973 | 32.9225 | 1.8855 | 0.76558 | 0.24475 | 2.8958 | 8.796% | 9.359% | 6.324% | 1.0964 | 1.1033 | 1.0675
2010-12-08 | 18 | 21.65 | 11.0957 | 32.7457 | 1.8653 | 0.76558 | 0.24344 | 2.8743 | 8.778% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2010-12-08 | 19 | 21.734 | 10.9099 | 32.6439 | 1.8537 | 0.76558 | 0.24268 | 2.862 | 8.767% | 9.328% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-12-08 | 20 | 21.816 | 10.8913 | 32.7073 | 1.8609 | 0.76558 | 0.24315 | 2.8696 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-12-08 | 21 | 22.022 | 10.8646 | 32.8866 | 1.8814 | 0.76558 | 0.24448 | 2.8914 | 8.792% | 9.355% | 6.322% | 1.0964 | 1.1032 | 1.0675
2010-12-08 | 22 | 21.972 | 11.029 | 33.001 | 1.8945 | 0.76558 | 0.24533 | 2.9054 | 8.804% | 9.367% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-12-08 | 23 | 22.018 | 10.8126 | 32.8306 | 1.875 | 0.76558 | 0.24407 | 2.8846 | 8.786% | 9.349% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-12-08 | 24 | 22.148 | 10.7813 | 32.9293 | 1.8863 | 0.76558 | 0.2448 | 2.8966 | 8.797% | 9.359% | 6.325% | 1.0964 | 1.1033 | 1.0675
2010-12-08 | 25 | 22.412 | 10.7814 | 33.1934 | 1.9166 | 0.76558 | 0.24676 | 2.929 | 8.824% | 9.389% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-12-08 | 26 | 21.92 | 10.6832 | 32.6032 | 1.8491 | 0.76558 | 0.24238 | 2.857 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-12-08 | 27 | 21.802 | 10.7976 | 32.5996 | 1.8487 | 0.76558 | 0.24235 | 2.8566 | 8.763% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-12-08 | 28 | 21.52 | 10.6133 | 32.1333 | 1.7962 | 0.76558 | 0.23888 | 2.8006 | 8.716% | 9.273% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-12-08 | 29 | 21.484 | 10.255 | 31.739 | 1.7523 | 0.76558 | 0.23595 | 2.7539 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-12-08 | 30 | 20.826 | 10.1126 | 30.9386 | 1.6651 | 0.76558 | 0.23 | 2.6607 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-12-08 | 31 | 20.642 | 9.8944 | 30.5364 | 1.6221 | 0.76558 | 0.22701 | 2.6147 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-12-08 | 32 | 20.298 | 9.7831 | 30.0811 | 1.5741 | 0.76558 | 0.22363 | 2.5633 | 8.521% | 9.067% | 6.127% | 1.0931 | 1.0997 | 1.0653
2010-12-08 | 33 | 20.456 | 10.2719 | 30.7279 | 1.6425 | 0.76558 | 0.22843 | 2.6365 | 8.58% | 9.129% | 6.169% | 1.0939 | 1.1005 | 1.0657
2010-12-08 | 34 | 20.488 | 10.4922 | 30.9802 | 1.6696 | 0.76558 | 0.23031 | 2.6654 | 8.604% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2010-12-08 | 35 | 20.75 | 10.8434 | 31.5934 | 1.7363 | 0.76558 | 0.23487 | 2.7368 | 8.662% | 9.217% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-12-08 | 36 | 21.532 | 11.1855 | 32.7175 | 1.8621 | 0.76558 | 0.24323 | 2.8709 | 8.775% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-12-08 | 37 | 22.22 | 11.1375 | 33.3575 | 1.9356 | 0.76558 | 0.24798 | 2.9492 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-12-08 | 38 | 22.034 | 11.0692 | 33.1032 | 1.9062 | 0.76558 | 0.24609 | 2.9179 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-12-08 | 39 | 21.544 | 10.9232 | 32.4672 | 1.8337 | 0.76558 | 0.24137 | 2.8406 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1026 | 1.0671
2010-12-08 | 40 | 21.512 | 10.4294 | 31.9414 | 1.7748 | 0.76558 | 0.23746 | 2.7778 | 8.697% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-12-08 | 41 | 20.838 | 10.1596 | 30.9976 | 1.6714 | 0.76558 | 0.23044 | 2.6675 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2010-12-08 | 42 | 21.152 | 10.1436 | 31.2956 | 1.7037 | 0.76558 | 0.23266 | 2.702 | 8.634% | 9.186% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-12-08 | 43 | 21.058 | 9.9659 | 31.0239 | 1.6743 | 0.76558 | 0.23064 | 2.6705 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-12-08 | 44 | 21.406 | 10.044 | 31.45 | 1.7206 | 0.76558 | 0.2338 | 2.72 | 8.649% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-08 | 45 | 20.268 | 9.4221 | 29.6901 | 1.5334 | 0.76558 | 0.22072 | 2.5197 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2010-12-08 | 46 | 18.974 | 8.6631 | 27.6371 | 1.3287 | 0.76558 | 0.20546 | 2.2997 | 8.321% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2010-12-08 | 47 | 17.474 | 8.2056 | 25.6796 | 1.1471 | 0.76558 | 0.19091 | 2.1036 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2010-12-08 | 48 | 16.258 | 8.246 | 24.504 | 1.0445 | 0.76558 | 0.18217 | 1.9922 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-12-09 | 1 | 14.55 | 7.4238 | 21.9738 | 0.83993 | 0.76558 | 0.16336 | 1.7689 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-09 | 2 | 13.406 | 6.9302 | 20.3362 | 0.7194 | 0.76558 | 0.15118 | 1.6362 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-09 | 3 | 12.55 | 6.633 | 19.183 | 0.64013 | 0.76558 | 0.14261 | 1.5483 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2010-12-09 | 4 | 12.046 | 6.3947 | 18.4407 | 0.59154 | 0.76558 | 0.13709 | 1.4942 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-12-09 | 5 | 11.778 | 6.2151 | 17.9931 | 0.56318 | 0.76558 | 0.13376 | 1.4625 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-12-09 | 6 | 11.468 | 6.1863 | 17.6543 | 0.54217 | 0.76558 | 0.13124 | 1.439 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2010-12-09 | 7 | 11.29 | 6.1177 | 17.4077 | 0.52713 | 0.76558 | 0.12941 | 1.4221 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2010-12-09 | 8 | 11.11 | 6.155 | 17.265 | 0.51853 | 0.76558 | 0.12835 | 1.4125 | 8.181% | 8.705% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-12-09 | 9 | 11.284 | 6.2766 | 17.5606 | 0.53643 | 0.76558 | 0.13055 | 1.4326 | 8.158% | 8.68% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-12-09 | 10 | 11.338 | 6.3257 | 17.6637 | 0.54275 | 0.76558 | 0.13131 | 1.4396 | 8.15% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0622
2010-12-09 | 11 | 11.76 | 6.5072 | 18.2672 | 0.58047 | 0.76558 | 0.1358 | 1.4818 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-12-09 | 12 | 12.044 | 6.5839 | 18.6279 | 0.60362 | 0.76558 | 0.13848 | 1.5077 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-09 | 13 | 13.552 | 7.2778 | 20.8298 | 0.75476 | 0.76558 | 0.15485 | 1.6752 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-09 | 14 | 15.604 | 8.4776 | 24.0816 | 1.0088 | 0.76558 | 0.17903 | 1.9534 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-12-09 | 15 | 18.816 | 10.1977 | 29.0137 | 1.4643 | 0.76558 | 0.21569 | 2.4456 | 8.429% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-12-09 | 16 | 21.288 | 11.2096 | 32.4976 | 1.8371 | 0.76558 | 0.24159 | 2.8443 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-09 | 17 | 22.852 | 11.6784 | 34.5304 | 2.0741 | 0.76558 | 0.2567 | 3.0964 | 8.967% | 9.541% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-12-09 | 18 | 23.024 | 11.5465 | 34.5705 | 2.079 | 0.76558 | 0.257 | 3.1015 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2010-12-09 | 19 | 23.106 | 11.2052 | 34.3112 | 2.0479 | 0.76558 | 0.25507 | 3.0685 | 8.943% | 9.516% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-12-09 | 20 | 22.662 | 10.8626 | 33.5246 | 1.9551 | 0.76558 | 0.24923 | 2.9699 | 8.859% | 9.426% | 6.369% | 1.0972 | 1.1041 | 1.068
2010-12-09 | 21 | 22.73 | 10.7066 | 33.4366 | 1.9448 | 0.76558 | 0.24857 | 2.959 | 8.849% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2010-12-09 | 22 | 22.512 | 10.8221 | 33.3341 | 1.9329 | 0.76558 | 0.24781 | 2.9463 | 8.839% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-12-09 | 23 | 22.184 | 10.5056 | 32.6896 | 1.8589 | 0.76558 | 0.24302 | 2.8675 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-12-09 | 24 | 21.89 | 10.5553 | 32.4453 | 1.8312 | 0.76558 | 0.2412 | 2.838 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-12-09 | 25 | 21.602 | 10.6773 | 32.2793 | 1.8125 | 0.76558 | 0.23997 | 2.8181 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-12-09 | 26 | 21.13 | 10.2067 | 31.3367 | 1.7082 | 0.76558 | 0.23296 | 2.7067 | 8.638% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-12-09 | 27 | 21.044 | 10.2803 | 31.3243 | 1.7069 | 0.76558 | 0.23287 | 2.7053 | 8.636% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-12-09 | 28 | 20.88 | 10.2554 | 31.1354 | 1.6863 | 0.76558 | 0.23146 | 2.6834 | 8.618% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-12-09 | 29 | 20.812 | 9.8358 | 30.6478 | 1.6339 | 0.76558 | 0.22784 | 2.6273 | 8.573% | 9.121% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-12-09 | 30 | 20.656 | 9.6118 | 30.2678 | 1.5937 | 0.76558 | 0.22501 | 2.5843 | 8.538% | 9.084% | 6.139% | 1.0933 | 1.0999 | 1.0654
2010-12-09 | 31 | 20.57 | 9.5604 | 30.1304 | 1.5792 | 0.76558 | 0.22399 | 2.5688 | 8.526% | 9.071% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-12-09 | 32 | 20.808 | 9.6279 | 30.4359 | 1.6114 | 0.76558 | 0.22626 | 2.6033 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2010-12-09 | 33 | 21.052 | 9.9019 | 30.9539 | 1.6667 | 0.76558 | 0.23012 | 2.6624 | 8.601% | 9.152% | 6.184% | 1.0941 | 1.1007 | 1.0659
2010-12-09 | 34 | 21.29 | 9.9529 | 31.2429 | 1.698 | 0.76558 | 0.23226 | 2.6958 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2010-12-09 | 35 | 21.192 | 10.2292 | 31.4212 | 1.7174 | 0.76558 | 0.23359 | 2.7166 | 8.646% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-12-09 | 36 | 21.888 | 10.6168 | 32.5048 | 1.8379 | 0.76558 | 0.24164 | 2.8452 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-09 | 37 | 22.524 | 10.6646 | 33.1886 | 1.9161 | 0.76558 | 0.24673 | 2.9284 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-12-09 | 38 | 22.718 | 10.4954 | 33.2134 | 1.9189 | 0.76558 | 0.24691 | 2.9314 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-12-09 | 39 | 22.884 | 10.1875 | 33.0715 | 1.9026 | 0.76558 | 0.24586 | 2.914 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1035 | 1.0676
2010-12-09 | 40 | 22.88 | 9.8785 | 32.7585 | 1.8667 | 0.76558 | 0.24353 | 2.8758 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-12-09 | 41 | 22.214 | 9.7961 | 32.0101 | 1.7824 | 0.76558 | 0.23797 | 2.786 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-12-09 | 42 | 21.56 | 9.4459 | 31.0059 | 1.6723 | 0.76558 | 0.2305 | 2.6684 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-12-09 | 43 | 20.882 | 9.3182 | 30.2002 | 1.5865 | 0.76558 | 0.22451 | 2.5766 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2010-12-09 | 44 | 21.264 | 9.5405 | 30.8045 | 1.6507 | 0.76558 | 0.229 | 2.6453 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-09 | 45 | 20.892 | 9.1494 | 30.0414 | 1.5699 | 0.76558 | 0.22333 | 2.5588 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2010-12-09 | 46 | 19.57 | 8.5265 | 28.0965 | 1.3732 | 0.76558 | 0.20887 | 2.3477 | 8.356% | 8.89% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-12-09 | 47 | 17.948 | 8.2476 | 26.1956 | 1.1937 | 0.76558 | 0.19474 | 2.154 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-12-09 | 48 | 16.566 | 8.2137 | 24.7797 | 1.0681 | 0.76558 | 0.18422 | 2.0179 | 8.143% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-12-10 | 1 | 15.14 | 7.1886 | 22.3286 | 0.86727 | 0.76558 | 0.16599 | 1.7988 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-12-10 | 2 | 13.88 | 6.6172 | 20.4972 | 0.73084 | 0.76558 | 0.15238 | 1.6488 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-10 | 3 | 13.184 | 6.3411 | 19.5251 | 0.66317 | 0.76558 | 0.14515 | 1.5739 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-10 | 4 | 12.588 | 6.13 | 18.718 | 0.60947 | 0.76558 | 0.13915 | 1.5142 | 8.09% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-12-10 | 5 | 12.222 | 6.055 | 18.277 | 0.58109 | 0.76558 | 0.13587 | 1.4825 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-12-10 | 6 | 11.992 | 6.0461 | 18.0381 | 0.566 | 0.76558 | 0.1341 | 1.4657 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-12-10 | 7 | 11.862 | 6.1539 | 18.0159 | 0.5646 | 0.76558 | 0.13393 | 1.4641 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2010-12-10 | 8 | 11.664 | 5.9886 | 17.6526 | 0.54207 | 0.76558 | 0.13123 | 1.4389 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2010-12-10 | 9 | 11.888 | 5.9095 | 17.7975 | 0.551 | 0.76558 | 0.13231 | 1.4489 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-12-10 | 10 | 12.04 | 5.9283 | 17.9683 | 0.56163 | 0.76558 | 0.13358 | 1.4608 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-12-10 | 11 | 12.76 | 6.0845 | 18.8445 | 0.61774 | 0.76558 | 0.14009 | 1.5234 | 8.084% | 8.601% | 5.812% | 1.088 | 1.0941 | 1.0617
2010-12-10 | 12 | 13.008 | 6.3942 | 19.4022 | 0.65484 | 0.76558 | 0.14424 | 1.5647 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-12-10 | 13 | 14.652 | 7.2715 | 21.9235 | 0.83609 | 0.76558 | 0.16298 | 1.7647 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-10 | 14 | 16.726 | 8.3799 | 25.1059 | 1.0964 | 0.76558 | 0.18664 | 2.0487 | 8.16% | 8.682% | 5.867% | 1.0889 | 1.0951 | 1.0623
2010-12-10 | 15 | 19.914 | 9.6035 | 29.5175 | 1.5156 | 0.76558 | 0.21944 | 2.5006 | 8.472% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2010-12-10 | 16 | 21.876 | 10.5904 | 32.4664 | 1.8336 | 0.76558 | 0.24136 | 2.8405 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1026 | 1.0671
2010-12-10 | 17 | 22.972 | 11.0005 | 33.9725 | 2.0077 | 0.76558 | 0.25256 | 3.0258 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-12-10 | 18 | 22.882 | 10.8811 | 33.7631 | 1.983 | 0.76558 | 0.251 | 2.9996 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2010-12-10 | 19 | 22.382 | 10.7323 | 33.1143 | 1.9075 | 0.76558 | 0.24618 | 2.9193 | 8.816% | 9.38% | 6.338% | 1.0967 | 1.1035 | 1.0677
2010-12-10 | 20 | 21.794 | 10.6155 | 32.4095 | 1.8272 | 0.76558 | 0.24094 | 2.8337 | 8.743% | 9.303% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-12-10 | 21 | 21.7 | 10.1691 | 31.8691 | 1.7667 | 0.76558 | 0.23692 | 2.7692 | 8.689% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-12-10 | 22 | 21.276 | 10.0723 | 31.3483 | 1.7095 | 0.76558 | 0.23305 | 2.7081 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-12-10 | 23 | 20.744 | 9.9041 | 30.6481 | 1.634 | 0.76558 | 0.22784 | 2.6274 | 8.573% | 9.121% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-12-10 | 24 | 20.304 | 9.8185 | 30.1225 | 1.5784 | 0.76558 | 0.22393 | 2.5679 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0998 | 1.0653
2010-12-10 | 25 | 20.046 | 9.8397 | 29.8857 | 1.5537 | 0.76558 | 0.22217 | 2.5414 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-10 | 26 | 19.644 | 9.616 | 29.26 | 1.4893 | 0.76558 | 0.21752 | 2.4724 | 8.45% | 8.991% | 6.075% | 1.0923 | 1.0988 | 1.0647
2010-12-10 | 27 | 19.478 | 9.9201 | 29.3981 | 1.5034 | 0.76558 | 0.21855 | 2.4875 | 8.462% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-12-10 | 28 | 19.242 | 9.9523 | 29.1943 | 1.4826 | 0.76558 | 0.21703 | 2.4652 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-12-10 | 29 | 19.248 | 9.788 | 29.036 | 1.4666 | 0.76558 | 0.21586 | 2.448 | 8.431% | 8.971% | 6.062% | 1.0921 | 1.0985 | 1.0645
2010-12-10 | 30 | 19.158 | 9.5762 | 28.7342 | 1.4363 | 0.76558 | 0.21361 | 2.4155 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-12-10 | 31 | 18.988 | 9.5872 | 28.5752 | 1.4204 | 0.76558 | 0.21243 | 2.3984 | 8.393% | 8.931% | 6.035% | 1.0916 | 1.0981 | 1.0642
2010-12-10 | 32 | 18.87 | 9.7334 | 28.6034 | 1.4232 | 0.76558 | 0.21264 | 2.4014 | 8.396% | 8.933% | 6.036% | 1.0917 | 1.0981 | 1.0642
2010-12-10 | 33 | 19.212 | 10.1406 | 29.3526 | 1.4987 | 0.76558 | 0.21821 | 2.4825 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-12-10 | 34 | 19.276 | 10.0521 | 29.3281 | 1.4962 | 0.76558 | 0.21803 | 2.4799 | 8.456% | 8.997% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-12-10 | 35 | 19.394 | 10.1608 | 29.5548 | 1.5195 | 0.76558 | 0.21971 | 2.5048 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-12-10 | 36 | 19.732 | 10.3876 | 30.1196 | 1.5781 | 0.76558 | 0.22391 | 2.5676 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-12-10 | 37 | 20.166 | 10.5452 | 30.7112 | 1.6407 | 0.76558 | 0.22831 | 2.6346 | 8.579% | 9.128% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-12-10 | 38 | 20.588 | 10.5628 | 31.1508 | 1.688 | 0.76558 | 0.23158 | 2.6852 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2010-12-10 | 39 | 20.406 | 10.4467 | 30.8527 | 1.6558 | 0.76558 | 0.22936 | 2.6508 | 8.592% | 9.142% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-12-10 | 40 | 20.376 | 10.1415 | 30.5175 | 1.6201 | 0.76558 | 0.22687 | 2.6125 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-12-10 | 41 | 20.02 | 9.8559 | 29.8759 | 1.5527 | 0.76558 | 0.2221 | 2.5403 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-10 | 42 | 19.954 | 9.9282 | 29.8822 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-10 | 43 | 19.806 | 10.0131 | 29.8191 | 1.5468 | 0.76558 | 0.22168 | 2.534 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-12-10 | 44 | 20.746 | 10.0619 | 30.8079 | 1.651 | 0.76558 | 0.22903 | 2.6457 | 8.588% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-10 | 45 | 20.118 | 9.7023 | 29.8203 | 1.5469 | 0.76558 | 0.22169 | 2.5342 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-12-10 | 46 | 18.566 | 9.053 | 27.619 | 1.3269 | 0.76558 | 0.20532 | 2.2978 | 8.32% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2010-12-10 | 47 | 17.266 | 8.6906 | 25.9566 | 1.172 | 0.76558 | 0.19296 | 2.1305 | 8.208% | 8.733% | 5.902% | 1.0894 | 1.0957 | 1.0627
2010-12-10 | 48 | 15.674 | 8.6495 | 24.3235 | 1.0292 | 0.76558 | 0.18082 | 1.9756 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-12-11 | 1 | 14.252 | 7.7789 | 22.0309 | 0.8443 | 0.76558 | 0.16378 | 1.7737 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-11 | 2 | 13.306 | 7.174 | 20.48 | 0.72961 | 0.76558 | 0.15225 | 1.6474 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-11 | 3 | 12.638 | 6.8626 | 19.5006 | 0.6615 | 0.76558 | 0.14497 | 1.572 | 8.062% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-11 | 4 | 12.03 | 6.5975 | 18.6275 | 0.6036 | 0.76558 | 0.13848 | 1.5077 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-11 | 5 | 11.602 | 6.5287 | 18.1307 | 0.57183 | 0.76558 | 0.13479 | 1.4722 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-12-11 | 6 | 11.344 | 6.5591 | 17.9031 | 0.55756 | 0.76558 | 0.13309 | 1.4562 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-12-11 | 7 | 11.146 | 6.6501 | 17.7961 | 0.55091 | 0.76558 | 0.1323 | 1.4488 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2010-12-11 | 8 | 11.086 | 6.4803 | 17.5663 | 0.53678 | 0.76558 | 0.13059 | 1.4329 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2010-12-11 | 9 | 11.186 | 6.4499 | 17.6359 | 0.54104 | 0.76558 | 0.13111 | 1.4377 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2010-12-11 | 10 | 11.372 | 6.4983 | 17.8703 | 0.55552 | 0.76558 | 0.13285 | 1.4539 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-12-11 | 11 | 11.63 | 6.7039 | 18.3339 | 0.58472 | 0.76558 | 0.1363 | 1.4866 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2010-12-11 | 12 | 11.984 | 7.0107 | 18.9947 | 0.62763 | 0.76558 | 0.14121 | 1.5344 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-11 | 13 | 13.216 | 7.3759 | 20.5919 | 0.73761 | 0.76558 | 0.15308 | 1.6563 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-11 | 14 | 15.112 | 8.4292 | 23.5412 | 0.96403 | 0.76558 | 0.17501 | 1.9046 | 8.091% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-12-11 | 15 | 18.072 | 9.8586 | 27.9306 | 1.357 | 0.76558 | 0.20764 | 2.3303 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2010-12-11 | 16 | 20.348 | 10.7477 | 31.0957 | 1.682 | 0.76558 | 0.23117 | 2.6788 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-12-11 | 17 | 21.542 | 11.1819 | 32.7239 | 1.8628 | 0.76558 | 0.24327 | 2.8717 | 8.775% | 9.337% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-12-11 | 18 | 21.754 | 11.289 | 33.043 | 1.8993 | 0.76558 | 0.24565 | 2.9105 | 8.808% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2010-12-11 | 19 | 21.668 | 11.0937 | 32.7617 | 1.8671 | 0.76558 | 0.24355 | 2.8762 | 8.779% | 9.341% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-12-11 | 20 | 21 | 10.8232 | 31.8232 | 1.7617 | 0.76558 | 0.23658 | 2.7638 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-12-11 | 21 | 20.918 | 10.4294 | 31.3474 | 1.7094 | 0.76558 | 0.23304 | 2.708 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-12-11 | 22 | 20.922 | 10.6465 | 31.5685 | 1.7336 | 0.76558 | 0.23468 | 2.7338 | 8.66% | 9.214% | 6.227% | 1.0948 | 1.1015 | 1.0664
2010-12-11 | 23 | 20.54 | 10.406 | 30.946 | 1.6659 | 0.76558 | 0.23006 | 2.6615 | 8.601% | 9.151% | 6.184% | 1.0941 | 1.1007 | 1.0659
2010-12-11 | 24 | 20.466 | 10.4928 | 30.9588 | 1.6673 | 0.76558 | 0.23015 | 2.663 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2010-12-11 | 25 | 20.148 | 10.4586 | 30.6066 | 1.6295 | 0.76558 | 0.22753 | 2.6226 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-12-11 | 26 | 19.868 | 10.2228 | 30.0908 | 1.5751 | 0.76558 | 0.2237 | 2.5644 | 8.522% | 9.067% | 6.127% | 1.0932 | 1.0997 | 1.0653
2010-12-11 | 27 | 19.654 | 10.325 | 29.979 | 1.5634 | 0.76558 | 0.22287 | 2.5518 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-12-11 | 28 | 19.64 | 10.3792 | 30.0192 | 1.5676 | 0.76558 | 0.22317 | 2.5563 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2010-12-11 | 29 | 19.4903 | 10.1817 | 29.6721 | 1.5315 | 0.76558 | 0.22059 | 2.5177 | 8.485% | 9.028% | 6.101% | 1.0927 | 1.0992 | 1.065
2010-12-11 | 30 | 19.488 | 10.0194 | 29.5074 | 1.5146 | 0.76558 | 0.21936 | 2.4995 | 8.471% | 9.013% | 6.091% | 1.0925 | 1.0991 | 1.0649
2010-12-11 | 31 | 19.624 | 9.7096 | 29.3336 | 1.4968 | 0.76558 | 0.21807 | 2.4805 | 8.456% | 8.997% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-12-11 | 32 | 19.6216 | 10.0809 | 29.7024 | 1.5347 | 0.76558 | 0.22081 | 2.5211 | 8.488% | 9.031% | 6.103% | 1.0928 | 1.0993 | 1.065
2010-12-11 | 33 | 20.1897 | 10.3269 | 30.5166 | 1.62 | 0.76558 | 0.22686 | 2.6124 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2010-12-11 | 34 | 20.3995 | 10.4032 | 30.8027 | 1.6505 | 0.76558 | 0.22899 | 2.6451 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-11 | 35 | 20.5253 | 10.9173 | 31.4426 | 1.7198 | 0.76558 | 0.23375 | 2.7191 | 8.648% | 9.201% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-11 | 36 | 20.7053 | 11.0511 | 31.7564 | 1.7543 | 0.76558 | 0.23608 | 2.7559 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0665
2010-12-11 | 37 | 21.0076 | 11.0534 | 32.061 | 1.7881 | 0.76558 | 0.23835 | 2.792 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-12-11 | 38 | 21.2796 | 11.0038 | 32.2835 | 1.813 | 0.76558 | 0.24 | 2.8186 | 8.731% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-12-11 | 39 | 21.1777 | 10.5842 | 31.7619 | 1.7549 | 0.76558 | 0.23612 | 2.7566 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2010-12-11 | 40 | 21.1197 | 10.4634 | 31.5831 | 1.7352 | 0.76558 | 0.23479 | 2.7356 | 8.661% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-12-11 | 41 | 20.5238 | 10.1572 | 30.681 | 1.6375 | 0.76558 | 0.22809 | 2.6311 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-12-11 | 42 | 20.05 | 9.7281 | 29.7781 | 1.5425 | 0.76558 | 0.22137 | 2.5295 | 8.494% | 9.038% | 6.107% | 1.0928 | 1.0994 | 1.065
2010-12-11 | 43 | 19.6801 | 9.693 | 29.3731 | 1.5008 | 0.76558 | 0.21836 | 2.4848 | 8.459% | 9.001% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-12-11 | 44 | 20.0821 | 9.7361 | 29.8183 | 1.5467 | 0.76558 | 0.22167 | 2.5339 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-12-11 | 45 | 19.76 | 9.4693 | 29.2293 | 1.4862 | 0.76558 | 0.21729 | 2.469 | 8.447% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-12-11 | 46 | 18.6678 | 9.1099 | 27.7777 | 1.3422 | 0.76558 | 0.2065 | 2.3143 | 8.332% | 8.865% | 5.99% | 1.0909 | 1.0973 | 1.0637
2010-12-11 | 47 | 17.3175 | 8.9186 | 26.2361 | 1.1974 | 0.76558 | 0.19504 | 2.158 | 8.225% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2010-12-11 | 48 | 15.9021 | 8.9335 | 24.8355 | 1.073 | 0.76558 | 0.18463 | 2.0232 | 8.146% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-12-12 | 1 | 14.3804 | 8.0694 | 22.4498 | 0.87672 | 0.76558 | 0.16689 | 1.8092 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-12-12 | 2 | 13.3385 | 7.5166 | 20.8551 | 0.75659 | 0.76558 | 0.15504 | 1.6772 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-12 | 3 | 12.6147 | 7.1588 | 19.7735 | 0.68015 | 0.76558 | 0.147 | 1.5927 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-12 | 4 | 12.3789 | 7.0569 | 19.4358 | 0.65711 | 0.76558 | 0.14449 | 1.5672 | 8.063% | 8.579% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-12-12 | 5 | 12.0685 | 7.1609 | 19.2293 | 0.64323 | 0.76558 | 0.14295 | 1.5518 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-12 | 6 | 11.6985 | 7.0222 | 18.7206 | 0.60964 | 0.76558 | 0.13917 | 1.5144 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-12-12 | 7 | 11.5165 | 6.9301 | 18.4466 | 0.59193 | 0.76558 | 0.13713 | 1.4946 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-12-12 | 8 | 11.3445 | 6.8627 | 18.2072 | 0.57666 | 0.76558 | 0.13535 | 1.4776 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-12-12 | 9 | 11.4323 | 6.8719 | 18.3042 | 0.58282 | 0.76558 | 0.13608 | 1.4845 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-12-12 | 10 | 11.1884 | 6.9482 | 18.1366 | 0.5722 | 0.76558 | 0.13483 | 1.4726 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-12-12 | 11 | 11.4565 | 7.1268 | 18.5833 | 0.60073 | 0.76558 | 0.13815 | 1.5045 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-12-12 | 12 | 11.5164 | 7.0038 | 18.5201 | 0.59665 | 0.76558 | 0.13768 | 1.4999 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-12-12 | 13 | 12.6164 | 7.1266 | 19.743 | 0.67805 | 0.76558 | 0.14677 | 1.5904 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-12 | 14 | 13.5799 | 7.3737 | 20.9536 | 0.76375 | 0.76558 | 0.15577 | 1.6851 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-12 | 15 | 15.1603 | 8.0762 | 23.2365 | 0.93924 | 0.76558 | 0.17274 | 1.8776 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-12 | 16 | 16.7399 | 8.8254 | 25.5653 | 1.1369 | 0.76558 | 0.19006 | 2.0926 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2010-12-12 | 17 | 18.3461 | 9.7217 | 28.0678 | 1.3704 | 0.76558 | 0.20866 | 2.3446 | 8.354% | 8.888% | 6.006% | 1.0911 | 1.0976 | 1.0639
2010-12-12 | 18 | 19.8401 | 10.2952 | 30.1353 | 1.5797 | 0.76558 | 0.22403 | 2.5693 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2010-12-12 | 19 | 21.3322 | 10.7101 | 32.0423 | 1.786 | 0.76558 | 0.23821 | 2.7898 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-12-12 | 20 | 22.3217 | 11.0867 | 33.4084 | 1.9415 | 0.76558 | 0.24836 | 2.9555 | 8.847% | 9.413% | 6.361% | 1.0971 | 1.1039 | 1.0679
2010-12-12 | 21 | 22.9032 | 11.1037 | 34.0068 | 2.0117 | 0.76558 | 0.25281 | 3.0301 | 8.91% | 9.481% | 6.406% | 1.0978 | 1.1047 | 1.0685
2010-12-12 | 22 | 22.8612 | 11.2615 | 34.1227 | 2.0254 | 0.76558 | 0.25367 | 3.0447 | 8.923% | 9.494% | 6.415% | 1.098 | 1.1049 | 1.0686
2010-12-12 | 23 | 22.5451 | 10.8175 | 33.3626 | 1.9362 | 0.76558 | 0.24802 | 2.9498 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2010-12-12 | 24 | 21.9892 | 10.7853 | 32.7745 | 1.8686 | 0.76558 | 0.24365 | 2.8778 | 8.781% | 9.343% | 6.313% | 1.0963 | 1.1031 | 1.0674
2010-12-12 | 25 | 21.2271 | 10.755 | 31.9821 | 1.7793 | 0.76558 | 0.23776 | 2.7826 | 8.701% | 9.257% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-12-12 | 26 | 20.7333 | 10.4631 | 31.1964 | 1.693 | 0.76558 | 0.23192 | 2.6904 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-12-12 | 27 | 20.6432 | 10.4458 | 31.089 | 1.6813 | 0.76558 | 0.23112 | 2.678 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2010-12-12 | 28 | 20.1475 | 10.1036 | 30.2511 | 1.5919 | 0.76558 | 0.22489 | 2.5824 | 8.536% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2010-12-12 | 29 | 19.614 | 9.7131 | 29.3271 | 1.4961 | 0.76558 | 0.21802 | 2.4797 | 8.455% | 8.997% | 6.079% | 1.0924 | 1.0989 | 1.0647
2010-12-12 | 30 | 19.3437 | 9.2977 | 28.6413 | 1.427 | 0.76558 | 0.21292 | 2.4055 | 8.399% | 8.936% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-12-12 | 31 | 19.2096 | 9.3646 | 28.5742 | 1.4203 | 0.76558 | 0.21242 | 2.3983 | 8.393% | 8.93% | 6.035% | 1.0916 | 1.0981 | 1.0642
2010-12-12 | 32 | 18.8015 | 9.1681 | 27.9696 | 1.3608 | 0.76558 | 0.20793 | 2.3344 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2010-12-12 | 33 | 18.8738 | 9.4755 | 28.3493 | 1.398 | 0.76558 | 0.21075 | 2.3744 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-12-12 | 34 | 18.8738 | 9.4973 | 28.3712 | 1.4002 | 0.76558 | 0.21091 | 2.3767 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2010-12-12 | 35 | 19.0697 | 9.8432 | 28.9129 | 1.4542 | 0.76558 | 0.21494 | 2.4347 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0644
2010-12-12 | 36 | 19.6654 | 10.1749 | 29.8403 | 1.549 | 0.76558 | 0.22184 | 2.5364 | 8.5% | 9.044% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-12-12 | 37 | 20.1657 | 10.1454 | 30.3111 | 1.5982 | 0.76558 | 0.22534 | 2.5891 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-12-12 | 38 | 20.5819 | 10.0742 | 30.6561 | 1.6348 | 0.76558 | 0.2279 | 2.6283 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-12-12 | 39 | 20.5915 | 9.7751 | 30.3666 | 1.6041 | 0.76558 | 0.22575 | 2.5954 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-12-12 | 40 | 20.3134 | 9.7436 | 30.057 | 1.5715 | 0.76558 | 0.22345 | 2.5606 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2010-12-12 | 41 | 20.2912 | 9.666 | 29.9572 | 1.5611 | 0.76558 | 0.22271 | 2.5494 | 8.51% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-12-12 | 42 | 20.189 | 9.5525 | 29.7414 | 1.5387 | 0.76558 | 0.2211 | 2.5254 | 8.491% | 9.035% | 6.105% | 1.0928 | 1.0993 | 1.065
2010-12-12 | 43 | 20.3767 | 9.5623 | 29.9391 | 1.5592 | 0.76558 | 0.22257 | 2.5474 | 8.509% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2010-12-12 | 44 | 20.6588 | 9.6291 | 30.2878 | 1.5958 | 0.76558 | 0.22516 | 2.5865 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2010-12-12 | 45 | 20.1327 | 9.4541 | 29.5868 | 1.5228 | 0.76558 | 0.21995 | 2.5083 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-12-12 | 46 | 18.9726 | 9.1019 | 28.0745 | 1.3711 | 0.76558 | 0.20871 | 2.3454 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2010-12-12 | 47 | 17.7451 | 8.6637 | 26.4088 | 1.2132 | 0.76558 | 0.19633 | 2.1751 | 8.236% | 8.763% | 5.922% | 1.0898 | 1.0961 | 1.0629
2010-12-12 | 48 | 16.8142 | 8.5372 | 25.3514 | 1.118 | 0.76558 | 0.18847 | 2.072 | 8.173% | 8.696% | 5.877% | 1.089 | 1.0952 | 1.0624
2010-12-13 | 1 | 15.4658 | 7.6166 | 23.0825 | 0.92683 | 0.76558 | 0.1716 | 1.864 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-13 | 2 | 14.5319 | 6.9832 | 21.515 | 0.80523 | 0.76558 | 0.15995 | 1.7308 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-13 | 3 | 13.5978 | 6.8243 | 20.4221 | 0.7255 | 0.76558 | 0.15182 | 1.6429 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-13 | 4 | 12.962 | 6.5934 | 19.5554 | 0.66522 | 0.76558 | 0.14538 | 1.5762 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-13 | 5 | 12.5275 | 6.3726 | 18.9001 | 0.62139 | 0.76558 | 0.14051 | 1.5275 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-13 | 6 | 12.4518 | 6.1785 | 18.6303 | 0.60377 | 0.76558 | 0.1385 | 1.5079 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-13 | 7 | 12.2695 | 6.2835 | 18.553 | 0.59878 | 0.76558 | 0.13793 | 1.5023 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-12-13 | 8 | 12.2177 | 6.3138 | 18.5315 | 0.59739 | 0.76558 | 0.13777 | 1.5007 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-12-13 | 9 | 12.2759 | 6.2265 | 18.5023 | 0.59551 | 0.76558 | 0.13755 | 1.4986 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-12-13 | 10 | 12.2937 | 6.3732 | 18.6669 | 0.60615 | 0.76558 | 0.13877 | 1.5105 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2010-12-13 | 11 | 12.592 | 6.3975 | 18.9894 | 0.62728 | 0.76558 | 0.14117 | 1.534 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-13 | 12 | 12.7596 | 6.3437 | 19.1033 | 0.63482 | 0.76558 | 0.14202 | 1.5424 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-12-13 | 13 | 13.2298 | 6.5019 | 19.7317 | 0.67727 | 0.76558 | 0.14669 | 1.5895 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-13 | 14 | 14.0353 | 6.8085 | 20.8438 | 0.75577 | 0.76558 | 0.15496 | 1.6763 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-13 | 15 | 15.1632 | 7.3889 | 22.5521 | 0.88473 | 0.76558 | 0.16766 | 1.818 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-13 | 16 | 16.5053 | 8.0354 | 24.5407 | 1.0476 | 0.76558 | 0.18244 | 1.9957 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-12-13 | 17 | 18.0534 | 8.9029 | 26.9563 | 1.264 | 0.76558 | 0.2004 | 2.23 | 8.273% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-12-13 | 18 | 19.9212 | 9.4878 | 29.409 | 1.5045 | 0.76558 | 0.21863 | 2.4887 | 8.462% | 9.004% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-12-13 | 19 | 21.3331 | 9.9996 | 31.3327 | 1.7078 | 0.76558 | 0.23293 | 2.7063 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-12-13 | 20 | 22.1112 | 10.2641 | 32.3753 | 1.8233 | 0.76558 | 0.24068 | 2.8296 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2010-12-13 | 21 | 22.8051 | 9.894 | 32.6991 | 1.86 | 0.76558 | 0.24309 | 2.8686 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-12-13 | 22 | 22.437 | 10.0036 | 32.4406 | 1.8307 | 0.76558 | 0.24117 | 2.8374 | 8.747% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2010-12-13 | 23 | 21.7029 | 9.7394 | 31.4423 | 1.7197 | 0.76558 | 0.23375 | 2.7191 | 8.648% | 9.201% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-13 | 24 | 21.6648 | 9.7426 | 31.4075 | 1.7159 | 0.76558 | 0.23349 | 2.715 | 8.644% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-12-13 | 25 | 21.1232 | 9.7847 | 30.9079 | 1.6618 | 0.76558 | 0.22977 | 2.6571 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2010-12-13 | 26 | 20.4833 | 9.3611 | 29.8444 | 1.5494 | 0.76558 | 0.22187 | 2.5368 | 8.5% | 9.044% | 6.112% | 1.0929 | 1.0994 | 1.0651
2010-12-13 | 27 | 20.1685 | 9.4284 | 29.5969 | 1.5238 | 0.76558 | 0.22003 | 2.5094 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-12-13 | 28 | 19.7583 | 9.2588 | 29.0171 | 1.4647 | 0.76558 | 0.21572 | 2.446 | 8.429% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2010-12-13 | 29 | 19.2944 | 8.8448 | 28.1392 | 1.3774 | 0.76558 | 0.20919 | 2.3522 | 8.359% | 8.894% | 6.01% | 1.0912 | 1.0976 | 1.0639
2010-12-13 | 30 | 19.1664 | 8.7927 | 27.9591 | 1.3598 | 0.76558 | 0.20785 | 2.3333 | 8.345% | 8.879% | 6% | 1.0911 | 1.0974 | 1.0638
2010-12-13 | 31 | 19.2806 | 8.6772 | 27.9578 | 1.3597 | 0.76558 | 0.20784 | 2.3331 | 8.345% | 8.879% | 6% | 1.091 | 1.0974 | 1.0638
2010-12-13 | 32 | 19.2086 | 8.5982 | 27.8068 | 1.345 | 0.76558 | 0.20672 | 2.3173 | 8.334% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-12-13 | 33 | 19.4846 | 8.869 | 28.3537 | 1.3985 | 0.76558 | 0.21078 | 2.3748 | 8.376% | 8.912% | 6.022% | 1.0914 | 1.0978 | 1.0641
2010-12-13 | 34 | 19.4062 | 8.8761 | 28.2824 | 1.3914 | 0.76558 | 0.21025 | 2.3673 | 8.37% | 8.906% | 6.018% | 1.0913 | 1.0978 | 1.064
2010-12-13 | 35 | 19.358 | 9.1153 | 28.4733 | 1.4103 | 0.76558 | 0.21167 | 2.3876 | 8.385% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2010-12-13 | 36 | 19.6998 | 9.6128 | 29.3126 | 1.4947 | 0.76558 | 0.21791 | 2.4782 | 8.454% | 8.995% | 6.079% | 1.0923 | 1.0988 | 1.0647
2010-12-13 | 37 | 20.1059 | 9.7987 | 29.9046 | 1.5556 | 0.76558 | 0.22231 | 2.5435 | 8.506% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-12-13 | 38 | 20.4857 | 9.7419 | 30.2276 | 1.5894 | 0.76558 | 0.22472 | 2.5797 | 8.534% | 9.081% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-12-13 | 39 | 20.6693 | 9.5658 | 30.2351 | 1.5902 | 0.76558 | 0.22477 | 2.5806 | 8.535% | 9.081% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-12-13 | 40 | 20.971 | 9.3516 | 30.3225 | 1.5994 | 0.76558 | 0.22542 | 2.5904 | 8.543% | 9.09% | 6.142% | 1.0934 | 1.1 | 1.0654
2010-12-13 | 41 | 20.7957 | 9.1575 | 29.9532 | 1.5607 | 0.76558 | 0.22268 | 2.549 | 8.51% | 9.054% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-12-13 | 42 | 20.9158 | 9.0111 | 29.9269 | 1.558 | 0.76558 | 0.22248 | 2.546 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-12-13 | 43 | 20.8678 | 9.2387 | 30.1065 | 1.5767 | 0.76558 | 0.22382 | 2.5661 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-12-13 | 44 | 21.0496 | 9.3628 | 30.4124 | 1.6089 | 0.76558 | 0.22609 | 2.6006 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2010-12-13 | 45 | 20.5874 | 9.0416 | 29.629 | 1.5271 | 0.76558 | 0.22027 | 2.5129 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-12-13 | 46 | 19.1693 | 8.4477 | 27.617 | 1.3267 | 0.76558 | 0.20531 | 2.2976 | 8.32% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2010-12-13 | 47 | 17.7592 | 8.0851 | 25.8443 | 1.1619 | 0.76558 | 0.19213 | 2.1196 | 8.201% | 8.726% | 5.897% | 1.0893 | 1.0956 | 1.0627
2010-12-13 | 48 | 16.4254 | 8.215 | 24.6404 | 1.0562 | 0.76558 | 0.18318 | 2.0049 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-12-14 | 1 | 14.8355 | 7.2593 | 22.0948 | 0.84921 | 0.76558 | 0.16426 | 1.779 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-12-14 | 2 | 13.8835 | 6.6461 | 20.5296 | 0.73315 | 0.76558 | 0.15262 | 1.6514 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-14 | 3 | 13.1352 | 6.4237 | 19.5589 | 0.66546 | 0.76558 | 0.1454 | 1.5764 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-14 | 4 | 12.539 | 6.0483 | 18.5873 | 0.60099 | 0.76558 | 0.13818 | 1.5047 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-12-14 | 5 | 12.2452 | 5.9723 | 18.2175 | 0.57731 | 0.76558 | 0.13543 | 1.4783 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-12-14 | 6 | 12.0173 | 5.9478 | 17.9651 | 0.56143 | 0.76558 | 0.13355 | 1.4606 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2010-12-14 | 7 | 11.8999 | 6.0921 | 17.992 | 0.56311 | 0.76558 | 0.13375 | 1.4624 | 8.128% | 8.649% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-12-14 | 8 | 11.9976 | 5.9429 | 17.9405 | 0.55989 | 0.76558 | 0.13337 | 1.4588 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2010-12-14 | 9 | 12.2416 | 6.0604 | 18.302 | 0.58268 | 0.76558 | 0.13606 | 1.4843 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-12-14 | 10 | 12.3395 | 6.1073 | 18.4468 | 0.59194 | 0.76558 | 0.13714 | 1.4947 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-12-14 | 11 | 12.6596 | 6.2111 | 18.8707 | 0.61946 | 0.76558 | 0.14029 | 1.5253 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-12-14 | 12 | 12.963 | 6.5455 | 19.5085 | 0.66204 | 0.76558 | 0.14503 | 1.5726 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-14 | 13 | 14.2038 | 7.1117 | 21.3155 | 0.79036 | 0.76558 | 0.15846 | 1.7144 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-14 | 14 | 16.17 | 8.1532 | 24.3232 | 1.0291 | 0.76558 | 0.18082 | 1.9755 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-12-14 | 15 | 19.4421 | 9.6457 | 29.0878 | 1.4718 | 0.76558 | 0.21624 | 2.4536 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-12-14 | 16 | 21.9634 | 10.7042 | 32.6676 | 1.8564 | 0.76558 | 0.24285 | 2.8648 | 8.77% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-12-14 | 17 | 23.8696 | 11.0996 | 34.9692 | 2.1272 | 0.76558 | 0.25997 | 3.1527 | 9.016% | 9.593% | 6.482% | 1.0991 | 1.1061 | 1.0693
2010-12-14 | 18 | 24.2477 | 11.3172 | 35.5649 | 2.2003 | 0.76558 | 0.26439 | 3.2303 | 9.083% | 9.664% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-12-14 | 19 | 24.1295 | 11.4478 | 35.5773 | 2.2018 | 0.76558 | 0.26449 | 3.2319 | 9.084% | 9.665% | 6.531% | 1.0999 | 1.107 | 1.0699
2010-12-14 | 20 | 23.4981 | 11.4535 | 34.9516 | 2.125 | 0.76558 | 0.25983 | 3.1505 | 9.014% | 9.591% | 6.481% | 1.0991 | 1.1061 | 1.0693
2010-12-14 | 21 | 23.3975 | 11.1211 | 34.5186 | 2.0727 | 0.76558 | 0.25662 | 3.0949 | 8.966% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2010-12-14 | 22 | 22.8092 | 11.1665 | 33.9757 | 2.008 | 0.76558 | 0.25258 | 3.0262 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-12-14 | 23 | 22.1975 | 11.0044 | 33.2019 | 1.9176 | 0.76558 | 0.24683 | 2.93 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-12-14 | 24 | 21.4736 | 11.1186 | 32.5923 | 1.8478 | 0.76558 | 0.24229 | 2.8557 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-12-14 | 25 | 20.9716 | 10.9701 | 31.9417 | 1.7748 | 0.76558 | 0.23746 | 2.7778 | 8.697% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2010-12-14 | 26 | 20.8455 | 10.6607 | 31.5063 | 1.7267 | 0.76558 | 0.23422 | 2.7265 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2010-12-14 | 27 | 20.6437 | 10.7519 | 31.3956 | 1.7146 | 0.76558 | 0.2334 | 2.7136 | 8.643% | 9.196% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-12-14 | 28 | 20.6038 | 10.6653 | 31.2691 | 1.7008 | 0.76558 | 0.23246 | 2.6989 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-12-14 | 29 | 20.3497 | 10.2396 | 30.5892 | 1.6277 | 0.76558 | 0.2274 | 2.6207 | 8.567% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-12-14 | 30 | 20.0076 | 10.0589 | 30.0665 | 1.5725 | 0.76558 | 0.22352 | 2.5616 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-12-14 | 31 | 19.8757 | 10.0483 | 29.924 | 1.5577 | 0.76558 | 0.22246 | 2.5457 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-12-14 | 32 | 19.9299 | 10.0655 | 29.9953 | 1.5651 | 0.76558 | 0.22299 | 2.5537 | 8.514% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2010-12-14 | 33 | 20.0417 | 10.5016 | 30.5433 | 1.6228 | 0.76558 | 0.22706 | 2.6154 | 8.563% | 9.111% | 6.157% | 1.0937 | 1.1002 | 1.0656
2010-12-14 | 34 | 20.3658 | 10.6569 | 31.0227 | 1.6741 | 0.76558 | 0.23063 | 2.6704 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2010-12-14 | 35 | 21.0278 | 11.0966 | 32.1244 | 1.7952 | 0.76558 | 0.23882 | 2.7996 | 8.715% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2010-12-14 | 36 | 22.3839 | 11.8875 | 34.2714 | 2.0431 | 0.76558 | 0.25478 | 3.0635 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2010-12-14 | 37 | 23.3777 | 12.2303 | 35.608 | 2.2056 | 0.76558 | 0.26471 | 3.2359 | 9.088% | 9.669% | 6.534% | 1.1 | 1.107 | 1.0699
2010-12-14 | 38 | 23.7717 | 11.8197 | 35.5914 | 2.2036 | 0.76558 | 0.26459 | 3.2337 | 9.086% | 9.667% | 6.533% | 1.0999 | 1.107 | 1.0699
2010-12-14 | 39 | 24.1141 | 11.521 | 35.635 | 2.209 | 0.76558 | 0.26492 | 3.2395 | 9.091% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2010-12-14 | 40 | 24.1759 | 11.2782 | 35.4541 | 2.1866 | 0.76558 | 0.26357 | 3.2157 | 9.07% | 9.651% | 6.521% | 1.0997 | 1.1068 | 1.0698
2010-12-14 | 41 | 24.2821 | 10.7601 | 35.0422 | 2.1361 | 0.76558 | 0.26051 | 3.1622 | 9.024% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-12-14 | 42 | 24.5442 | 10.5452 | 35.0894 | 2.1418 | 0.76558 | 0.26086 | 3.1683 | 9.029% | 9.607% | 6.492% | 1.0993 | 1.1063 | 1.0694
2010-12-14 | 43 | 24.3921 | 10.4766 | 34.8687 | 2.115 | 0.76558 | 0.25922 | 3.1398 | 9.005% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2010-12-14 | 44 | 24.4859 | 10.5562 | 35.0421 | 2.1361 | 0.76558 | 0.26051 | 3.1622 | 9.024% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2010-12-14 | 45 | 23.3156 | 10.0174 | 33.333 | 1.9328 | 0.76558 | 0.2478 | 2.9462 | 8.839% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2010-12-14 | 46 | 21.6831 | 9.0758 | 30.7589 | 1.6458 | 0.76558 | 0.22867 | 2.64 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2010-12-14 | 47 | 19.5791 | 8.5249 | 28.104 | 1.3739 | 0.76558 | 0.20893 | 2.3485 | 8.356% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2010-12-14 | 48 | 18.3512 | 8.3663 | 26.7175 | 1.2417 | 0.76558 | 0.19862 | 2.2059 | 8.256% | 8.785% | 5.936% | 1.09 | 1.0963 | 1.0631
2010-12-15 | 1 | 16.6752 | 7.5349 | 24.2101 | 1.0196 | 0.76558 | 0.17998 | 1.9652 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-12-15 | 2 | 15.2454 | 7.0059 | 22.2513 | 0.86128 | 0.76558 | 0.16542 | 1.7923 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-15 | 3 | 14.5214 | 6.714 | 21.2355 | 0.78444 | 0.76558 | 0.15787 | 1.7079 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-15 | 4 | 13.9074 | 6.4257 | 20.3331 | 0.71919 | 0.76558 | 0.15116 | 1.6359 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-15 | 5 | 13.7254 | 6.2982 | 20.0236 | 0.69746 | 0.76558 | 0.14886 | 1.6119 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-15 | 6 | 13.4253 | 6.2405 | 19.6658 | 0.67276 | 0.76558 | 0.1462 | 1.5845 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-12-15 | 7 | 13.2372 | 6.088 | 19.3252 | 0.64965 | 0.76558 | 0.14367 | 1.5589 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-12-15 | 8 | 13.2452 | 6.056 | 19.3013 | 0.64805 | 0.76558 | 0.14349 | 1.5571 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2010-12-15 | 9 | 13.2292 | 6.0507 | 19.2799 | 0.64661 | 0.76558 | 0.14333 | 1.5555 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-15 | 10 | 13.4432 | 6.1992 | 19.6424 | 0.67116 | 0.76558 | 0.14602 | 1.5828 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-15 | 11 | 13.9692 | 6.4233 | 20.3924 | 0.72339 | 0.76558 | 0.1516 | 1.6406 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-15 | 12 | 14.479 | 6.8201 | 21.2991 | 0.78915 | 0.76558 | 0.15834 | 1.7131 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-15 | 13 | 15.9911 | 7.671 | 23.6621 | 0.97396 | 0.76558 | 0.17591 | 1.9154 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-15 | 14 | 18.1137 | 8.8507 | 26.9644 | 1.2648 | 0.76558 | 0.20046 | 2.2308 | 8.273% | 8.803% | 5.948% | 1.0902 | 1.0965 | 1.0632
2010-12-15 | 15 | 21.7102 | 10.3623 | 32.0725 | 1.7894 | 0.76558 | 0.23843 | 2.7934 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-12-15 | 16 | 24.24 | 11.6784 | 35.9184 | 2.2442 | 0.76558 | 0.26702 | 3.2768 | 9.123% | 9.707% | 6.559% | 1.1004 | 1.1075 | 1.0702
2010-12-15 | 17 | 25.1897 | 12.0708 | 37.2605 | 2.4151 | 0.76558 | 0.277 | 3.4577 | 9.28% | 9.874% | 6.672% | 1.1023 | 1.1096 | 1.0715
2010-12-15 | 18 | 25.312 | 12.0555 | 37.3675 | 2.429 | 0.76558 | 0.27779 | 3.4723 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2010-12-15 | 19 | 24.9177 | 11.7346 | 36.6523 | 2.3369 | 0.76558 | 0.27248 | 3.3749 | 9.208% | 9.797% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-12-15 | 20 | 24.2622 | 11.3815 | 35.6437 | 2.21 | 0.76558 | 0.26498 | 3.2406 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-12-15 | 21 | 23.7399 | 11.0277 | 34.7677 | 2.1027 | 0.76558 | 0.25847 | 3.1268 | 8.993% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2010-12-15 | 22 | 23.1098 | 11.0554 | 34.1653 | 2.0305 | 0.76558 | 0.25399 | 3.0501 | 8.927% | 9.499% | 6.419% | 1.098 | 1.105 | 1.0686
2010-12-15 | 23 | 22.4974 | 10.8822 | 33.3796 | 1.9382 | 0.76558 | 0.24815 | 2.9519 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2010-12-15 | 24 | 21.9311 | 10.7244 | 32.6555 | 1.855 | 0.76558 | 0.24277 | 2.8634 | 8.768% | 9.33% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-12-15 | 25 | 21.271 | 10.7101 | 31.981 | 1.7792 | 0.76558 | 0.23775 | 2.7825 | 8.7% | 9.257% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-12-15 | 26 | 20.835 | 10.2774 | 31.1124 | 1.6838 | 0.76558 | 0.23129 | 2.6807 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-15 | 27 | 20.6751 | 10.4389 | 31.114 | 1.684 | 0.76558 | 0.23131 | 2.6809 | 8.616% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-15 | 28 | 20.4513 | 10.4209 | 30.8722 | 1.6579 | 0.76558 | 0.22951 | 2.653 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-12-15 | 29 | 20.4738 | 10.0212 | 30.4949 | 1.6177 | 0.76558 | 0.2267 | 2.61 | 8.559% | 9.106% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-12-15 | 30 | 20.0722 | 9.8068 | 29.879 | 1.553 | 0.76558 | 0.22212 | 2.5407 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-15 | 31 | 19.9359 | 9.8576 | 29.7935 | 1.5441 | 0.76558 | 0.22149 | 2.5312 | 8.496% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2010-12-15 | 32 | 20.0761 | 9.6769 | 29.753 | 1.5399 | 0.76558 | 0.22119 | 2.5267 | 8.492% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2010-12-15 | 33 | 20.0101 | 9.9065 | 29.9166 | 1.5569 | 0.76558 | 0.2224 | 2.5449 | 8.507% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2010-12-15 | 34 | 20.6019 | 9.9831 | 30.585 | 1.6272 | 0.76558 | 0.22737 | 2.6202 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-12-15 | 35 | 20.9719 | 10.517 | 31.4889 | 1.7248 | 0.76558 | 0.23409 | 2.7245 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-12-15 | 36 | 21.6335 | 10.9993 | 32.6328 | 1.8524 | 0.76558 | 0.2426 | 2.8606 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-12-15 | 37 | 22.7416 | 11.2397 | 33.9813 | 2.0087 | 0.76558 | 0.25262 | 3.0269 | 8.908% | 9.478% | 6.405% | 1.0978 | 1.1047 | 1.0684
2010-12-15 | 38 | 23.1435 | 11.1802 | 34.3237 | 2.0494 | 0.76558 | 0.25517 | 3.0701 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2010-12-15 | 39 | 22.9055 | 10.9125 | 33.818 | 1.9894 | 0.76558 | 0.25141 | 3.0064 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-12-15 | 40 | 22.6815 | 10.4046 | 33.0861 | 1.9043 | 0.76558 | 0.24597 | 2.9158 | 8.813% | 9.377% | 6.336% | 1.0966 | 1.1035 | 1.0677
2010-12-15 | 41 | 22.4078 | 9.9886 | 32.3964 | 1.8257 | 0.76558 | 0.24084 | 2.8321 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-12-15 | 42 | 22.4198 | 9.8751 | 32.2948 | 1.8143 | 0.76558 | 0.24008 | 2.8199 | 8.732% | 9.291% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-12-15 | 43 | 22.7349 | 9.8588 | 32.5937 | 1.848 | 0.76558 | 0.24231 | 2.8559 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-12-15 | 44 | 22.9568 | 10.0988 | 33.0556 | 1.9007 | 0.76558 | 0.24574 | 2.9121 | 8.81% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2010-12-15 | 45 | 22.0246 | 9.6294 | 31.654 | 1.743 | 0.76558 | 0.23532 | 2.7439 | 8.668% | 9.223% | 6.233% | 1.0949 | 1.1016 | 1.0665
2010-12-15 | 46 | 20.5405 | 9.084 | 29.6244 | 1.5266 | 0.76558 | 0.22023 | 2.5124 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-12-15 | 47 | 18.9183 | 8.6379 | 27.5562 | 1.3209 | 0.76558 | 0.20486 | 2.2913 | 8.315% | 8.847% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-12-15 | 48 | 17.5145 | 8.5607 | 26.0752 | 1.1827 | 0.76558 | 0.19385 | 2.1422 | 8.215% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2010-12-16 | 1 | 15.8303 | 7.6563 | 23.4866 | 0.95956 | 0.76558 | 0.1746 | 1.8997 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-12-16 | 2 | 14.6003 | 7.0876 | 21.6878 | 0.81821 | 0.76558 | 0.16123 | 1.745 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-16 | 3 | 13.91 | 6.6202 | 20.5303 | 0.7332 | 0.76558 | 0.15262 | 1.6514 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-16 | 4 | 13.3041 | 6.499 | 19.8031 | 0.68218 | 0.76558 | 0.14722 | 1.595 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-16 | 5 | 12.9279 | 6.3625 | 19.2904 | 0.64732 | 0.76558 | 0.14341 | 1.5563 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-16 | 6 | 12.4487 | 6.279 | 18.7276 | 0.6101 | 0.76558 | 0.13922 | 1.5149 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2010-12-16 | 7 | 12.2547 | 6.1748 | 18.4295 | 0.59083 | 0.76558 | 0.13701 | 1.4934 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2010-12-16 | 8 | 11.8709 | 6.1261 | 17.997 | 0.56342 | 0.76558 | 0.13379 | 1.4628 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2010-12-16 | 9 | 12.0889 | 6.3361 | 18.425 | 0.59054 | 0.76558 | 0.13697 | 1.4931 | 8.104% | 8.622% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-12-16 | 10 | 12.4891 | 6.5186 | 19.0078 | 0.62849 | 0.76558 | 0.14131 | 1.5354 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-16 | 11 | 13.1691 | 6.7879 | 19.9569 | 0.69282 | 0.76558 | 0.14836 | 1.6068 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-16 | 12 | 13.4052 | 6.9615 | 20.3667 | 0.72157 | 0.76558 | 0.15141 | 1.6386 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-16 | 13 | 14.8407 | 7.6142 | 22.4549 | 0.87712 | 0.76558 | 0.16693 | 1.8096 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-12-16 | 14 | 17.0608 | 8.661 | 25.7218 | 1.1509 | 0.76558 | 0.19122 | 2.1077 | 8.194% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2010-12-16 | 15 | 20.2991 | 10.2859 | 30.5851 | 1.6272 | 0.76558 | 0.22737 | 2.6202 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2010-12-16 | 16 | 22.5617 | 11.5066 | 34.0683 | 2.019 | 0.76558 | 0.25327 | 3.0378 | 8.917% | 9.488% | 6.411% | 1.0979 | 1.1048 | 1.0685
2010-12-16 | 17 | 23.9117 | 12.3463 | 36.2579 | 2.2869 | 0.76558 | 0.26955 | 3.322 | 9.162% | 9.748% | 6.588% | 1.1009 | 1.108 | 1.0705
2010-12-16 | 18 | 24.5952 | 12.3926 | 36.9878 | 2.3799 | 0.76558 | 0.27497 | 3.4204 | 9.247% | 9.839% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-12-16 | 19 | 24.1091 | 12.3063 | 36.4154 | 2.3068 | 0.76558 | 0.27072 | 3.3431 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-12-16 | 20 | 23.7869 | 12.0062 | 35.7931 | 2.2286 | 0.76558 | 0.26609 | 3.2603 | 9.109% | 9.692% | 6.549% | 1.1002 | 1.1073 | 1.0701
2010-12-16 | 21 | 23.3089 | 11.5909 | 34.8998 | 2.1188 | 0.76558 | 0.25945 | 3.1438 | 9.008% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2010-12-16 | 22 | 22.6849 | 11.5502 | 34.2351 | 2.0388 | 0.76558 | 0.25451 | 3.0589 | 8.935% | 9.507% | 6.424% | 1.0981 | 1.1051 | 1.0687
2010-12-16 | 23 | 21.831 | 11.3871 | 33.2181 | 1.9195 | 0.76558 | 0.24695 | 2.932 | 8.827% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2010-12-16 | 24 | 21.5228 | 11.4808 | 33.0035 | 1.8948 | 0.76558 | 0.24535 | 2.9057 | 8.804% | 9.368% | 6.33% | 1.0965 | 1.1034 | 1.0676
2010-12-16 | 25 | 20.9358 | 11.4048 | 32.3405 | 1.8194 | 0.76558 | 0.24042 | 2.8254 | 8.736% | 9.296% | 6.281% | 1.0957 | 1.1025 | 1.067
2010-12-16 | 26 | 20.5779 | 11.1173 | 31.6952 | 1.7475 | 0.76558 | 0.23563 | 2.7487 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1017 | 1.0665
2010-12-16 | 27 | 20.294 | 11.2624 | 31.5564 | 1.7322 | 0.76558 | 0.23459 | 2.7324 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-12-16 | 28 | 20.2803 | 11.2098 | 31.4901 | 1.725 | 0.76558 | 0.2341 | 2.7247 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-12-16 | 29 | 19.9525 | 10.9881 | 30.9406 | 1.6653 | 0.76558 | 0.23002 | 2.6609 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-12-16 | 30 | 19.6528 | 10.554 | 30.2067 | 1.5872 | 0.76558 | 0.22456 | 2.5774 | 8.532% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2010-12-16 | 31 | 19.5509 | 10.3352 | 29.886 | 1.5537 | 0.76558 | 0.22218 | 2.5415 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-16 | 32 | 19.5632 | 10.0087 | 29.5719 | 1.5212 | 0.76558 | 0.21984 | 2.5066 | 8.476% | 9.019% | 6.095% | 1.0926 | 1.0991 | 1.0649
2010-12-16 | 33 | 20.0214 | 10.2481 | 30.2695 | 1.5938 | 0.76558 | 0.22503 | 2.5844 | 8.538% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-12-16 | 34 | 20.1135 | 10.1242 | 30.2377 | 1.5905 | 0.76558 | 0.22479 | 2.5809 | 8.535% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-12-16 | 35 | 19.9055 | 10.4717 | 30.3771 | 1.6052 | 0.76558 | 0.22583 | 2.5966 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2010-12-16 | 36 | 20.4596 | 10.9155 | 31.3751 | 1.7124 | 0.76558 | 0.23325 | 2.7112 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2010-12-16 | 37 | 21.1177 | 10.8989 | 32.0166 | 1.7831 | 0.76558 | 0.23802 | 2.7867 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-12-16 | 38 | 21.4236 | 10.9804 | 32.4039 | 1.8265 | 0.76558 | 0.24089 | 2.833 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2010-12-16 | 39 | 21.2638 | 10.8272 | 32.091 | 1.7914 | 0.76558 | 0.23857 | 2.7956 | 8.711% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-12-16 | 40 | 21.406 | 10.4501 | 31.8561 | 1.7653 | 0.76558 | 0.23682 | 2.7677 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-12-16 | 41 | 21.3722 | 10.0669 | 31.4391 | 1.7194 | 0.76558 | 0.23372 | 2.7187 | 8.647% | 9.201% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-16 | 42 | 20.9863 | 9.9318 | 30.9181 | 1.6629 | 0.76558 | 0.22985 | 2.6583 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-12-16 | 43 | 20.9387 | 10.1241 | 31.0628 | 1.6785 | 0.76558 | 0.23092 | 2.675 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-12-16 | 44 | 21.4931 | 10.5609 | 32.0539 | 1.7873 | 0.76558 | 0.23829 | 2.7912 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-12-16 | 45 | 20.989 | 10.4088 | 31.3978 | 1.7149 | 0.76558 | 0.23342 | 2.7139 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-12-16 | 46 | 20.0789 | 9.8252 | 29.904 | 1.5556 | 0.76558 | 0.22231 | 2.5435 | 8.505% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2010-12-16 | 47 | 18.4809 | 9.3079 | 27.7888 | 1.3433 | 0.76558 | 0.20659 | 2.3155 | 8.332% | 8.866% | 5.991% | 1.0909 | 1.0973 | 1.0637
2010-12-16 | 48 | 17.2048 | 9.1337 | 26.3385 | 1.2067 | 0.76558 | 0.1958 | 2.1681 | 8.232% | 8.759% | 5.919% | 1.0897 | 1.096 | 1.0629
2010-12-17 | 1 | 15.3607 | 8.2913 | 23.652 | 0.97313 | 0.76558 | 0.17583 | 1.9145 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-17 | 2 | 14.1287 | 7.6598 | 21.7886 | 0.82583 | 0.76558 | 0.16198 | 1.7534 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-17 | 3 | 13.1449 | 7.2999 | 20.4447 | 0.72711 | 0.76558 | 0.15199 | 1.6447 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-17 | 4 | 12.4464 | 7.0632 | 19.5096 | 0.66211 | 0.76558 | 0.14504 | 1.5727 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-17 | 5 | 12.0618 | 6.9477 | 19.0095 | 0.6286 | 0.76558 | 0.14132 | 1.5355 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-17 | 6 | 11.7942 | 6.8911 | 18.6853 | 0.60734 | 0.76558 | 0.13891 | 1.5118 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-12-17 | 7 | 11.6858 | 6.9255 | 18.6114 | 0.60255 | 0.76558 | 0.13836 | 1.5065 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-17 | 8 | 11.7716 | 6.8564 | 18.628 | 0.60362 | 0.76558 | 0.13848 | 1.5077 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-17 | 9 | 12.0499 | 6.8796 | 18.9295 | 0.62332 | 0.76558 | 0.14072 | 1.5296 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-17 | 10 | 12.2179 | 6.8009 | 19.0188 | 0.62922 | 0.76558 | 0.14139 | 1.5362 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-12-17 | 11 | 12.5077 | 6.9583 | 19.4659 | 0.65915 | 0.76558 | 0.14471 | 1.5694 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-12-17 | 12 | 12.9298 | 7.2788 | 20.2086 | 0.7104 | 0.76558 | 0.15023 | 1.6262 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-17 | 13 | 14.3199 | 7.9435 | 22.2634 | 0.86222 | 0.76558 | 0.16551 | 1.7933 | 8.055% | 8.57% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-17 | 14 | 16.3243 | 8.8602 | 25.1845 | 1.1033 | 0.76558 | 0.18722 | 2.0561 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2010-12-17 | 15 | 19.2744 | 10.0872 | 29.3617 | 1.4997 | 0.76558 | 0.21828 | 2.4835 | 8.458% | 9% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-12-17 | 16 | 21.3067 | 10.9554 | 32.2621 | 1.8106 | 0.76558 | 0.23984 | 2.816 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-12-17 | 17 | 22.6585 | 11.5912 | 34.2497 | 2.0405 | 0.76558 | 0.25462 | 3.0607 | 8.937% | 9.509% | 6.425% | 1.0981 | 1.1051 | 1.0687
2010-12-17 | 18 | 23.1984 | 11.535 | 34.7334 | 2.0986 | 0.76558 | 0.25821 | 3.1224 | 8.99% | 9.565% | 6.464% | 1.0988 | 1.1058 | 1.0691
2010-12-17 | 19 | 22.8786 | 11.5815 | 34.4601 | 2.0657 | 0.76558 | 0.25618 | 3.0875 | 8.96% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2010-12-17 | 20 | 22.3724 | 11.4344 | 33.8068 | 1.9881 | 0.76558 | 0.25132 | 3.005 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-12-17 | 21 | 22.2641 | 11.1272 | 33.3913 | 1.9396 | 0.76558 | 0.24824 | 2.9534 | 8.845% | 9.411% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-12-17 | 22 | 21.7178 | 11.1275 | 32.8453 | 1.8766 | 0.76558 | 0.24418 | 2.8864 | 8.788% | 9.35% | 6.318% | 1.0963 | 1.1031 | 1.0674
2010-12-17 | 23 | 21.4575 | 11.0394 | 32.4969 | 1.837 | 0.76558 | 0.24159 | 2.8442 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-17 | 24 | 20.8371 | 11.0923 | 31.9295 | 1.7734 | 0.76558 | 0.23737 | 2.7764 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2010-12-17 | 25 | 20.6563 | 11.234 | 31.8902 | 1.7691 | 0.76558 | 0.23708 | 2.7717 | 8.692% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-12-17 | 26 | 20.3714 | 10.982 | 31.3534 | 1.71 | 0.76558 | 0.23309 | 2.7087 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-12-17 | 27 | 20.179 | 11.2152 | 31.3942 | 1.7145 | 0.76558 | 0.23339 | 2.7135 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2010-12-17 | 28 | 20.1153 | 11.1634 | 31.2787 | 1.7019 | 0.76558 | 0.23253 | 2.7 | 8.632% | 9.185% | 6.206% | 1.0945 | 1.1011 | 1.0662
2010-12-17 | 29 | 20.0116 | 10.7937 | 30.8053 | 1.6508 | 0.76558 | 0.22901 | 2.6454 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2010-12-17 | 30 | 19.7158 | 10.6382 | 30.354 | 1.6028 | 0.76558 | 0.22566 | 2.594 | 8.546% | 9.093% | 6.144% | 1.0934 | 1.1 | 1.0655
2010-12-17 | 31 | 19.7438 | 10.62 | 30.3638 | 1.6038 | 0.76558 | 0.22573 | 2.5951 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2010-12-17 | 32 | 19.7362 | 10.4914 | 30.2275 | 1.5894 | 0.76558 | 0.22472 | 2.5797 | 8.534% | 9.081% | 6.136% | 1.0933 | 1.0999 | 1.0654
2010-12-17 | 33 | 20.004 | 10.6502 | 30.6542 | 1.6346 | 0.76558 | 0.22789 | 2.6281 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-12-17 | 34 | 20.1018 | 10.6848 | 30.7866 | 1.6488 | 0.76558 | 0.22887 | 2.6432 | 8.586% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-12-17 | 35 | 20.1619 | 11.1591 | 31.321 | 1.7065 | 0.76558 | 0.23284 | 2.7049 | 8.636% | 9.189% | 6.209% | 1.0945 | 1.1012 | 1.0662
2010-12-17 | 36 | 20.5961 | 11.204 | 31.8001 | 1.7591 | 0.76558 | 0.23641 | 2.7611 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-12-17 | 37 | 21.0422 | 11.5844 | 32.6265 | 1.8517 | 0.76558 | 0.24255 | 2.8599 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1029 | 1.0673
2010-12-17 | 38 | 21.5089 | 11.6627 | 33.1717 | 1.9141 | 0.76558 | 0.2466 | 2.9263 | 8.822% | 9.386% | 6.343% | 1.0968 | 1.1036 | 1.0677
2010-12-17 | 39 | 21.4272 | 11.3448 | 32.772 | 1.8683 | 0.76558 | 0.24363 | 2.8775 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.103 | 1.0674
2010-12-17 | 40 | 21.5833 | 11.0558 | 32.6391 | 1.8532 | 0.76558 | 0.24264 | 2.8614 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-12-17 | 41 | 21.6415 | 10.6691 | 32.3106 | 1.816 | 0.76558 | 0.2402 | 2.8218 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2010-12-17 | 42 | 21.3076 | 10.6488 | 31.9565 | 1.7764 | 0.76558 | 0.23757 | 2.7796 | 8.698% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2010-12-17 | 43 | 21.2073 | 10.8482 | 32.0555 | 1.7875 | 0.76558 | 0.2383 | 2.7914 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-12-17 | 44 | 21.5173 | 11.146 | 32.6633 | 1.8559 | 0.76558 | 0.24282 | 2.8643 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2010-12-17 | 45 | 20.9813 | 10.8407 | 31.822 | 1.7615 | 0.76558 | 0.23657 | 2.7637 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-12-17 | 46 | 19.7133 | 10.1248 | 29.8382 | 1.5487 | 0.76558 | 0.22182 | 2.5361 | 8.5% | 9.044% | 6.111% | 1.0929 | 1.0994 | 1.0651
2010-12-17 | 47 | 18.1535 | 9.499 | 27.6525 | 1.3302 | 0.76558 | 0.20557 | 2.3013 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-12-17 | 48 | 16.8596 | 9.2569 | 26.1164 | 1.1865 | 0.76558 | 0.19415 | 2.1462 | 8.218% | 8.744% | 5.909% | 1.0895 | 1.0958 | 1.0628
2010-12-18 | 1 | 15.2036 | 8.2378 | 23.4414 | 0.95588 | 0.76558 | 0.17427 | 1.8957 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2010-12-18 | 2 | 13.8974 | 7.6846 | 21.582 | 0.81025 | 0.76558 | 0.16044 | 1.7363 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-18 | 3 | 13.0711 | 7.2679 | 20.339 | 0.71961 | 0.76558 | 0.1512 | 1.6364 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-18 | 4 | 12.5013 | 6.99 | 19.4913 | 0.66087 | 0.76558 | 0.1449 | 1.5714 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-18 | 5 | 12.2331 | 7.0167 | 19.2498 | 0.6446 | 0.76558 | 0.14311 | 1.5533 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-18 | 6 | 11.9196 | 6.9741 | 18.8937 | 0.62097 | 0.76558 | 0.14046 | 1.527 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-18 | 7 | 11.7414 | 6.9474 | 18.6889 | 0.60758 | 0.76558 | 0.13894 | 1.5121 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-12-18 | 8 | 11.731 | 7.004 | 18.735 | 0.61058 | 0.76558 | 0.13928 | 1.5154 | 8.089% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2010-12-18 | 9 | 11.5747 | 6.8366 | 18.4113 | 0.58966 | 0.76558 | 0.13687 | 1.4921 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-12-18 | 10 | 11.6525 | 6.7926 | 18.4451 | 0.59183 | 0.76558 | 0.13712 | 1.4945 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-12-18 | 11 | 11.9417 | 6.9513 | 18.893 | 0.62092 | 0.76558 | 0.14045 | 1.5269 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-18 | 12 | 12.6125 | 7.2092 | 19.8217 | 0.68347 | 0.76558 | 0.14736 | 1.5964 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-18 | 13 | 13.859 | 7.6972 | 21.5561 | 0.80831 | 0.76558 | 0.16025 | 1.7341 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-18 | 14 | 15.8428 | 7.8712 | 23.7139 | 0.97823 | 0.76558 | 0.17629 | 1.9201 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2010-12-18 | 15 | 18.8369 | 8.8463 | 27.6832 | 1.3331 | 0.76558 | 0.2058 | 2.3045 | 8.325% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2010-12-18 | 16 | 21.3368 | 9.7814 | 31.1182 | 1.6845 | 0.76558 | 0.23134 | 2.6814 | 8.617% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-18 | 17 | 22.9086 | 10.5578 | 33.4664 | 1.9483 | 0.76558 | 0.24879 | 2.9627 | 8.853% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2010-12-18 | 18 | 23.283 | 10.9395 | 34.2225 | 2.0373 | 0.76558 | 0.25441 | 3.0573 | 8.934% | 9.505% | 6.423% | 1.0981 | 1.105 | 1.0686
2010-12-18 | 19 | 23.1104 | 11.0051 | 34.1155 | 2.0246 | 0.76558 | 0.25362 | 3.0438 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-12-18 | 20 | 22.7841 | 10.918 | 33.7021 | 1.9758 | 0.76558 | 0.25055 | 2.9919 | 8.878% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-12-18 | 21 | 22.6251 | 10.9296 | 33.5547 | 1.9586 | 0.76558 | 0.24945 | 2.9736 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-12-18 | 22 | 22.4211 | 10.9811 | 33.4022 | 1.9408 | 0.76558 | 0.24832 | 2.9547 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-12-18 | 23 | 21.9508 | 10.6475 | 32.5983 | 1.8485 | 0.76558 | 0.24234 | 2.8564 | 8.763% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2010-12-18 | 24 | 21.5908 | 10.3932 | 31.984 | 1.7795 | 0.76558 | 0.23777 | 2.7829 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-12-18 | 25 | 21.2863 | 10.6099 | 31.8962 | 1.7697 | 0.76558 | 0.23712 | 2.7724 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2010-12-18 | 26 | 20.8951 | 10.5513 | 31.4463 | 1.7202 | 0.76558 | 0.23378 | 2.7195 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-18 | 27 | 20.3052 | 10.631 | 30.9363 | 1.6648 | 0.76558 | 0.22998 | 2.6604 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-12-18 | 28 | 19.9526 | 10.8984 | 30.851 | 1.6557 | 0.76558 | 0.22935 | 2.6506 | 8.592% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2010-12-18 | 29 | 19.5056 | 10.6493 | 30.1549 | 1.5818 | 0.76558 | 0.22417 | 2.5715 | 8.528% | 9.074% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-12-18 | 30 | 19.0455 | 10.3576 | 29.4032 | 1.5039 | 0.76558 | 0.21859 | 2.4881 | 8.462% | 9.004% | 6.084% | 1.0924 | 1.0989 | 1.0648
2010-12-18 | 31 | 19.1823 | 10.2081 | 29.3904 | 1.5026 | 0.76558 | 0.21849 | 2.4867 | 8.461% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2010-12-18 | 32 | 19.9345 | 10.2232 | 30.1577 | 1.5821 | 0.76558 | 0.2242 | 2.5719 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-12-18 | 33 | 20.0185 | 10.6744 | 30.6929 | 1.6387 | 0.76558 | 0.22818 | 2.6325 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-12-18 | 34 | 20.2263 | 10.6598 | 30.886 | 1.6594 | 0.76558 | 0.22961 | 2.6546 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-12-18 | 35 | 20.9679 | 10.7728 | 31.7407 | 1.7525 | 0.76558 | 0.23596 | 2.7541 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2010-12-18 | 36 | 21.5539 | 10.7101 | 32.2639 | 1.8108 | 0.76558 | 0.23985 | 2.8162 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-12-18 | 37 | 22.004 | 10.7003 | 32.7043 | 1.8606 | 0.76558 | 0.24313 | 2.8693 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-12-18 | 38 | 22.5323 | 10.6651 | 33.1974 | 1.9171 | 0.76558 | 0.24679 | 2.9295 | 8.824% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-12-18 | 39 | 22.4266 | 10.4901 | 32.9168 | 1.8848 | 0.76558 | 0.24471 | 2.8951 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2010-12-18 | 40 | 22.3484 | 10.2857 | 32.634 | 1.8526 | 0.76558 | 0.24261 | 2.8608 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2010-12-18 | 41 | 22.354 | 10.2911 | 32.6452 | 1.8538 | 0.76558 | 0.24269 | 2.8621 | 8.767% | 9.328% | 6.304% | 1.0961 | 1.1029 | 1.0673
2010-12-18 | 42 | 21.7093 | 10.5138 | 32.2231 | 1.8062 | 0.76558 | 0.23955 | 2.8113 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-12-18 | 43 | 21.086 | 10.4988 | 31.5848 | 1.7354 | 0.76558 | 0.23481 | 2.7357 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2010-12-18 | 44 | 21.0155 | 10.3593 | 31.3749 | 1.7124 | 0.76558 | 0.23324 | 2.7112 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2010-12-18 | 45 | 17.4493 | 10.118 | 27.5672 | 1.322 | 0.76558 | 0.20494 | 2.2925 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-12-18 | 46 | 16.1846 | 9.0562 | 25.2408 | 1.1083 | 0.76558 | 0.18764 | 2.0615 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-12-18 | 47 | 15.0733 | 8.7026 | 23.7758 | 0.98334 | 0.76558 | 0.17675 | 1.9257 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2010-12-18 | 48 | 14.0011 | 8.746 | 22.7471 | 0.90009 | 0.76558 | 0.1691 | 1.8348 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-19 | 1 | 12.9194 | 7.7505 | 20.6699 | 0.74321 | 0.76558 | 0.15366 | 1.6625 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-19 | 2 | 13.8895 | 7.2894 | 21.1789 | 0.78026 | 0.76558 | 0.15745 | 1.7033 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-19 | 3 | 13.9032 | 7.015 | 20.9182 | 0.76117 | 0.76558 | 0.15551 | 1.6823 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-19 | 4 | 12.7728 | 6.7589 | 19.5316 | 0.66361 | 0.76558 | 0.1452 | 1.5744 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-19 | 5 | 12.2666 | 6.6383 | 18.9049 | 0.62171 | 0.76558 | 0.14054 | 1.5278 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-19 | 6 | 11.7812 | 6.6026 | 18.3838 | 0.5879 | 0.76558 | 0.13667 | 1.4901 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-12-19 | 7 | 11.5571 | 6.3882 | 17.9452 | 0.56019 | 0.76558 | 0.13341 | 1.4592 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-12-19 | 8 | 11.2089 | 6.2511 | 17.46 | 0.5303 | 0.76558 | 0.1298 | 1.4257 | 8.165% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-12-19 | 9 | 11.4391 | 6.2868 | 17.7259 | 0.54658 | 0.76558 | 0.13178 | 1.4439 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-12-19 | 10 | 11.5191 | 6.3972 | 17.9163 | 0.55838 | 0.76558 | 0.13319 | 1.4572 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2010-12-19 | 11 | 11.9755 | 6.3708 | 18.3463 | 0.58551 | 0.76558 | 0.13639 | 1.4875 | 8.108% | 8.627% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-12-19 | 12 | 12.0952 | 6.5271 | 18.6222 | 0.60325 | 0.76558 | 0.13844 | 1.5073 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-19 | 13 | 12.8951 | 6.8315 | 19.7266 | 0.67692 | 0.76558 | 0.14665 | 1.5891 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0938 | 1.0615
2010-12-19 | 14 | 13.9129 | 7.1516 | 21.0645 | 0.77186 | 0.76558 | 0.1566 | 1.694 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-19 | 15 | 15.4347 | 8.0174 | 23.4521 | 0.95675 | 0.76558 | 0.17435 | 1.8967 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-12-19 | 16 | 17.1651 | 9.1706 | 26.3357 | 1.2065 | 0.76558 | 0.19578 | 2.1678 | 8.232% | 8.758% | 5.919% | 1.0897 | 1.096 | 1.0629
2010-12-19 | 17 | 18.8573 | 10.3228 | 29.18 | 1.4812 | 0.76558 | 0.21693 | 2.4637 | 8.443% | 8.983% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-12-19 | 18 | 20.7915 | 11.007 | 31.7985 | 1.7589 | 0.76558 | 0.23639 | 2.7609 | 8.682% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-12-19 | 19 | 21.9613 | 11.5819 | 33.5432 | 1.9572 | 0.76558 | 0.24936 | 2.9722 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2010-12-19 | 20 | 22.4612 | 11.7686 | 34.2298 | 2.0382 | 0.76558 | 0.25447 | 3.0582 | 8.934% | 9.506% | 6.424% | 1.0981 | 1.105 | 1.0686
2010-12-19 | 21 | 22.6872 | 11.7678 | 34.455 | 2.0651 | 0.76558 | 0.25614 | 3.0868 | 8.959% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2010-12-19 | 22 | 22.3472 | 11.9613 | 34.3085 | 2.0476 | 0.76558 | 0.25505 | 3.0682 | 8.943% | 9.515% | 6.43% | 1.0982 | 1.1052 | 1.0687
2010-12-19 | 23 | 21.4966 | 11.8851 | 33.3817 | 1.9384 | 0.76558 | 0.24816 | 2.9522 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-12-19 | 24 | 21.051 | 11.7624 | 32.8134 | 1.873 | 0.76558 | 0.24394 | 2.8825 | 8.785% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-12-19 | 25 | 20.6854 | 11.5995 | 32.285 | 1.8132 | 0.76558 | 0.24001 | 2.8187 | 8.731% | 9.29% | 6.277% | 1.0957 | 1.1024 | 1.067
2010-12-19 | 26 | 20.3491 | 11.1623 | 31.5113 | 1.7273 | 0.76558 | 0.23426 | 2.7271 | 8.654% | 9.208% | 6.223% | 1.0947 | 1.1014 | 1.0664
2010-12-19 | 27 | 20.3416 | 11.1664 | 31.5079 | 1.7269 | 0.76558 | 0.23423 | 2.7267 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2010-12-19 | 28 | 20.001 | 10.8934 | 30.8944 | 1.6603 | 0.76558 | 0.22967 | 2.6556 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2010-12-19 | 29 | 19.5635 | 10.4091 | 29.9727 | 1.5627 | 0.76558 | 0.22282 | 2.5511 | 8.512% | 9.056% | 6.12% | 1.093 | 1.0996 | 1.0652
2010-12-19 | 30 | 19.1145 | 10.0747 | 29.1891 | 1.4821 | 0.76558 | 0.217 | 2.4647 | 8.444% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-12-19 | 31 | 19.053 | 10.2105 | 29.2635 | 1.4897 | 0.76558 | 0.21755 | 2.4728 | 8.45% | 8.991% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-12-19 | 32 | 19.0278 | 10.2503 | 29.2781 | 1.4911 | 0.76558 | 0.21766 | 2.4744 | 8.451% | 8.992% | 6.076% | 1.0923 | 1.0988 | 1.0647
2010-12-19 | 33 | 18.9163 | 10.1913 | 29.1076 | 1.4738 | 0.76558 | 0.21639 | 2.4558 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-12-19 | 34 | 19.0785 | 10.073 | 29.1515 | 1.4783 | 0.76558 | 0.21672 | 2.4606 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2010-12-19 | 35 | 19.2851 | 10.3444 | 29.6295 | 1.5272 | 0.76558 | 0.22027 | 2.513 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2010-12-19 | 36 | 20.0596 | 11.0308 | 31.0904 | 1.6815 | 0.76558 | 0.23113 | 2.6782 | 8.614% | 9.165% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-12-19 | 37 | 20.4141 | 11.2417 | 31.6557 | 1.7432 | 0.76558 | 0.23533 | 2.7441 | 8.669% | 9.223% | 6.233% | 1.0949 | 1.1016 | 1.0665
2010-12-19 | 38 | 20.814 | 11.2382 | 32.0522 | 1.7871 | 0.76558 | 0.23828 | 2.791 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-12-19 | 39 | 20.7645 | 11.0093 | 31.7738 | 1.7562 | 0.76558 | 0.23621 | 2.758 | 8.68% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2010-12-19 | 40 | 20.4947 | 10.7257 | 31.2204 | 1.6956 | 0.76558 | 0.2321 | 2.6932 | 8.626% | 9.179% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-12-19 | 41 | 20.3144 | 10.358 | 30.6724 | 1.6365 | 0.76558 | 0.22802 | 2.6301 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2010-12-19 | 42 | 20.2068 | 9.97 | 30.1767 | 1.5841 | 0.76558 | 0.22434 | 2.574 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2010-12-19 | 43 | 19.6406 | 9.8455 | 29.4861 | 1.5124 | 0.76558 | 0.2192 | 2.4972 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2010-12-19 | 44 | 19.6088 | 9.7446 | 29.3534 | 1.4988 | 0.76558 | 0.21822 | 2.4826 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0647
2010-12-19 | 45 | 19.3311 | 9.8125 | 29.1437 | 1.4775 | 0.76558 | 0.21666 | 2.4597 | 8.44% | 8.98% | 6.068% | 1.0922 | 1.0987 | 1.0646
2010-12-19 | 46 | 18.9247 | 9.5143 | 28.4389 | 1.4069 | 0.76558 | 0.21142 | 2.3839 | 8.382% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2010-12-19 | 47 | 17.907 | 9.3676 | 27.2746 | 1.294 | 0.76558 | 0.20276 | 2.2624 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2010-12-19 | 48 | 16.971 | 9.4764 | 26.4474 | 1.2167 | 0.76558 | 0.19661 | 2.1789 | 8.239% | 8.766% | 5.924% | 1.0898 | 1.0961 | 1.063
2010-12-20 | 1 | 15.2825 | 8.6577 | 23.9401 | 0.99698 | 0.76558 | 0.17797 | 1.9405 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2010-12-20 | 2 | 14.2586 | 7.9992 | 22.2578 | 0.86179 | 0.76558 | 0.16547 | 1.7928 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-20 | 3 | 13.4426 | 7.4984 | 20.941 | 0.76284 | 0.76558 | 0.15568 | 1.6841 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-20 | 4 | 12.8647 | 7.1807 | 20.0454 | 0.69898 | 0.76558 | 0.14902 | 1.6136 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-20 | 5 | 12.2154 | 7.14 | 19.3554 | 0.65169 | 0.76558 | 0.14389 | 1.5612 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-20 | 6 | 11.8894 | 7.0016 | 18.891 | 0.62079 | 0.76558 | 0.14044 | 1.5268 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-20 | 7 | 11.5409 | 6.6822 | 18.223 | 0.57767 | 0.76558 | 0.13547 | 1.4787 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-12-20 | 8 | 11.5412 | 6.6371 | 18.1783 | 0.57483 | 0.76558 | 0.13514 | 1.4756 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-12-20 | 9 | 11.5949 | 6.6528 | 18.2477 | 0.57923 | 0.76558 | 0.13566 | 1.4805 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-12-20 | 10 | 11.4589 | 6.7812 | 18.2401 | 0.57875 | 0.76558 | 0.1356 | 1.4799 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2010-12-20 | 11 | 11.6973 | 6.8865 | 18.5837 | 0.60076 | 0.76558 | 0.13815 | 1.5045 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-12-20 | 12 | 11.7573 | 6.7322 | 18.4896 | 0.59469 | 0.76558 | 0.13745 | 1.4977 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-12-20 | 13 | 12.3574 | 6.5801 | 18.9375 | 0.62385 | 0.76558 | 0.14078 | 1.5302 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-20 | 14 | 13.2795 | 6.805 | 20.0846 | 0.70171 | 0.76558 | 0.14931 | 1.6166 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-20 | 15 | 14.6277 | 7.4439 | 22.0716 | 0.84743 | 0.76558 | 0.16408 | 1.7771 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-20 | 16 | 15.9696 | 8.2441 | 24.2137 | 1.0199 | 0.76558 | 0.18001 | 1.9655 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2010-12-20 | 17 | 17.9395 | 9.1479 | 27.0874 | 1.2763 | 0.76558 | 0.20137 | 2.2433 | 8.282% | 8.812% | 5.955% | 1.0903 | 1.0966 | 1.0633
2010-12-20 | 18 | 19.7398 | 9.8127 | 29.5525 | 1.5192 | 0.76558 | 0.2197 | 2.5045 | 8.475% | 9.017% | 6.093% | 1.0926 | 1.0991 | 1.0649
2010-12-20 | 19 | 21.2836 | 10.3517 | 31.6352 | 1.7409 | 0.76558 | 0.23518 | 2.7417 | 8.667% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2010-12-20 | 20 | 21.9556 | 10.4912 | 32.4468 | 1.8314 | 0.76558 | 0.24121 | 2.8382 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2010-12-20 | 21 | 22.7654 | 10.9523 | 33.7177 | 1.9777 | 0.76558 | 0.25066 | 2.9939 | 8.879% | 9.448% | 6.384% | 1.0974 | 1.1043 | 1.0682
2010-12-20 | 22 | 22.9973 | 11.3752 | 34.3725 | 2.0552 | 0.76558 | 0.25553 | 3.0763 | 8.95% | 9.523% | 6.435% | 1.0983 | 1.1053 | 1.0688
2010-12-20 | 23 | 22.3615 | 11.2447 | 33.6062 | 1.9646 | 0.76558 | 0.24983 | 2.98 | 8.867% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2010-12-20 | 24 | 22.1812 | 11.1388 | 33.3199 | 1.9313 | 0.76558 | 0.2477 | 2.9446 | 8.837% | 9.403% | 6.354% | 1.0969 | 1.1038 | 1.0679
2010-12-20 | 25 | 21.535 | 10.8533 | 32.3882 | 1.8248 | 0.76558 | 0.24078 | 2.8311 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-12-20 | 26 | 21.0348 | 10.6536 | 31.6883 | 1.7468 | 0.76558 | 0.23557 | 2.7479 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2010-12-20 | 27 | 20.4886 | 10.648 | 31.1366 | 1.6865 | 0.76558 | 0.23147 | 2.6835 | 8.619% | 9.17% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-12-20 | 28 | 19.9227 | 10.4611 | 30.3839 | 1.6059 | 0.76558 | 0.22588 | 2.5974 | 8.548% | 9.096% | 6.146% | 1.0935 | 1.1001 | 1.0655
2010-12-20 | 29 | 19.485 | 10.0148 | 29.4997 | 1.5138 | 0.76558 | 0.2193 | 2.4987 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0649
2010-12-20 | 30 | 19.2811 | 9.9562 | 29.2374 | 1.487 | 0.76558 | 0.21735 | 2.4699 | 8.448% | 8.989% | 6.074% | 1.0923 | 1.0988 | 1.0647
2010-12-20 | 31 | 19.109 | 9.7931 | 28.902 | 1.4531 | 0.76558 | 0.21486 | 2.4335 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-12-20 | 32 | 19.0226 | 9.7624 | 28.785 | 1.4413 | 0.76558 | 0.21399 | 2.4209 | 8.41% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-12-20 | 33 | 19.0849 | 10.1104 | 29.1954 | 1.4827 | 0.76558 | 0.21704 | 2.4654 | 8.444% | 8.985% | 6.071% | 1.0922 | 1.0987 | 1.0646
2010-12-20 | 34 | 18.9513 | 10.2699 | 29.2211 | 1.4853 | 0.76558 | 0.21723 | 2.4682 | 8.446% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2010-12-20 | 35 | 19.2552 | 10.8527 | 30.1079 | 1.5769 | 0.76558 | 0.22383 | 2.5663 | 8.524% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2010-12-20 | 36 | 19.6013 | 11.3442 | 30.9455 | 1.6658 | 0.76558 | 0.23005 | 2.6615 | 8.6% | 9.151% | 6.184% | 1.0941 | 1.1007 | 1.0659
2010-12-20 | 37 | 20.4308 | 11.5418 | 31.9725 | 1.7782 | 0.76558 | 0.23769 | 2.7815 | 8.7% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-12-20 | 38 | 21.1449 | 11.398 | 32.5429 | 1.8422 | 0.76558 | 0.24193 | 2.8497 | 8.757% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2010-12-20 | 39 | 21.3752 | 11.3371 | 32.7123 | 1.8615 | 0.76558 | 0.24319 | 2.8702 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-12-20 | 40 | 21.4415 | 11.1134 | 32.5549 | 1.8436 | 0.76558 | 0.24202 | 2.8512 | 8.758% | 9.319% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-12-20 | 41 | 21.3454 | 10.8261 | 32.1716 | 1.8004 | 0.76558 | 0.23917 | 2.8052 | 8.719% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-12-20 | 42 | 21.4418 | 10.4319 | 31.8737 | 1.7673 | 0.76558 | 0.23695 | 2.7698 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-12-20 | 43 | 21.592 | 10.1906 | 31.7827 | 1.7572 | 0.76558 | 0.23628 | 2.759 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2010-12-20 | 44 | 22.3922 | 10.1638 | 32.556 | 1.8437 | 0.76558 | 0.24203 | 2.8513 | 8.758% | 9.319% | 6.297% | 1.096 | 1.1028 | 1.0672
2010-12-20 | 45 | 22.184 | 9.8378 | 32.0218 | 1.7837 | 0.76558 | 0.23805 | 2.7873 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2010-12-20 | 46 | 20.7579 | 9.2287 | 29.9865 | 1.5642 | 0.76558 | 0.22292 | 2.5527 | 8.513% | 9.058% | 6.121% | 1.093 | 1.0996 | 1.0652
2010-12-20 | 47 | 19.2456 | 8.7414 | 27.987 | 1.3625 | 0.76558 | 0.20806 | 2.3362 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0638
2010-12-20 | 48 | 17.9895 | 8.766 | 26.7556 | 1.2453 | 0.76558 | 0.1989 | 2.2097 | 8.259% | 8.788% | 5.938% | 1.09 | 1.0963 | 1.0631
2010-12-21 | 1 | 16.2991 | 7.8737 | 24.1728 | 1.0165 | 0.76558 | 0.1797 | 1.9617 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-12-21 | 2 | 14.9349 | 7.4955 | 22.4303 | 0.8752 | 0.76558 | 0.16675 | 1.8075 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-21 | 3 | 14.193 | 7.1572 | 21.3501 | 0.79293 | 0.76558 | 0.15872 | 1.7172 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-21 | 4 | 13.677 | 6.7366 | 20.4135 | 0.72489 | 0.76558 | 0.15176 | 1.6422 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-21 | 5 | 13.079 | 6.5424 | 19.6213 | 0.66972 | 0.76558 | 0.14587 | 1.5812 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-21 | 6 | 12.749 | 6.5124 | 19.2614 | 0.64537 | 0.76558 | 0.14319 | 1.5541 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-21 | 7 | 12.7488 | 6.5052 | 19.254 | 0.64488 | 0.76558 | 0.14314 | 1.5536 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-21 | 8 | 12.8627 | 6.6937 | 19.5565 | 0.6653 | 0.76558 | 0.14539 | 1.5763 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2010-12-21 | 9 | 13.0068 | 6.8092 | 19.816 | 0.68307 | 0.76558 | 0.14731 | 1.596 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-21 | 10 | 13.2327 | 7.0978 | 20.3306 | 0.71901 | 0.76558 | 0.15114 | 1.6357 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-21 | 11 | 13.6327 | 7.5617 | 21.1944 | 0.78141 | 0.76558 | 0.15756 | 1.7045 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-21 | 12 | 14.2363 | 7.9963 | 22.2326 | 0.85984 | 0.76558 | 0.16528 | 1.7907 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-21 | 13 | 15.3604 | 8.7203 | 24.0807 | 1.0087 | 0.76558 | 0.17902 | 1.9533 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2010-12-21 | 14 | 17.452 | 9.7429 | 27.1949 | 1.2865 | 0.76558 | 0.20217 | 2.2542 | 8.289% | 8.82% | 5.96% | 1.0904 | 1.0967 | 1.0634
2010-12-21 | 15 | 20.2222 | 10.9735 | 31.1957 | 1.6929 | 0.76558 | 0.23191 | 2.6904 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2010-12-21 | 16 | 22.1164 | 11.2644 | 33.3808 | 1.9383 | 0.76558 | 0.24816 | 2.9521 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-12-21 | 17 | 23.4623 | 11.937 | 35.3993 | 2.1798 | 0.76558 | 0.26316 | 3.2086 | 9.064% | 9.644% | 6.517% | 1.0997 | 1.1067 | 1.0697
2010-12-21 | 18 | 24.586 | 12.3845 | 36.9705 | 2.3776 | 0.76558 | 0.27484 | 3.4181 | 9.245% | 9.837% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-12-21 | 19 | 24.7529 | 12.217 | 36.9698 | 2.3776 | 0.76558 | 0.27484 | 3.418 | 9.245% | 9.837% | 6.647% | 1.1019 | 1.1091 | 1.0712
2010-12-21 | 20 | 24.2767 | 12.2337 | 36.5104 | 2.3188 | 0.76558 | 0.27142 | 3.3558 | 9.191% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2010-12-21 | 21 | 24.0087 | 12.1746 | 36.1833 | 2.2775 | 0.76558 | 0.26899 | 3.312 | 9.153% | 9.739% | 6.581% | 1.1008 | 1.1079 | 1.0705
2010-12-21 | 22 | 23.5465 | 12.3531 | 35.8996 | 2.2419 | 0.76558 | 0.26688 | 3.2743 | 9.121% | 9.705% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-12-21 | 23 | 23.044 | 12.2067 | 35.2508 | 2.1616 | 0.76558 | 0.26206 | 3.1892 | 9.047% | 9.626% | 6.505% | 1.0995 | 1.1065 | 1.0696
2010-12-21 | 24 | 22.1378 | 11.9834 | 34.1212 | 2.0253 | 0.76558 | 0.25366 | 3.0445 | 8.923% | 9.494% | 6.415% | 1.098 | 1.1049 | 1.0686
2010-12-21 | 25 | 21.8358 | 11.9959 | 33.8316 | 1.991 | 0.76558 | 0.25151 | 3.0081 | 8.891% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2010-12-21 | 26 | 21.2721 | 11.5658 | 32.8379 | 1.8758 | 0.76558 | 0.24412 | 2.8855 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2010-12-21 | 27 | 21.2904 | 11.5066 | 32.7969 | 1.8711 | 0.76558 | 0.24382 | 2.8805 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-12-21 | 28 | 21.2202 | 11.401 | 32.6212 | 1.8511 | 0.76558 | 0.24251 | 2.8592 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1028 | 1.0673
2010-12-21 | 29 | 20.8303 | 11.1607 | 31.991 | 1.7803 | 0.76558 | 0.23782 | 2.7837 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-12-21 | 30 | 20.5705 | 10.9193 | 31.4898 | 1.7249 | 0.76558 | 0.2341 | 2.7246 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2010-12-21 | 31 | 20.2187 | 10.9729 | 31.1916 | 1.6924 | 0.76558 | 0.23188 | 2.6899 | 8.624% | 9.176% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-12-21 | 32 | 20.0575 | 10.638 | 30.6955 | 1.639 | 0.76558 | 0.22819 | 2.6328 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2010-12-21 | 33 | 20.166 | 10.7153 | 30.8813 | 1.6589 | 0.76558 | 0.22958 | 2.6541 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-12-21 | 34 | 20.112 | 10.5009 | 30.6129 | 1.6302 | 0.76558 | 0.22758 | 2.6234 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-12-21 | 35 | 19.8718 | 11.0515 | 30.9234 | 1.6634 | 0.76558 | 0.22989 | 2.6589 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-12-21 | 36 | 19.8978 | 11.5126 | 31.4103 | 1.7162 | 0.76558 | 0.23351 | 2.7153 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-12-21 | 37 | 20.7055 | 12.0501 | 32.7557 | 1.8664 | 0.76558 | 0.24351 | 2.8755 | 8.779% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2010-12-21 | 38 | 21.0218 | 11.77 | 32.7918 | 1.8705 | 0.76558 | 0.24378 | 2.8799 | 8.782% | 9.344% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-12-21 | 39 | 21.2396 | 11.5877 | 32.8273 | 1.8746 | 0.76558 | 0.24404 | 2.8842 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2010-12-21 | 40 | 21.2439 | 11.2269 | 32.4708 | 1.8341 | 0.76558 | 0.24139 | 2.8411 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2010-12-21 | 41 | 21.2765 | 10.9442 | 32.2207 | 1.8059 | 0.76558 | 0.23953 | 2.8111 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2010-12-21 | 42 | 21.0028 | 10.6012 | 31.604 | 1.7375 | 0.76558 | 0.23495 | 2.738 | 8.663% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2010-12-21 | 43 | 21.1174 | 10.9774 | 32.0949 | 1.7919 | 0.76558 | 0.2386 | 2.796 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2010-12-21 | 44 | 21.6997 | 11.3958 | 33.0955 | 1.9053 | 0.76558 | 0.24604 | 2.917 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2010-12-21 | 45 | 21.8179 | 11.4874 | 33.3053 | 1.9296 | 0.76558 | 0.2476 | 2.9427 | 8.836% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2010-12-21 | 46 | 20.8378 | 10.7219 | 31.5597 | 1.7326 | 0.76558 | 0.23462 | 2.7328 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2010-12-21 | 47 | 19.2176 | 9.9943 | 29.2119 | 1.4844 | 0.76558 | 0.21716 | 2.4671 | 8.446% | 8.986% | 6.072% | 1.0922 | 1.0987 | 1.0647
2010-12-21 | 48 | 17.7999 | 9.7718 | 27.5717 | 1.3224 | 0.76558 | 0.20497 | 2.293 | 8.316% | 8.849% | 5.979% | 1.0907 | 1.0971 | 1.0636
2010-12-22 | 1 | 16.0837 | 8.8848 | 24.9685 | 1.0845 | 0.76558 | 0.18562 | 2.0357 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2010-12-22 | 2 | 14.7013 | 8.2674 | 22.9687 | 0.91771 | 0.76558 | 0.17075 | 1.854 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-22 | 3 | 13.9277 | 7.8684 | 21.7961 | 0.8264 | 0.76558 | 0.16203 | 1.754 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2010-12-22 | 4 | 13.0834 | 7.6495 | 20.7328 | 0.74774 | 0.76558 | 0.15413 | 1.6675 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-22 | 5 | 12.9611 | 7.5364 | 20.4975 | 0.73086 | 0.76558 | 0.15238 | 1.6488 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-22 | 6 | 12.5429 | 7.3701 | 19.913 | 0.68978 | 0.76558 | 0.14804 | 1.6034 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2010-12-22 | 7 | 12.4807 | 7.4042 | 19.8849 | 0.68783 | 0.76558 | 0.14783 | 1.6012 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-22 | 8 | 12.3206 | 7.3349 | 19.6555 | 0.67205 | 0.76558 | 0.14612 | 1.5838 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-12-22 | 9 | 12.3147 | 7.3034 | 19.6181 | 0.6695 | 0.76558 | 0.14584 | 1.5809 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-22 | 10 | 12.6666 | 7.3604 | 20.027 | 0.6977 | 0.76558 | 0.14888 | 1.6122 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-22 | 11 | 13.0485 | 7.6744 | 20.7229 | 0.74702 | 0.76558 | 0.15406 | 1.6667 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-22 | 12 | 13.5604 | 8.0601 | 21.6205 | 0.81314 | 0.76558 | 0.16073 | 1.7395 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-22 | 13 | 14.9182 | 8.7828 | 23.7011 | 0.97717 | 0.76558 | 0.1762 | 1.9189 | 8.096% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2010-12-22 | 14 | 16.8341 | 9.5497 | 26.3839 | 1.2109 | 0.76558 | 0.19614 | 2.1726 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2010-12-22 | 15 | 19.2743 | 10.6895 | 29.9638 | 1.5618 | 0.76558 | 0.22275 | 2.5501 | 8.511% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-12-22 | 16 | 21.0459 | 11.2009 | 32.2468 | 1.8089 | 0.76558 | 0.23973 | 2.8142 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.0669
2010-12-22 | 17 | 22.4265 | 11.6874 | 34.114 | 2.0244 | 0.76558 | 0.25361 | 3.0436 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-12-22 | 18 | 23.0308 | 11.8095 | 34.8403 | 2.1115 | 0.76558 | 0.25901 | 3.1361 | 9.001% | 9.578% | 6.472% | 1.0989 | 1.1059 | 1.0692
2010-12-22 | 19 | 23.5628 | 11.8793 | 35.4421 | 2.1851 | 0.76558 | 0.26348 | 3.2142 | 9.069% | 9.649% | 6.52% | 1.0997 | 1.1068 | 1.0698
2010-12-22 | 20 | 23.2489 | 11.8275 | 35.0764 | 2.1402 | 0.76558 | 0.26076 | 3.1666 | 9.028% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2010-12-22 | 21 | 23.2683 | 11.6369 | 34.9051 | 2.1194 | 0.76558 | 0.25949 | 3.1445 | 9.009% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2010-12-22 | 22 | 23.004 | 11.6058 | 34.6098 | 2.0837 | 0.76558 | 0.25729 | 3.1066 | 8.976% | 9.55% | 6.454% | 1.0986 | 1.1056 | 1.069
2010-12-22 | 23 | 22.4458 | 11.2995 | 33.7453 | 1.9809 | 0.76558 | 0.25087 | 2.9973 | 8.882% | 9.451% | 6.386% | 1.0975 | 1.1044 | 1.0682
2010-12-22 | 24 | 21.9154 | 11.2863 | 33.2017 | 1.9176 | 0.76558 | 0.24683 | 2.93 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0677
2010-12-22 | 25 | 21.5212 | 11.4018 | 32.923 | 1.8855 | 0.76558 | 0.24475 | 2.8959 | 8.796% | 9.359% | 6.324% | 1.0964 | 1.1033 | 1.0675
2010-12-22 | 26 | 21.1691 | 11.1202 | 32.2893 | 1.8136 | 0.76558 | 0.24004 | 2.8193 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2010-12-22 | 27 | 20.8371 | 11.1694 | 32.0065 | 1.782 | 0.76558 | 0.23794 | 2.7855 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.1021 | 1.0668
2010-12-22 | 28 | 20.6012 | 11.1804 | 31.7816 | 1.7571 | 0.76558 | 0.23627 | 2.7589 | 8.681% | 9.236% | 6.242% | 1.0951 | 1.1018 | 1.0666
2010-12-22 | 29 | 20.2451 | 11.017 | 31.2621 | 1.7001 | 0.76558 | 0.23241 | 2.6981 | 8.63% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-12-22 | 30 | 20.2529 | 10.8232 | 31.0762 | 1.6799 | 0.76558 | 0.23102 | 2.6765 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2010-12-22 | 31 | 20.3313 | 10.5917 | 30.923 | 1.6634 | 0.76558 | 0.22989 | 2.6589 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2010-12-22 | 32 | 20.0234 | 10.8526 | 30.876 | 1.6584 | 0.76558 | 0.22954 | 2.6535 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2010-12-22 | 33 | 20.0638 | 11.3902 | 31.454 | 1.721 | 0.76558 | 0.23383 | 2.7204 | 8.649% | 9.202% | 6.219% | 1.0947 | 1.1014 | 1.0663
2010-12-22 | 34 | 20.0015 | 11.3508 | 31.3523 | 1.7099 | 0.76558 | 0.23308 | 2.7086 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-12-22 | 35 | 20.0896 | 11.5729 | 31.6625 | 1.7439 | 0.76558 | 0.23538 | 2.7449 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2010-12-22 | 36 | 20.0574 | 11.9282 | 31.9856 | 1.7797 | 0.76558 | 0.23779 | 2.7831 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2010-12-22 | 37 | 20.5056 | 12.1024 | 32.608 | 1.8496 | 0.76558 | 0.24241 | 2.8576 | 8.764% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2010-12-22 | 38 | 20.7636 | 12.1827 | 32.9464 | 1.8882 | 0.76558 | 0.24493 | 2.8987 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-12-22 | 39 | 21.0442 | 12.1843 | 33.2285 | 1.9207 | 0.76558 | 0.24702 | 2.9333 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2010-12-22 | 40 | 20.9823 | 11.7254 | 32.7078 | 1.861 | 0.76558 | 0.24315 | 2.8697 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2010-12-22 | 41 | 20.6985 | 11.3509 | 32.0493 | 1.7868 | 0.76558 | 0.23826 | 2.7906 | 8.707% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2010-12-22 | 42 | 20.765 | 11.0367 | 31.8017 | 1.7593 | 0.76558 | 0.23642 | 2.7613 | 8.683% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2010-12-22 | 43 | 20.6828 | 11.0464 | 31.7292 | 1.7513 | 0.76558 | 0.23588 | 2.7527 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-12-22 | 44 | 21.204 | 11.2935 | 32.4975 | 1.8371 | 0.76558 | 0.24159 | 2.8443 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-22 | 45 | 21.0259 | 10.994 | 32.0199 | 1.7835 | 0.76558 | 0.23804 | 2.7871 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-12-22 | 46 | 20.1399 | 10.2824 | 30.4224 | 1.61 | 0.76558 | 0.22616 | 2.6017 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2010-12-22 | 47 | 18.5542 | 9.8389 | 28.3932 | 1.4024 | 0.76558 | 0.21108 | 2.379 | 8.379% | 8.915% | 6.024% | 1.0915 | 1.0979 | 1.0641
2010-12-22 | 48 | 17.3141 | 9.8404 | 27.1545 | 1.2827 | 0.76558 | 0.20187 | 2.2501 | 8.286% | 8.817% | 5.958% | 1.0904 | 1.0967 | 1.0634
2010-12-23 | 1 | 15.3821 | 8.7921 | 24.1742 | 1.0166 | 0.76558 | 0.17971 | 1.9619 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2010-12-23 | 2 | 14.3621 | 8.0863 | 22.4483 | 0.8766 | 0.76558 | 0.16688 | 1.8091 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2010-12-23 | 3 | 13.2899 | 7.9191 | 21.209 | 0.78248 | 0.76558 | 0.15767 | 1.7057 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-23 | 4 | 12.6733 | 7.5989 | 20.2722 | 0.71489 | 0.76558 | 0.15071 | 1.6312 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-23 | 5 | 12.4335 | 7.5322 | 19.9657 | 0.69343 | 0.76558 | 0.14843 | 1.6074 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-23 | 6 | 12.1511 | 7.2551 | 19.4062 | 0.65511 | 0.76558 | 0.14427 | 1.565 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2010-12-23 | 7 | 11.9113 | 7.0065 | 18.9179 | 0.62256 | 0.76558 | 0.14064 | 1.5288 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-23 | 8 | 11.9892 | 6.9767 | 18.9659 | 0.62572 | 0.76558 | 0.14099 | 1.5323 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-12-23 | 9 | 11.8954 | 7.0144 | 18.9098 | 0.62202 | 0.76558 | 0.14058 | 1.5282 | 8.081% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-23 | 10 | 12.0532 | 7.3288 | 19.382 | 0.65348 | 0.76558 | 0.14409 | 1.5631 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-23 | 11 | 12.2631 | 7.5744 | 19.8375 | 0.68456 | 0.76558 | 0.14747 | 1.5976 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-23 | 12 | 12.7791 | 7.7107 | 20.4898 | 0.73031 | 0.76558 | 0.15232 | 1.6482 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-23 | 13 | 14.0834 | 8.2932 | 22.3765 | 0.871 | 0.76558 | 0.16635 | 1.8029 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-12-23 | 14 | 15.7633 | 9.1054 | 24.8687 | 1.0758 | 0.76558 | 0.18488 | 2.0263 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2010-12-23 | 15 | 18.2575 | 10.2738 | 28.5313 | 1.416 | 0.76558 | 0.21211 | 2.3937 | 8.39% | 8.927% | 6.032% | 1.0916 | 1.098 | 1.0642
2010-12-23 | 16 | 20.6593 | 11.235 | 31.8943 | 1.7695 | 0.76558 | 0.23711 | 2.7722 | 8.692% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2010-12-23 | 17 | 21.9813 | 11.9903 | 33.9717 | 2.0076 | 0.76558 | 0.25255 | 3.0257 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2010-12-23 | 18 | 23.0117 | 12.3032 | 35.3149 | 2.1695 | 0.76558 | 0.26254 | 3.1976 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-12-23 | 19 | 23.8657 | 12.6388 | 36.5044 | 2.3181 | 0.76558 | 0.27138 | 3.355 | 9.191% | 9.779% | 6.608% | 1.1012 | 1.1084 | 1.0708
2010-12-23 | 20 | 23.7773 | 12.4411 | 36.2184 | 2.2819 | 0.76558 | 0.26925 | 3.3167 | 9.158% | 9.744% | 6.584% | 1.1008 | 1.108 | 1.0705
2010-12-23 | 21 | 23.4071 | 12.1378 | 35.5449 | 2.1978 | 0.76558 | 0.26424 | 3.2276 | 9.08% | 9.662% | 6.529% | 1.0999 | 1.1069 | 1.0698
2010-12-23 | 22 | 23.407 | 11.9043 | 35.3114 | 2.169 | 0.76558 | 0.26251 | 3.1971 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-12-23 | 23 | 22.6789 | 11.6538 | 34.3327 | 2.0505 | 0.76558 | 0.25523 | 3.0713 | 8.946% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2010-12-23 | 24 | 22.2724 | 11.787 | 34.0594 | 2.0179 | 0.76558 | 0.2532 | 3.0367 | 8.916% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2010-12-23 | 25 | 21.7743 | 11.793 | 33.5673 | 1.9601 | 0.76558 | 0.24954 | 2.9752 | 8.863% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-12-23 | 26 | 21.378 | 11.5986 | 32.9766 | 1.8917 | 0.76558 | 0.24515 | 2.9024 | 8.801% | 9.365% | 6.328% | 1.0965 | 1.1033 | 1.0676
2010-12-23 | 27 | 20.8363 | 11.6674 | 32.5036 | 1.8378 | 0.76558 | 0.24164 | 2.845 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-23 | 28 | 20.6464 | 11.8421 | 32.4885 | 1.8361 | 0.76558 | 0.24152 | 2.8432 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-12-23 | 29 | 20.254 | 11.5682 | 31.8223 | 1.7616 | 0.76558 | 0.23657 | 2.7637 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2010-12-23 | 30 | 20.0601 | 11.2286 | 31.2887 | 1.703 | 0.76558 | 0.2326 | 2.7012 | 8.633% | 9.186% | 6.207% | 1.0945 | 1.1011 | 1.0662
2010-12-23 | 31 | 19.5465 | 11.0815 | 30.628 | 1.6318 | 0.76558 | 0.22769 | 2.6251 | 8.571% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2010-12-23 | 32 | 19.6885 | 11.0265 | 30.715 | 1.6411 | 0.76558 | 0.22834 | 2.635 | 8.579% | 9.128% | 6.168% | 1.0938 | 1.1004 | 1.0657
2010-12-23 | 33 | 19.8266 | 11.1768 | 31.0034 | 1.6721 | 0.76558 | 0.23048 | 2.6681 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2010-12-23 | 34 | 20.6188 | 11.3308 | 31.9496 | 1.7757 | 0.76558 | 0.23752 | 2.7788 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2010-12-23 | 35 | 21.0888 | 11.6044 | 32.6932 | 1.8593 | 0.76558 | 0.24305 | 2.8679 | 8.772% | 9.334% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-12-23 | 36 | 22.0052 | 11.9932 | 33.9984 | 2.0107 | 0.76558 | 0.25275 | 3.029 | 8.909% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2010-12-23 | 37 | 22.9419 | 12.194 | 35.1359 | 2.1475 | 0.76558 | 0.2612 | 3.1743 | 9.034% | 9.613% | 6.496% | 1.0993 | 1.1063 | 1.0695
2010-12-23 | 38 | 23.2635 | 12.3836 | 35.6471 | 2.2105 | 0.76558 | 0.265 | 3.241 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-12-23 | 39 | 23.0277 | 12.5001 | 35.5278 | 2.1957 | 0.76558 | 0.26412 | 3.2254 | 9.078% | 9.66% | 6.527% | 1.0998 | 1.1069 | 1.0698
2010-12-23 | 40 | 22.6816 | 12.2402 | 34.9218 | 2.1214 | 0.76558 | 0.25961 | 3.1466 | 9.01% | 9.587% | 6.479% | 1.099 | 1.106 | 1.0693
2010-12-23 | 41 | 22.3291 | 12.1066 | 34.4358 | 2.0628 | 0.76558 | 0.256 | 3.0844 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2010-12-23 | 42 | 21.7342 | 11.8914 | 33.6256 | 1.9669 | 0.76558 | 0.24998 | 2.9824 | 8.869% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-12-23 | 43 | 21.5021 | 11.452 | 32.9541 | 1.8891 | 0.76558 | 0.24499 | 2.8997 | 8.799% | 9.362% | 6.327% | 1.0965 | 1.1033 | 1.0675
2010-12-23 | 44 | 21.6673 | 11.4019 | 33.0691 | 1.9023 | 0.76558 | 0.24584 | 2.9137 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2010-12-23 | 45 | 21.3453 | 10.7851 | 32.1304 | 1.7958 | 0.76558 | 0.23886 | 2.8003 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2010-12-23 | 46 | 20.075 | 10.0753 | 30.1503 | 1.5813 | 0.76558 | 0.22414 | 2.571 | 8.527% | 9.073% | 6.131% | 1.0932 | 1.0998 | 1.0653
2010-12-23 | 47 | 18.627 | 9.8858 | 28.5128 | 1.4142 | 0.76558 | 0.21197 | 2.3918 | 8.388% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2010-12-23 | 48 | 17.5429 | 9.7207 | 27.2635 | 1.293 | 0.76558 | 0.20268 | 2.2613 | 8.294% | 8.825% | 5.963% | 1.0904 | 1.0968 | 1.0634
2010-12-24 | 1 | 15.7988 | 8.6051 | 24.404 | 1.036 | 0.76558 | 0.18142 | 1.983 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2010-12-24 | 2 | 14.6207 | 8.029 | 22.6497 | 0.8924 | 0.76558 | 0.16838 | 1.8264 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2010-12-24 | 3 | 13.7844 | 7.632 | 21.4164 | 0.79786 | 0.76558 | 0.15921 | 1.7226 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-24 | 4 | 13.1222 | 7.3579 | 20.4801 | 0.72962 | 0.76558 | 0.15225 | 1.6475 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-24 | 5 | 12.6839 | 7.3958 | 20.0797 | 0.70137 | 0.76558 | 0.14928 | 1.6162 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-24 | 6 | 12.294 | 7.1853 | 19.4793 | 0.66005 | 0.76558 | 0.14481 | 1.5704 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-12-24 | 7 | 12.15 | 6.8793 | 19.0293 | 0.62991 | 0.76558 | 0.14147 | 1.537 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-12-24 | 8 | 11.998 | 6.8192 | 18.8172 | 0.61595 | 0.76558 | 0.13989 | 1.5214 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-12-24 | 9 | 12.1019 | 6.9658 | 19.0677 | 0.63246 | 0.76558 | 0.14175 | 1.5398 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-24 | 10 | 12.1618 | 7.0098 | 19.1717 | 0.63937 | 0.76558 | 0.14252 | 1.5475 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-24 | 11 | 12.4298 | 7.1828 | 19.6125 | 0.66912 | 0.76558 | 0.1458 | 1.5805 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-24 | 12 | 12.7317 | 7.2195 | 19.9512 | 0.69243 | 0.76558 | 0.14832 | 1.6063 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-24 | 13 | 13.8032 | 7.6983 | 21.5014 | 0.80421 | 0.76558 | 0.15984 | 1.7296 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-24 | 14 | 15.3093 | 8.5067 | 23.816 | 0.98667 | 0.76558 | 0.17705 | 1.9293 | 8.101% | 8.619% | 5.825% | 1.0881 | 1.0943 | 1.0618
2010-12-24 | 15 | 17.9334 | 9.3554 | 27.2888 | 1.2954 | 0.76558 | 0.20287 | 2.2638 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-12-24 | 16 | 19.8295 | 10.3639 | 30.1934 | 1.5858 | 0.76558 | 0.22446 | 2.5759 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-12-24 | 17 | 21.6739 | 11.2407 | 32.9146 | 1.8846 | 0.76558 | 0.24469 | 2.8948 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2010-12-24 | 18 | 22.7879 | 11.7456 | 34.5335 | 2.0745 | 0.76558 | 0.25673 | 3.0968 | 8.968% | 9.541% | 6.448% | 1.0985 | 1.1055 | 1.0689
2010-12-24 | 19 | 23.5959 | 12.0464 | 35.6423 | 2.2099 | 0.76558 | 0.26497 | 3.2404 | 9.091% | 9.673% | 6.537% | 1.1 | 1.1071 | 1.0699
2010-12-24 | 20 | 23.4258 | 12.1787 | 35.6045 | 2.2052 | 0.76558 | 0.26469 | 3.2355 | 9.087% | 9.669% | 6.534% | 1.1 | 1.107 | 1.0699
2010-12-24 | 21 | 23.3319 | 11.982 | 35.3138 | 2.1693 | 0.76558 | 0.26253 | 3.1974 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2010-12-24 | 22 | 23.2253 | 12.1502 | 35.3756 | 2.1769 | 0.76558 | 0.26299 | 3.2055 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2010-12-24 | 23 | 22.7992 | 11.784 | 34.5832 | 2.0805 | 0.76558 | 0.2571 | 3.1032 | 8.973% | 9.547% | 6.452% | 1.0986 | 1.1056 | 1.069
2010-12-24 | 24 | 22.2812 | 11.7358 | 34.017 | 2.0129 | 0.76558 | 0.25289 | 3.0314 | 8.911% | 9.482% | 6.407% | 1.0978 | 1.1047 | 1.0685
2010-12-24 | 25 | 21.8471 | 11.7781 | 33.6252 | 1.9668 | 0.76558 | 0.24997 | 2.9824 | 8.869% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2010-12-24 | 26 | 21.3791 | 11.3547 | 32.7338 | 1.8639 | 0.76558 | 0.24335 | 2.8728 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-12-24 | 27 | 20.7912 | 11.4805 | 32.2717 | 1.8117 | 0.76558 | 0.23991 | 2.8172 | 8.73% | 9.288% | 6.277% | 1.0956 | 1.1024 | 1.067
2010-12-24 | 28 | 20.9433 | 11.6599 | 32.6032 | 1.8491 | 0.76558 | 0.24238 | 2.857 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2010-12-24 | 29 | 20.7714 | 11.3945 | 32.1659 | 1.7998 | 0.76558 | 0.23913 | 2.8045 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-12-24 | 30 | 20.5276 | 11.1572 | 31.6848 | 1.7464 | 0.76558 | 0.23555 | 2.7475 | 8.671% | 9.226% | 6.235% | 1.0949 | 1.1016 | 1.0665
2010-12-24 | 31 | 20.3619 | 10.9874 | 31.3492 | 1.7096 | 0.76558 | 0.23305 | 2.7082 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2010-12-24 | 32 | 20.2539 | 10.8568 | 31.1107 | 1.6837 | 0.76558 | 0.23128 | 2.6805 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-24 | 33 | 20.528 | 10.8517 | 31.3797 | 1.7129 | 0.76558 | 0.23328 | 2.7118 | 8.642% | 9.195% | 6.213% | 1.0946 | 1.1013 | 1.0663
2010-12-24 | 34 | 20.4321 | 10.8667 | 31.2987 | 1.7041 | 0.76558 | 0.23268 | 2.7023 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2010-12-24 | 35 | 20.7081 | 11.0647 | 31.7729 | 1.7561 | 0.76558 | 0.2362 | 2.7579 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1018 | 1.0666
2010-12-24 | 36 | 21.1621 | 11.0278 | 32.1899 | 1.8025 | 0.76558 | 0.2393 | 2.8074 | 8.721% | 9.279% | 6.271% | 1.0955 | 1.1023 | 1.0669
2010-12-24 | 37 | 21.4783 | 11.3078 | 32.7861 | 1.8699 | 0.76558 | 0.24374 | 2.8792 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-12-24 | 38 | 21.5023 | 11.2337 | 32.736 | 1.8642 | 0.76558 | 0.24336 | 2.8731 | 8.777% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-12-24 | 39 | 21.0044 | 11.0614 | 32.0658 | 1.7886 | 0.76558 | 0.23838 | 2.7926 | 8.709% | 9.266% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-12-24 | 40 | 20.9065 | 10.826 | 31.7326 | 1.7516 | 0.76558 | 0.2359 | 2.7531 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2010-12-24 | 41 | 20.8388 | 10.6066 | 31.4455 | 1.7201 | 0.76558 | 0.23377 | 2.7194 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2010-12-24 | 42 | 20.667 | 10.4419 | 31.1088 | 1.6835 | 0.76558 | 0.23127 | 2.6803 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2010-12-24 | 43 | 20.4072 | 10.1962 | 30.6033 | 1.6292 | 0.76558 | 0.22751 | 2.6223 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2010-12-24 | 44 | 20.7771 | 10.2947 | 31.0718 | 1.6795 | 0.76558 | 0.23099 | 2.676 | 8.612% | 9.164% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-12-24 | 45 | 20.7672 | 10.5737 | 31.3409 | 1.7087 | 0.76558 | 0.23299 | 2.7072 | 8.638% | 9.191% | 6.211% | 1.0945 | 1.1012 | 1.0662
2010-12-24 | 46 | 19.7808 | 10.3835 | 30.1643 | 1.5828 | 0.76558 | 0.22424 | 2.5726 | 8.529% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2010-12-24 | 47 | 18.4887 | 10.1303 | 28.6191 | 1.4248 | 0.76558 | 0.21276 | 2.4031 | 8.397% | 8.934% | 6.037% | 1.0917 | 1.0981 | 1.0643
2010-12-24 | 48 | 17.4353 | 9.9063 | 27.3416 | 1.3004 | 0.76558 | 0.20326 | 2.2693 | 8.3% | 8.831% | 5.967% | 1.0905 | 1.0969 | 1.0635
2010-12-25 | 1 | 15.8636 | 8.8906 | 24.7542 | 1.0659 | 0.76558 | 0.18403 | 2.0155 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0949 | 1.0622
2010-12-25 | 2 | 14.5731 | 8.1396 | 22.7126 | 0.89737 | 0.76558 | 0.16885 | 1.8318 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-25 | 3 | 13.595 | 7.7254 | 21.3204 | 0.79072 | 0.76558 | 0.1585 | 1.7148 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-25 | 4 | 13.1333 | 7.3391 | 20.4724 | 0.72908 | 0.76558 | 0.15219 | 1.6468 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-25 | 5 | 12.3214 | 7.2107 | 19.5321 | 0.66364 | 0.76558 | 0.1452 | 1.5744 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-25 | 6 | 11.9116 | 6.9884 | 18.9 | 0.62138 | 0.76558 | 0.1405 | 1.5275 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-25 | 7 | 11.6953 | 6.8988 | 18.5942 | 0.60144 | 0.76558 | 0.13823 | 1.5052 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2010-12-25 | 8 | 11.5375 | 6.9139 | 18.4514 | 0.59223 | 0.76558 | 0.13717 | 1.495 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2010-12-25 | 9 | 11.4696 | 6.8227 | 18.2923 | 0.58206 | 0.76558 | 0.13599 | 1.4836 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0944 | 1.0619
2010-12-25 | 10 | 11.4841 | 6.6025 | 18.0866 | 0.56905 | 0.76558 | 0.13446 | 1.4691 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-12-25 | 11 | 11.7515 | 6.3088 | 18.0603 | 0.5674 | 0.76558 | 0.13426 | 1.4672 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2010-12-25 | 12 | 11.8076 | 6.3121 | 18.1197 | 0.57113 | 0.76558 | 0.1347 | 1.4714 | 8.121% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2010-12-25 | 13 | 12.3394 | 6.3568 | 18.6962 | 0.60805 | 0.76558 | 0.13899 | 1.5126 | 8.091% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2010-12-25 | 14 | 13.1433 | 6.9146 | 20.058 | 0.69986 | 0.76558 | 0.14911 | 1.6145 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-25 | 15 | 14.4973 | 7.5832 | 22.0805 | 0.84811 | 0.76558 | 0.16415 | 1.7778 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-25 | 16 | 15.9514 | 8.5617 | 24.5131 | 1.0453 | 0.76558 | 0.18223 | 1.9931 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2010-12-25 | 17 | 17.6369 | 9.6519 | 27.2888 | 1.2954 | 0.76558 | 0.20287 | 2.2638 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2010-12-25 | 18 | 19.3549 | 10.5222 | 29.8771 | 1.5528 | 0.76558 | 0.22211 | 2.5405 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2010-12-25 | 19 | 20.6489 | 10.897 | 31.5459 | 1.7311 | 0.76558 | 0.23452 | 2.7312 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2010-12-25 | 20 | 21.2467 | 11.282 | 32.5287 | 1.8406 | 0.76558 | 0.24182 | 2.848 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2010-12-25 | 21 | 21.9987 | 11.1649 | 33.1636 | 1.9132 | 0.76558 | 0.24654 | 2.9253 | 8.821% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-12-25 | 22 | 21.9286 | 11.3191 | 33.2477 | 1.9229 | 0.76558 | 0.24717 | 2.9357 | 8.83% | 9.395% | 6.349% | 1.0968 | 1.1037 | 1.0678
2010-12-25 | 23 | 21.8886 | 11.0526 | 32.9411 | 1.8876 | 0.76558 | 0.24489 | 2.8981 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2010-12-25 | 24 | 21.5726 | 10.9266 | 32.4992 | 1.8373 | 0.76558 | 0.2416 | 2.8445 | 8.752% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2010-12-25 | 25 | 20.8305 | 10.8047 | 31.6352 | 1.7409 | 0.76558 | 0.23518 | 2.7417 | 8.667% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2010-12-25 | 26 | 20.1265 | 10.3691 | 30.4956 | 1.6177 | 0.76558 | 0.22671 | 2.61 | 8.559% | 9.106% | 6.154% | 1.0936 | 1.1002 | 1.0656
2010-12-25 | 27 | 19.6964 | 10.1223 | 29.8188 | 1.5467 | 0.76558 | 0.22168 | 2.534 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2010-12-25 | 28 | 19.039 | 9.7533 | 28.7923 | 1.4421 | 0.76558 | 0.21405 | 2.4217 | 8.411% | 8.949% | 6.047% | 1.0918 | 1.0983 | 1.0644
2010-12-25 | 29 | 18.4009 | 9.2548 | 27.6556 | 1.3305 | 0.76558 | 0.2056 | 2.3016 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2010-12-25 | 30 | 18.2294 | 8.8448 | 27.0742 | 1.2751 | 0.76558 | 0.20127 | 2.242 | 8.281% | 8.811% | 5.954% | 1.0903 | 1.0966 | 1.0633
2010-12-25 | 31 | 18.0773 | 8.5545 | 26.6318 | 1.2338 | 0.76558 | 0.19798 | 2.1973 | 8.251% | 8.779% | 5.932% | 1.0899 | 1.0962 | 1.0631
2010-12-25 | 32 | 17.5232 | 8.391 | 25.9142 | 1.1682 | 0.76558 | 0.19265 | 2.1264 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2010-12-25 | 33 | 17.375 | 8.381 | 25.756 | 1.154 | 0.76558 | 0.19147 | 2.111 | 8.196% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2010-12-25 | 34 | 17.1288 | 8.0812 | 25.21 | 1.1056 | 0.76558 | 0.18741 | 2.0586 | 8.166% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2010-12-25 | 35 | 16.7393 | 7.9287 | 24.668 | 1.0585 | 0.76558 | 0.18339 | 2.0075 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2010-12-25 | 36 | 16.7212 | 8.0419 | 24.7631 | 1.0667 | 0.76558 | 0.18409 | 2.0164 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2010-12-25 | 37 | 16.971 | 8.1173 | 25.0883 | 1.0949 | 0.76558 | 0.18651 | 2.047 | 8.159% | 8.681% | 5.866% | 1.0888 | 1.0951 | 1.0623
2010-12-25 | 38 | 17.0046 | 8.2426 | 25.2472 | 1.1088 | 0.76558 | 0.18769 | 2.0621 | 8.168% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-12-25 | 39 | 17.0285 | 8.3258 | 25.3543 | 1.1183 | 0.76558 | 0.18849 | 2.0723 | 8.173% | 8.697% | 5.877% | 1.089 | 1.0952 | 1.0624
2010-12-25 | 40 | 16.9688 | 8.1946 | 25.1634 | 1.1015 | 0.76558 | 0.18707 | 2.0541 | 8.163% | 8.686% | 5.869% | 1.0889 | 1.0951 | 1.0624
2010-12-25 | 41 | 16.9168 | 8.4603 | 25.3772 | 1.1203 | 0.76558 | 0.18866 | 2.0745 | 8.175% | 8.698% | 5.878% | 1.089 | 1.0953 | 1.0624
2010-12-25 | 42 | 16.963 | 8.4705 | 25.4335 | 1.1252 | 0.76558 | 0.18908 | 2.0799 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2010-12-25 | 43 | 17.3629 | 8.6876 | 26.0505 | 1.1805 | 0.76558 | 0.19366 | 2.1397 | 8.214% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2010-12-25 | 44 | 18.2929 | 8.9223 | 27.2152 | 1.2884 | 0.76558 | 0.20232 | 2.2563 | 8.291% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2010-12-25 | 45 | 18.5851 | 8.8559 | 27.4409 | 1.3099 | 0.76558 | 0.204 | 2.2795 | 8.307% | 8.838% | 5.973% | 1.0906 | 1.097 | 1.0635
2010-12-25 | 46 | 17.911 | 8.5855 | 26.4965 | 1.2213 | 0.76558 | 0.19698 | 2.1838 | 8.242% | 8.769% | 5.926% | 1.0898 | 1.0961 | 1.063
2010-12-25 | 47 | 17.163 | 8.7399 | 25.9029 | 1.1672 | 0.76558 | 0.19257 | 2.1253 | 8.205% | 8.73% | 5.899% | 1.0894 | 1.0957 | 1.0627
2010-12-25 | 48 | 16.331 | 8.5097 | 24.8407 | 1.0734 | 0.76558 | 0.18467 | 2.0237 | 8.147% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-12-26 | 1 | 14.7567 | 7.5995 | 22.3562 | 0.86942 | 0.76558 | 0.1662 | 1.8012 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2010-12-26 | 2 | 13.4885 | 7.0987 | 20.5873 | 0.73728 | 0.76558 | 0.15305 | 1.6559 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-26 | 3 | 12.5522 | 6.7889 | 19.3411 | 0.65072 | 0.76558 | 0.14378 | 1.5601 | 8.066% | 8.582% | 5.8% | 1.0877 | 1.0939 | 1.0616
2010-12-26 | 4 | 12.066 | 6.5487 | 18.6147 | 0.60276 | 0.76558 | 0.13838 | 1.5067 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-26 | 5 | 11.7156 | 6.5963 | 18.312 | 0.58332 | 0.76558 | 0.13613 | 1.485 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-12-26 | 6 | 11.4235 | 6.4336 | 17.8571 | 0.5547 | 0.76558 | 0.13275 | 1.453 | 8.137% | 8.658% | 5.85% | 1.0886 | 1.0948 | 1.0621
2010-12-26 | 7 | 11.3552 | 6.2426 | 17.5978 | 0.53871 | 0.76558 | 0.13082 | 1.4351 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2010-12-26 | 8 | 11.3673 | 6.2258 | 17.5931 | 0.53842 | 0.76558 | 0.13079 | 1.4348 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-12-26 | 9 | 11.3411 | 6.3092 | 17.6503 | 0.54193 | 0.76558 | 0.13121 | 1.4387 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2010-12-26 | 10 | 11.247 | 6.3441 | 17.5911 | 0.5383 | 0.76558 | 0.13077 | 1.4346 | 8.156% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2010-12-26 | 11 | 11.4031 | 6.2797 | 17.6828 | 0.54392 | 0.76558 | 0.13146 | 1.441 | 8.149% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2010-12-26 | 12 | 11.5472 | 6.1699 | 17.7171 | 0.54603 | 0.76558 | 0.13171 | 1.4433 | 8.147% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2010-12-26 | 13 | 12.1529 | 6.247 | 18.3999 | 0.58893 | 0.76558 | 0.13679 | 1.4913 | 8.105% | 8.624% | 5.827% | 1.0882 | 1.0944 | 1.0619
2010-12-26 | 14 | 12.8189 | 6.4769 | 19.2958 | 0.64768 | 0.76558 | 0.14345 | 1.5567 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-26 | 15 | 14.1011 | 7.0078 | 21.1089 | 0.77511 | 0.76558 | 0.15693 | 1.6976 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-26 | 16 | 15.4212 | 7.9028 | 23.324 | 0.94632 | 0.76558 | 0.17339 | 1.8853 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2010-12-26 | 17 | 17.1352 | 9.0633 | 26.1985 | 1.194 | 0.76558 | 0.19476 | 2.1543 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2010-12-26 | 18 | 18.7874 | 9.9621 | 28.7496 | 1.4378 | 0.76558 | 0.21373 | 2.4171 | 8.407% | 8.946% | 6.045% | 1.0918 | 1.0982 | 1.0643
2010-12-26 | 19 | 20.6116 | 10.7115 | 31.3231 | 1.7067 | 0.76558 | 0.23286 | 2.7052 | 8.636% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2010-12-26 | 20 | 21.3156 | 11.2697 | 32.5853 | 1.847 | 0.76558 | 0.24224 | 2.8549 | 8.761% | 9.322% | 6.299% | 1.096 | 1.1028 | 1.0672
2010-12-26 | 21 | 21.9914 | 11.584 | 33.5754 | 1.961 | 0.76558 | 0.2496 | 2.9762 | 8.864% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2010-12-26 | 22 | 22.0074 | 11.6448 | 33.6522 | 1.97 | 0.76558 | 0.25017 | 2.9857 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-12-26 | 23 | 21.7317 | 11.4518 | 33.1835 | 1.9155 | 0.76558 | 0.24669 | 2.9277 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2010-12-26 | 24 | 21.1276 | 11.1881 | 32.3157 | 1.8166 | 0.76558 | 0.24024 | 2.8224 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2010-12-26 | 25 | 20.4472 | 11.1977 | 31.6449 | 1.742 | 0.76558 | 0.23525 | 2.7428 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-12-26 | 26 | 20.3211 | 10.7713 | 31.0924 | 1.6817 | 0.76558 | 0.23114 | 2.6784 | 8.614% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2010-12-26 | 27 | 20.1036 | 10.9627 | 31.0663 | 1.6789 | 0.76558 | 0.23095 | 2.6754 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2010-12-26 | 28 | 19.892 | 10.8901 | 30.7821 | 1.6483 | 0.76558 | 0.22884 | 2.6427 | 8.585% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2010-12-26 | 29 | 19.6545 | 10.8078 | 30.4623 | 1.6142 | 0.76558 | 0.22646 | 2.6062 | 8.556% | 9.103% | 6.152% | 1.0936 | 1.1001 | 1.0655
2010-12-26 | 30 | 19.6707 | 10.412 | 30.0826 | 1.5742 | 0.76558 | 0.22364 | 2.5634 | 8.521% | 9.067% | 6.127% | 1.0932 | 1.0997 | 1.0653
2010-12-26 | 31 | 19.6352 | 10.3684 | 30.0036 | 1.566 | 0.76558 | 0.22305 | 2.5546 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2010-12-26 | 32 | 19.3852 | 10.2979 | 29.6831 | 1.5327 | 0.76558 | 0.22067 | 2.5189 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0993 | 1.065
2010-12-26 | 33 | 19.5446 | 10.414 | 29.9587 | 1.5613 | 0.76558 | 0.22272 | 2.5496 | 8.51% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2010-12-26 | 34 | 19.8907 | 10.3843 | 30.2751 | 1.5944 | 0.76558 | 0.22507 | 2.5851 | 8.539% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2010-12-26 | 35 | 20.5009 | 10.706 | 31.2069 | 1.6941 | 0.76558 | 0.232 | 2.6917 | 8.625% | 9.177% | 6.202% | 1.0944 | 1.101 | 1.0661
2010-12-26 | 36 | 21.1848 | 11.0129 | 32.1977 | 1.8034 | 0.76558 | 0.23936 | 2.8083 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2010-12-26 | 37 | 21.7609 | 11.1748 | 32.9358 | 1.887 | 0.76558 | 0.24485 | 2.8974 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2010-12-26 | 38 | 22.2589 | 11.1374 | 33.3964 | 1.9401 | 0.76558 | 0.24827 | 2.954 | 8.845% | 9.411% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-12-26 | 39 | 22.7389 | 11.0866 | 33.8255 | 1.9903 | 0.76558 | 0.25146 | 3.0074 | 8.891% | 9.46% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-12-26 | 40 | 22.3942 | 11.0082 | 33.4023 | 1.9408 | 0.76558 | 0.24832 | 2.9547 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2010-12-26 | 41 | 22.0105 | 10.6142 | 32.6247 | 1.8515 | 0.76558 | 0.24254 | 2.8596 | 8.765% | 9.326% | 6.302% | 1.0961 | 1.1029 | 1.0673
2010-12-26 | 42 | 21.5339 | 10.533 | 32.0669 | 1.7887 | 0.76558 | 0.23839 | 2.7927 | 8.709% | 9.266% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-12-26 | 43 | 21.5415 | 10.6004 | 32.1419 | 1.7971 | 0.76558 | 0.23895 | 2.8017 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-12-26 | 44 | 21.7171 | 10.4462 | 32.1633 | 1.7995 | 0.76558 | 0.23911 | 2.8042 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-12-26 | 45 | 20.8691 | 10.2981 | 31.1672 | 1.6898 | 0.76558 | 0.2317 | 2.6871 | 8.621% | 9.173% | 6.199% | 1.0943 | 1.101 | 1.0661
2010-12-26 | 46 | 19.48 | 9.8604 | 29.3405 | 1.4975 | 0.76558 | 0.21812 | 2.4812 | 8.457% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2010-12-26 | 47 | 18.2422 | 9.518 | 27.7602 | 1.3405 | 0.76558 | 0.20637 | 2.3125 | 8.33% | 8.863% | 5.989% | 1.0909 | 1.0973 | 1.0637
2010-12-26 | 48 | 16.5167 | 9.4251 | 25.9419 | 1.1707 | 0.76558 | 0.19285 | 2.1291 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2010-12-27 | 1 | 14.8524 | 8.5192 | 23.3716 | 0.95019 | 0.76558 | 0.17375 | 1.8895 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-12-27 | 2 | 14.0067 | 7.953 | 21.9598 | 0.83886 | 0.76558 | 0.16325 | 1.7677 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2010-12-27 | 3 | 13.0989 | 7.5242 | 20.6231 | 0.73985 | 0.76558 | 0.15331 | 1.6587 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-27 | 4 | 12.5483 | 7.3422 | 19.8905 | 0.68822 | 0.76558 | 0.14787 | 1.6017 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-27 | 5 | 11.9901 | 7.3776 | 19.3677 | 0.65251 | 0.76558 | 0.14398 | 1.5621 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-27 | 6 | 11.7331 | 7.3919 | 19.125 | 0.63627 | 0.76558 | 0.14218 | 1.544 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-12-27 | 7 | 11.5014 | 7.3297 | 18.8311 | 0.61686 | 0.76558 | 0.13999 | 1.5224 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-12-27 | 8 | 11.4126 | 7.206 | 18.6186 | 0.60301 | 0.76558 | 0.13841 | 1.507 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2010-12-27 | 9 | 11.7086 | 7.1768 | 18.8854 | 0.62042 | 0.76558 | 0.1404 | 1.5264 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-27 | 10 | 11.8545 | 7.2292 | 19.0836 | 0.63351 | 0.76558 | 0.14187 | 1.541 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-27 | 11 | 11.9263 | 7.0765 | 19.0028 | 0.62816 | 0.76558 | 0.14127 | 1.535 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-27 | 12 | 12.288 | 7.0587 | 19.3467 | 0.6511 | 0.76558 | 0.14383 | 1.5605 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2010-12-27 | 13 | 12.9874 | 6.9523 | 19.9397 | 0.69163 | 0.76558 | 0.14823 | 1.6054 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-27 | 14 | 13.8931 | 7.1919 | 21.085 | 0.77336 | 0.76558 | 0.15675 | 1.6957 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-27 | 15 | 15.3851 | 7.6279 | 23.013 | 0.92126 | 0.76558 | 0.17108 | 1.8579 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2010-12-27 | 16 | 16.6629 | 8.4345 | 25.0974 | 1.0957 | 0.76558 | 0.18658 | 2.0479 | 8.16% | 8.682% | 5.867% | 1.0888 | 1.0951 | 1.0623
2010-12-27 | 17 | 18.7792 | 9.477 | 28.2561 | 1.3889 | 0.76558 | 0.21006 | 2.3645 | 8.368% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2010-12-27 | 18 | 20.2813 | 10.4064 | 30.6877 | 1.6382 | 0.76558 | 0.22814 | 2.6319 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2010-12-27 | 19 | 22.0711 | 11.0923 | 33.1634 | 1.9132 | 0.76558 | 0.24654 | 2.9253 | 8.821% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-12-27 | 20 | 23.2504 | 11.6207 | 34.8711 | 2.1153 | 0.76558 | 0.25924 | 3.1401 | 9.005% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2010-12-27 | 21 | 23.6146 | 11.5561 | 35.1707 | 2.1518 | 0.76558 | 0.26146 | 3.1788 | 9.038% | 9.617% | 6.498% | 1.0994 | 1.1064 | 1.0695
2010-12-27 | 22 | 23.3356 | 11.6715 | 35.0071 | 2.1318 | 0.76558 | 0.26025 | 3.1576 | 9.02% | 9.597% | 6.485% | 1.0991 | 1.1062 | 1.0694
2010-12-27 | 23 | 22.9621 | 11.4733 | 34.4354 | 2.0627 | 0.76558 | 0.256 | 3.0843 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2010-12-27 | 24 | 22.2243 | 11.3186 | 33.5429 | 1.9572 | 0.76558 | 0.24936 | 2.9721 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2010-12-27 | 25 | 21.4941 | 11.4092 | 32.9033 | 1.8833 | 0.76558 | 0.24461 | 2.8935 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2010-12-27 | 26 | 20.8585 | 11.1581 | 32.0166 | 1.7831 | 0.76558 | 0.23802 | 2.7867 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2010-12-27 | 27 | 20.4525 | 10.9623 | 31.4148 | 1.7167 | 0.76558 | 0.23354 | 2.7159 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2010-12-27 | 28 | 19.9425 | 10.8838 | 30.8263 | 1.653 | 0.76558 | 0.22917 | 2.6478 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2010-12-27 | 29 | 19.4484 | 10.4882 | 29.9366 | 1.559 | 0.76558 | 0.22255 | 2.5471 | 8.508% | 9.053% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-12-27 | 30 | 19.0966 | 10.0149 | 29.1115 | 1.4742 | 0.76558 | 0.21642 | 2.4562 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2010-12-27 | 31 | 18.9954 | 9.736 | 28.7314 | 1.436 | 0.76558 | 0.21359 | 2.4152 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2010-12-27 | 32 | 18.8194 | 9.5809 | 28.4003 | 1.4031 | 0.76558 | 0.21113 | 2.3798 | 8.379% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2010-12-27 | 33 | 18.8413 | 9.8042 | 28.6455 | 1.4274 | 0.76558 | 0.21295 | 2.4059 | 8.399% | 8.937% | 6.039% | 1.0917 | 1.0981 | 1.0643
2010-12-27 | 34 | 18.8832 | 9.7874 | 28.6707 | 1.4299 | 0.76558 | 0.21314 | 2.4086 | 8.401% | 8.939% | 6.04% | 1.0917 | 1.0982 | 1.0643
2010-12-27 | 35 | 19.0106 | 10.0727 | 29.0832 | 1.4714 | 0.76558 | 0.21621 | 2.4531 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2010-12-27 | 36 | 19.5667 | 10.6221 | 30.1888 | 1.5854 | 0.76558 | 0.22443 | 2.5754 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2010-12-27 | 37 | 20.5123 | 11.0156 | 31.5279 | 1.7291 | 0.76558 | 0.23438 | 2.7291 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2010-12-27 | 38 | 20.7282 | 10.9115 | 31.6398 | 1.7414 | 0.76558 | 0.23521 | 2.7422 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-12-27 | 39 | 21.0962 | 10.7809 | 31.8772 | 1.7676 | 0.76558 | 0.23698 | 2.7702 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2010-12-27 | 40 | 20.9024 | 10.4973 | 31.3997 | 1.7151 | 0.76558 | 0.23343 | 2.7141 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2010-12-27 | 41 | 21.0228 | 10.4153 | 31.4381 | 1.7193 | 0.76558 | 0.23371 | 2.7186 | 8.647% | 9.201% | 6.217% | 1.0947 | 1.1013 | 1.0663
2010-12-27 | 42 | 20.8978 | 10.3584 | 31.2562 | 1.6994 | 0.76558 | 0.23236 | 2.6974 | 8.63% | 9.182% | 6.205% | 1.0945 | 1.1011 | 1.0662
2010-12-27 | 43 | 20.8843 | 10.3333 | 31.2176 | 1.6953 | 0.76558 | 0.23208 | 2.6929 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2010-12-27 | 44 | 21.4109 | 10.7041 | 32.115 | 1.7941 | 0.76558 | 0.23875 | 2.7984 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2010-12-27 | 45 | 21.6291 | 9.2989 | 30.928 | 1.6639 | 0.76558 | 0.22992 | 2.6594 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2010-12-27 | 46 | 20.691 | 9.8397 | 30.5306 | 1.6215 | 0.76558 | 0.22697 | 2.614 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2010-12-27 | 47 | 19.2626 | 9.4477 | 28.7103 | 1.4339 | 0.76558 | 0.21344 | 2.4129 | 8.404% | 8.942% | 6.043% | 1.0918 | 1.0982 | 1.0643
2010-12-27 | 48 | 17.7522 | 9.2728 | 27.0249 | 1.2705 | 0.76558 | 0.20091 | 2.237 | 8.277% | 8.807% | 5.951% | 1.0902 | 1.0966 | 1.0633
2010-12-28 | 1 | 15.7381 | 8.3546 | 24.0927 | 1.0097 | 0.76558 | 0.17911 | 1.9544 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2010-12-28 | 2 | 14.3083 | 7.8159 | 22.1241 | 0.85146 | 0.76558 | 0.16447 | 1.7815 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2010-12-28 | 3 | 13.3281 | 7.5074 | 20.8356 | 0.75517 | 0.76558 | 0.15489 | 1.6756 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-28 | 4 | 12.6885 | 7.3056 | 19.994 | 0.6954 | 0.76558 | 0.14864 | 1.6096 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-12-28 | 5 | 12.1624 | 7.0777 | 19.2401 | 0.64395 | 0.76558 | 0.14303 | 1.5526 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-28 | 6 | 11.8463 | 6.9026 | 18.7489 | 0.61148 | 0.76558 | 0.13938 | 1.5164 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-12-28 | 7 | 11.6701 | 6.8223 | 18.4924 | 0.59487 | 0.76558 | 0.13747 | 1.4979 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2010-12-28 | 8 | 11.6538 | 6.6437 | 18.2974 | 0.58239 | 0.76558 | 0.13603 | 1.484 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2010-12-28 | 9 | 11.6662 | 6.702 | 18.3682 | 0.58691 | 0.76558 | 0.13655 | 1.489 | 8.107% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2010-12-28 | 10 | 11.8301 | 6.7963 | 18.6264 | 0.60352 | 0.76558 | 0.13847 | 1.5076 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2010-12-28 | 11 | 12.0538 | 6.7047 | 18.7585 | 0.61211 | 0.76558 | 0.13945 | 1.5171 | 8.088% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2010-12-28 | 12 | 12.3079 | 6.784 | 19.0919 | 0.63407 | 0.76558 | 0.14193 | 1.5416 | 8.074% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2010-12-28 | 13 | 13.2373 | 7.2729 | 20.5102 | 0.73177 | 0.76558 | 0.15248 | 1.6498 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2010-12-28 | 14 | 14.2768 | 7.777 | 22.0537 | 0.84605 | 0.76558 | 0.16395 | 1.7756 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-28 | 15 | 15.8673 | 8.4547 | 24.322 | 1.029 | 0.76558 | 0.18081 | 1.9754 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2010-12-28 | 16 | 17.2225 | 9.1918 | 26.4143 | 1.2137 | 0.76558 | 0.19637 | 2.1756 | 8.237% | 8.764% | 5.922% | 1.0898 | 1.0961 | 1.0629
2010-12-28 | 17 | 19.3327 | 10.029 | 29.3618 | 1.4997 | 0.76558 | 0.21828 | 2.4835 | 8.458% | 9% | 6.082% | 1.0924 | 1.0989 | 1.0648
2010-12-28 | 18 | 21.0817 | 11.0522 | 32.1339 | 1.7962 | 0.76558 | 0.23889 | 2.8007 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2010-12-28 | 19 | 22.9214 | 11.9097 | 34.831 | 2.1104 | 0.76558 | 0.25894 | 3.1349 | 9% | 9.576% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-12-28 | 20 | 23.1392 | 12.4246 | 35.5638 | 2.2001 | 0.76558 | 0.26439 | 3.2301 | 9.083% | 9.664% | 6.53% | 1.0999 | 1.107 | 1.0699
2010-12-28 | 21 | 23.581 | 12.5542 | 36.1352 | 2.2714 | 0.76558 | 0.26863 | 3.3056 | 9.148% | 9.733% | 6.577% | 1.1007 | 1.1078 | 1.0704
2010-12-28 | 22 | 23.2865 | 12.5415 | 35.828 | 2.2329 | 0.76558 | 0.26635 | 3.2649 | 9.113% | 9.696% | 6.552% | 1.1003 | 1.1074 | 1.0701
2010-12-28 | 23 | 22.8122 | 12.147 | 34.9592 | 2.126 | 0.76558 | 0.25989 | 3.1514 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2010-12-28 | 24 | 21.87 | 11.9366 | 33.8066 | 1.9881 | 0.76558 | 0.25132 | 3.005 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2010-12-28 | 25 | 21.188 | 11.9314 | 33.1194 | 1.9081 | 0.76558 | 0.24621 | 2.9199 | 8.816% | 9.38% | 6.339% | 1.0967 | 1.1035 | 1.0677
2010-12-28 | 26 | 20.7658 | 11.4125 | 32.1782 | 1.8012 | 0.76558 | 0.23922 | 2.806 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2010-12-28 | 27 | 20.4614 | 11.607 | 32.0684 | 1.7889 | 0.76558 | 0.2384 | 2.7929 | 8.709% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2010-12-28 | 28 | 19.9373 | 11.4179 | 31.3552 | 1.7102 | 0.76558 | 0.2331 | 2.7089 | 8.639% | 9.192% | 6.212% | 1.0946 | 1.1012 | 1.0662
2010-12-28 | 29 | 19.6154 | 11.0418 | 30.6572 | 1.6349 | 0.76558 | 0.22791 | 2.6284 | 8.574% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2010-12-28 | 30 | 19.3155 | 10.7955 | 30.111 | 1.5772 | 0.76558 | 0.22385 | 2.5666 | 8.524% | 9.069% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-12-28 | 31 | 19.2617 | 10.663 | 29.9247 | 1.5577 | 0.76558 | 0.22246 | 2.5458 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2010-12-28 | 32 | 19.0997 | 10.4696 | 29.5693 | 1.521 | 0.76558 | 0.21982 | 2.5064 | 8.476% | 9.019% | 6.094% | 1.0926 | 1.0991 | 1.0649
2010-12-28 | 33 | 19.2193 | 10.6278 | 29.847 | 1.5497 | 0.76558 | 0.22189 | 2.5371 | 8.5% | 9.044% | 6.112% | 1.0929 | 1.0994 | 1.0651
2010-12-28 | 34 | 19.6371 | 10.6058 | 30.2429 | 1.591 | 0.76558 | 0.22483 | 2.5815 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2010-12-28 | 35 | 19.9852 | 11.0057 | 30.9909 | 1.6707 | 0.76558 | 0.23039 | 2.6667 | 8.605% | 9.155% | 6.187% | 1.0941 | 1.1008 | 1.0659
2010-12-28 | 36 | 20.7015 | 11.7814 | 32.4829 | 1.8355 | 0.76558 | 0.24148 | 2.8425 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2010-12-28 | 37 | 21.3237 | 12.0566 | 33.3803 | 1.9383 | 0.76558 | 0.24815 | 2.952 | 8.844% | 9.41% | 6.359% | 1.097 | 1.1039 | 1.0679
2010-12-28 | 38 | 21.9798 | 11.9829 | 33.9628 | 2.0065 | 0.76558 | 0.25248 | 3.0246 | 8.906% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2010-12-28 | 39 | 22.188 | 11.7728 | 33.9608 | 2.0063 | 0.76558 | 0.25247 | 3.0243 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2010-12-28 | 40 | 22.0341 | 11.5615 | 33.5956 | 1.9634 | 0.76558 | 0.24975 | 2.9787 | 8.866% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2010-12-28 | 41 | 21.9323 | 11.3127 | 33.245 | 1.9226 | 0.76558 | 0.24715 | 2.9353 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2010-12-28 | 42 | 21.8364 | 11.08 | 32.9164 | 1.8848 | 0.76558 | 0.2447 | 2.8951 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2010-12-28 | 43 | 21.4171 | 10.9043 | 32.3215 | 1.8173 | 0.76558 | 0.24028 | 2.8231 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2010-12-28 | 44 | 21.3789 | 10.9842 | 32.363 | 1.8219 | 0.76558 | 0.24059 | 2.8281 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2010-12-28 | 45 | 21.5149 | 11.1754 | 32.6903 | 1.859 | 0.76558 | 0.24302 | 2.8676 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2010-12-28 | 46 | 20.4808 | 10.6434 | 31.1242 | 1.6851 | 0.76558 | 0.23138 | 2.6821 | 8.617% | 9.169% | 6.196% | 1.0943 | 1.1009 | 1.0661
2010-12-28 | 47 | 18.8968 | 10.0004 | 28.8972 | 1.4526 | 0.76558 | 0.21483 | 2.433 | 8.42% | 8.958% | 6.054% | 1.0919 | 1.0984 | 1.0644
2010-12-28 | 48 | 17.4765 | 9.6912 | 27.1676 | 1.2839 | 0.76558 | 0.20197 | 2.2515 | 8.287% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2010-12-29 | 1 | 15.6239 | 8.6476 | 24.2716 | 1.0248 | 0.76558 | 0.18044 | 1.9708 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2010-12-29 | 2 | 14.2119 | 8.0617 | 22.2736 | 0.86301 | 0.76558 | 0.16558 | 1.7942 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-29 | 3 | 13.2937 | 7.7553 | 21.049 | 0.77072 | 0.76558 | 0.15648 | 1.6928 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-29 | 4 | 12.5657 | 7.5451 | 20.1108 | 0.70355 | 0.76558 | 0.14951 | 1.6186 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-29 | 5 | 12.1557 | 7.4675 | 19.6232 | 0.66985 | 0.76558 | 0.14588 | 1.5813 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-29 | 6 | 11.8675 | 7.3654 | 19.2329 | 0.64346 | 0.76558 | 0.14298 | 1.552 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-29 | 7 | 11.6196 | 7.3819 | 19.0015 | 0.62807 | 0.76558 | 0.14126 | 1.5349 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-29 | 8 | 11.5354 | 7.494 | 19.0293 | 0.62992 | 0.76558 | 0.14147 | 1.537 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2010-12-29 | 9 | 11.6488 | 7.4997 | 19.1485 | 0.63783 | 0.76558 | 0.14235 | 1.5458 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2010-12-29 | 10 | 11.548 | 7.4277 | 18.9757 | 0.62637 | 0.76558 | 0.14107 | 1.533 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2010-12-29 | 11 | 11.8079 | 7.4141 | 19.222 | 0.64273 | 0.76558 | 0.1429 | 1.5512 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2010-12-29 | 12 | 12.1357 | 7.3209 | 19.4566 | 0.65852 | 0.76558 | 0.14464 | 1.5687 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2010-12-29 | 13 | 13.1798 | 7.5611 | 20.7409 | 0.74832 | 0.76558 | 0.15419 | 1.6681 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-29 | 14 | 14.5216 | 8.0613 | 22.5829 | 0.88714 | 0.76558 | 0.16788 | 1.8206 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-29 | 15 | 16.427 | 9.0536 | 25.4806 | 1.1294 | 0.76558 | 0.18943 | 2.0844 | 8.18% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2010-12-29 | 16 | 18.1309 | 10.0444 | 28.1753 | 1.3809 | 0.76558 | 0.20946 | 2.356 | 8.362% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2010-12-29 | 17 | 20.4909 | 11.3621 | 31.853 | 1.765 | 0.76558 | 0.2368 | 2.7673 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2010-12-29 | 18 | 22.1749 | 12.1022 | 34.2771 | 2.0438 | 0.76558 | 0.25482 | 3.0642 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2010-12-29 | 19 | 23.655 | 12.6318 | 36.2868 | 2.2905 | 0.76558 | 0.26976 | 3.3258 | 9.165% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0705
2010-12-29 | 20 | 23.781 | 12.8935 | 36.6745 | 2.3397 | 0.76558 | 0.27264 | 3.3779 | 9.211% | 9.8% | 6.622% | 1.1015 | 1.1086 | 1.0709
2010-12-29 | 21 | 24.0709 | 12.9215 | 36.9924 | 2.3804 | 0.76558 | 0.27501 | 3.421 | 9.248% | 9.84% | 6.649% | 1.1019 | 1.1091 | 1.0712
2010-12-29 | 22 | 23.7484 | 12.8605 | 36.6089 | 2.3314 | 0.76558 | 0.27216 | 3.3691 | 9.203% | 9.792% | 6.617% | 1.1014 | 1.1085 | 1.0709
2010-12-29 | 23 | 23.1739 | 12.4947 | 35.6686 | 2.2131 | 0.76558 | 0.26516 | 3.2439 | 9.094% | 9.677% | 6.539% | 1.1 | 1.1071 | 1.07
2010-12-29 | 24 | 22.6661 | 12.6251 | 35.2912 | 2.1665 | 0.76558 | 0.26236 | 3.1945 | 9.052% | 9.631% | 6.508% | 1.0995 | 1.1066 | 1.0696
2010-12-29 | 25 | 22.1615 | 12.7263 | 34.8878 | 2.1173 | 0.76558 | 0.25936 | 3.1422 | 9.007% | 9.583% | 6.476% | 1.099 | 1.106 | 1.0692
2010-12-29 | 26 | 21.6314 | 12.518 | 34.1493 | 2.0286 | 0.76558 | 0.25387 | 3.0481 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-12-29 | 27 | 21.6753 | 12.6677 | 34.3429 | 2.0517 | 0.76558 | 0.25531 | 3.0726 | 8.947% | 9.519% | 6.433% | 1.0983 | 1.1052 | 1.0687
2010-12-29 | 28 | 21.2752 | 12.4224 | 33.6976 | 1.9753 | 0.76558 | 0.25051 | 2.9914 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2010-12-29 | 29 | 20.6493 | 11.8052 | 32.4545 | 1.8323 | 0.76558 | 0.24127 | 2.8391 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2010-12-29 | 30 | 20.5872 | 11.6635 | 32.2507 | 1.8093 | 0.76558 | 0.23976 | 2.8146 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2010-12-29 | 31 | 20.5013 | 11.5433 | 32.0445 | 1.7863 | 0.76558 | 0.23822 | 2.7901 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-12-29 | 32 | 20.4096 | 11.5577 | 31.9674 | 1.7777 | 0.76558 | 0.23765 | 2.7809 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2010-12-29 | 33 | 20.4718 | 11.7877 | 32.2596 | 1.8103 | 0.76558 | 0.23982 | 2.8157 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2010-12-29 | 34 | 20.4637 | 11.6835 | 32.1473 | 1.7977 | 0.76558 | 0.23899 | 2.8023 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2010-12-29 | 35 | 20.722 | 12.011 | 32.7331 | 1.8638 | 0.76558 | 0.24334 | 2.8728 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2010-12-29 | 36 | 21.4516 | 12.226 | 33.6776 | 1.973 | 0.76558 | 0.25036 | 2.9889 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2010-12-29 | 37 | 22.1032 | 12.6928 | 34.796 | 2.1062 | 0.76558 | 0.25868 | 3.1304 | 8.997% | 9.572% | 6.468% | 1.0989 | 1.1059 | 1.0692
2010-12-29 | 38 | 22.615 | 12.7317 | 35.3467 | 2.1734 | 0.76558 | 0.26277 | 3.2017 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2010-12-29 | 39 | 22.7947 | 12.6616 | 35.4563 | 2.1869 | 0.76558 | 0.26359 | 3.216 | 9.07% | 9.651% | 6.522% | 1.0998 | 1.1068 | 1.0698
2010-12-29 | 40 | 22.6666 | 12.1598 | 34.8264 | 2.1098 | 0.76558 | 0.2589 | 3.1343 | 9% | 9.576% | 6.471% | 1.0989 | 1.1059 | 1.0692
2010-12-29 | 41 | 22.2405 | 11.7145 | 33.955 | 2.0056 | 0.76558 | 0.25243 | 3.0236 | 8.905% | 9.475% | 6.402% | 1.0978 | 1.1047 | 1.0684
2010-12-29 | 42 | 22.1587 | 11.4876 | 33.6462 | 1.9693 | 0.76558 | 0.25013 | 2.985 | 8.872% | 9.439% | 6.379% | 1.0974 | 1.1042 | 1.0681
2010-12-29 | 43 | 22.3857 | 11.0854 | 33.471 | 1.9488 | 0.76558 | 0.24883 | 2.9632 | 8.853% | 9.42% | 6.365% | 1.0971 | 1.104 | 1.068
2010-12-29 | 44 | 22.6035 | 11.2195 | 33.823 | 1.99 | 0.76558 | 0.25144 | 3.007 | 8.891% | 9.46% | 6.392% | 1.0976 | 1.1045 | 1.0683
2010-12-29 | 45 | 22.4061 | 11.2587 | 33.6648 | 1.9714 | 0.76558 | 0.25027 | 2.9873 | 8.874% | 9.442% | 6.38% | 1.0974 | 1.1043 | 1.0681
2010-12-29 | 46 | 20.9862 | 10.654 | 31.6402 | 1.7415 | 0.76558 | 0.23522 | 2.7423 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2010-12-29 | 47 | 19.4322 | 10.165 | 29.5972 | 1.5238 | 0.76558 | 0.22003 | 2.5094 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2010-12-29 | 48 | 17.7181 | 10.098 | 27.8162 | 1.346 | 0.76558 | 0.20679 | 2.3183 | 8.334% | 8.868% | 5.992% | 1.0909 | 1.0973 | 1.0637
2010-12-30 | 1 | 16.0279 | 9.2127 | 25.2406 | 1.1082 | 0.76558 | 0.18764 | 2.0615 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2010-12-30 | 2 | 14.7169 | 8.5196 | 23.2365 | 0.93924 | 0.76558 | 0.17274 | 1.8776 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2010-12-30 | 3 | 13.8133 | 8.203 | 22.0163 | 0.84318 | 0.76558 | 0.16367 | 1.7724 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2010-12-30 | 4 | 13.1969 | 7.8245 | 21.0213 | 0.7687 | 0.76558 | 0.15628 | 1.6906 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-30 | 5 | 12.631 | 7.6886 | 20.3195 | 0.71823 | 0.76558 | 0.15106 | 1.6349 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-30 | 6 | 12.2061 | 7.5285 | 19.7346 | 0.67747 | 0.76558 | 0.14671 | 1.5898 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-30 | 7 | 11.9528 | 7.5468 | 19.4996 | 0.66143 | 0.76558 | 0.14496 | 1.572 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2010-12-30 | 8 | 11.7209 | 7.57 | 19.2909 | 0.64735 | 0.76558 | 0.14341 | 1.5563 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2010-12-30 | 9 | 11.9108 | 7.736 | 19.6468 | 0.67145 | 0.76558 | 0.14606 | 1.5831 | 8.058% | 8.573% | 5.794% | 1.0876 | 1.0938 | 1.0615
2010-12-30 | 10 | 11.9386 | 7.7943 | 19.7329 | 0.67735 | 0.76558 | 0.1467 | 1.5896 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2010-12-30 | 11 | 12.3005 | 7.6567 | 19.9572 | 0.69284 | 0.76558 | 0.14836 | 1.6068 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2010-12-30 | 12 | 12.4328 | 7.6854 | 20.1183 | 0.70407 | 0.76558 | 0.14956 | 1.6192 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-30 | 13 | 13.5319 | 8.1107 | 21.6426 | 0.81481 | 0.76558 | 0.16089 | 1.7413 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2010-12-30 | 14 | 14.6708 | 8.7198 | 23.3906 | 0.95174 | 0.76558 | 0.17389 | 1.8912 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2010-12-30 | 15 | 16.7109 | 9.2837 | 25.9946 | 1.1754 | 0.76558 | 0.19325 | 2.1343 | 8.21% | 8.736% | 5.903% | 1.0894 | 1.0957 | 1.0627
2010-12-30 | 16 | 18.3364 | 9.9738 | 28.3101 | 1.3942 | 0.76558 | 0.21046 | 2.3702 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-12-30 | 17 | 20.9878 | 11.182 | 32.1698 | 1.8002 | 0.76558 | 0.23915 | 2.805 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2010-12-30 | 18 | 22.8493 | 12.079 | 34.9283 | 2.1222 | 0.76558 | 0.25966 | 3.1475 | 9.011% | 9.588% | 6.479% | 1.099 | 1.106 | 1.0693
2010-12-30 | 19 | 24.4452 | 12.6589 | 37.1041 | 2.3949 | 0.76558 | 0.27584 | 3.4363 | 9.261% | 9.854% | 6.659% | 1.1021 | 1.1093 | 1.0713
2010-12-30 | 20 | 25.3786 | 13.1105 | 38.4891 | 2.577 | 0.76558 | 0.28613 | 3.6287 | 9.428% | 10.03% | 6.779% | 1.1041 | 1.1115 | 1.0727
2010-12-30 | 21 | 26.0086 | 12.9958 | 39.0045 | 2.6464 | 0.76558 | 0.28996 | 3.702 | 9.491% | 10.1% | 6.824% | 1.1049 | 1.1123 | 1.0732
2010-12-30 | 22 | 26.4745 | 13.0979 | 39.5724 | 2.7241 | 0.76558 | 0.29419 | 3.7838 | 9.562% | 10.17% | 6.875% | 1.1057 | 1.1133 | 1.0738
2010-12-30 | 23 | 26.5285 | 13.312 | 39.8405 | 2.7611 | 0.76558 | 0.29618 | 3.8229 | 9.595% | 10.21% | 6.899% | 1.1061 | 1.1137 | 1.0741
2010-12-30 | 24 | 25.8484 | 13.3134 | 39.1618 | 2.6678 | 0.76558 | 0.29113 | 3.7246 | 9.511% | 10.12% | 6.838% | 1.1051 | 1.1126 | 1.0734
2010-12-30 | 25 | 25.0559 | 13.385 | 38.441 | 2.5705 | 0.76558 | 0.28577 | 3.6219 | 9.422% | 10.02% | 6.774% | 1.104 | 1.1114 | 1.0727
2010-12-30 | 26 | 24.14 | 13.0057 | 37.1457 | 2.4002 | 0.76558 | 0.27615 | 3.4419 | 9.266% | 9.859% | 6.662% | 1.1021 | 1.1094 | 1.0714
2010-12-30 | 27 | 23.6254 | 12.5197 | 36.1451 | 2.2727 | 0.76558 | 0.26871 | 3.3069 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-12-30 | 28 | 22.9331 | 12.2603 | 35.1934 | 2.1546 | 0.76558 | 0.26163 | 3.1818 | 9.041% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2010-12-30 | 29 | 22.4749 | 11.4058 | 33.8807 | 1.9968 | 0.76558 | 0.25187 | 3.0143 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2010-12-30 | 30 | 21.841 | 10.9426 | 32.7836 | 1.8696 | 0.76558 | 0.24372 | 2.8789 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2010-12-30 | 31 | 21.8111 | 10.9824 | 32.7936 | 1.8707 | 0.76558 | 0.24379 | 2.8801 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2010-12-30 | 32 | 21.897 | 10.8268 | 32.7238 | 1.8628 | 0.76558 | 0.24327 | 2.8716 | 8.775% | 9.337% | 6.309% | 1.0962 | 1.103 | 1.0673
2010-12-30 | 33 | 22.2877 | 10.8691 | 33.1567 | 1.9124 | 0.76558 | 0.24649 | 2.9245 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2010-12-30 | 34 | 22.5628 | 11.0423 | 33.605 | 1.9645 | 0.76558 | 0.24982 | 2.9799 | 8.867% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2010-12-30 | 35 | 22.7826 | 11.78 | 34.5626 | 2.078 | 0.76558 | 0.25694 | 3.1005 | 8.971% | 9.545% | 6.45% | 1.0985 | 1.1055 | 1.0689
2010-12-30 | 36 | 23.3586 | 12.0677 | 35.4263 | 2.1832 | 0.76558 | 0.26336 | 3.2121 | 9.067% | 9.647% | 6.519% | 1.0997 | 1.1068 | 1.0697
2010-12-30 | 37 | 24.2164 | 12.1978 | 36.4142 | 2.3066 | 0.76558 | 0.27071 | 3.3429 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2010-12-30 | 38 | 24.8328 | 12.2637 | 37.0966 | 2.3939 | 0.76558 | 0.27578 | 3.4352 | 9.26% | 9.853% | 6.658% | 1.1021 | 1.1093 | 1.0713
2010-12-30 | 39 | 25.1803 | 11.9963 | 37.1767 | 2.4042 | 0.76558 | 0.27638 | 3.4462 | 9.27% | 9.863% | 6.665% | 1.1022 | 1.1094 | 1.0714
2010-12-30 | 40 | 25.0867 | 11.4646 | 36.5513 | 2.324 | 0.76558 | 0.27173 | 3.3613 | 9.196% | 9.785% | 6.612% | 1.1013 | 1.1085 | 1.0708
2010-12-30 | 41 | 24.9968 | 11.0174 | 36.0142 | 2.2562 | 0.76558 | 0.26773 | 3.2895 | 9.134% | 9.719% | 6.567% | 1.1005 | 1.1076 | 1.0703
2010-12-30 | 42 | 24.8349 | 11.0618 | 35.8967 | 2.2415 | 0.76558 | 0.26686 | 3.274 | 9.121% | 9.704% | 6.558% | 1.1004 | 1.1075 | 1.0702
2010-12-30 | 43 | 24.717 | 11.0993 | 35.8163 | 2.2315 | 0.76558 | 0.26626 | 3.2633 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1074 | 1.0701
2010-12-30 | 44 | 25.2669 | 11.3894 | 36.6564 | 2.3374 | 0.76558 | 0.27251 | 3.3755 | 9.208% | 9.798% | 6.621% | 1.1014 | 1.1086 | 1.0709
2010-12-30 | 45 | 24.9367 | 11.2709 | 36.2076 | 2.2805 | 0.76558 | 0.26917 | 3.3153 | 9.156% | 9.742% | 6.583% | 1.1008 | 1.1079 | 1.0705
2010-12-30 | 46 | 23.5966 | 10.5208 | 34.1174 | 2.0248 | 0.76558 | 0.25363 | 3.044 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2010-12-30 | 47 | 22.0007 | 10.0467 | 32.0473 | 1.7866 | 0.76558 | 0.23824 | 2.7904 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2010-12-30 | 48 | 20.2764 | 9.7973 | 30.0737 | 1.5733 | 0.76558 | 0.22357 | 2.5624 | 8.521% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2010-12-31 | 1 | 18.1902 | 8.9179 | 27.1081 | 1.2783 | 0.76558 | 0.20152 | 2.2454 | 8.283% | 8.813% | 5.956% | 1.0903 | 1.0967 | 1.0633
2010-12-31 | 2 | 16.4543 | 8.3291 | 24.7834 | 1.0685 | 0.76558 | 0.18424 | 2.0183 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2010-12-31 | 3 | 15.376 | 7.9364 | 23.3124 | 0.94538 | 0.76558 | 0.17331 | 1.8843 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2010-12-31 | 4 | 14.5439 | 7.6483 | 22.1922 | 0.85671 | 0.76558 | 0.16498 | 1.7873 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2010-12-31 | 5 | 14.2058 | 7.6386 | 21.8444 | 0.83007 | 0.76558 | 0.16239 | 1.758 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-31 | 6 | 13.8178 | 7.4735 | 21.2913 | 0.78857 | 0.76558 | 0.15828 | 1.7124 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 7 | 13.6237 | 7.3592 | 20.983 | 0.76589 | 0.76558 | 0.15599 | 1.6875 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 8 | 13.6939 | 7.367 | 21.0609 | 0.77159 | 0.76558 | 0.15657 | 1.6937 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 9 | 13.8057 | 7.3926 | 21.1983 | 0.78169 | 0.76558 | 0.15759 | 1.7049 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 10 | 13.716 | 7.3376 | 21.0536 | 0.77106 | 0.76558 | 0.15652 | 1.6932 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 11 | 14.1023 | 7.2272 | 21.3295 | 0.7914 | 0.76558 | 0.15857 | 1.7155 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2010-12-31 | 12 | 14.4023 | 7.4699 | 21.8721 | 0.83218 | 0.76558 | 0.1626 | 1.7604 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2010-12-31 | 13 | 15.39 | 7.7885 | 23.1786 | 0.93456 | 0.76558 | 0.17231 | 1.8725 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2010-12-31 | 14 | 16.874 | 8.2462 | 25.1202 | 1.0977 | 0.76558 | 0.18675 | 2.05 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2010-12-31 | 15 | 19.2022 | 9.109 | 28.3112 | 1.3943 | 0.76558 | 0.21047 | 2.3703 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2010-12-31 | 16 | 21.0142 | 10.1729 | 31.1871 | 1.6919 | 0.76558 | 0.23185 | 2.6894 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2010-12-31 | 17 | 23.7428 | 11.2848 | 35.0276 | 2.1343 | 0.76558 | 0.2604 | 3.1603 | 9.022% | 9.6% | 6.487% | 1.0992 | 1.1062 | 1.0694
2010-12-31 | 18 | 25.5608 | 12.3025 | 37.8632 | 2.4938 | 0.76558 | 0.28148 | 3.5409 | 9.352% | 9.95% | 6.724% | 1.1032 | 1.1105 | 1.0721
2010-12-31 | 19 | 27.2847 | 13.0178 | 40.3025 | 2.8255 | 0.76558 | 0.29961 | 3.8907 | 9.654% | 10.27% | 6.941% | 1.1069 | 1.1145 | 1.0746
2010-12-31 | 20 | 27.7908 | 13.4004 | 41.1913 | 2.9515 | 0.76558 | 0.30622 | 4.0233 | 9.767% | 10.39% | 7.023% | 1.1082 | 1.116 | 1.0755
2010-12-31 | 21 | 28.3388 | 13.1995 | 41.5383 | 3.0015 | 0.76558 | 0.3088 | 4.0758 | 9.812% | 10.44% | 7.055% | 1.1088 | 1.1166 | 1.0759
2010-12-31 | 22 | 27.7649 | 13.2811 | 41.046 | 2.9307 | 0.76558 | 0.30514 | 4.0014 | 9.749% | 10.37% | 7.009% | 1.108 | 1.1157 | 1.0754
2010-12-31 | 23 | 27.1447 | 12.9971 | 40.1417 | 2.803 | 0.76558 | 0.29842 | 3.867 | 9.633% | 10.25% | 6.926% | 1.1066 | 1.1142 | 1.0744
2010-12-31 | 24 | 26.0706 | 12.8149 | 38.8855 | 2.6303 | 0.76558 | 0.28908 | 3.685 | 9.477% | 10.08% | 6.814% | 1.1047 | 1.1121 | 1.0731
2010-12-31 | 25 | 25.4384 | 12.518 | 37.9564 | 2.5061 | 0.76558 | 0.28217 | 3.5539 | 9.363% | 9.962% | 6.732% | 1.1033 | 1.1106 | 1.0722
2010-12-31 | 26 | 24.7804 | 12.1308 | 36.9112 | 2.37 | 0.76558 | 0.2744 | 3.41 | 9.238% | 9.83% | 6.642% | 1.1018 | 1.109 | 1.0711
2010-12-31 | 27 | 24.5341 | 11.938 | 36.4721 | 2.314 | 0.76558 | 0.27114 | 3.3507 | 9.187% | 9.775% | 6.605% | 1.1012 | 1.1083 | 1.0707
2010-12-31 | 28 | 24.1016 | 11.8805 | 35.9821 | 2.2522 | 0.76558 | 0.2675 | 3.2853 | 9.13% | 9.715% | 6.565% | 1.1005 | 1.1076 | 1.0703
2010-12-31 | 29 | 23.6716 | 11.4807 | 35.1523 | 2.1495 | 0.76558 | 0.26133 | 3.1764 | 9.036% | 9.615% | 6.497% | 1.0993 | 1.1064 | 1.0695
2010-12-31 | 30 | 23.3657 | 10.9868 | 34.3525 | 2.0528 | 0.76558 | 0.25538 | 3.0738 | 8.948% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2010-12-31 | 31 | 23.1817 | 10.7743 | 33.956 | 2.0057 | 0.76558 | 0.25243 | 3.0237 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2010-12-31 | 32 | 23.0215 | 10.5306 | 33.5521 | 1.9583 | 0.76558 | 0.24943 | 2.9733 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2010-12-31 | 33 | 23.4018 | 10.7488 | 34.1506 | 2.0288 | 0.76558 | 0.25388 | 3.0482 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2010-12-31 | 34 | 23.8764 | 10.8192 | 34.6956 | 2.094 | 0.76558 | 0.25793 | 3.1175 | 8.985% | 9.56% | 6.461% | 1.0987 | 1.1057 | 1.0691
2010-12-31 | 35 | 24.975 | 11.1698 | 36.1449 | 2.2726 | 0.76558 | 0.26871 | 3.3069 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2010-12-31 | 36 | 25.8812 | 11.5234 | 37.4045 | 2.4338 | 0.76558 | 0.27807 | 3.4774 | 9.297% | 9.892% | 6.684% | 1.1025 | 1.1098 | 1.0716
2010-12-31 | 37 | 26.7732 | 11.6295 | 38.4027 | 2.5654 | 0.76558 | 0.28549 | 3.6165 | 9.417% | 10.02% | 6.771% | 1.104 | 1.1114 | 1.0726
2010-12-31 | 38 | 26.7489 | 11.5066 | 38.2555 | 2.5458 | 0.76558 | 0.2844 | 3.5958 | 9.399% | 10% | 6.758% | 1.1037 | 1.1111 | 1.0725
2010-12-31 | 39 | 26.429 | 11.2575 | 37.6864 | 2.4706 | 0.76558 | 0.28017 | 3.5164 | 9.331% | 9.928% | 6.709% | 1.1029 | 1.1102 | 1.0719
2010-12-31 | 40 | 25.3868 | 10.6985 | 36.0853 | 2.2651 | 0.76558 | 0.26826 | 3.299 | 9.142% | 9.727% | 6.573% | 1.1006 | 1.1078 | 1.0704
2010-12-31 | 41 | 24.5268 | 10.226 | 34.7528 | 2.1009 | 0.76558 | 0.25836 | 3.1249 | 8.992% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2010-12-31 | 42 | 23.661 | 9.8356 | 33.4966 | 1.9518 | 0.76558 | 0.24902 | 2.9664 | 8.856% | 9.423% | 6.367% | 1.0972 | 1.104 | 1.068
2010-12-31 | 43 | 22.857 | 9.5313 | 32.3883 | 1.8248 | 0.76558 | 0.24078 | 2.8311 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2010-12-31 | 44 | 23.1331 | 9.6731 | 32.8062 | 1.8722 | 0.76558 | 0.24389 | 2.8816 | 8.784% | 9.346% | 6.316% | 1.0963 | 1.1031 | 1.0674
2010-12-31 | 45 | 22.7372 | 9.7325 | 32.4697 | 1.834 | 0.76558 | 0.24138 | 2.8409 | 8.749% | 9.309% | 6.291% | 1.0959 | 1.1027 | 1.0671
2010-12-31 | 46 | 21.6889 | 9.4563 | 31.1452 | 1.6874 | 0.76558 | 0.23154 | 2.6845 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2010-12-31 | 47 | 20.7528 | 9.3646 | 30.1174 | 1.5779 | 0.76558 | 0.2239 | 2.5673 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2010-12-31 | 48 | 20.2108 | 9.5381 | 29.7489 | 1.5395 | 0.76558 | 0.22116 | 2.5262 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-01-01 | 1 | 18.7248 | 8.8486 | 27.5733 | 1.3226 | 0.76558 | 0.20498 | 2.2931 | 8.316% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2011-01-01 | 2 | 18.4623 | 8.395 | 26.8573 | 1.2548 | 0.76558 | 0.19966 | 2.22 | 8.266% | 8.795% | 5.943% | 1.0901 | 1.0964 | 1.0632
2011-01-01 | 3 | 17.8164 | 7.8586 | 25.6751 | 1.1467 | 0.76558 | 0.19087 | 2.1032 | 8.191% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2011-01-01 | 4 | 16.6943 | 7.3627 | 24.0571 | 1.0067 | 0.76558 | 0.17884 | 1.9512 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0944 | 1.0619
2011-01-01 | 5 | 15.8663 | 7.203 | 23.0693 | 0.92577 | 0.76558 | 0.1715 | 1.8628 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-01-01 | 6 | 14.9303 | 7.0504 | 21.9807 | 0.84046 | 0.76558 | 0.16341 | 1.7694 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-01 | 7 | 14.3308 | 6.8965 | 21.2273 | 0.78383 | 0.76558 | 0.15781 | 1.7072 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 8 | 13.9907 | 6.8293 | 20.82 | 0.75404 | 0.76558 | 0.15478 | 1.6744 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 9 | 13.8487 | 6.7236 | 20.5723 | 0.73621 | 0.76558 | 0.15294 | 1.6547 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 10 | 13.561 | 6.578 | 20.1391 | 0.70553 | 0.76558 | 0.14972 | 1.6208 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-01 | 11 | 13.6028 | 6.4894 | 20.0922 | 0.70225 | 0.76558 | 0.14937 | 1.6172 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-01 | 12 | 13.9066 | 6.4624 | 20.369 | 0.72173 | 0.76558 | 0.15143 | 1.6387 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 13 | 14.0982 | 6.3996 | 20.4979 | 0.73089 | 0.76558 | 0.15238 | 1.6489 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 14 | 14.6804 | 6.5003 | 21.1807 | 0.7804 | 0.76558 | 0.15746 | 1.7034 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-01 | 15 | 15.6903 | 6.8349 | 22.5252 | 0.88261 | 0.76558 | 0.16745 | 1.8156 | 8.061% | 8.576% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-01-01 | 16 | 16.2923 | 7.3222 | 23.6145 | 0.97005 | 0.76558 | 0.17555 | 1.9112 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-01 | 17 | 17.8741 | 8.3244 | 26.1985 | 1.194 | 0.76558 | 0.19476 | 2.1543 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2011-01-01 | 18 | 19.6619 | 9.165 | 28.8268 | 1.4455 | 0.76558 | 0.2143 | 2.4254 | 8.414% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2011-01-01 | 19 | 21.648 | 10.0892 | 31.7371 | 1.7521 | 0.76558 | 0.23594 | 2.7537 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-01-01 | 20 | 23.002 | 10.5398 | 33.5418 | 1.9571 | 0.76558 | 0.24935 | 2.972 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-01-01 | 21 | 24.5214 | 10.9477 | 35.4691 | 2.1884 | 0.76558 | 0.26368 | 3.2177 | 9.072% | 9.652% | 6.523% | 1.0998 | 1.1068 | 1.0698
2011-01-01 | 22 | 25.0314 | 11.221 | 36.2524 | 2.2862 | 0.76558 | 0.2695 | 3.3213 | 9.161% | 9.748% | 6.587% | 1.1009 | 1.108 | 1.0705
2011-01-01 | 23 | 25.2875 | 11.3421 | 36.6297 | 2.334 | 0.76558 | 0.27231 | 3.3719 | 9.205% | 9.794% | 6.619% | 1.1014 | 1.1086 | 1.0709
2011-01-01 | 24 | 24.8455 | 11.3529 | 36.1984 | 2.2794 | 0.76558 | 0.2691 | 3.314 | 9.155% | 9.741% | 6.583% | 1.1008 | 1.1079 | 1.0705
2011-01-01 | 25 | 24.3059 | 11.2151 | 35.5209 | 2.1948 | 0.76558 | 0.26407 | 3.2245 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2011-01-01 | 26 | 23.7522 | 10.9456 | 34.6978 | 2.0943 | 0.76558 | 0.25795 | 3.1178 | 8.986% | 9.561% | 6.461% | 1.0987 | 1.1057 | 1.0691
2011-01-01 | 27 | 23.2659 | 10.9068 | 34.1727 | 2.0314 | 0.76558 | 0.25404 | 3.051 | 8.928% | 9.5% | 6.419% | 1.098 | 1.105 | 1.0686
2011-01-01 | 28 | 22.5659 | 10.8763 | 33.4422 | 1.9455 | 0.76558 | 0.24861 | 2.9597 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.104 | 1.068
2011-01-01 | 29 | 22.168 | 10.4742 | 32.6422 | 1.8535 | 0.76558 | 0.24267 | 2.8617 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-01-01 | 30 | 21.4138 | 10.2104 | 31.6242 | 1.7397 | 0.76558 | 0.2351 | 2.7404 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-01 | 31 | 21.072 | 10.0972 | 31.1693 | 1.69 | 0.76558 | 0.23172 | 2.6873 | 8.622% | 9.173% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-01-01 | 32 | 20.9902 | 10.0286 | 31.0189 | 1.6737 | 0.76558 | 0.2306 | 2.6699 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-01-01 | 33 | 20.8065 | 10.4288 | 31.2353 | 1.6972 | 0.76558 | 0.23221 | 2.695 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-01-01 | 34 | 20.8418 | 10.4477 | 31.2895 | 1.7031 | 0.76558 | 0.23261 | 2.7013 | 8.633% | 9.186% | 6.207% | 1.0945 | 1.1011 | 1.0662
2011-01-01 | 35 | 21.0138 | 10.8831 | 31.8969 | 1.7698 | 0.76558 | 0.23713 | 2.7725 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-01-01 | 36 | 21.8383 | 11.2975 | 33.1358 | 1.91 | 0.76558 | 0.24634 | 2.9219 | 8.818% | 9.382% | 6.34% | 1.0967 | 1.1035 | 1.0677
2011-01-01 | 37 | 22.33 | 11.3141 | 33.6441 | 1.969 | 0.76558 | 0.25011 | 2.9847 | 8.871% | 9.439% | 6.379% | 1.0974 | 1.1042 | 1.0681
2011-01-01 | 38 | 22.9421 | 11.4381 | 34.3802 | 2.0561 | 0.76558 | 0.25559 | 3.0773 | 8.951% | 9.524% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-01-01 | 39 | 23.0018 | 11.3454 | 34.3472 | 2.0522 | 0.76558 | 0.25534 | 3.0731 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2011-01-01 | 40 | 22.9797 | 10.9262 | 33.906 | 1.9998 | 0.76558 | 0.25206 | 3.0174 | 8.899% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2011-01-01 | 41 | 22.7195 | 10.1042 | 32.8237 | 1.8742 | 0.76558 | 0.24402 | 2.8838 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-01-01 | 42 | 23.1595 | 10.2344 | 33.3939 | 1.9398 | 0.76558 | 0.24825 | 2.9537 | 8.845% | 9.411% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-01-01 | 43 | 23.2739 | 10.3426 | 33.6164 | 1.9658 | 0.76558 | 0.24991 | 2.9813 | 8.869% | 9.436% | 6.376% | 1.0973 | 1.1042 | 1.0681
2011-01-01 | 44 | 23.5675 | 10.4922 | 34.0596 | 2.018 | 0.76558 | 0.2532 | 3.0367 | 8.916% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2011-01-01 | 45 | 22.8398 | 10.4527 | 33.2925 | 1.9281 | 0.76558 | 0.2475 | 2.9412 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1037 | 1.0678
2011-01-01 | 46 | 21.2099 | 9.9197 | 31.1295 | 1.6857 | 0.76558 | 0.23142 | 2.6827 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-01-01 | 47 | 19.5153 | 9.5734 | 29.0886 | 1.4719 | 0.76558 | 0.21625 | 2.4537 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2011-01-01 | 48 | 17.983 | 9.5196 | 27.5026 | 1.3158 | 0.76558 | 0.20446 | 2.2858 | 8.311% | 8.843% | 5.976% | 1.0906 | 1.097 | 1.0636
2011-01-02 | 1 | 16.0775 | 8.511 | 24.5885 | 1.0517 | 0.76558 | 0.18279 | 2.0001 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0947 | 1.0621
2011-01-02 | 2 | 14.4877 | 8.1059 | 22.5936 | 0.88799 | 0.76558 | 0.16796 | 1.8215 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-02 | 3 | 13.6015 | 7.5646 | 21.1661 | 0.77932 | 0.76558 | 0.15735 | 1.7023 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-02 | 4 | 12.8978 | 7.0341 | 19.9319 | 0.69108 | 0.76558 | 0.14818 | 1.6048 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-02 | 5 | 12.4552 | 6.8753 | 19.3305 | 0.65001 | 0.76558 | 0.1437 | 1.5593 | 8.066% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-01-02 | 6 | 12.1075 | 6.7619 | 18.8694 | 0.61937 | 0.76558 | 0.14028 | 1.5252 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-01-02 | 7 | 11.8175 | 6.6349 | 18.4523 | 0.59229 | 0.76558 | 0.13718 | 1.495 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-01-02 | 8 | 11.7981 | 6.5702 | 18.3683 | 0.58691 | 0.76558 | 0.13655 | 1.489 | 8.107% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-01-02 | 9 | 11.8492 | 6.5558 | 18.4049 | 0.58926 | 0.76558 | 0.13682 | 1.4917 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-01-02 | 10 | 11.2622 | 6.6817 | 17.944 | 0.56011 | 0.76558 | 0.1334 | 1.4591 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-01-02 | 11 | 10.512 | 6.8975 | 17.4095 | 0.52724 | 0.76558 | 0.12942 | 1.4222 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-01-02 | 12 | 12.172 | 6.8854 | 19.0574 | 0.63178 | 0.76558 | 0.14168 | 1.539 | 8.076% | 8.593% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-01-02 | 13 | 12.802 | 6.891 | 19.693 | 0.67462 | 0.76558 | 0.1464 | 1.5866 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-02 | 14 | 13.516 | 7.1091 | 20.6251 | 0.73999 | 0.76558 | 0.15333 | 1.6589 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-02 | 15 | 15.2278 | 7.861 | 23.0888 | 0.92734 | 0.76558 | 0.17164 | 1.8646 | 8.076% | 8.592% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-01-02 | 16 | 17.2176 | 8.4721 | 25.6897 | 1.148 | 0.76558 | 0.19098 | 2.1046 | 8.192% | 8.717% | 5.89% | 1.0892 | 1.0955 | 1.0626
2011-01-02 | 17 | 19.5379 | 9.4258 | 28.9637 | 1.4593 | 0.76558 | 0.21532 | 2.4402 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2011-01-02 | 18 | 21.8301 | 10.5694 | 32.3995 | 1.826 | 0.76558 | 0.24086 | 2.8325 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-01-02 | 19 | 23.907 | 11.4927 | 35.3998 | 2.1799 | 0.76558 | 0.26317 | 3.2086 | 9.064% | 9.644% | 6.517% | 1.0997 | 1.1067 | 1.0697
2011-01-02 | 20 | 24.8563 | 12.0597 | 36.916 | 2.3706 | 0.76558 | 0.27444 | 3.4106 | 9.239% | 9.83% | 6.643% | 1.1018 | 1.109 | 1.0712
2011-01-02 | 21 | 25.2938 | 12.2594 | 37.5532 | 2.4532 | 0.76558 | 0.27917 | 3.4979 | 9.315% | 9.911% | 6.697% | 1.1027 | 1.11 | 1.0718
2011-01-02 | 22 | 25.0517 | 12.267 | 37.3187 | 2.4226 | 0.76558 | 0.27743 | 3.4656 | 9.287% | 9.881% | 6.677% | 1.1024 | 1.1096 | 1.0715
2011-01-02 | 23 | 24.5179 | 11.8373 | 36.3552 | 2.2992 | 0.76558 | 0.27027 | 3.335 | 9.173% | 9.76% | 6.596% | 1.101 | 1.1082 | 1.0706
2011-01-02 | 24 | 23.3058 | 11.4783 | 34.784 | 2.1047 | 0.76558 | 0.25859 | 3.1289 | 8.995% | 9.571% | 6.468% | 1.0988 | 1.1058 | 1.0691
2011-01-02 | 25 | 22.6596 | 11.2816 | 33.9412 | 2.004 | 0.76558 | 0.25232 | 3.0219 | 8.903% | 9.473% | 6.401% | 1.0977 | 1.1046 | 1.0684
2011-01-02 | 26 | 21.8565 | 10.8913 | 32.7478 | 1.8655 | 0.76558 | 0.24345 | 2.8745 | 8.778% | 9.34% | 6.311% | 1.0962 | 1.103 | 1.0674
2011-01-02 | 27 | 20.9589 | 10.7531 | 31.712 | 1.7494 | 0.76558 | 0.23575 | 2.7507 | 8.674% | 9.229% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-01-02 | 28 | 20.7232 | 10.2631 | 30.9864 | 1.6702 | 0.76558 | 0.23036 | 2.6662 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-01-02 | 29 | 20.3994 | 9.7662 | 30.1656 | 1.5829 | 0.76558 | 0.22425 | 2.5727 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-01-02 | 30 | 19.5954 | 9.5819 | 29.1773 | 1.4809 | 0.76558 | 0.21691 | 2.4634 | 8.443% | 8.983% | 6.07% | 1.0922 | 1.0987 | 1.0646
2011-01-02 | 31 | 19.5819 | 9.418 | 28.9999 | 1.4629 | 0.76558 | 0.21559 | 2.4441 | 8.428% | 8.967% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-01-02 | 32 | 19.3887 | 9.253 | 28.6417 | 1.427 | 0.76558 | 0.21293 | 2.4055 | 8.399% | 8.936% | 6.039% | 1.0917 | 1.0981 | 1.0643
2011-01-02 | 33 | 19.2651 | 9.5463 | 28.8114 | 1.444 | 0.76558 | 0.21419 | 2.4238 | 8.412% | 8.951% | 6.049% | 1.0919 | 1.0983 | 1.0644
2011-01-02 | 34 | 19.4873 | 9.6765 | 29.1638 | 1.4795 | 0.76558 | 0.21681 | 2.4619 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2011-01-02 | 35 | 19.835 | 10.0834 | 29.9184 | 1.5571 | 0.76558 | 0.22242 | 2.5451 | 8.507% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2011-01-02 | 36 | 20.5765 | 10.5039 | 31.0804 | 1.6804 | 0.76558 | 0.23106 | 2.677 | 8.613% | 9.164% | 6.193% | 1.0942 | 1.1009 | 1.066
2011-01-02 | 37 | 21.3066 | 10.749 | 32.0556 | 1.7875 | 0.76558 | 0.23831 | 2.7914 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-01-02 | 38 | 21.8288 | 10.8588 | 32.6877 | 1.8587 | 0.76558 | 0.243 | 2.8673 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2011-01-02 | 39 | 21.9974 | 10.8345 | 32.8319 | 1.8751 | 0.76558 | 0.24408 | 2.8848 | 8.786% | 9.349% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-01-02 | 40 | 21.9672 | 10.8246 | 32.7917 | 1.8705 | 0.76558 | 0.24378 | 2.8799 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-01-02 | 41 | 21.5954 | 10.57 | 32.1654 | 1.7998 | 0.76558 | 0.23912 | 2.8045 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2011-01-02 | 42 | 21.5332 | 10.5397 | 32.0729 | 1.7894 | 0.76558 | 0.23843 | 2.7934 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2011-01-02 | 43 | 21.3474 | 10.604 | 31.9513 | 1.7759 | 0.76558 | 0.23753 | 2.779 | 8.698% | 9.254% | 6.254% | 1.0953 | 1.102 | 1.0667
2011-01-02 | 44 | 21.6933 | 10.791 | 32.4842 | 1.8356 | 0.76558 | 0.24149 | 2.8427 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-01-02 | 45 | 22.0832 | 10.8757 | 32.959 | 1.8897 | 0.76558 | 0.24502 | 2.9003 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-01-02 | 46 | 21.3673 | 10.5761 | 31.9434 | 1.775 | 0.76558 | 0.23747 | 2.778 | 8.697% | 9.253% | 6.253% | 1.0953 | 1.102 | 1.0667
2011-01-02 | 47 | 19.8368 | 10.1322 | 29.969 | 1.5624 | 0.76558 | 0.22279 | 2.5507 | 8.511% | 9.056% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-01-02 | 48 | 18.2302 | 10.013 | 28.2432 | 1.3876 | 0.76558 | 0.20996 | 2.3631 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2011-01-03 | 1 | 16.2142 | 8.9721 | 25.1863 | 1.1035 | 0.76558 | 0.18724 | 2.0563 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-01-03 | 2 | 14.8 | 8.2834 | 23.0834 | 0.92691 | 0.76558 | 0.17161 | 1.8641 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-01-03 | 3 | 13.8558 | 7.883 | 21.7388 | 0.82206 | 0.76558 | 0.16161 | 1.7493 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-03 | 4 | 13.2298 | 7.5867 | 20.8165 | 0.75379 | 0.76558 | 0.15475 | 1.6741 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-03 | 5 | 12.6335 | 7.6665 | 20.3 | 0.71685 | 0.76558 | 0.15091 | 1.6333 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-03 | 6 | 12.2517 | 7.4925 | 19.7442 | 0.67813 | 0.76558 | 0.14678 | 1.5905 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-01-03 | 7 | 11.9414 | 7.3191 | 19.2605 | 0.64531 | 0.76558 | 0.14319 | 1.5541 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-03 | 8 | 11.7836 | 7.2752 | 19.0588 | 0.63187 | 0.76558 | 0.14169 | 1.5391 | 8.076% | 8.593% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-01-03 | 9 | 11.8033 | 7.2982 | 19.1015 | 0.6347 | 0.76558 | 0.142 | 1.5423 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-03 | 10 | 11.8914 | 7.3094 | 19.2008 | 0.64132 | 0.76558 | 0.14274 | 1.5496 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-01-03 | 11 | 11.9554 | 7.3552 | 19.3107 | 0.64868 | 0.76558 | 0.14356 | 1.5578 | 8.067% | 8.583% | 5.8% | 1.0878 | 1.0939 | 1.0616
2011-01-03 | 12 | 12.1275 | 7.2105 | 19.338 | 0.65052 | 0.76558 | 0.14376 | 1.5599 | 8.066% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-01-03 | 13 | 12.6176 | 7.1304 | 19.748 | 0.67839 | 0.76558 | 0.14681 | 1.5908 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-01-03 | 14 | 13.4238 | 7.4729 | 20.8967 | 0.75961 | 0.76558 | 0.15535 | 1.6805 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-03 | 15 | 14.8464 | 7.9621 | 22.8085 | 0.90496 | 0.76558 | 0.16956 | 1.8401 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-03 | 16 | 16.5131 | 8.6306 | 25.1437 | 1.0997 | 0.76558 | 0.18692 | 2.0522 | 8.162% | 8.684% | 5.869% | 1.0889 | 1.0951 | 1.0623
2011-01-03 | 17 | 18.4776 | 9.4554 | 27.9331 | 1.3573 | 0.76558 | 0.20766 | 2.3305 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2011-01-03 | 18 | 20.7881 | 10.4145 | 31.2026 | 1.6936 | 0.76558 | 0.23196 | 2.6912 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-01-03 | 19 | 23.357 | 11.3899 | 34.7469 | 2.1002 | 0.76558 | 0.25831 | 3.1241 | 8.991% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2011-01-03 | 20 | 24.9949 | 11.9454 | 36.9403 | 2.3737 | 0.76558 | 0.27462 | 3.4139 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2011-01-03 | 21 | 26.1071 | 12.0526 | 38.1597 | 2.5331 | 0.76558 | 0.28368 | 3.5823 | 9.388% | 9.989% | 6.75% | 1.1036 | 1.111 | 1.0724
2011-01-03 | 22 | 26.613 | 12.0665 | 38.6795 | 2.6025 | 0.76558 | 0.28755 | 3.6557 | 9.451% | 10.06% | 6.795% | 1.1044 | 1.1118 | 1.0729
2011-01-03 | 23 | 26.299 | 11.894 | 38.193 | 2.5375 | 0.76558 | 0.28393 | 3.587 | 9.392% | 9.993% | 6.753% | 1.1037 | 1.111 | 1.0724
2011-01-03 | 24 | 25.6634 | 12.0512 | 37.7146 | 2.4743 | 0.76558 | 0.28037 | 3.5203 | 9.334% | 9.931% | 6.711% | 1.1029 | 1.1103 | 1.0719
2011-01-03 | 25 | 25.066 | 12.0911 | 37.1571 | 2.4017 | 0.76558 | 0.27623 | 3.4435 | 9.267% | 9.861% | 6.663% | 1.1021 | 1.1094 | 1.0714
2011-01-03 | 26 | 24.2217 | 11.5887 | 35.8104 | 2.2308 | 0.76558 | 0.26622 | 3.2626 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1073 | 1.0701
2011-01-03 | 27 | 23.543 | 11.3807 | 34.9237 | 2.1217 | 0.76558 | 0.25963 | 3.1469 | 9.011% | 9.587% | 6.479% | 1.099 | 1.106 | 1.0693
2011-01-03 | 28 | 22.7523 | 11.0623 | 33.8146 | 1.989 | 0.76558 | 0.25138 | 3.006 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2011-01-03 | 29 | 22.138 | 10.7806 | 32.9185 | 1.885 | 0.76558 | 0.24472 | 2.8953 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-01-03 | 30 | 21.6199 | 10.4908 | 32.1107 | 1.7936 | 0.76558 | 0.23871 | 2.7979 | 8.713% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2011-01-03 | 31 | 21.1207 | 10.2537 | 31.3744 | 1.7123 | 0.76558 | 0.23324 | 2.7111 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2011-01-03 | 32 | 20.7985 | 10.1461 | 30.9445 | 1.6657 | 0.76558 | 0.23005 | 2.6613 | 8.6% | 9.151% | 6.184% | 1.0941 | 1.1007 | 1.0659
2011-01-03 | 33 | 20.7999 | 10.2833 | 31.0832 | 1.6807 | 0.76558 | 0.23108 | 2.6773 | 8.613% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2011-01-03 | 34 | 20.6264 | 10.5626 | 31.189 | 1.6921 | 0.76558 | 0.23186 | 2.6896 | 8.624% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-01-03 | 35 | 20.8699 | 10.8093 | 31.6791 | 1.7457 | 0.76558 | 0.23551 | 2.7468 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-01-03 | 36 | 21.3995 | 11.3758 | 32.7753 | 1.8687 | 0.76558 | 0.24366 | 2.8779 | 8.781% | 9.343% | 6.313% | 1.0963 | 1.1031 | 1.0674
2011-01-03 | 37 | 21.9191 | 11.6986 | 33.6177 | 1.9659 | 0.76558 | 0.24992 | 2.9814 | 8.869% | 9.436% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-01-03 | 38 | 22.1909 | 11.4514 | 33.6424 | 1.9688 | 0.76558 | 0.2501 | 2.9845 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2011-01-03 | 39 | 22.1989 | 11.2805 | 33.4795 | 1.9498 | 0.76558 | 0.24889 | 2.9643 | 8.854% | 9.421% | 6.366% | 1.0971 | 1.104 | 1.068
2011-01-03 | 40 | 21.959 | 11.2348 | 33.1938 | 1.9167 | 0.76558 | 0.24677 | 2.929 | 8.824% | 9.389% | 6.344% | 1.0968 | 1.1036 | 1.0677
2011-01-03 | 41 | 21.629 | 10.9164 | 32.5454 | 1.8425 | 0.76558 | 0.24195 | 2.8501 | 8.757% | 9.318% | 6.296% | 1.096 | 1.1028 | 1.0672
2011-01-03 | 42 | 21.5592 | 10.8208 | 32.38 | 1.8238 | 0.76558 | 0.24072 | 2.8301 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-01-03 | 43 | 21.3879 | 10.8559 | 32.2438 | 1.8085 | 0.76558 | 0.2397 | 2.8138 | 8.727% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2011-01-03 | 44 | 21.3044 | 10.8674 | 32.1718 | 1.8005 | 0.76558 | 0.23917 | 2.8052 | 8.719% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2011-01-03 | 45 | 21.5949 | 10.7327 | 32.3276 | 1.8179 | 0.76558 | 0.24033 | 2.8239 | 8.735% | 9.294% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-01-03 | 46 | 20.8471 | 10.3641 | 31.2112 | 1.6946 | 0.76558 | 0.23203 | 2.6922 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2011-01-03 | 47 | 19.546 | 9.9814 | 29.5274 | 1.5166 | 0.76558 | 0.21951 | 2.5017 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-01-03 | 48 | 17.7674 | 9.6761 | 27.4435 | 1.3101 | 0.76558 | 0.20402 | 2.2797 | 8.307% | 8.839% | 5.973% | 1.0906 | 1.097 | 1.0635
2011-01-04 | 1 | 15.8908 | 8.6868 | 24.5776 | 1.0508 | 0.76558 | 0.18271 | 1.9991 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-01-04 | 2 | 14.3127 | 8.0496 | 22.3622 | 0.86989 | 0.76558 | 0.16624 | 1.8017 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-04 | 3 | 13.1981 | 7.5309 | 20.729 | 0.74747 | 0.76558 | 0.1541 | 1.6671 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-04 | 4 | 12.3964 | 7.388 | 19.7844 | 0.6809 | 0.76558 | 0.14708 | 1.5936 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-01-04 | 5 | 12.1792 | 7.2828 | 19.462 | 0.65889 | 0.76558 | 0.14468 | 1.5691 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-04 | 6 | 11.6322 | 7.1016 | 18.7337 | 0.6105 | 0.76558 | 0.13927 | 1.5153 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2011-01-04 | 7 | 11.5121 | 6.9149 | 18.427 | 0.59067 | 0.76558 | 0.13699 | 1.4932 | 8.104% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2011-01-04 | 8 | 11.4822 | 6.8582 | 18.3405 | 0.58514 | 0.76558 | 0.13635 | 1.4871 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-01-04 | 9 | 11.5003 | 6.8333 | 18.3336 | 0.58469 | 0.76558 | 0.13629 | 1.4866 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-01-04 | 10 | 11.7522 | 6.9402 | 18.6923 | 0.6078 | 0.76558 | 0.13896 | 1.5123 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-01-04 | 11 | 11.9181 | 6.8382 | 18.7563 | 0.61197 | 0.76558 | 0.13944 | 1.517 | 8.088% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-01-04 | 12 | 11.9639 | 7.1659 | 19.1298 | 0.63658 | 0.76558 | 0.14221 | 1.5444 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-04 | 13 | 12.6158 | 7.4167 | 20.0324 | 0.69807 | 0.76558 | 0.14892 | 1.6126 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-04 | 14 | 13.6798 | 7.8342 | 21.514 | 0.80515 | 0.76558 | 0.15994 | 1.7307 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-04 | 15 | 15.3163 | 8.5949 | 23.9112 | 0.99458 | 0.76558 | 0.17776 | 1.9379 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-01-04 | 16 | 16.9442 | 9.3026 | 26.2467 | 1.1984 | 0.76558 | 0.19512 | 2.1591 | 8.226% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2011-01-04 | 17 | 19.0464 | 10.0361 | 29.0825 | 1.4713 | 0.76558 | 0.2162 | 2.4531 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2011-01-04 | 18 | 21.3076 | 11.0664 | 32.374 | 1.8232 | 0.76558 | 0.24067 | 2.8294 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-01-04 | 19 | 23.0659 | 11.9593 | 35.0252 | 2.134 | 0.76558 | 0.26038 | 3.16 | 9.022% | 9.599% | 6.487% | 1.0992 | 1.1062 | 1.0694
2011-01-04 | 20 | 23.974 | 12.2504 | 36.2243 | 2.2826 | 0.76558 | 0.2693 | 3.3175 | 9.158% | 9.744% | 6.585% | 1.1008 | 1.108 | 1.0705
2011-01-04 | 21 | 24.838 | 12.682 | 37.52 | 2.4488 | 0.76558 | 0.27893 | 3.4934 | 9.311% | 9.907% | 6.694% | 1.1027 | 1.11 | 1.0717
2011-01-04 | 22 | 24.7201 | 13.0785 | 37.7986 | 2.4853 | 0.76558 | 0.281 | 3.5319 | 9.344% | 9.942% | 6.718% | 1.1031 | 1.1104 | 1.072
2011-01-04 | 23 | 24.4198 | 12.6026 | 37.0224 | 2.3843 | 0.76558 | 0.27523 | 3.4251 | 9.251% | 9.844% | 6.652% | 1.1019 | 1.1092 | 1.0713
2011-01-04 | 24 | 23.9619 | 12.5686 | 36.5305 | 2.3214 | 0.76558 | 0.27157 | 3.3585 | 9.194% | 9.782% | 6.61% | 1.1012 | 1.1084 | 1.0708
2011-01-04 | 25 | 23.5137 | 12.6309 | 36.1446 | 2.2726 | 0.76558 | 0.2687 | 3.3069 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2011-01-04 | 26 | 22.9575 | 12.0461 | 35.0035 | 2.1314 | 0.76558 | 0.26022 | 3.1572 | 9.02% | 9.597% | 6.485% | 1.0991 | 1.1062 | 1.0693
2011-01-04 | 27 | 22.3294 | 11.9468 | 34.2761 | 2.0437 | 0.76558 | 0.25481 | 3.0641 | 8.939% | 9.512% | 6.427% | 1.0982 | 1.1051 | 1.0687
2011-01-04 | 28 | 21.655 | 11.4657 | 33.1207 | 1.9082 | 0.76558 | 0.24622 | 2.92 | 8.816% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2011-01-04 | 29 | 21.1311 | 11.0568 | 32.1878 | 1.8023 | 0.76558 | 0.23929 | 2.8071 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-01-04 | 30 | 20.4692 | 10.953 | 31.4222 | 1.7175 | 0.76558 | 0.2336 | 2.7167 | 8.646% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-01-04 | 31 | 20.2853 | 10.7291 | 31.0144 | 1.6733 | 0.76558 | 0.23056 | 2.6694 | 8.607% | 9.158% | 6.188% | 1.0942 | 1.1008 | 1.066
2011-01-04 | 32 | 19.9955 | 10.5152 | 30.5107 | 1.6193 | 0.76558 | 0.22682 | 2.6117 | 8.56% | 9.108% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-01-04 | 33 | 20.0713 | 10.4559 | 30.5272 | 1.6211 | 0.76558 | 0.22694 | 2.6136 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-01-04 | 34 | 20.3711 | 10.4654 | 30.8365 | 1.6541 | 0.76558 | 0.22924 | 2.6489 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-01-04 | 35 | 20.8609 | 11.0158 | 31.8767 | 1.7676 | 0.76558 | 0.23698 | 2.7701 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-01-04 | 36 | 21.5166 | 11.8781 | 33.3947 | 1.9399 | 0.76558 | 0.24826 | 2.9538 | 8.845% | 9.411% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-01-04 | 37 | 22.4308 | 12.1813 | 34.6121 | 2.084 | 0.76558 | 0.25731 | 3.1069 | 8.976% | 9.551% | 6.454% | 1.0986 | 1.1056 | 1.069
2011-01-04 | 38 | 22.8771 | 12.2226 | 35.0998 | 2.1431 | 0.76558 | 0.26094 | 3.1696 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2011-01-04 | 39 | 22.8071 | 12.0985 | 34.9056 | 2.1195 | 0.76558 | 0.25949 | 3.1445 | 9.009% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2011-01-04 | 40 | 22.5412 | 11.8429 | 34.3841 | 2.0566 | 0.76558 | 0.25562 | 3.0778 | 8.951% | 9.524% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-01-04 | 41 | 22.523 | 11.4245 | 33.9475 | 2.0047 | 0.76558 | 0.25237 | 3.0227 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-01-04 | 42 | 22.2855 | 10.9104 | 33.1959 | 1.9169 | 0.76558 | 0.24678 | 2.9293 | 8.824% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2011-01-04 | 43 | 21.8659 | 11.0787 | 32.9446 | 1.888 | 0.76558 | 0.24491 | 2.8985 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-01-04 | 44 | 22.5598 | 11.3879 | 33.9477 | 2.0047 | 0.76558 | 0.25237 | 3.0227 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-01-04 | 45 | 22.7176 | 11.3848 | 34.1024 | 2.023 | 0.76558 | 0.25352 | 3.0421 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2011-01-04 | 46 | 21.5494 | 10.8537 | 32.4031 | 1.8264 | 0.76558 | 0.24089 | 2.8329 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-01-04 | 47 | 19.5875 | 10.2524 | 29.8399 | 1.5489 | 0.76558 | 0.22183 | 2.5363 | 8.5% | 9.044% | 6.111% | 1.0929 | 1.0994 | 1.0651
2011-01-04 | 48 | 17.9515 | 10.126 | 28.0775 | 1.3714 | 0.76558 | 0.20873 | 2.3457 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2011-01-05 | 1 | 16.0131 | 9.1564 | 25.1694 | 1.102 | 0.76558 | 0.18711 | 2.0547 | 8.163% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-01-05 | 2 | 14.6589 | 8.5418 | 23.2008 | 0.93635 | 0.76558 | 0.17248 | 1.8744 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-01-05 | 3 | 13.4436 | 8.0086 | 21.4523 | 0.80054 | 0.76558 | 0.15948 | 1.7256 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-05 | 4 | 12.9136 | 7.6611 | 20.5746 | 0.73638 | 0.76558 | 0.15295 | 1.6549 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-05 | 5 | 12.5374 | 7.5847 | 20.1221 | 0.70434 | 0.76558 | 0.14959 | 1.6195 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-05 | 6 | 12.0794 | 7.3961 | 19.4756 | 0.6598 | 0.76558 | 0.14478 | 1.5702 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-05 | 7 | 11.9433 | 7.3779 | 19.3212 | 0.64939 | 0.76558 | 0.14364 | 1.5586 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-01-05 | 8 | 11.915 | 7.4107 | 19.3257 | 0.64969 | 0.76558 | 0.14367 | 1.5589 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-01-05 | 9 | 12.0771 | 7.3454 | 19.4225 | 0.65621 | 0.76558 | 0.14439 | 1.5662 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-01-05 | 10 | 12.229 | 7.5195 | 19.7485 | 0.67843 | 0.76558 | 0.14681 | 1.5908 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-01-05 | 11 | 12.4711 | 7.6102 | 20.0813 | 0.70149 | 0.76558 | 0.14929 | 1.6164 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-05 | 12 | 12.7811 | 7.8551 | 20.6362 | 0.74079 | 0.76558 | 0.15341 | 1.6598 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-05 | 13 | 13.9509 | 8.2018 | 22.1527 | 0.85367 | 0.76558 | 0.16469 | 1.7839 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-01-05 | 14 | 15.3687 | 8.9327 | 24.3014 | 1.0273 | 0.76558 | 0.18066 | 1.9735 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-01-05 | 15 | 18.0932 | 10.0566 | 28.1498 | 1.3784 | 0.76558 | 0.20927 | 2.3533 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2011-01-05 | 16 | 20.167 | 11.3518 | 31.5187 | 1.7281 | 0.76558 | 0.23431 | 2.728 | 8.655% | 9.209% | 6.223% | 1.0948 | 1.1014 | 1.0664
2011-01-05 | 17 | 22.4693 | 12.5283 | 34.9975 | 2.1306 | 0.76558 | 0.26018 | 3.1564 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1061 | 1.0693
2011-01-05 | 18 | 24.077 | 13.2944 | 37.3714 | 2.4295 | 0.76558 | 0.27782 | 3.4729 | 9.293% | 9.888% | 6.682% | 1.1024 | 1.1097 | 1.0716
2011-01-05 | 19 | 25.0734 | 13.6433 | 38.7167 | 2.6075 | 0.76558 | 0.28782 | 3.6609 | 9.456% | 10.06% | 6.799% | 1.1044 | 1.1119 | 1.0729
2011-01-05 | 20 | 25.3374 | 13.7759 | 39.1133 | 2.6612 | 0.76558 | 0.29077 | 3.7176 | 9.505% | 10.11% | 6.834% | 1.105 | 1.1125 | 1.0734
2011-01-05 | 21 | 25.1894 | 13.3731 | 38.5624 | 2.5868 | 0.76558 | 0.28668 | 3.6391 | 9.437% | 10.04% | 6.785% | 1.1042 | 1.1116 | 1.0728
2011-01-05 | 22 | 24.9694 | 13.1859 | 38.1553 | 2.5325 | 0.76558 | 0.28365 | 3.5817 | 9.387% | 9.988% | 6.749% | 1.1036 | 1.111 | 1.0724
2011-01-05 | 23 | 24.1552 | 12.8865 | 37.0417 | 2.3868 | 0.76558 | 0.27537 | 3.4278 | 9.254% | 9.846% | 6.653% | 1.102 | 1.1092 | 1.0713
2011-01-05 | 24 | 23.6392 | 12.7194 | 36.3586 | 2.2996 | 0.76558 | 0.27029 | 3.3355 | 9.174% | 9.761% | 6.596% | 1.101 | 1.1082 | 1.0706
2011-01-05 | 25 | 23.1651 | 12.8929 | 36.0581 | 2.2617 | 0.76558 | 0.26806 | 3.2954 | 9.139% | 9.724% | 6.571% | 1.1006 | 1.1077 | 1.0703
2011-01-05 | 26 | 22.5772 | 12.6264 | 35.2035 | 2.1558 | 0.76558 | 0.26171 | 3.1831 | 9.042% | 9.621% | 6.501% | 1.0994 | 1.1064 | 1.0695
2011-01-05 | 27 | 22.305 | 12.6576 | 34.9626 | 2.1264 | 0.76558 | 0.25992 | 3.1519 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-01-05 | 28 | 22.0329 | 12.4282 | 34.461 | 2.0658 | 0.76558 | 0.25619 | 3.0876 | 8.96% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2011-01-05 | 29 | 21.651 | 11.839 | 33.49 | 1.951 | 0.76558 | 0.24897 | 2.9656 | 8.855% | 9.422% | 6.367% | 1.0972 | 1.104 | 1.068
2011-01-05 | 30 | 21.365 | 11.3763 | 32.7412 | 1.8648 | 0.76558 | 0.2434 | 2.8737 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2011-01-05 | 31 | 21.2851 | 11.2098 | 32.4948 | 1.8368 | 0.76558 | 0.24157 | 2.844 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-01-05 | 32 | 20.9291 | 11.2752 | 32.2043 | 1.8041 | 0.76558 | 0.23941 | 2.8091 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-01-05 | 33 | 20.9388 | 11.6228 | 32.5616 | 1.8444 | 0.76558 | 0.24207 | 2.852 | 8.759% | 9.319% | 6.298% | 1.096 | 1.1028 | 1.0672
2011-01-05 | 34 | 21.1429 | 11.7592 | 32.902 | 1.8831 | 0.76558 | 0.2446 | 2.8933 | 8.794% | 9.356% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-01-05 | 35 | 21.5309 | 12.2457 | 33.7766 | 1.9846 | 0.76558 | 0.2511 | 3.0012 | 8.886% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-01-05 | 36 | 22.3185 | 12.8286 | 35.1471 | 2.1489 | 0.76558 | 0.26129 | 3.1758 | 9.036% | 9.614% | 6.497% | 1.0993 | 1.1064 | 1.0695
2011-01-05 | 37 | 23.1701 | 12.9772 | 36.1473 | 2.2729 | 0.76558 | 0.26872 | 3.3072 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2011-01-05 | 38 | 23.4261 | 13.0551 | 36.4813 | 2.3151 | 0.76558 | 0.27121 | 3.3519 | 9.188% | 9.776% | 6.606% | 1.1012 | 1.1084 | 1.0707
2011-01-05 | 39 | 23.4063 | 12.7531 | 36.1594 | 2.2745 | 0.76558 | 0.26881 | 3.3089 | 9.151% | 9.736% | 6.579% | 1.1007 | 1.1079 | 1.0704
2011-01-05 | 40 | 23.1247 | 12.4362 | 35.5609 | 2.1998 | 0.76558 | 0.26436 | 3.2297 | 9.082% | 9.664% | 6.53% | 1.0999 | 1.107 | 1.0699
2011-01-05 | 41 | 22.7547 | 11.9619 | 34.7166 | 2.0966 | 0.76558 | 0.25809 | 3.1202 | 8.988% | 9.563% | 6.462% | 1.0988 | 1.1057 | 1.0691
2011-01-05 | 42 | 22.8407 | 11.7354 | 34.5761 | 2.0796 | 0.76558 | 0.25704 | 3.1023 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2011-01-05 | 43 | 22.439 | 11.7988 | 34.2378 | 2.0391 | 0.76558 | 0.25453 | 3.0592 | 8.935% | 9.507% | 6.424% | 1.0981 | 1.1051 | 1.0687
2011-01-05 | 44 | 22.8932 | 12.0149 | 34.9081 | 2.1198 | 0.76558 | 0.25951 | 3.1449 | 9.009% | 9.586% | 6.477% | 1.099 | 1.106 | 1.0693
2011-01-05 | 45 | 22.4974 | 11.6283 | 34.1256 | 2.0258 | 0.76558 | 0.25369 | 3.0451 | 8.923% | 9.494% | 6.416% | 1.098 | 1.1049 | 1.0686
2011-01-05 | 46 | 21.1676 | 11.0358 | 32.2035 | 1.804 | 0.76558 | 0.2394 | 2.809 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-01-05 | 47 | 19.4638 | 10.762 | 30.2258 | 1.5892 | 0.76558 | 0.2247 | 2.5795 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-01-05 | 48 | 17.8256 | 10.6032 | 28.4288 | 1.4059 | 0.76558 | 0.21134 | 2.3828 | 8.382% | 8.918% | 6.026% | 1.0915 | 1.0979 | 1.0641
2011-01-06 | 1 | 16.0578 | 9.5726 | 25.6303 | 1.1427 | 0.76558 | 0.19054 | 2.0988 | 8.189% | 8.713% | 5.888% | 1.0892 | 1.0954 | 1.0626
2011-01-06 | 2 | 14.5097 | 9.0562 | 23.5659 | 0.96606 | 0.76558 | 0.17519 | 1.9068 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-01-06 | 3 | 13.7356 | 8.6373 | 22.3729 | 0.87072 | 0.76558 | 0.16632 | 1.8026 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-06 | 4 | 12.8455 | 8.3018 | 21.1474 | 0.77794 | 0.76558 | 0.15721 | 1.7007 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-06 | 5 | 12.5356 | 8.0275 | 20.5631 | 0.73555 | 0.76558 | 0.15287 | 1.654 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-06 | 6 | 12.1555 | 7.8958 | 20.0513 | 0.69939 | 0.76558 | 0.14906 | 1.614 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-06 | 7 | 12.0254 | 7.9282 | 19.9537 | 0.6926 | 0.76558 | 0.14834 | 1.6065 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-06 | 8 | 11.9795 | 7.7537 | 19.7332 | 0.67737 | 0.76558 | 0.1467 | 1.5896 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-01-06 | 9 | 11.8794 | 7.7907 | 19.6701 | 0.67305 | 0.76558 | 0.14623 | 1.5849 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-06 | 10 | 12.0555 | 7.9865 | 20.042 | 0.69874 | 0.76558 | 0.14899 | 1.6133 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-06 | 11 | 12.2319 | 8.0359 | 20.2678 | 0.71457 | 0.76558 | 0.15067 | 1.6308 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-06 | 12 | 12.6416 | 8.4503 | 21.0919 | 0.77387 | 0.76558 | 0.1568 | 1.6962 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-06 | 13 | 13.5714 | 8.6493 | 22.2207 | 0.85892 | 0.76558 | 0.16519 | 1.7897 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-01-06 | 14 | 15.0821 | 9.2727 | 24.3548 | 1.0318 | 0.76558 | 0.18106 | 1.9785 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-01-06 | 15 | 17.4259 | 10.2009 | 27.6268 | 1.3277 | 0.76558 | 0.20538 | 2.2987 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2011-01-06 | 16 | 19.3939 | 11.16 | 30.554 | 1.6239 | 0.76558 | 0.22714 | 2.6167 | 8.564% | 9.112% | 6.158% | 1.0937 | 1.1003 | 1.0656
2011-01-06 | 17 | 21.7719 | 12.1325 | 33.9044 | 1.9996 | 0.76558 | 0.25205 | 3.0172 | 8.899% | 9.469% | 6.399% | 1.0977 | 1.1046 | 1.0684
2011-01-06 | 18 | 23.3177 | 12.5882 | 35.9059 | 2.2427 | 0.76558 | 0.26693 | 3.2752 | 9.122% | 9.705% | 6.558% | 1.1004 | 1.1075 | 1.0702
2011-01-06 | 19 | 24.2139 | 12.9579 | 37.1718 | 2.4036 | 0.76558 | 0.27634 | 3.4455 | 9.269% | 9.862% | 6.665% | 1.1022 | 1.1094 | 1.0714
2011-01-06 | 20 | 24.2598 | 13.2714 | 37.5312 | 2.4503 | 0.76558 | 0.27901 | 3.4949 | 9.312% | 9.908% | 6.695% | 1.1027 | 1.11 | 1.0718
2011-01-06 | 21 | 24.7316 | 13.1306 | 37.8621 | 2.4937 | 0.76558 | 0.28147 | 3.5408 | 9.352% | 9.95% | 6.724% | 1.1032 | 1.1105 | 1.0721
2011-01-06 | 22 | 24.3415 | 12.8859 | 37.2275 | 2.4108 | 0.76558 | 0.27675 | 3.4531 | 9.276% | 9.869% | 6.669% | 1.1022 | 1.1095 | 1.0715
2011-01-06 | 23 | 23.8253 | 12.5972 | 36.4225 | 2.3077 | 0.76558 | 0.27077 | 3.344 | 9.181% | 9.769% | 6.601% | 1.1011 | 1.1083 | 1.0707
2011-01-06 | 24 | 23.4454 | 12.5805 | 36.0258 | 2.2577 | 0.76558 | 0.26782 | 3.2911 | 9.135% | 9.72% | 6.568% | 1.1005 | 1.1077 | 1.0703
2011-01-06 | 25 | 23.0651 | 12.6667 | 35.7318 | 2.221 | 0.76558 | 0.26563 | 3.2522 | 9.102% | 9.684% | 6.544% | 1.1001 | 1.1072 | 1.07
2011-01-06 | 26 | 22.5811 | 12.4452 | 35.0264 | 2.1341 | 0.76558 | 0.26039 | 3.1601 | 9.022% | 9.6% | 6.487% | 1.0992 | 1.1062 | 1.0694
2011-01-06 | 27 | 21.9891 | 12.4572 | 34.4463 | 2.064 | 0.76558 | 0.25608 | 3.0857 | 8.958% | 9.531% | 6.441% | 1.0984 | 1.1054 | 1.0688
2011-01-06 | 28 | 21.6009 | 12.0724 | 33.6733 | 1.9725 | 0.76558 | 0.25033 | 2.9884 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-01-06 | 29 | 21.0767 | 11.8471 | 32.9238 | 1.8856 | 0.76558 | 0.24476 | 2.896 | 8.796% | 9.359% | 6.324% | 1.0964 | 1.1033 | 1.0675
2011-01-06 | 30 | 20.8058 | 11.7558 | 32.5615 | 1.8444 | 0.76558 | 0.24207 | 2.852 | 8.759% | 9.319% | 6.298% | 1.096 | 1.1028 | 1.0672
2011-01-06 | 31 | 21.3079 | 11.5977 | 32.9056 | 1.8835 | 0.76558 | 0.24462 | 2.8937 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-01-06 | 32 | 21.5183 | 11.5197 | 33.038 | 1.8987 | 0.76558 | 0.24561 | 2.9099 | 8.808% | 9.371% | 6.333% | 1.0966 | 1.1034 | 1.0676
2011-01-06 | 33 | 21.6087 | 11.9926 | 33.6013 | 1.964 | 0.76558 | 0.2498 | 2.9794 | 8.867% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2011-01-06 | 34 | 21.5369 | 12.0505 | 33.5873 | 1.9624 | 0.76558 | 0.24969 | 2.9777 | 8.865% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2011-01-06 | 35 | 21.9067 | 12.5875 | 34.4942 | 2.0698 | 0.76558 | 0.25643 | 3.0918 | 8.963% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2011-01-06 | 36 | 23.6265 | 13.2469 | 36.8735 | 2.3652 | 0.76558 | 0.27412 | 3.4049 | 9.234% | 9.825% | 6.639% | 1.1017 | 1.109 | 1.0711
2011-01-06 | 37 | 26.1386 | 13.4474 | 39.5861 | 2.726 | 0.76558 | 0.29429 | 3.7858 | 9.564% | 10.18% | 6.876% | 1.1057 | 1.1133 | 1.0738
2011-01-06 | 38 | 26.0546 | 13.4116 | 39.4662 | 2.7095 | 0.76558 | 0.2934 | 3.7685 | 9.549% | 10.16% | 6.865% | 1.1056 | 1.1131 | 1.0737
2011-01-06 | 39 | 26.3449 | 13.0053 | 39.3502 | 2.6936 | 0.76558 | 0.29253 | 3.7517 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2011-01-06 | 40 | 26.4564 | 12.5855 | 39.0419 | 2.6515 | 0.76558 | 0.29024 | 3.7074 | 9.496% | 10.1% | 6.828% | 1.1049 | 1.1124 | 1.0733
2011-01-06 | 41 | 25.5108 | 12.3986 | 37.9093 | 2.4999 | 0.76558 | 0.28182 | 3.5473 | 9.357% | 9.956% | 6.728% | 1.1032 | 1.1106 | 1.0721
2011-01-06 | 42 | 24.9275 | 11.8994 | 36.8268 | 2.3592 | 0.76558 | 0.27378 | 3.3985 | 9.228% | 9.819% | 6.635% | 1.1017 | 1.1089 | 1.0711
2011-01-06 | 43 | 23.9141 | 11.6893 | 35.6035 | 2.2051 | 0.76558 | 0.26468 | 3.2353 | 9.087% | 9.669% | 6.534% | 1.1 | 1.107 | 1.0699
2011-01-06 | 44 | 23.5737 | 11.7188 | 35.2925 | 2.1667 | 0.76558 | 0.26237 | 3.1947 | 9.052% | 9.631% | 6.508% | 1.0995 | 1.1066 | 1.0696
2011-01-06 | 45 | 23.0738 | 11.4501 | 34.5239 | 2.0734 | 0.76558 | 0.25666 | 3.0956 | 8.967% | 9.54% | 6.447% | 1.0985 | 1.1055 | 1.0689
2011-01-06 | 46 | 21.7888 | 10.9864 | 32.7752 | 1.8686 | 0.76558 | 0.24365 | 2.8779 | 8.781% | 9.343% | 6.313% | 1.0963 | 1.1031 | 1.0674
2011-01-06 | 47 | 19.6061 | 10.3161 | 29.9222 | 1.5575 | 0.76558 | 0.22244 | 2.5455 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2011-01-06 | 48 | 17.8873 | 10.1016 | 27.9889 | 1.3627 | 0.76558 | 0.20807 | 2.3364 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2011-01-07 | 1 | 16.0204 | 9.2062 | 25.2266 | 1.107 | 0.76558 | 0.18754 | 2.0601 | 8.166% | 8.689% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-01-07 | 2 | 14.6923 | 8.5443 | 23.2366 | 0.93924 | 0.76558 | 0.17274 | 1.8776 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-01-07 | 3 | 13.6497 | 8.1303 | 21.78 | 0.82518 | 0.76558 | 0.16191 | 1.7527 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 4 | 13.2894 | 7.9092 | 21.1986 | 0.78171 | 0.76558 | 0.15759 | 1.7049 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 5 | 12.9309 | 7.9321 | 20.863 | 0.75716 | 0.76558 | 0.1551 | 1.6778 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 6 | 12.5459 | 7.7654 | 20.3113 | 0.71765 | 0.76558 | 0.151 | 1.6342 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 7 | 12.1803 | 7.8022 | 19.9825 | 0.6946 | 0.76558 | 0.14855 | 1.6087 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-01-07 | 8 | 12.1325 | 7.5827 | 19.7152 | 0.67614 | 0.76558 | 0.14656 | 1.5883 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2011-01-07 | 9 | 12.2665 | 7.5893 | 19.8557 | 0.68581 | 0.76558 | 0.14761 | 1.599 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-01-07 | 10 | 12.2705 | 7.6704 | 19.9409 | 0.69171 | 0.76558 | 0.14824 | 1.6055 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-07 | 11 | 12.7087 | 7.7038 | 20.4125 | 0.72481 | 0.76558 | 0.15175 | 1.6421 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 12 | 13.1267 | 8.0555 | 21.1822 | 0.78051 | 0.76558 | 0.15747 | 1.7036 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-07 | 13 | 14.1483 | 8.2685 | 22.4168 | 0.87414 | 0.76558 | 0.16665 | 1.8064 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-01-07 | 14 | 15.4923 | 8.6613 | 24.1537 | 1.0148 | 0.76558 | 0.17956 | 1.96 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-01-07 | 15 | 17.9623 | 9.6654 | 27.6277 | 1.3278 | 0.76558 | 0.20539 | 2.2987 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2011-01-07 | 16 | 20.0144 | 10.8798 | 30.8942 | 1.6603 | 0.76558 | 0.22967 | 2.6556 | 8.596% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-01-07 | 17 | 22.7542 | 11.7581 | 34.5123 | 2.072 | 0.76558 | 0.25657 | 3.0941 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2011-01-07 | 18 | 24.4881 | 12.273 | 36.7611 | 2.3508 | 0.76558 | 0.27329 | 3.3896 | 9.221% | 9.811% | 6.63% | 1.1016 | 1.1088 | 1.071
2011-01-07 | 19 | 25.312 | 12.8642 | 38.1763 | 2.5353 | 0.76558 | 0.28381 | 3.5846 | 9.39% | 9.991% | 6.751% | 1.1036 | 1.111 | 1.0724
2011-01-07 | 20 | 25.5661 | 13.0559 | 38.6219 | 2.5948 | 0.76558 | 0.28712 | 3.6475 | 9.444% | 10.05% | 6.79% | 1.1043 | 1.1117 | 1.0728
2011-01-07 | 21 | 25.5341 | 12.7976 | 38.3317 | 2.5559 | 0.76558 | 0.28496 | 3.6065 | 9.409% | 10.01% | 6.765% | 1.1039 | 1.1112 | 1.0726
2011-01-07 | 22 | 24.9922 | 12.9712 | 37.9634 | 2.5071 | 0.76558 | 0.28222 | 3.5549 | 9.364% | 9.963% | 6.733% | 1.1033 | 1.1107 | 1.0722
2011-01-07 | 23 | 24.3841 | 12.7879 | 37.1719 | 2.4036 | 0.76558 | 0.27634 | 3.4455 | 9.269% | 9.862% | 6.665% | 1.1022 | 1.1094 | 1.0714
2011-01-07 | 24 | 23.887 | 12.4811 | 36.3681 | 2.3008 | 0.76558 | 0.27036 | 3.3367 | 9.175% | 9.762% | 6.597% | 1.101 | 1.1082 | 1.0706
2011-01-07 | 25 | 22.868 | 12.4859 | 35.3539 | 2.1743 | 0.76558 | 0.26283 | 3.2027 | 9.059% | 9.639% | 6.513% | 1.0996 | 1.1067 | 1.0697
2011-01-07 | 26 | 22.3309 | 12.012 | 34.3429 | 2.0517 | 0.76558 | 0.25531 | 3.0726 | 8.947% | 9.519% | 6.433% | 1.0983 | 1.1052 | 1.0687
2011-01-07 | 27 | 21.9613 | 11.9849 | 33.9462 | 2.0046 | 0.76558 | 0.25236 | 3.0225 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-01-07 | 28 | 21.6436 | 11.7213 | 33.3649 | 1.9365 | 0.76558 | 0.24804 | 2.9501 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-01-07 | 29 | 21.3057 | 11.2392 | 32.5449 | 1.8425 | 0.76558 | 0.24194 | 2.85 | 8.757% | 9.318% | 6.296% | 1.096 | 1.1027 | 1.0672
2011-01-07 | 30 | 21.1677 | 11.1632 | 32.3309 | 1.8183 | 0.76558 | 0.24035 | 2.8242 | 8.735% | 9.295% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-01-07 | 31 | 21.0755 | 11.0107 | 32.0862 | 1.7909 | 0.76558 | 0.23853 | 2.795 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1022 | 1.0668
2011-01-07 | 32 | 20.8488 | 10.8268 | 31.6756 | 1.7454 | 0.76558 | 0.23548 | 2.7464 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-01-07 | 33 | 21.2919 | 11.0299 | 32.3218 | 1.8173 | 0.76558 | 0.24028 | 2.8232 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2011-01-07 | 34 | 21.8079 | 11.1851 | 32.993 | 1.8936 | 0.76558 | 0.24527 | 2.9044 | 8.803% | 9.367% | 6.329% | 1.0965 | 1.1033 | 1.0676
2011-01-07 | 35 | 22.164 | 11.6744 | 33.8384 | 1.9918 | 0.76558 | 0.25156 | 3.009 | 8.892% | 9.461% | 6.393% | 1.0976 | 1.1045 | 1.0683
2011-01-07 | 36 | 22.9743 | 12.4707 | 35.445 | 2.1855 | 0.76558 | 0.2635 | 3.2145 | 9.069% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2011-01-07 | 37 | 24.1516 | 12.0888 | 36.2403 | 2.2846 | 0.76558 | 0.26942 | 3.3196 | 9.16% | 9.746% | 6.586% | 1.1008 | 1.108 | 1.0705
2011-01-07 | 38 | 24.8128 | 11.7808 | 36.5936 | 2.3294 | 0.76558 | 0.27204 | 3.367 | 9.201% | 9.79% | 6.616% | 1.1013 | 1.1085 | 1.0708
2011-01-07 | 39 | 24.7309 | 11.314 | 36.0448 | 2.2601 | 0.76558 | 0.26796 | 3.2936 | 9.138% | 9.722% | 6.57% | 1.1006 | 1.1077 | 1.0703
2011-01-07 | 40 | 24.5308 | 10.9905 | 35.5213 | 2.1949 | 0.76558 | 0.26407 | 3.2245 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2011-01-07 | 41 | 24.859 | 10.5891 | 35.4481 | 2.1858 | 0.76558 | 0.26353 | 3.215 | 9.069% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2011-01-07 | 42 | 24.733 | 10.3547 | 35.0877 | 2.1416 | 0.76558 | 0.26085 | 3.168 | 9.029% | 9.607% | 6.492% | 1.0993 | 1.1063 | 1.0694
2011-01-07 | 43 | 24.5412 | 10.3779 | 34.9191 | 2.1211 | 0.76558 | 0.25959 | 3.1463 | 9.01% | 9.587% | 6.478% | 1.099 | 1.106 | 1.0693
2011-01-07 | 44 | 24.9994 | 10.6005 | 35.5999 | 2.2046 | 0.76558 | 0.26465 | 3.2348 | 9.087% | 9.668% | 6.533% | 1.0999 | 1.107 | 1.0699
2011-01-07 | 45 | 24.3696 | 10.5783 | 34.9479 | 2.1246 | 0.76558 | 0.25981 | 3.15 | 9.013% | 9.59% | 6.481% | 1.0991 | 1.1061 | 1.0693
2011-01-07 | 46 | 22.9137 | 9.9687 | 32.8823 | 1.8809 | 0.76558 | 0.24445 | 2.8909 | 8.792% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-01-07 | 47 | 20.8977 | 9.2675 | 30.1652 | 1.5829 | 0.76558 | 0.22425 | 2.5727 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-01-07 | 48 | 19.1437 | 9.1184 | 28.2621 | 1.3894 | 0.76558 | 0.2101 | 2.3651 | 8.369% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2011-01-08 | 1 | 16.9196 | 8.0876 | 25.0072 | 1.0878 | 0.76558 | 0.18591 | 2.0393 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2011-01-08 | 2 | 15.6477 | 7.3739 | 23.0216 | 0.92195 | 0.76558 | 0.17115 | 1.8587 | 8.074% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-08 | 3 | 14.7237 | 6.9762 | 21.6999 | 0.81912 | 0.76558 | 0.16132 | 1.746 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 4 | 14.1778 | 6.8276 | 21.0053 | 0.76753 | 0.76558 | 0.15616 | 1.6893 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 5 | 13.8538 | 6.7524 | 20.6061 | 0.73863 | 0.76558 | 0.15319 | 1.6574 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 6 | 13.5797 | 6.6217 | 20.2014 | 0.7099 | 0.76558 | 0.15018 | 1.6257 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 7 | 13.2977 | 6.701 | 19.9987 | 0.69572 | 0.76558 | 0.14867 | 1.61 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-01-08 | 8 | 13.1256 | 6.7097 | 19.8353 | 0.6844 | 0.76558 | 0.14746 | 1.5974 | 8.054% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-01-08 | 9 | 13.3615 | 6.8247 | 20.1862 | 0.70883 | 0.76558 | 0.15007 | 1.6245 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 10 | 13.5097 | 6.7821 | 20.2917 | 0.71626 | 0.76558 | 0.15085 | 1.6327 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 11 | 13.6997 | 6.9376 | 20.6374 | 0.74087 | 0.76558 | 0.15342 | 1.6599 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 12 | 14.2937 | 7.1081 | 21.4018 | 0.79678 | 0.76558 | 0.1591 | 1.7215 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-08 | 13 | 15.3678 | 7.435 | 22.8028 | 0.9045 | 0.76558 | 0.16952 | 1.8396 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2011-01-08 | 14 | 17.0698 | 8.1788 | 25.2487 | 1.109 | 0.76558 | 0.1877 | 2.0622 | 8.168% | 8.69% | 5.873% | 1.0889 | 1.0952 | 1.0624
2011-01-08 | 15 | 19.6718 | 9.2635 | 28.9353 | 1.4564 | 0.76558 | 0.21511 | 2.4371 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-01-08 | 16 | 22.0698 | 10.1287 | 32.1986 | 1.8035 | 0.76558 | 0.23937 | 2.8084 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2011-01-08 | 17 | 24.9518 | 11.1402 | 36.092 | 2.266 | 0.76558 | 0.26831 | 3.2999 | 9.143% | 9.728% | 6.574% | 1.1006 | 1.1078 | 1.0704
2011-01-08 | 18 | 26.6778 | 12.1783 | 38.8561 | 2.6264 | 0.76558 | 0.28886 | 3.6808 | 9.473% | 10.08% | 6.811% | 1.1046 | 1.1121 | 1.0731
2011-01-08 | 19 | 27.9637 | 12.9023 | 40.8659 | 2.9051 | 0.76558 | 0.3038 | 3.9745 | 9.726% | 10.35% | 6.993% | 1.1077 | 1.1154 | 1.0752
2011-01-08 | 20 | 27.6518 | 13.58 | 41.2319 | 2.9573 | 0.76558 | 0.30652 | 4.0294 | 9.773% | 10.4% | 7.027% | 1.1083 | 1.116 | 1.0756
2011-01-08 | 21 | 27.082 | 13.5389 | 40.6209 | 2.8703 | 0.76558 | 0.30198 | 3.9379 | 9.694% | 10.31% | 6.97% | 1.1073 | 1.115 | 1.0749
2011-01-08 | 22 | 26.6701 | 13.5714 | 40.2415 | 2.817 | 0.76558 | 0.29916 | 3.8817 | 9.646% | 10.26% | 6.936% | 1.1068 | 1.1144 | 1.0745
2011-01-08 | 23 | 25.734 | 13.0841 | 38.8181 | 2.6212 | 0.76558 | 0.28858 | 3.6754 | 9.468% | 10.07% | 6.808% | 1.1046 | 1.112 | 1.073
2011-01-08 | 24 | 25.1856 | 12.8232 | 38.0089 | 2.5131 | 0.76558 | 0.28256 | 3.5612 | 9.369% | 9.969% | 6.737% | 1.1034 | 1.1107 | 1.0722
2011-01-08 | 25 | 24.6196 | 12.6475 | 37.2671 | 2.4159 | 0.76558 | 0.27705 | 3.4586 | 9.28% | 9.874% | 6.673% | 1.1023 | 1.1096 | 1.0715
2011-01-08 | 26 | 24.3476 | 12.3728 | 36.7204 | 2.3456 | 0.76558 | 0.27298 | 3.3841 | 9.216% | 9.806% | 6.626% | 1.1015 | 1.1087 | 1.071
2011-01-08 | 27 | 24.2397 | 12.4473 | 36.6871 | 2.3413 | 0.76558 | 0.27274 | 3.3796 | 9.212% | 9.802% | 6.623% | 1.1015 | 1.1087 | 1.0709
2011-01-08 | 28 | 23.2588 | 12.425 | 35.6838 | 2.215 | 0.76558 | 0.26528 | 3.2459 | 9.096% | 9.678% | 6.54% | 1.1001 | 1.1072 | 1.07
2011-01-08 | 29 | 22.9893 | 12.2054 | 35.1947 | 2.1547 | 0.76558 | 0.26164 | 3.1819 | 9.041% | 9.62% | 6.5% | 1.0994 | 1.1064 | 1.0695
2011-01-08 | 30 | 22.885 | 12.0552 | 34.9402 | 2.1237 | 0.76558 | 0.25975 | 3.149 | 9.013% | 9.589% | 6.48% | 1.0991 | 1.1061 | 1.0693
2011-01-08 | 31 | 23.1236 | 11.9523 | 35.0759 | 2.1402 | 0.76558 | 0.26076 | 3.1665 | 9.028% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2011-01-08 | 32 | 23.2315 | 11.6299 | 34.8615 | 2.1141 | 0.76558 | 0.25916 | 3.1388 | 9.004% | 9.58% | 6.474% | 1.0989 | 1.106 | 1.0692
2011-01-08 | 33 | 24.3376 | 11.9763 | 36.3139 | 2.2939 | 0.76558 | 0.26996 | 3.3295 | 9.169% | 9.755% | 6.592% | 1.1009 | 1.1081 | 1.0706
2011-01-08 | 34 | 24.3318 | 12.0093 | 36.3411 | 2.2974 | 0.76558 | 0.27016 | 3.3331 | 9.172% | 9.759% | 6.594% | 1.101 | 1.1081 | 1.0706
2011-01-08 | 35 | 23.8158 | 12.3039 | 36.1198 | 2.2695 | 0.76558 | 0.26852 | 3.3036 | 9.146% | 9.732% | 6.576% | 1.1007 | 1.1078 | 1.0704
2011-01-08 | 36 | 23.846 | 12.9298 | 36.7758 | 2.3527 | 0.76558 | 0.2734 | 3.3916 | 9.222% | 9.813% | 6.631% | 1.1016 | 1.1088 | 1.071
2011-01-08 | 37 | 24.3961 | 13.0914 | 37.4875 | 2.4446 | 0.76558 | 0.27869 | 3.4889 | 9.307% | 9.902% | 6.692% | 1.1026 | 1.1099 | 1.0717
2011-01-08 | 38 | 25.1483 | 13.1558 | 38.3041 | 2.5523 | 0.76558 | 0.28476 | 3.6026 | 9.405% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2011-01-08 | 39 | 25.2264 | 12.9369 | 38.1633 | 2.5335 | 0.76558 | 0.28371 | 3.5828 | 9.388% | 9.989% | 6.75% | 1.1036 | 1.111 | 1.0724
2011-01-08 | 40 | 25.0003 | 12.2621 | 37.2624 | 2.4153 | 0.76558 | 0.27701 | 3.4579 | 9.28% | 9.874% | 6.672% | 1.1023 | 1.1096 | 1.0715
2011-01-08 | 41 | 24.9461 | 11.8326 | 36.7787 | 2.353 | 0.76558 | 0.27342 | 3.392 | 9.223% | 9.813% | 6.631% | 1.1016 | 1.1088 | 1.071
2011-01-08 | 42 | 25.0365 | 11.4522 | 36.4887 | 2.3161 | 0.76558 | 0.27126 | 3.3529 | 9.189% | 9.777% | 6.607% | 1.1012 | 1.1084 | 1.0707
2011-01-08 | 43 | 25.0265 | 11.3561 | 36.3826 | 2.3026 | 0.76558 | 0.27047 | 3.3387 | 9.177% | 9.764% | 6.598% | 1.101 | 1.1082 | 1.0706
2011-01-08 | 44 | 25.4147 | 11.5498 | 36.9645 | 2.3769 | 0.76558 | 0.2748 | 3.4172 | 9.245% | 9.836% | 6.647% | 1.1019 | 1.1091 | 1.0712
2011-01-08 | 45 | 25.2088 | 11.308 | 36.5168 | 2.3196 | 0.76558 | 0.27147 | 3.3567 | 9.192% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2011-01-08 | 46 | 23.8386 | 10.5128 | 34.3514 | 2.0527 | 0.76558 | 0.25537 | 3.0736 | 8.948% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2011-01-08 | 47 | 22.1685 | 9.9157 | 32.0842 | 1.7907 | 0.76558 | 0.23852 | 2.7948 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1021 | 1.0668
2011-01-08 | 48 | 20.7023 | 9.9521 | 30.6545 | 1.6346 | 0.76558 | 0.22789 | 2.6281 | 8.573% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2011-01-09 | 1 | 18.7082 | 9.0003 | 27.7085 | 1.3355 | 0.76558 | 0.20599 | 2.3071 | 8.326% | 8.859% | 5.987% | 1.0908 | 1.0972 | 1.0637
2011-01-09 | 2 | 16.902 | 8.2552 | 25.1573 | 1.1009 | 0.76558 | 0.18702 | 2.0535 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2011-01-09 | 3 | 15.7201 | 7.7188 | 23.4389 | 0.95568 | 0.76558 | 0.17425 | 1.8955 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2011-01-09 | 4 | 15.1442 | 7.3367 | 22.4808 | 0.87914 | 0.76558 | 0.16713 | 1.8118 | 8.06% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-09 | 5 | 14.6164 | 7.2153 | 21.8317 | 0.82911 | 0.76558 | 0.1623 | 1.757 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 6 | 14.1684 | 7.0134 | 21.1818 | 0.78048 | 0.76558 | 0.15747 | 1.7035 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 7 | 13.8685 | 6.9672 | 20.8357 | 0.75518 | 0.76558 | 0.15489 | 1.6757 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 8 | 13.6846 | 6.8833 | 20.5679 | 0.73589 | 0.76558 | 0.1529 | 1.6544 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 9 | 13.8828 | 6.8231 | 20.706 | 0.74581 | 0.76558 | 0.15393 | 1.6653 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 10 | 13.9767 | 6.9064 | 20.8832 | 0.75862 | 0.76558 | 0.15525 | 1.6795 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 11 | 14.0925 | 6.9875 | 21.08 | 0.773 | 0.76558 | 0.15671 | 1.6953 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 12 | 14.3727 | 7.0676 | 21.4402 | 0.79964 | 0.76558 | 0.15939 | 1.7246 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-09 | 13 | 14.9827 | 7.2155 | 22.1981 | 0.85717 | 0.76558 | 0.16502 | 1.7878 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-01-09 | 14 | 16.2486 | 7.4215 | 23.6701 | 0.97462 | 0.76558 | 0.17597 | 1.9162 | 8.095% | 8.613% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-01-09 | 15 | 18.08 | 8.2579 | 26.3379 | 1.2067 | 0.76558 | 0.1958 | 2.1681 | 8.232% | 8.759% | 5.919% | 1.0897 | 1.096 | 1.0629
2011-01-09 | 16 | 19.8121 | 9.2283 | 29.0404 | 1.467 | 0.76558 | 0.21589 | 2.4485 | 8.431% | 8.971% | 6.062% | 1.0921 | 1.0986 | 1.0645
2011-01-09 | 17 | 22.0506 | 10.3423 | 32.3929 | 1.8253 | 0.76558 | 0.24081 | 2.8317 | 8.742% | 9.301% | 6.285% | 1.0958 | 1.1026 | 1.0671
2011-01-09 | 18 | 24.3552 | 11.3887 | 35.7439 | 2.2225 | 0.76558 | 0.26572 | 3.2538 | 9.103% | 9.686% | 6.545% | 1.1001 | 1.1072 | 1.07
2011-01-09 | 19 | 26.4294 | 12.2794 | 38.7089 | 2.6065 | 0.76558 | 0.28777 | 3.6598 | 9.455% | 10.06% | 6.798% | 1.1044 | 1.1119 | 1.0729
2011-01-09 | 20 | 27.7737 | 12.9451 | 40.7188 | 2.8842 | 0.76558 | 0.30271 | 3.9525 | 9.707% | 10.33% | 6.979% | 1.1075 | 1.1152 | 1.075
2011-01-09 | 21 | 28.2035 | 13.5454 | 41.7489 | 3.032 | 0.76558 | 0.31037 | 4.1079 | 9.84% | 10.47% | 7.075% | 1.1091 | 1.1169 | 1.0761
2011-01-09 | 22 | 27.9338 | 13.9003 | 41.8341 | 3.0444 | 0.76558 | 0.311 | 4.1209 | 9.851% | 10.48% | 7.083% | 1.1093 | 1.1171 | 1.0762
2011-01-09 | 23 | 26.8738 | 13.6114 | 40.4851 | 2.8512 | 0.76558 | 0.30097 | 3.9177 | 9.677% | 10.3% | 6.958% | 1.1071 | 1.1148 | 1.0748
2011-01-09 | 24 | 26.2197 | 13.276 | 39.4957 | 2.7135 | 0.76558 | 0.29362 | 3.7727 | 9.552% | 10.16% | 6.868% | 1.1056 | 1.1131 | 1.0737
2011-01-09 | 25 | 25.5718 | 12.8291 | 38.4009 | 2.5652 | 0.76558 | 0.28548 | 3.6162 | 9.417% | 10.02% | 6.771% | 1.104 | 1.1114 | 1.0726
2011-01-09 | 26 | 24.6436 | 11.9342 | 36.5778 | 2.3274 | 0.76558 | 0.27192 | 3.3649 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2011-01-09 | 27 | 23.9338 | 11.6138 | 35.5476 | 2.1981 | 0.76558 | 0.26426 | 3.228 | 9.081% | 9.662% | 6.529% | 1.0999 | 1.107 | 1.0699
2011-01-09 | 28 | 23.5717 | 11.1815 | 34.7532 | 2.101 | 0.76558 | 0.25836 | 3.1249 | 8.992% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2011-01-09 | 29 | 23.0279 | 10.6308 | 33.6587 | 1.9707 | 0.76558 | 0.25022 | 2.9865 | 8.873% | 9.441% | 6.38% | 1.0974 | 1.1043 | 1.0681
2011-01-09 | 30 | 22.4919 | 10.369 | 32.8609 | 1.8784 | 0.76558 | 0.24429 | 2.8883 | 8.789% | 9.352% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-01-09 | 31 | 22.4919 | 10.4296 | 32.9215 | 1.8854 | 0.76558 | 0.24474 | 2.8957 | 8.796% | 9.359% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-01-09 | 32 | 22.5279 | 10.3736 | 32.9015 | 1.8831 | 0.76558 | 0.24459 | 2.8932 | 8.794% | 9.356% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-01-09 | 33 | 22.7519 | 10.5957 | 33.3476 | 1.9345 | 0.76558 | 0.24791 | 2.948 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-01-09 | 34 | 23.0502 | 10.6489 | 33.6991 | 1.9755 | 0.76558 | 0.25052 | 2.9916 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-01-09 | 35 | 23.422 | 11.0128 | 34.4348 | 2.0627 | 0.76558 | 0.25599 | 3.0842 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2011-01-09 | 36 | 23.9442 | 11.4338 | 35.378 | 2.1772 | 0.76558 | 0.263 | 3.2058 | 9.062% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2011-01-09 | 37 | 24.8318 | 11.812 | 36.6438 | 2.3358 | 0.76558 | 0.27241 | 3.3738 | 9.207% | 9.796% | 6.62% | 1.1014 | 1.1086 | 1.0709
2011-01-09 | 38 | 26.916 | 11.7952 | 38.7112 | 2.6068 | 0.76558 | 0.28778 | 3.6602 | 9.455% | 10.06% | 6.798% | 1.1044 | 1.1119 | 1.0729
2011-01-09 | 39 | 27.7603 | 11.7311 | 39.4915 | 2.7129 | 0.76558 | 0.29358 | 3.7721 | 9.552% | 10.16% | 6.868% | 1.1056 | 1.1131 | 1.0737
2011-01-09 | 40 | 27.6326 | 11.7149 | 39.3475 | 2.6932 | 0.76558 | 0.29251 | 3.7513 | 9.534% | 10.14% | 6.855% | 1.1054 | 1.1129 | 1.0736
2011-01-09 | 41 | 27.5569 | 11.3148 | 38.8717 | 2.6285 | 0.76558 | 0.28898 | 3.683 | 9.475% | 10.08% | 6.812% | 1.1047 | 1.1121 | 1.0731
2011-01-09 | 42 | 27.329 | 11.0614 | 38.3903 | 2.5638 | 0.76558 | 0.2854 | 3.6147 | 9.416% | 10.02% | 6.77% | 1.1039 | 1.1113 | 1.0726
2011-01-09 | 43 | 26.8809 | 10.7819 | 37.6628 | 2.4675 | 0.76558 | 0.27999 | 3.5131 | 9.328% | 9.925% | 6.707% | 1.1029 | 1.1102 | 1.0719
2011-01-09 | 44 | 26.2613 | 10.6805 | 36.9418 | 2.3739 | 0.76558 | 0.27463 | 3.4142 | 9.242% | 9.833% | 6.645% | 1.1018 | 1.1091 | 1.0712
2011-01-09 | 45 | 24.9995 | 10.5829 | 35.5824 | 2.2025 | 0.76558 | 0.26452 | 3.2326 | 9.085% | 9.666% | 6.532% | 1.0999 | 1.107 | 1.0699
2011-01-09 | 46 | 23.354 | 9.9043 | 33.2584 | 1.9241 | 0.76558 | 0.24725 | 2.937 | 8.831% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-01-09 | 47 | 21.7436 | 9.3722 | 31.1158 | 1.6842 | 0.76558 | 0.23132 | 2.6811 | 8.617% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-01-09 | 48 | 20.3358 | 9.1727 | 29.5085 | 1.5147 | 0.76558 | 0.21937 | 2.4997 | 8.471% | 9.013% | 6.091% | 1.0925 | 1.0991 | 1.0649
2011-01-10 | 1 | 18.5214 | 8.3255 | 26.8469 | 1.2538 | 0.76558 | 0.19958 | 2.2189 | 8.265% | 8.794% | 5.943% | 1.0901 | 1.0964 | 1.0632
2011-01-10 | 2 | 17.0094 | 7.7212 | 24.7307 | 1.0639 | 0.76558 | 0.18385 | 2.0133 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2011-01-10 | 3 | 16.0577 | 7.4917 | 23.5493 | 0.9647 | 0.76558 | 0.17507 | 1.9053 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-01-10 | 4 | 15.3758 | 7.2927 | 22.6685 | 0.89388 | 0.76558 | 0.16852 | 1.828 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-01-10 | 5 | 14.7057 | 7.0482 | 21.7538 | 0.8232 | 0.76558 | 0.16172 | 1.7505 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 6 | 14.3315 | 6.8112 | 21.1427 | 0.7776 | 0.76558 | 0.15718 | 1.7004 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 7 | 13.9296 | 6.6682 | 20.5978 | 0.73803 | 0.76558 | 0.15313 | 1.6567 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 8 | 13.7255 | 6.5908 | 20.3162 | 0.71799 | 0.76558 | 0.15103 | 1.6346 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 9 | 13.7394 | 6.6553 | 20.3947 | 0.72355 | 0.76558 | 0.15162 | 1.6407 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 10 | 13.8222 | 6.5501 | 20.3723 | 0.72196 | 0.76558 | 0.15145 | 1.639 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 11 | 14.0309 | 6.6025 | 20.6335 | 0.74059 | 0.76558 | 0.15339 | 1.6596 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 12 | 14.2791 | 6.5932 | 20.8723 | 0.75783 | 0.76558 | 0.15517 | 1.6786 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 13 | 14.7148 | 6.6854 | 21.4003 | 0.79666 | 0.76558 | 0.15909 | 1.7213 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-10 | 14 | 15.5867 | 7.0642 | 22.6509 | 0.89249 | 0.76558 | 0.16839 | 1.8265 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2011-01-10 | 15 | 16.7561 | 7.3038 | 24.0599 | 1.007 | 0.76558 | 0.17886 | 1.9514 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0944 | 1.0619
2011-01-10 | 16 | 18.3116 | 7.8992 | 26.2109 | 1.1951 | 0.76558 | 0.19485 | 2.1555 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2011-01-10 | 17 | 20.2658 | 8.7668 | 29.0326 | 1.4662 | 0.76558 | 0.21583 | 2.4477 | 8.431% | 8.97% | 6.062% | 1.0921 | 1.0985 | 1.0645
2011-01-10 | 18 | 22.3042 | 9.6794 | 31.9837 | 1.7795 | 0.76558 | 0.23777 | 2.7828 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2011-01-10 | 19 | 24.4262 | 10.6842 | 35.1105 | 2.1444 | 0.76558 | 0.26102 | 3.171 | 9.032% | 9.61% | 6.494% | 1.0993 | 1.1063 | 1.0694
2011-01-10 | 20 | 25.5279 | 11.5287 | 37.0566 | 2.3887 | 0.76558 | 0.27548 | 3.4298 | 9.256% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2011-01-10 | 21 | 26.6242 | 11.6822 | 38.3064 | 2.5526 | 0.76558 | 0.28477 | 3.6029 | 9.406% | 10.01% | 6.763% | 1.1038 | 1.1112 | 1.0725
2011-01-10 | 22 | 27.1544 | 12.0213 | 39.1757 | 2.6697 | 0.76558 | 0.29124 | 3.7266 | 9.512% | 10.12% | 6.839% | 1.1051 | 1.1126 | 1.0734
2011-01-10 | 23 | 27.5844 | 12.0222 | 39.6065 | 2.7288 | 0.76558 | 0.29444 | 3.7888 | 9.566% | 10.18% | 6.878% | 1.1058 | 1.1133 | 1.0739
2011-01-10 | 24 | 28.4525 | 12.1094 | 40.5619 | 2.862 | 0.76558 | 0.30154 | 3.9291 | 9.687% | 10.31% | 6.965% | 1.1073 | 1.1149 | 1.0749
2011-01-10 | 25 | 29.0679 | 12.6177 | 41.6856 | 3.0228 | 0.76558 | 0.3099 | 4.0983 | 9.831% | 10.46% | 7.069% | 1.109 | 1.1168 | 1.0761
2011-01-10 | 26 | 29.198 | 12.4744 | 41.6724 | 3.0209 | 0.76558 | 0.3098 | 4.0962 | 9.83% | 10.46% | 7.068% | 1.109 | 1.1168 | 1.076
2011-01-10 | 27 | 29.1346 | 12.6671 | 41.8018 | 3.0397 | 0.76558 | 0.31076 | 4.116 | 9.846% | 10.48% | 7.08% | 1.1092 | 1.117 | 1.0762
2011-01-10 | 28 | 28.824 | 12.5861 | 41.41 | 2.983 | 0.76558 | 0.30785 | 4.0564 | 9.796% | 10.42% | 7.043% | 1.1086 | 1.1164 | 1.0758
2011-01-10 | 29 | 27.5685 | 11.8642 | 39.4327 | 2.7049 | 0.76558 | 0.29315 | 3.7636 | 9.544% | 10.16% | 6.862% | 1.1055 | 1.113 | 1.0737
2011-01-10 | 30 | 26.3783 | 11.0908 | 37.469 | 2.4422 | 0.76558 | 0.27855 | 3.4863 | 9.305% | 9.9% | 6.69% | 1.1026 | 1.1099 | 1.0717
2011-01-10 | 31 | 25.5119 | 10.4858 | 35.9977 | 2.2542 | 0.76558 | 0.26761 | 3.2873 | 9.132% | 9.717% | 6.566% | 1.1005 | 1.1076 | 1.0703
2011-01-10 | 32 | 24.9284 | 10.2599 | 35.1882 | 2.1539 | 0.76558 | 0.26159 | 3.1811 | 9.04% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2011-01-10 | 33 | 25.075 | 10.3859 | 35.4609 | 2.1874 | 0.76558 | 0.26362 | 3.2166 | 9.071% | 9.651% | 6.522% | 1.0998 | 1.1068 | 1.0698
2011-01-10 | 34 | 25.3127 | 10.2545 | 35.5672 | 2.2006 | 0.76558 | 0.26441 | 3.2306 | 9.083% | 9.664% | 6.531% | 1.0999 | 1.107 | 1.0699
2011-01-10 | 35 | 26.0466 | 10.5278 | 36.5744 | 2.327 | 0.76558 | 0.2719 | 3.3644 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2011-01-10 | 36 | 27.0083 | 11.1963 | 38.2046 | 2.539 | 0.76558 | 0.28402 | 3.5886 | 9.393% | 9.994% | 6.754% | 1.1037 | 1.111 | 1.0724
2011-01-10 | 37 | 27.3842 | 11.2796 | 38.6637 | 2.6004 | 0.76558 | 0.28743 | 3.6534 | 9.449% | 10.05% | 6.794% | 1.1044 | 1.1118 | 1.0729
2011-01-10 | 38 | 27.756 | 11.1053 | 38.8613 | 2.6271 | 0.76558 | 0.2889 | 3.6815 | 9.474% | 10.08% | 6.811% | 1.1046 | 1.1121 | 1.0731
2011-01-10 | 39 | 28.1919 | 11.0271 | 39.219 | 2.6756 | 0.76558 | 0.29156 | 3.7328 | 9.518% | 10.13% | 6.843% | 1.1052 | 1.1127 | 1.0735
2011-01-10 | 40 | 27.9138 | 10.8528 | 38.7666 | 2.6143 | 0.76558 | 0.2882 | 3.668 | 9.462% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2011-01-10 | 41 | 27.6454 | 10.5291 | 38.1745 | 2.535 | 0.76558 | 0.28379 | 3.5844 | 9.389% | 9.99% | 6.751% | 1.1036 | 1.111 | 1.0724
2011-01-10 | 42 | 27.0353 | 10.3672 | 37.4025 | 2.4335 | 0.76558 | 0.27805 | 3.4772 | 9.297% | 9.892% | 6.684% | 1.1025 | 1.1098 | 1.0716
2011-01-10 | 43 | 26.8514 | 10.2337 | 37.0851 | 2.3924 | 0.76558 | 0.2757 | 3.4337 | 9.259% | 9.851% | 6.657% | 1.102 | 1.1093 | 1.0713
2011-01-10 | 44 | 26.9694 | 10.2473 | 37.2167 | 2.4094 | 0.76558 | 0.27667 | 3.4517 | 9.274% | 9.868% | 6.668% | 1.1022 | 1.1095 | 1.0714
2011-01-10 | 45 | 26.0034 | 9.9896 | 35.993 | 2.2536 | 0.76558 | 0.26758 | 3.2867 | 9.132% | 9.716% | 6.566% | 1.1005 | 1.1076 | 1.0703
2011-01-10 | 46 | 24.1294 | 9.1244 | 33.2538 | 1.9236 | 0.76558 | 0.24721 | 2.9364 | 8.83% | 9.395% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-01-10 | 47 | 22.1791 | 8.6869 | 30.866 | 1.6573 | 0.76558 | 0.22946 | 2.6523 | 8.593% | 9.143% | 6.178% | 1.094 | 1.1006 | 1.0659
2011-01-10 | 48 | 20.7131 | 8.6435 | 29.3566 | 1.4992 | 0.76558 | 0.21824 | 2.483 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0648
2011-01-11 | 1 | 18.6771 | 7.4967 | 26.1738 | 1.1917 | 0.76558 | 0.19458 | 2.1519 | 8.221% | 8.748% | 5.911% | 1.0896 | 1.0959 | 1.0628
2011-01-11 | 2 | 17.1893 | 6.9657 | 24.155 | 1.015 | 0.76558 | 0.17957 | 1.9601 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-01-11 | 3 | 16.2589 | 6.4799 | 22.7388 | 0.89944 | 0.76558 | 0.16904 | 1.8341 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-01-11 | 4 | 15.4666 | 6.2265 | 21.693 | 0.81861 | 0.76558 | 0.16127 | 1.7455 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 5 | 15.1024 | 6.1762 | 21.2786 | 0.78763 | 0.76558 | 0.15819 | 1.7114 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 6 | 14.7025 | 6.0641 | 20.7666 | 0.75018 | 0.76558 | 0.15438 | 1.6701 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 7 | 14.3947 | 6.0149 | 20.4096 | 0.72461 | 0.76558 | 0.15173 | 1.6419 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 8 | 14.3785 | 5.9176 | 20.2961 | 0.71657 | 0.76558 | 0.15088 | 1.633 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 9 | 14.5785 | 6.0574 | 20.636 | 0.74077 | 0.76558 | 0.15341 | 1.6598 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 10 | 14.6764 | 6.1936 | 20.8699 | 0.75766 | 0.76558 | 0.15515 | 1.6784 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 11 | 14.6525 | 6.2567 | 20.9092 | 0.76052 | 0.76558 | 0.15544 | 1.6815 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-11 | 12 | 15.3123 | 6.6804 | 21.9926 | 0.84137 | 0.76558 | 0.1635 | 1.7704 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-11 | 13 | 16.3798 | 7.2179 | 23.5977 | 0.96866 | 0.76558 | 0.17543 | 1.9097 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-11 | 14 | 18.3077 | 8.2192 | 26.5269 | 1.2241 | 0.76558 | 0.1972 | 2.1869 | 8.244% | 8.772% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-01-11 | 15 | 21.3819 | 9.3717 | 30.7536 | 1.6452 | 0.76558 | 0.22863 | 2.6394 | 8.583% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-01-11 | 16 | 24.1842 | 10.4557 | 34.6399 | 2.0873 | 0.76558 | 0.25752 | 3.1104 | 8.979% | 9.554% | 6.456% | 1.0987 | 1.1056 | 1.069
2011-01-11 | 17 | 26.9179 | 11.5542 | 38.4721 | 2.5747 | 0.76558 | 0.28601 | 3.6263 | 9.426% | 10.03% | 6.777% | 1.1041 | 1.1115 | 1.0727
2011-01-11 | 18 | 28.6105 | 12.3282 | 40.9386 | 2.9154 | 0.76558 | 0.30434 | 3.9853 | 9.735% | 10.36% | 6.999% | 1.1078 | 1.1155 | 1.0753
2011-01-11 | 19 | 29.8106 | 12.7489 | 42.5595 | 3.1509 | 0.76558 | 0.31639 | 4.2328 | 9.946% | 10.58% | 7.151% | 1.1104 | 1.1183 | 1.077
2011-01-11 | 20 | 30.1185 | 13.0737 | 43.1922 | 3.2452 | 0.76558 | 0.3211 | 4.3319 | 10.03% | 10.67% | 7.211% | 1.1115 | 1.1195 | 1.0777
2011-01-11 | 21 | 30.4904 | 13.1424 | 43.6328 | 3.3118 | 0.76558 | 0.32437 | 4.4017 | 10.09% | 10.73% | 7.253% | 1.1122 | 1.1202 | 1.0782
2011-01-11 | 22 | 30.1621 | 13.1397 | 43.3019 | 3.2617 | 0.76558 | 0.32191 | 4.3492 | 10.04% | 10.69% | 7.222% | 1.1117 | 1.1197 | 1.0778
2011-01-11 | 23 | 29.3896 | 12.5839 | 41.9735 | 3.0647 | 0.76558 | 0.31204 | 4.1423 | 9.869% | 10.5% | 7.096% | 1.1095 | 1.1173 | 1.0764
2011-01-11 | 24 | 28.7538 | 12.4481 | 41.2019 | 2.953 | 0.76558 | 0.3063 | 4.0249 | 9.769% | 10.39% | 7.024% | 1.1083 | 1.116 | 1.0755
2011-01-11 | 25 | 28.0716 | 12.3509 | 40.4225 | 2.8424 | 0.76558 | 0.30051 | 3.9085 | 9.669% | 10.29% | 6.952% | 1.107 | 1.1147 | 1.0747
2011-01-11 | 26 | 27.2137 | 12.0298 | 39.2435 | 2.679 | 0.76558 | 0.29174 | 3.7363 | 9.521% | 10.13% | 6.845% | 1.1052 | 1.1127 | 1.0735
2011-01-11 | 27 | 26.7377 | 12.1462 | 38.8839 | 2.6301 | 0.76558 | 0.28907 | 3.6848 | 9.476% | 10.08% | 6.813% | 1.1047 | 1.1121 | 1.0731
2011-01-11 | 28 | 26.2017 | 12.0791 | 38.2808 | 2.5492 | 0.76558 | 0.28458 | 3.5993 | 9.402% | 10% | 6.76% | 1.1038 | 1.1112 | 1.0725
2011-01-11 | 29 | 25.8361 | 11.8076 | 37.6437 | 2.465 | 0.76558 | 0.27985 | 3.5104 | 9.325% | 9.922% | 6.705% | 1.1028 | 1.1102 | 1.0719
2011-01-11 | 30 | 25.346 | 11.5334 | 36.8794 | 2.3659 | 0.76558 | 0.27417 | 3.4057 | 9.235% | 9.826% | 6.64% | 1.1017 | 1.109 | 1.0711
2011-01-11 | 31 | 26.0742 | 11.4138 | 37.488 | 2.4447 | 0.76558 | 0.27869 | 3.4889 | 9.307% | 9.902% | 6.692% | 1.1026 | 1.1099 | 1.0717
2011-01-11 | 32 | 25.956 | 11.5567 | 37.5127 | 2.4479 | 0.76558 | 0.27887 | 3.4923 | 9.31% | 9.906% | 6.694% | 1.1027 | 1.1099 | 1.0717
2011-01-11 | 33 | 26.2929 | 12.0048 | 38.2977 | 2.5514 | 0.76558 | 0.28471 | 3.6017 | 9.404% | 10.01% | 6.762% | 1.1038 | 1.1112 | 1.0725
2011-01-11 | 34 | 26.5315 | 12.0532 | 38.5846 | 2.5898 | 0.76558 | 0.28684 | 3.6422 | 9.44% | 10.04% | 6.787% | 1.1042 | 1.1117 | 1.0728
2011-01-11 | 35 | 27.5831 | 12.6089 | 40.192 | 2.81 | 0.76558 | 0.29879 | 3.8744 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2011-01-11 | 36 | 28.3122 | 12.4403 | 40.7525 | 2.889 | 0.76558 | 0.30296 | 3.9575 | 9.711% | 10.33% | 6.982% | 1.1076 | 1.1152 | 1.0751
2011-01-11 | 37 | 28.4773 | 12.0743 | 40.5516 | 2.8606 | 0.76558 | 0.30147 | 3.9276 | 9.685% | 10.31% | 6.964% | 1.1072 | 1.1149 | 1.0749
2011-01-11 | 38 | 31.8364 | 13.39 | 45.2264 | 3.5581 | 0.76558 | 0.33622 | 4.6599 | 10.3% | 10.96% | 7.408% | 1.1149 | 1.1231 | 1.08
2011-01-11 | 39 | 31.5066 | 12.6741 | 44.1807 | 3.3955 | 0.76558 | 0.32844 | 4.4895 | 10.16% | 10.81% | 7.306% | 1.1131 | 1.1212 | 1.0788
2011-01-11 | 40 | 30.9047 | 11.9962 | 42.9009 | 3.2016 | 0.76558 | 0.31893 | 4.2861 | 9.991% | 10.63% | 7.183% | 1.111 | 1.1189 | 1.0774
2011-01-11 | 41 | 30.4885 | 11.6081 | 42.0965 | 3.0827 | 0.76558 | 0.31295 | 4.1612 | 9.885% | 10.52% | 7.107% | 1.1097 | 1.1175 | 1.0765
2011-01-11 | 42 | 29.9884 | 11.2061 | 41.1944 | 2.952 | 0.76558 | 0.30624 | 4.0238 | 9.768% | 10.39% | 7.023% | 1.1083 | 1.116 | 1.0755
2011-01-11 | 43 | 29.2519 | 10.9163 | 40.1682 | 2.8067 | 0.76558 | 0.29862 | 3.8709 | 9.637% | 10.25% | 6.929% | 1.1066 | 1.1142 | 1.0744
2011-01-11 | 44 | 28.5119 | 10.6161 | 39.128 | 2.6632 | 0.76558 | 0.29088 | 3.7197 | 9.506% | 10.11% | 6.835% | 1.1051 | 1.1125 | 1.0734
2011-01-11 | 45 | 26.8969 | 10.1111 | 37.008 | 2.3825 | 0.76558 | 0.27512 | 3.4232 | 9.25% | 9.842% | 6.651% | 1.1019 | 1.1092 | 1.0712
2011-01-11 | 46 | 24.2382 | 9.0357 | 33.274 | 1.9259 | 0.76558 | 0.24736 | 2.9389 | 8.832% | 9.398% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-01-11 | 47 | 21.9476 | 8.372 | 30.3197 | 1.5991 | 0.76558 | 0.2254 | 2.5901 | 8.543% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2011-01-11 | 48 | 21.0297 | 8.3477 | 29.3774 | 1.5013 | 0.76558 | 0.21839 | 2.4852 | 8.46% | 9.001% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-01-12 | 1 | 18.8308 | 7.533 | 26.3638 | 1.2091 | 0.76558 | 0.19599 | 2.1706 | 8.233% | 8.76% | 5.92% | 1.0897 | 1.096 | 1.0629
2011-01-12 | 2 | 17.4446 | 6.9384 | 24.383 | 1.0342 | 0.76558 | 0.18127 | 1.9811 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-01-12 | 3 | 16.4564 | 6.5353 | 22.9917 | 0.91956 | 0.76558 | 0.17092 | 1.8561 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-01-12 | 4 | 15.9101 | 6.2822 | 22.1922 | 0.85672 | 0.76558 | 0.16498 | 1.7873 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-01-12 | 5 | 15.3081 | 6.1069 | 21.415 | 0.79776 | 0.76558 | 0.1592 | 1.7225 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 6 | 14.9722 | 5.968 | 20.9402 | 0.76277 | 0.76558 | 0.15567 | 1.684 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 7 | 14.6839 | 5.9599 | 20.6438 | 0.74133 | 0.76558 | 0.15347 | 1.6604 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 8 | 14.3767 | 5.9052 | 20.2819 | 0.71557 | 0.76558 | 0.15078 | 1.6319 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 9 | 14.5208 | 5.8952 | 20.4159 | 0.72506 | 0.76558 | 0.15177 | 1.6424 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 10 | 14.6297 | 6.0114 | 20.6411 | 0.74114 | 0.76558 | 0.15345 | 1.6602 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 11 | 15.1233 | 6.257 | 21.3804 | 0.79518 | 0.76558 | 0.15894 | 1.7197 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-12 | 12 | 15.4491 | 6.5248 | 21.9739 | 0.83994 | 0.76558 | 0.16336 | 1.7689 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-12 | 13 | 16.9531 | 7.0329 | 23.986 | 1.0008 | 0.76558 | 0.17832 | 1.9447 | 8.108% | 8.627% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-01-12 | 14 | 18.7711 | 7.8728 | 26.6439 | 1.2349 | 0.76558 | 0.19807 | 2.1985 | 8.252% | 8.78% | 5.933% | 1.0899 | 1.0962 | 1.0631
2011-01-12 | 15 | 21.4934 | 9.0465 | 30.54 | 1.6225 | 0.76558 | 0.22704 | 2.6151 | 8.563% | 9.111% | 6.157% | 1.0936 | 1.1002 | 1.0656
2011-01-12 | 16 | 23.6135 | 10.0959 | 33.7095 | 1.9767 | 0.76558 | 0.2506 | 2.9929 | 8.878% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-01-12 | 17 | 25.5052 | 10.942 | 36.4473 | 2.3108 | 0.76558 | 0.27095 | 3.3473 | 9.184% | 9.772% | 6.603% | 1.1011 | 1.1083 | 1.0707
2011-01-12 | 18 | 26.1963 | 11.1276 | 37.3239 | 2.4233 | 0.76558 | 0.27747 | 3.4664 | 9.287% | 9.882% | 6.678% | 1.1024 | 1.1097 | 1.0716
2011-01-12 | 19 | 26.7326 | 11.2755 | 38.0081 | 2.513 | 0.76558 | 0.28256 | 3.5611 | 9.369% | 9.969% | 6.737% | 1.1034 | 1.1107 | 1.0722
2011-01-12 | 20 | 26.1368 | 11.1698 | 37.3066 | 2.4211 | 0.76558 | 0.27734 | 3.464 | 9.285% | 9.879% | 6.676% | 1.1024 | 1.1096 | 1.0715
2011-01-12 | 21 | 25.7888 | 10.9575 | 36.7463 | 2.3489 | 0.76558 | 0.27318 | 3.3876 | 9.219% | 9.809% | 6.628% | 1.1016 | 1.1088 | 1.071
2011-01-12 | 22 | 25.0886 | 10.9363 | 36.0249 | 2.2576 | 0.76558 | 0.26781 | 3.291 | 9.135% | 9.72% | 6.568% | 1.1005 | 1.1077 | 1.0703
2011-01-12 | 23 | 24.3544 | 10.8303 | 35.1847 | 2.1535 | 0.76558 | 0.26157 | 3.1806 | 9.04% | 9.618% | 6.5% | 1.0994 | 1.1064 | 1.0695
2011-01-12 | 24 | 23.668 | 10.6551 | 34.3231 | 2.0493 | 0.76558 | 0.25516 | 3.0701 | 8.945% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2011-01-12 | 25 | 23.1306 | 10.624 | 33.7546 | 1.982 | 0.76558 | 0.25094 | 2.9985 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-01-12 | 26 | 22.4466 | 10.2813 | 32.7279 | 1.8633 | 0.76558 | 0.2433 | 2.8721 | 8.776% | 9.337% | 6.31% | 1.0962 | 1.103 | 1.0673
2011-01-12 | 27 | 21.9383 | 10.4336 | 32.3719 | 1.8229 | 0.76558 | 0.24066 | 2.8292 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-01-12 | 28 | 21.6002 | 10.4114 | 32.0116 | 1.7826 | 0.76558 | 0.23798 | 2.7861 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-01-12 | 29 | 21.3408 | 9.9495 | 31.2904 | 1.7032 | 0.76558 | 0.23262 | 2.7014 | 8.633% | 9.186% | 6.207% | 1.0945 | 1.1011 | 1.0662
2011-01-12 | 30 | 20.7611 | 9.949 | 30.7101 | 1.6406 | 0.76558 | 0.2283 | 2.6345 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-01-12 | 31 | 21.1152 | 9.7103 | 30.8256 | 1.6529 | 0.76558 | 0.22916 | 2.6477 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-01-12 | 32 | 20.5933 | 9.5114 | 30.1047 | 1.5765 | 0.76558 | 0.2238 | 2.5659 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-01-12 | 33 | 20.5414 | 9.7423 | 30.2837 | 1.5953 | 0.76558 | 0.22513 | 2.586 | 8.539% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-01-12 | 34 | 20.6075 | 9.7743 | 30.3818 | 1.6057 | 0.76558 | 0.22586 | 2.5971 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1001 | 1.0655
2011-01-12 | 35 | 20.8737 | 10.0335 | 30.9072 | 1.6617 | 0.76558 | 0.22977 | 2.6571 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2011-01-12 | 36 | 22.0599 | 10.6521 | 32.712 | 1.8614 | 0.76558 | 0.24319 | 2.8702 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-01-12 | 37 | 23.0817 | 11.0062 | 34.0879 | 2.0213 | 0.76558 | 0.25341 | 3.0403 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1048 | 1.0685
2011-01-12 | 38 | 23.326 | 11.0634 | 34.3894 | 2.0572 | 0.76558 | 0.25565 | 3.0785 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-01-12 | 39 | 23.4957 | 11.1253 | 34.621 | 2.085 | 0.76558 | 0.25738 | 3.108 | 8.977% | 9.552% | 6.455% | 1.0986 | 1.1056 | 1.069
2011-01-12 | 40 | 22.8637 | 10.8134 | 33.677 | 1.9729 | 0.76558 | 0.25036 | 2.9888 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-01-12 | 41 | 22.9837 | 10.2653 | 33.249 | 1.9231 | 0.76558 | 0.24718 | 2.9358 | 8.83% | 9.395% | 6.349% | 1.0968 | 1.1037 | 1.0678
2011-01-12 | 42 | 23.1818 | 9.985 | 33.1668 | 1.9136 | 0.76558 | 0.24657 | 2.9257 | 8.821% | 9.386% | 6.342% | 1.0967 | 1.1036 | 1.0677
2011-01-12 | 43 | 22.9222 | 9.9007 | 32.8228 | 1.8741 | 0.76558 | 0.24401 | 2.8837 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-01-12 | 44 | 23.5979 | 10.117 | 33.715 | 1.9773 | 0.76558 | 0.25064 | 2.9936 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-01-12 | 45 | 22.8433 | 9.6093 | 32.4526 | 1.832 | 0.76558 | 0.24126 | 2.8389 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-01-12 | 46 | 21.309 | 8.8767 | 30.1856 | 1.585 | 0.76558 | 0.2244 | 2.575 | 8.531% | 9.077% | 6.133% | 1.0933 | 1.0998 | 1.0653
2011-01-12 | 47 | 19.4868 | 8.355 | 27.8418 | 1.3484 | 0.76558 | 0.20698 | 2.321 | 8.336% | 8.87% | 5.994% | 1.0909 | 1.0973 | 1.0638
2011-01-12 | 48 | 17.8473 | 8.3564 | 26.2037 | 1.1944 | 0.76558 | 0.1948 | 2.1548 | 8.223% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2011-01-13 | 1 | 16.2056 | 7.4105 | 23.6161 | 0.97017 | 0.76558 | 0.17556 | 1.9113 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-13 | 2 | 14.6294 | 6.8298 | 21.4593 | 0.80106 | 0.76558 | 0.15953 | 1.7262 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-13 | 3 | 13.8193 | 6.4493 | 20.2686 | 0.71463 | 0.76558 | 0.15068 | 1.6309 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-13 | 4 | 13.1936 | 6.2547 | 19.4483 | 0.65796 | 0.76558 | 0.14458 | 1.5681 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-13 | 5 | 12.7615 | 6.0918 | 18.8533 | 0.61831 | 0.76558 | 0.14016 | 1.524 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-01-13 | 6 | 12.3555 | 5.9636 | 18.3191 | 0.58377 | 0.76558 | 0.13619 | 1.4855 | 8.109% | 8.628% | 5.831% | 1.0882 | 1.0944 | 1.0619
2011-01-13 | 7 | 12.1173 | 6.0246 | 18.1419 | 0.57253 | 0.76558 | 0.13487 | 1.473 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-01-13 | 8 | 11.9772 | 5.9137 | 17.8909 | 0.5568 | 0.76558 | 0.133 | 1.4554 | 8.135% | 8.655% | 5.849% | 1.0886 | 1.0948 | 1.0621
2011-01-13 | 9 | 12.1492 | 5.8989 | 18.0481 | 0.56663 | 0.76558 | 0.13417 | 1.4664 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-01-13 | 10 | 12.1338 | 6.0068 | 18.1406 | 0.57245 | 0.76558 | 0.13486 | 1.4729 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-01-13 | 11 | 12.6225 | 6.2329 | 18.8554 | 0.61845 | 0.76558 | 0.14017 | 1.5242 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-01-13 | 12 | 13.1061 | 6.5571 | 19.6631 | 0.67257 | 0.76558 | 0.14618 | 1.5843 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-13 | 13 | 14.3393 | 7.1253 | 21.4647 | 0.80146 | 0.76558 | 0.15957 | 1.7266 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-13 | 14 | 15.9222 | 8.0935 | 24.0157 | 1.0033 | 0.76558 | 0.17854 | 1.9474 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-01-13 | 15 | 18.6385 | 9.386 | 28.0245 | 1.3662 | 0.76558 | 0.20834 | 2.3401 | 8.35% | 8.885% | 6.004% | 1.0911 | 1.0975 | 1.0639
2011-01-13 | 16 | 20.7467 | 10.2495 | 30.9962 | 1.6713 | 0.76558 | 0.23043 | 2.6673 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2011-01-13 | 17 | 23.1087 | 11.0734 | 34.182 | 2.0325 | 0.76558 | 0.25411 | 3.0522 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2011-01-13 | 18 | 24.2068 | 11.349 | 35.5558 | 2.1992 | 0.76558 | 0.26433 | 3.2291 | 9.082% | 9.663% | 6.53% | 1.0999 | 1.107 | 1.0699
2011-01-13 | 19 | 24.6368 | 11.6189 | 36.2558 | 2.2866 | 0.76558 | 0.26953 | 3.3217 | 9.162% | 9.748% | 6.587% | 1.1009 | 1.108 | 1.0705
2011-01-13 | 20 | 24.1108 | 11.4268 | 35.5377 | 2.1969 | 0.76558 | 0.26419 | 3.2267 | 9.08% | 9.661% | 6.528% | 1.0999 | 1.1069 | 1.0698
2011-01-13 | 21 | 24.0789 | 11.2324 | 35.3114 | 2.169 | 0.76558 | 0.26251 | 3.1971 | 9.054% | 9.634% | 6.51% | 1.0996 | 1.1066 | 1.0696
2011-01-13 | 22 | 23.9471 | 11.2564 | 35.2034 | 2.1558 | 0.76558 | 0.26171 | 3.1831 | 9.042% | 9.621% | 6.501% | 1.0994 | 1.1064 | 1.0695
2011-01-13 | 23 | 23.6745 | 10.9907 | 34.6652 | 2.0904 | 0.76558 | 0.25771 | 3.1137 | 8.982% | 9.557% | 6.458% | 1.0987 | 1.1057 | 1.069
2011-01-13 | 24 | 23.1658 | 10.9059 | 34.0717 | 2.0194 | 0.76558 | 0.25329 | 3.0383 | 8.917% | 9.488% | 6.412% | 1.0979 | 1.1048 | 1.0685
2011-01-13 | 25 | 22.549 | 10.955 | 33.5039 | 1.9527 | 0.76558 | 0.24907 | 2.9673 | 8.857% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2011-01-13 | 26 | 22.2251 | 10.7442 | 32.9693 | 1.8908 | 0.76558 | 0.2451 | 2.9015 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-01-13 | 27 | 21.9672 | 10.9733 | 32.9405 | 1.8875 | 0.76558 | 0.24488 | 2.898 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-01-13 | 28 | 21.7594 | 10.7573 | 32.5167 | 1.8393 | 0.76558 | 0.24173 | 2.8466 | 8.754% | 9.315% | 6.294% | 1.0959 | 1.1027 | 1.0672
2011-01-13 | 29 | 21.3181 | 10.4924 | 31.8104 | 1.7602 | 0.76558 | 0.23648 | 2.7623 | 8.684% | 9.239% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-01-13 | 30 | 20.8544 | 10.1953 | 31.0497 | 1.6771 | 0.76558 | 0.23083 | 2.6735 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-01-13 | 31 | 20.8698 | 10.2152 | 31.085 | 1.6809 | 0.76558 | 0.23109 | 2.6775 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2011-01-13 | 32 | 20.6247 | 10.1393 | 30.7641 | 1.6463 | 0.76558 | 0.2287 | 2.6406 | 8.583% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-01-13 | 33 | 20.7429 | 10.3838 | 31.1267 | 1.6854 | 0.76558 | 0.2314 | 2.6824 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.1009 | 1.0661
2011-01-13 | 34 | 20.9778 | 10.3268 | 31.3045 | 1.7047 | 0.76558 | 0.23272 | 2.703 | 8.635% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-01-13 | 35 | 21.2841 | 10.6027 | 31.8868 | 1.7687 | 0.76558 | 0.23705 | 2.7713 | 8.691% | 9.247% | 6.249% | 1.0952 | 1.1019 | 1.0667
2011-01-13 | 36 | 21.8347 | 11.0574 | 32.8922 | 1.882 | 0.76558 | 0.24452 | 2.8921 | 8.793% | 9.355% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-01-13 | 37 | 22.6695 | 11.5032 | 34.1726 | 2.0314 | 0.76558 | 0.25404 | 3.051 | 8.928% | 9.5% | 6.419% | 1.098 | 1.105 | 1.0686
2011-01-13 | 38 | 23.0906 | 11.7049 | 34.7955 | 2.1061 | 0.76558 | 0.25867 | 3.1304 | 8.996% | 9.572% | 6.468% | 1.0989 | 1.1059 | 1.0692
2011-01-13 | 39 | 22.855 | 11.493 | 34.348 | 2.0523 | 0.76558 | 0.25535 | 3.0732 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2011-01-13 | 40 | 22.1889 | 10.8202 | 33.0091 | 1.8954 | 0.76558 | 0.24539 | 2.9064 | 8.805% | 9.368% | 6.331% | 1.0965 | 1.1034 | 1.0676
2011-01-13 | 41 | 21.7431 | 10.3892 | 32.1323 | 1.796 | 0.76558 | 0.23888 | 2.8005 | 8.716% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2011-01-13 | 42 | 21.5812 | 10.2292 | 31.8104 | 1.7602 | 0.76558 | 0.23648 | 2.7623 | 8.684% | 9.239% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-01-13 | 43 | 21.6853 | 10.1336 | 31.8189 | 1.7612 | 0.76558 | 0.23655 | 2.7633 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-01-13 | 44 | 22.3294 | 10.2621 | 32.5915 | 1.8477 | 0.76558 | 0.24229 | 2.8556 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-01-13 | 45 | 21.7954 | 9.9636 | 31.7589 | 1.7546 | 0.76558 | 0.2361 | 2.7562 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-01-13 | 46 | 20.3355 | 9.3221 | 29.6577 | 1.5301 | 0.76558 | 0.22048 | 2.5161 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-01-13 | 47 | 18.7334 | 8.7719 | 27.5054 | 1.316 | 0.76558 | 0.20448 | 2.2861 | 8.311% | 8.843% | 5.976% | 1.0906 | 1.097 | 1.0636
2011-01-13 | 48 | 16.9814 | 8.5965 | 25.5779 | 1.1381 | 0.76558 | 0.19015 | 2.0938 | 8.186% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2011-01-14 | 1 | 15.1916 | 7.5151 | 22.7066 | 0.89689 | 0.76558 | 0.1688 | 1.8313 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-01-14 | 2 | 13.7928 | 6.9222 | 20.715 | 0.74646 | 0.76558 | 0.154 | 1.666 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-14 | 3 | 12.9706 | 6.5299 | 19.5004 | 0.66149 | 0.76558 | 0.14497 | 1.572 | 8.062% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-01-14 | 4 | 12.4546 | 6.3598 | 18.8144 | 0.61576 | 0.76558 | 0.13987 | 1.5212 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-01-14 | 5 | 11.9568 | 6.2502 | 18.207 | 0.57665 | 0.76558 | 0.13535 | 1.4776 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-01-14 | 6 | 11.7592 | 6.089 | 17.8482 | 0.55415 | 0.76558 | 0.13269 | 1.4524 | 8.138% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-01-14 | 7 | 11.4794 | 6.0646 | 17.544 | 0.53542 | 0.76558 | 0.13042 | 1.4314 | 8.159% | 8.681% | 5.866% | 1.0888 | 1.0951 | 1.0623
2011-01-14 | 8 | 11.2713 | 6.0639 | 17.3352 | 0.52275 | 0.76558 | 0.12887 | 1.4172 | 8.175% | 8.698% | 5.878% | 1.089 | 1.0953 | 1.0625
2011-01-14 | 9 | 11.3753 | 6.1213 | 17.4965 | 0.53252 | 0.76558 | 0.13007 | 1.4282 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2011-01-14 | 10 | 11.4254 | 6.2173 | 17.6427 | 0.54146 | 0.76558 | 0.13116 | 1.4382 | 8.152% | 8.673% | 5.861% | 1.0888 | 1.095 | 1.0623
2011-01-14 | 11 | 11.8918 | 6.2364 | 18.1282 | 0.57167 | 0.76558 | 0.13477 | 1.472 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-01-14 | 12 | 12.2778 | 6.557 | 18.8348 | 0.6171 | 0.76558 | 0.14002 | 1.5227 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-01-14 | 13 | 13.3697 | 6.9494 | 20.3191 | 0.7182 | 0.76558 | 0.15105 | 1.6348 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-14 | 14 | 14.8537 | 7.8134 | 22.6671 | 0.89377 | 0.76558 | 0.16851 | 1.8279 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-01-14 | 15 | 17.4028 | 8.958 | 26.3608 | 1.2088 | 0.76558 | 0.19597 | 2.1703 | 8.233% | 8.76% | 5.92% | 1.0897 | 1.096 | 1.0629
2011-01-14 | 16 | 19.669 | 9.8966 | 29.5657 | 1.5206 | 0.76558 | 0.21979 | 2.506 | 8.476% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2011-01-14 | 17 | 21.6005 | 10.7006 | 32.3012 | 1.815 | 0.76558 | 0.24013 | 2.8207 | 8.732% | 9.291% | 6.279% | 1.0957 | 1.1024 | 1.067
2011-01-14 | 18 | 23.2246 | 11.2002 | 34.4248 | 2.0615 | 0.76558 | 0.25592 | 3.083 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2011-01-14 | 19 | 24.3005 | 11.7341 | 36.0346 | 2.2588 | 0.76558 | 0.26789 | 3.2922 | 9.136% | 9.721% | 6.569% | 1.1006 | 1.1077 | 1.0703
2011-01-14 | 20 | 24.1871 | 11.5947 | 35.7818 | 2.2272 | 0.76558 | 0.26601 | 3.2588 | 9.107% | 9.69% | 6.548% | 1.1002 | 1.1073 | 1.0701
2011-01-14 | 21 | 24.1296 | 11.3929 | 35.5225 | 2.195 | 0.76558 | 0.26408 | 3.2247 | 9.078% | 9.659% | 6.527% | 1.0998 | 1.1069 | 1.0698
2011-01-14 | 22 | 23.6116 | 11.4654 | 35.077 | 2.1403 | 0.76558 | 0.26077 | 3.1667 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2011-01-14 | 23 | 23.3474 | 11.3085 | 34.656 | 2.0893 | 0.76558 | 0.25764 | 3.1125 | 8.981% | 9.556% | 6.457% | 1.0987 | 1.1057 | 1.069
2011-01-14 | 24 | 22.9458 | 11.1601 | 34.1059 | 2.0235 | 0.76558 | 0.25355 | 3.0426 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2011-01-14 | 25 | 22.4553 | 11.104 | 33.5593 | 1.9591 | 0.76558 | 0.24948 | 2.9742 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2011-01-14 | 26 | 21.9839 | 10.6548 | 32.6387 | 1.8531 | 0.76558 | 0.24264 | 2.8613 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-01-14 | 27 | 21.5199 | 10.6578 | 32.1777 | 1.8011 | 0.76558 | 0.23921 | 2.8059 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-01-14 | 28 | 20.9978 | 10.4016 | 31.3994 | 1.7151 | 0.76558 | 0.23343 | 2.7141 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-01-14 | 29 | 20.7892 | 9.8905 | 30.6796 | 1.6373 | 0.76558 | 0.22808 | 2.631 | 8.576% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-01-14 | 30 | 20.409 | 9.7596 | 30.1686 | 1.5832 | 0.76558 | 0.22428 | 2.5731 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-01-14 | 31 | 20.4392 | 9.6349 | 30.0741 | 1.5733 | 0.76558 | 0.22357 | 2.5625 | 8.521% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2011-01-14 | 32 | 20.2296 | 9.5202 | 29.7498 | 1.5396 | 0.76558 | 0.22116 | 2.5263 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-01-14 | 33 | 20.2407 | 10.0072 | 30.248 | 1.5916 | 0.76558 | 0.22487 | 2.582 | 8.536% | 9.082% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-01-14 | 34 | 20.4782 | 10.1532 | 30.6315 | 1.6322 | 0.76558 | 0.22772 | 2.6255 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2011-01-14 | 35 | 20.852 | 10.3391 | 31.1911 | 1.6924 | 0.76558 | 0.23188 | 2.6898 | 8.624% | 9.176% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-01-14 | 36 | 21.4976 | 10.8707 | 32.3683 | 1.8225 | 0.76558 | 0.24063 | 2.8287 | 8.739% | 9.299% | 6.283% | 1.0958 | 1.1025 | 1.067
2011-01-14 | 37 | 22.2995 | 11.1207 | 33.4202 | 1.9429 | 0.76558 | 0.24845 | 2.9569 | 8.848% | 9.414% | 6.362% | 1.0971 | 1.1039 | 1.0679
2011-01-14 | 38 | 22.8698 | 11.0117 | 33.8816 | 1.9969 | 0.76558 | 0.25188 | 3.0144 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2011-01-14 | 39 | 22.8259 | 10.709 | 33.5349 | 1.9563 | 0.76558 | 0.2493 | 2.9711 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-01-14 | 40 | 22.4362 | 10.2693 | 32.7055 | 1.8607 | 0.76558 | 0.24314 | 2.8694 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-14 | 41 | 22.098 | 9.8771 | 31.9751 | 1.7785 | 0.76558 | 0.23771 | 2.7818 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-01-14 | 42 | 21.9414 | 9.7611 | 31.7025 | 1.7483 | 0.76558 | 0.23568 | 2.7496 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-01-14 | 43 | 21.6359 | 9.6618 | 31.2977 | 1.704 | 0.76558 | 0.23267 | 2.7022 | 8.634% | 9.186% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-01-14 | 44 | 21.7817 | 9.6114 | 31.3931 | 1.7144 | 0.76558 | 0.23338 | 2.7133 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-01-14 | 45 | 20.9179 | 9.2396 | 30.1575 | 1.5821 | 0.76558 | 0.22419 | 2.5718 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-01-14 | 46 | 19.8218 | 8.6165 | 28.4383 | 1.4068 | 0.76558 | 0.21141 | 2.3838 | 8.382% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2011-01-14 | 47 | 18.182 | 8.1397 | 26.3217 | 1.2052 | 0.76558 | 0.19568 | 2.1665 | 8.231% | 8.757% | 5.918% | 1.0897 | 1.096 | 1.0629
2011-01-14 | 48 | 16.8801 | 7.9699 | 24.8501 | 1.0742 | 0.76558 | 0.18474 | 2.0245 | 8.147% | 8.668% | 5.858% | 1.0887 | 1.0949 | 1.0622
2011-01-15 | 1 | 15.1282 | 7.0145 | 22.1427 | 0.8529 | 0.76558 | 0.16461 | 1.7831 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-01-15 | 2 | 13.8677 | 6.479 | 20.3467 | 0.72015 | 0.76558 | 0.15126 | 1.637 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-15 | 3 | 12.9933 | 6.135 | 19.1283 | 0.63648 | 0.76558 | 0.1422 | 1.5443 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-15 | 4 | 12.4071 | 5.8505 | 18.2576 | 0.57986 | 0.76558 | 0.13573 | 1.4812 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-01-15 | 5 | 11.8248 | 5.7007 | 17.5255 | 0.53429 | 0.76558 | 0.13029 | 1.4302 | 8.16% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2011-01-15 | 6 | 11.619 | 5.6176 | 17.2366 | 0.51682 | 0.76558 | 0.12814 | 1.4105 | 8.183% | 8.707% | 5.884% | 1.0891 | 1.0954 | 1.0625
2011-01-15 | 7 | 11.5488 | 5.6627 | 17.2115 | 0.51531 | 0.76558 | 0.12795 | 1.4088 | 8.185% | 8.709% | 5.885% | 1.0892 | 1.0954 | 1.0625
2011-01-15 | 8 | 11.3875 | 5.6578 | 17.0454 | 0.50541 | 0.76558 | 0.12672 | 1.3977 | 8.2% | 8.725% | 5.896% | 1.0893 | 1.0956 | 1.0627
2011-01-15 | 9 | 11.5966 | 5.651 | 17.2475 | 0.51747 | 0.76558 | 0.12822 | 1.4113 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2011-01-15 | 10 | 11.7441 | 5.6706 | 17.4147 | 0.52755 | 0.76558 | 0.12946 | 1.4226 | 8.169% | 8.692% | 5.873% | 1.089 | 1.0952 | 1.0624
2011-01-15 | 11 | 12.0919 | 5.8237 | 17.9156 | 0.55834 | 0.76558 | 0.13319 | 1.4571 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-01-15 | 12 | 12.5277 | 6.1395 | 18.6672 | 0.60617 | 0.76558 | 0.13877 | 1.5105 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-01-15 | 13 | 13.4902 | 6.5546 | 20.0448 | 0.69894 | 0.76558 | 0.14902 | 1.6135 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-01-15 | 14 | 14.9145 | 7.4306 | 22.3451 | 0.86856 | 0.76558 | 0.16612 | 1.8003 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-15 | 15 | 17.7623 | 8.6107 | 26.373 | 1.2099 | 0.76558 | 0.19606 | 2.1715 | 8.234% | 8.761% | 5.92% | 1.0897 | 1.096 | 1.0629
2011-01-15 | 16 | 19.8546 | 9.6403 | 29.4948 | 1.5133 | 0.76558 | 0.21927 | 2.4982 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2011-01-15 | 17 | 22.2465 | 10.4629 | 32.7094 | 1.8611 | 0.76558 | 0.24317 | 2.8699 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-15 | 18 | 23.6125 | 10.8123 | 34.4248 | 2.0615 | 0.76558 | 0.25592 | 3.083 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2011-01-15 | 19 | 24.0308 | 11.0599 | 35.0907 | 2.142 | 0.76558 | 0.26087 | 3.1684 | 9.029% | 9.607% | 6.492% | 1.0993 | 1.1063 | 1.0694
2011-01-15 | 20 | 24.0431 | 10.8492 | 34.8923 | 2.1178 | 0.76558 | 0.25939 | 3.1428 | 9.007% | 9.584% | 6.476% | 1.099 | 1.106 | 1.0692
2011-01-15 | 21 | 23.947 | 10.7723 | 34.7192 | 2.0969 | 0.76558 | 0.25811 | 3.1206 | 8.988% | 9.563% | 6.462% | 1.0988 | 1.1057 | 1.0691
2011-01-15 | 22 | 23.6229 | 10.825 | 34.448 | 2.0642 | 0.76558 | 0.25609 | 3.0859 | 8.958% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2011-01-15 | 23 | 22.6648 | 10.5707 | 33.2355 | 1.9215 | 0.76558 | 0.24708 | 2.9342 | 8.828% | 9.393% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-01-15 | 24 | 22.3787 | 10.3211 | 32.6998 | 1.8601 | 0.76558 | 0.24309 | 2.8687 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-15 | 25 | 21.9646 | 10.2672 | 32.2318 | 1.8072 | 0.76558 | 0.23962 | 2.8124 | 8.725% | 9.284% | 6.274% | 1.0956 | 1.1023 | 1.0669
2011-01-15 | 26 | 21.4682 | 9.9918 | 31.46 | 1.7217 | 0.76558 | 0.23388 | 2.7211 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-01-15 | 27 | 21.2776 | 10.2103 | 31.4879 | 1.7247 | 0.76558 | 0.23408 | 2.7244 | 8.652% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-01-15 | 28 | 21.1914 | 10.2067 | 31.3981 | 1.7149 | 0.76558 | 0.23342 | 2.7139 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-01-15 | 29 | 20.8472 | 10.0433 | 30.8905 | 1.6599 | 0.76558 | 0.22964 | 2.6551 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-01-15 | 30 | 20.3555 | 9.5315 | 29.887 | 1.5538 | 0.76558 | 0.22218 | 2.5416 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-01-15 | 31 | 20.1297 | 9.5343 | 29.664 | 1.5307 | 0.76558 | 0.22053 | 2.5168 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-01-15 | 32 | 20.1075 | 9.6055 | 29.713 | 1.5358 | 0.76558 | 0.22089 | 2.5222 | 8.489% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2011-01-15 | 33 | 20.1056 | 9.8194 | 29.925 | 1.5578 | 0.76558 | 0.22247 | 2.5458 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2011-01-15 | 34 | 20.2498 | 9.7887 | 30.0385 | 1.5696 | 0.76558 | 0.22331 | 2.5585 | 8.517% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-01-15 | 35 | 20.4316 | 10.1803 | 30.6119 | 1.6301 | 0.76558 | 0.22757 | 2.6233 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2011-01-15 | 36 | 20.8695 | 10.3141 | 31.1837 | 1.6916 | 0.76558 | 0.23182 | 2.689 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-01-15 | 37 | 21.4316 | 10.3763 | 31.8079 | 1.76 | 0.76558 | 0.23646 | 2.762 | 8.683% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-01-15 | 38 | 21.6625 | 10.2579 | 31.9204 | 1.7724 | 0.76558 | 0.2373 | 2.7753 | 8.694% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2011-01-15 | 39 | 21.5351 | 10.0559 | 31.591 | 1.736 | 0.76558 | 0.23485 | 2.7365 | 8.662% | 9.217% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-01-15 | 40 | 21.2136 | 9.6424 | 30.8559 | 1.6562 | 0.76558 | 0.22939 | 2.6512 | 8.592% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2011-01-15 | 41 | 21.0935 | 9.3953 | 30.4888 | 1.617 | 0.76558 | 0.22666 | 2.6093 | 8.558% | 9.106% | 6.153% | 1.0936 | 1.1002 | 1.0656
2011-01-15 | 42 | 21.2957 | 9.1273 | 30.423 | 1.61 | 0.76558 | 0.22617 | 2.6018 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-01-15 | 43 | 20.812 | 9.0702 | 29.8822 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-01-15 | 44 | 20.8941 | 9.1986 | 30.0927 | 1.5753 | 0.76558 | 0.22371 | 2.5646 | 8.522% | 9.068% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-01-15 | 45 | 20.726 | 9.1749 | 29.9009 | 1.5553 | 0.76558 | 0.22229 | 2.5431 | 8.505% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2011-01-15 | 46 | 19.608 | 8.573 | 28.181 | 1.3815 | 0.76558 | 0.2095 | 2.3566 | 8.362% | 8.897% | 6.012% | 1.0913 | 1.0977 | 1.064
2011-01-15 | 47 | 18.0698 | 8.2589 | 26.3287 | 1.2058 | 0.76558 | 0.19573 | 2.1672 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2011-01-15 | 48 | 16.8279 | 8.2345 | 25.0623 | 1.0926 | 0.76558 | 0.18632 | 2.0445 | 8.158% | 8.68% | 5.865% | 1.0888 | 1.095 | 1.0623
2011-01-16 | 1 | 15.1379 | 7.336 | 22.4739 | 0.8786 | 0.76558 | 0.16707 | 1.8113 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-16 | 2 | 13.7679 | 6.6518 | 20.4196 | 0.72532 | 0.76558 | 0.1518 | 1.6427 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-16 | 3 | 12.8759 | 6.3181 | 19.1941 | 0.64087 | 0.76558 | 0.14269 | 1.5491 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-01-16 | 4 | 12.3639 | 6.0253 | 18.3891 | 0.58824 | 0.76558 | 0.13671 | 1.4905 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-01-16 | 5 | 12.0276 | 5.9774 | 18.005 | 0.56392 | 0.76558 | 0.13385 | 1.4634 | 8.127% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-01-16 | 6 | 11.6933 | 5.8293 | 17.5226 | 0.53411 | 0.76558 | 0.13027 | 1.43 | 8.161% | 8.683% | 5.867% | 1.0889 | 1.0951 | 1.0623
2011-01-16 | 7 | 11.5376 | 5.8333 | 17.3709 | 0.5249 | 0.76558 | 0.12914 | 1.4196 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-01-16 | 8 | 11.4136 | 5.6813 | 17.0949 | 0.50836 | 0.76558 | 0.12709 | 1.401 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2011-01-16 | 9 | 11.4294 | 5.6653 | 17.0947 | 0.50834 | 0.76558 | 0.12708 | 1.401 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2011-01-16 | 10 | 11.6236 | 5.7666 | 17.3901 | 0.52607 | 0.76558 | 0.12928 | 1.4209 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-01-16 | 11 | 11.8533 | 5.926 | 17.7793 | 0.54988 | 0.76558 | 0.13217 | 1.4476 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0949 | 1.0622
2011-01-16 | 12 | 12.2115 | 6.0218 | 18.2332 | 0.57831 | 0.76558 | 0.13555 | 1.4794 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-01-16 | 13 | 12.8508 | 6.2263 | 19.077 | 0.63308 | 0.76558 | 0.14182 | 1.5405 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-01-16 | 14 | 13.7988 | 6.5376 | 20.3364 | 0.71942 | 0.76558 | 0.15118 | 1.6362 | 8.046% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-16 | 15 | 15.4765 | 7.0688 | 22.5453 | 0.88419 | 0.76558 | 0.1676 | 1.8174 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-01-16 | 16 | 16.9849 | 7.9088 | 24.8936 | 1.078 | 0.76558 | 0.18506 | 2.0286 | 8.149% | 8.671% | 5.859% | 1.0887 | 1.0949 | 1.0622
2011-01-16 | 17 | 19.0291 | 8.6286 | 27.6577 | 1.3307 | 0.76558 | 0.20561 | 2.3018 | 8.323% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2011-01-16 | 18 | 20.443 | 9.4359 | 29.8789 | 1.553 | 0.76558 | 0.22212 | 2.5407 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-01-16 | 19 | 21.8832 | 10.1919 | 32.0751 | 1.7897 | 0.76558 | 0.23845 | 2.7937 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2011-01-16 | 20 | 22.6193 | 10.7517 | 33.3709 | 1.9372 | 0.76558 | 0.24808 | 2.9508 | 8.843% | 9.408% | 6.358% | 1.097 | 1.1039 | 1.0679
2011-01-16 | 21 | 22.8668 | 10.9722 | 33.8391 | 1.9919 | 0.76558 | 0.25156 | 3.0091 | 8.892% | 9.461% | 6.394% | 1.0976 | 1.1045 | 1.0683
2011-01-16 | 22 | 22.6403 | 11.1372 | 33.7776 | 1.9847 | 0.76558 | 0.25111 | 3.0014 | 8.886% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-01-16 | 23 | 22.0163 | 10.5811 | 32.5974 | 1.8484 | 0.76558 | 0.24233 | 2.8563 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-01-16 | 24 | 21.53 | 10.5234 | 32.0534 | 1.7872 | 0.76558 | 0.23829 | 2.7911 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-01-16 | 25 | 20.8501 | 10.4319 | 31.282 | 1.7022 | 0.76558 | 0.23255 | 2.7004 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2011-01-16 | 26 | 20.4459 | 10.0155 | 30.4613 | 1.6141 | 0.76558 | 0.22645 | 2.6061 | 8.556% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2011-01-16 | 27 | 20.026 | 10.0086 | 30.0346 | 1.5692 | 0.76558 | 0.22328 | 2.5581 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-01-16 | 28 | 19.7838 | 9.896 | 29.6798 | 1.5323 | 0.76558 | 0.22064 | 2.5186 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0993 | 1.065
2011-01-16 | 29 | 19.3499 | 9.4492 | 28.7991 | 1.4428 | 0.76558 | 0.2141 | 2.4224 | 8.411% | 8.95% | 6.048% | 1.0918 | 1.0983 | 1.0644
2011-01-16 | 30 | 18.7201 | 9.1984 | 27.9185 | 1.3559 | 0.76558 | 0.20755 | 2.329 | 8.342% | 8.876% | 5.998% | 1.091 | 1.0974 | 1.0638
2011-01-16 | 31 | 18.6922 | 9.0575 | 27.7497 | 1.3395 | 0.76558 | 0.20629 | 2.3114 | 8.329% | 8.863% | 5.989% | 1.0909 | 1.0972 | 1.0637
2011-01-16 | 32 | 18.6139 | 9.1002 | 27.7141 | 1.3361 | 0.76558 | 0.20603 | 2.3077 | 8.327% | 8.86% | 5.987% | 1.0908 | 1.0972 | 1.0637
2011-01-16 | 33 | 18.6821 | 9.4091 | 28.0911 | 1.3727 | 0.76558 | 0.20883 | 2.3471 | 8.355% | 8.89% | 6.007% | 1.0912 | 1.0976 | 1.0639
2011-01-16 | 34 | 18.9141 | 9.3919 | 28.3059 | 1.3938 | 0.76558 | 0.21043 | 2.3698 | 8.372% | 8.908% | 6.019% | 1.0914 | 1.0978 | 1.0641
2011-01-16 | 35 | 19.1757 | 9.4414 | 28.6172 | 1.4246 | 0.76558 | 0.21274 | 2.4029 | 8.397% | 8.934% | 6.037% | 1.0917 | 1.0981 | 1.0643
2011-01-16 | 36 | 19.6175 | 9.9688 | 29.5863 | 1.5227 | 0.76558 | 0.21995 | 2.5082 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2011-01-16 | 37 | 20.0196 | 10.3262 | 30.3458 | 1.6019 | 0.76558 | 0.22559 | 2.5931 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-01-16 | 38 | 20.3471 | 10.2873 | 30.6344 | 1.6325 | 0.76558 | 0.22774 | 2.6258 | 8.571% | 9.12% | 6.163% | 1.0938 | 1.1004 | 1.0657
2011-01-16 | 39 | 20.3731 | 10.1472 | 30.5203 | 1.6204 | 0.76558 | 0.22689 | 2.6128 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-01-16 | 40 | 20.331 | 9.8634 | 30.1944 | 1.5859 | 0.76558 | 0.22447 | 2.576 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-01-16 | 41 | 20.1374 | 9.4568 | 29.5942 | 1.5235 | 0.76558 | 0.22001 | 2.5091 | 8.478% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2011-01-16 | 42 | 19.7314 | 9.3809 | 29.1123 | 1.4743 | 0.76558 | 0.21642 | 2.4563 | 8.437% | 8.977% | 6.066% | 1.0921 | 1.0986 | 1.0646
2011-01-16 | 43 | 19.4644 | 9.2278 | 28.6922 | 1.4321 | 0.76558 | 0.2133 | 2.4109 | 8.403% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2011-01-16 | 44 | 19.8966 | 9.4955 | 29.3921 | 1.5028 | 0.76558 | 0.2185 | 2.4869 | 8.461% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-01-16 | 45 | 20.0367 | 9.6276 | 29.6643 | 1.5307 | 0.76558 | 0.22053 | 2.5169 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-01-16 | 46 | 19.2008 | 9.3439 | 28.5447 | 1.4174 | 0.76558 | 0.2122 | 2.3952 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2011-01-16 | 47 | 17.8985 | 9.1163 | 27.0148 | 1.2695 | 0.76558 | 0.20083 | 2.2359 | 8.277% | 8.806% | 5.951% | 1.0902 | 1.0966 | 1.0633
2011-01-16 | 48 | 16.4504 | 9.106 | 25.5564 | 1.1361 | 0.76558 | 0.18999 | 2.0917 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2011-01-17 | 1 | 15.0108 | 8.2022 | 23.2129 | 0.93734 | 0.76558 | 0.17257 | 1.8755 | 8.079% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-01-17 | 2 | 13.7451 | 7.8655 | 21.6106 | 0.8124 | 0.76558 | 0.16066 | 1.7386 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-17 | 3 | 13.2571 | 7.6622 | 20.9192 | 0.76125 | 0.76558 | 0.15552 | 1.6823 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-17 | 4 | 12.607 | 7.3648 | 19.9718 | 0.69385 | 0.76558 | 0.14847 | 1.6079 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-17 | 5 | 12.1071 | 7.0803 | 19.1874 | 0.64042 | 0.76558 | 0.14264 | 1.5486 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-01-17 | 6 | 11.7812 | 6.7621 | 18.5432 | 0.59814 | 0.76558 | 0.13785 | 1.5016 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-01-17 | 7 | 11.3988 | 6.5365 | 17.9352 | 0.55956 | 0.76558 | 0.13333 | 1.4585 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-01-17 | 8 | 11.2765 | 6.3972 | 17.6737 | 0.54336 | 0.76558 | 0.13139 | 1.4403 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2011-01-17 | 9 | 11.3184 | 6.428 | 17.7464 | 0.54784 | 0.76558 | 0.13193 | 1.4454 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-01-17 | 10 | 11.2584 | 6.3357 | 17.5941 | 0.53848 | 0.76558 | 0.1308 | 1.4349 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-01-17 | 11 | 11.4626 | 6.3268 | 17.7894 | 0.5505 | 0.76558 | 0.13225 | 1.4483 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-01-17 | 12 | 11.7322 | 6.3478 | 18.08 | 0.56863 | 0.76558 | 0.13441 | 1.4686 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-01-17 | 13 | 11.9581 | 6.248 | 18.2062 | 0.5766 | 0.76558 | 0.13535 | 1.4775 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-01-17 | 14 | 12.4745 | 6.4708 | 18.9452 | 0.62436 | 0.76558 | 0.14084 | 1.5308 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-01-17 | 15 | 13.8647 | 6.9602 | 20.8249 | 0.7544 | 0.76558 | 0.15481 | 1.6748 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-17 | 16 | 15.2567 | 7.4909 | 22.7476 | 0.90013 | 0.76558 | 0.16911 | 1.8348 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-01-17 | 17 | 16.9427 | 8.3511 | 25.2938 | 1.1129 | 0.76558 | 0.18804 | 2.0665 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-01-17 | 18 | 18.7669 | 9.206 | 27.9729 | 1.3612 | 0.76558 | 0.20795 | 2.3347 | 8.346% | 8.88% | 6.001% | 1.0911 | 1.0975 | 1.0638
2011-01-17 | 19 | 20.781 | 9.6761 | 30.4571 | 1.6137 | 0.76558 | 0.22642 | 2.6057 | 8.555% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2011-01-17 | 20 | 21.457 | 10.0705 | 31.5275 | 1.7291 | 0.76558 | 0.23438 | 2.729 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2011-01-17 | 21 | 21.9545 | 10.3025 | 32.257 | 1.81 | 0.76558 | 0.2398 | 2.8154 | 8.728% | 9.287% | 6.275% | 1.0956 | 1.1024 | 1.067
2011-01-17 | 22 | 21.8731 | 10.738 | 32.6111 | 1.85 | 0.76558 | 0.24244 | 2.858 | 8.764% | 9.325% | 6.301% | 1.0961 | 1.1028 | 1.0672
2011-01-17 | 23 | 21.6289 | 10.7676 | 32.3965 | 1.8257 | 0.76558 | 0.24084 | 2.8321 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-01-17 | 24 | 21.3407 | 10.6484 | 31.9891 | 1.7801 | 0.76558 | 0.23781 | 2.7835 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2011-01-17 | 25 | 21.2347 | 10.6564 | 31.8911 | 1.7692 | 0.76558 | 0.23708 | 2.7718 | 8.692% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2011-01-17 | 26 | 20.6759 | 10.2804 | 30.9563 | 1.667 | 0.76558 | 0.23013 | 2.6627 | 8.601% | 9.152% | 6.184% | 1.0941 | 1.1007 | 1.0659
2011-01-17 | 27 | 20.4874 | 10.257 | 30.7445 | 1.6443 | 0.76558 | 0.22856 | 2.6384 | 8.582% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-01-17 | 28 | 20.1192 | 10.1144 | 30.2336 | 1.5901 | 0.76558 | 0.22476 | 2.5804 | 8.535% | 9.081% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-01-17 | 29 | 19.6733 | 9.7267 | 29.4001 | 1.5036 | 0.76558 | 0.21856 | 2.4877 | 8.462% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2011-01-17 | 30 | 19.3673 | 9.5208 | 28.8881 | 1.4517 | 0.76558 | 0.21476 | 2.432 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2011-01-17 | 31 | 18.9616 | 9.3842 | 28.3458 | 1.3977 | 0.76558 | 0.21073 | 2.374 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-01-17 | 32 | 18.8739 | 9.4647 | 28.3385 | 1.397 | 0.76558 | 0.21067 | 2.3732 | 8.375% | 8.911% | 6.021% | 1.0914 | 1.0978 | 1.0641
2011-01-17 | 33 | 19.2182 | 9.6865 | 28.9046 | 1.4533 | 0.76558 | 0.21488 | 2.4338 | 8.42% | 8.959% | 6.054% | 1.0919 | 1.0984 | 1.0644
2011-01-17 | 34 | 19.3362 | 9.7371 | 29.0733 | 1.4704 | 0.76558 | 0.21613 | 2.4521 | 8.434% | 8.974% | 6.064% | 1.0921 | 1.0986 | 1.0646
2011-01-17 | 35 | 19.5822 | 10.2836 | 29.8657 | 1.5516 | 0.76558 | 0.22203 | 2.5392 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2011-01-17 | 36 | 20.1684 | 11.0419 | 31.2104 | 1.6945 | 0.76558 | 0.23202 | 2.6921 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.101 | 1.0661
2011-01-17 | 37 | 20.5742 | 11.1766 | 31.7508 | 1.7537 | 0.76558 | 0.23604 | 2.7553 | 8.678% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-01-17 | 38 | 20.8864 | 11.4396 | 32.326 | 1.8178 | 0.76558 | 0.24032 | 2.8237 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2011-01-17 | 39 | 20.8424 | 11.4464 | 32.2887 | 1.8136 | 0.76558 | 0.24004 | 2.8192 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2011-01-17 | 40 | 20.5404 | 11.1809 | 31.7214 | 1.7504 | 0.76558 | 0.23582 | 2.7518 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-01-17 | 41 | 20.3307 | 10.7123 | 31.0429 | 1.6763 | 0.76558 | 0.23078 | 2.6727 | 8.61% | 9.161% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-01-17 | 42 | 20.3806 | 10.4049 | 30.7855 | 1.6486 | 0.76558 | 0.22886 | 2.6431 | 8.585% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2011-01-17 | 43 | 20.0969 | 10.0994 | 30.1963 | 1.5861 | 0.76558 | 0.22448 | 2.5762 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2011-01-17 | 44 | 20.6131 | 10.1769 | 30.7899 | 1.6491 | 0.76558 | 0.2289 | 2.6436 | 8.586% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2011-01-17 | 45 | 20.6612 | 10.1666 | 30.8278 | 1.6532 | 0.76558 | 0.22918 | 2.6479 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-01-17 | 46 | 19.2937 | 9.4605 | 28.7542 | 1.4383 | 0.76558 | 0.21376 | 2.4176 | 8.408% | 8.946% | 6.045% | 1.0918 | 1.0982 | 1.0643
2011-01-17 | 47 | 17.6237 | 8.8957 | 26.5194 | 1.2234 | 0.76558 | 0.19715 | 2.1861 | 8.243% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-01-17 | 48 | 16.0875 | 8.6534 | 24.7409 | 1.0648 | 0.76558 | 0.18393 | 2.0143 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-01-18 | 1 | 14.6337 | 7.7288 | 22.3625 | 0.86991 | 0.76558 | 0.16625 | 1.8017 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-18 | 2 | 13.3216 | 7.2481 | 20.5697 | 0.73602 | 0.76558 | 0.15292 | 1.6545 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-18 | 3 | 12.6494 | 6.995 | 19.6444 | 0.67129 | 0.76558 | 0.14604 | 1.5829 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-01-18 | 4 | 11.9193 | 6.7248 | 18.6441 | 0.60467 | 0.76558 | 0.1386 | 1.5088 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-18 | 5 | 11.5947 | 6.6804 | 18.2751 | 0.58097 | 0.76558 | 0.13586 | 1.4824 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-01-18 | 6 | 11.4351 | 6.6567 | 18.0918 | 0.56938 | 0.76558 | 0.1345 | 1.4695 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-01-18 | 7 | 11.2871 | 6.4892 | 17.7764 | 0.54969 | 0.76558 | 0.13215 | 1.4474 | 8.142% | 8.664% | 5.854% | 1.0886 | 1.0949 | 1.0622
2011-01-18 | 8 | 11.1231 | 6.5744 | 17.6976 | 0.54483 | 0.76558 | 0.13157 | 1.442 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2011-01-18 | 9 | 11.211 | 6.5414 | 17.7524 | 0.54821 | 0.76558 | 0.13197 | 1.4458 | 8.144% | 8.665% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-01-18 | 10 | 11.2011 | 6.5836 | 17.7848 | 0.55021 | 0.76558 | 0.13221 | 1.448 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-01-18 | 11 | 11.461 | 6.4743 | 17.9353 | 0.55956 | 0.76558 | 0.13333 | 1.4585 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-01-18 | 12 | 11.8211 | 6.7432 | 18.5643 | 0.5995 | 0.76558 | 0.13801 | 1.5031 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-01-18 | 13 | 12.8508 | 7.3077 | 20.1585 | 0.70689 | 0.76558 | 0.14986 | 1.6223 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-18 | 14 | 14.5329 | 8.3035 | 22.8364 | 0.90717 | 0.76558 | 0.16977 | 1.8425 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-18 | 15 | 17.0649 | 9.4781 | 26.543 | 1.2256 | 0.76558 | 0.19732 | 2.1885 | 8.245% | 8.773% | 5.928% | 1.0899 | 1.0962 | 1.063
2011-01-18 | 16 | 19.0491 | 10.4466 | 29.4957 | 1.5134 | 0.76558 | 0.21927 | 2.4982 | 8.47% | 9.012% | 6.09% | 1.0925 | 1.099 | 1.0648
2011-01-18 | 17 | 20.9451 | 11.3276 | 32.2728 | 1.8118 | 0.76558 | 0.23992 | 2.8173 | 8.73% | 9.288% | 6.277% | 1.0956 | 1.1024 | 1.067
2011-01-18 | 18 | 22.0886 | 11.7348 | 33.8234 | 1.9901 | 0.76558 | 0.25145 | 3.0071 | 8.891% | 9.46% | 6.392% | 1.0976 | 1.1045 | 1.0683
2011-01-18 | 19 | 22.8266 | 11.9331 | 34.7596 | 2.1018 | 0.76558 | 0.25841 | 3.1258 | 8.992% | 9.568% | 6.466% | 1.0988 | 1.1058 | 1.0691
2011-01-18 | 20 | 22.9466 | 12.0909 | 35.0374 | 2.1355 | 0.76558 | 0.26047 | 3.1615 | 9.023% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2011-01-18 | 21 | 22.8005 | 11.6353 | 34.4358 | 2.0628 | 0.76558 | 0.256 | 3.0844 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2011-01-18 | 22 | 22.6564 | 11.7303 | 34.3867 | 2.0569 | 0.76558 | 0.25564 | 3.0781 | 8.952% | 9.524% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-01-18 | 23 | 22.1386 | 11.6405 | 33.7791 | 1.9849 | 0.76558 | 0.25112 | 3.0016 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-01-18 | 24 | 22.1059 | 11.742 | 33.8479 | 1.993 | 0.76558 | 0.25163 | 3.0102 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2011-01-18 | 25 | 21.6898 | 11.7102 | 33.3999 | 1.9406 | 0.76558 | 0.2483 | 2.9544 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-01-18 | 26 | 21.5777 | 11.6661 | 33.2438 | 1.9225 | 0.76558 | 0.24714 | 2.9352 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-01-18 | 27 | 21.5619 | 11.5832 | 33.1451 | 1.9111 | 0.76558 | 0.2464 | 2.923 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2011-01-18 | 28 | 21.3122 | 11.5112 | 32.8234 | 1.8741 | 0.76558 | 0.24401 | 2.8837 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-01-18 | 29 | 21.0702 | 11.197 | 32.2672 | 1.8112 | 0.76558 | 0.23988 | 2.8166 | 8.729% | 9.288% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-01-18 | 30 | 20.6501 | 11.0698 | 31.72 | 1.7502 | 0.76558 | 0.23581 | 2.7516 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-01-18 | 31 | 20.6024 | 10.9235 | 31.5259 | 1.7289 | 0.76558 | 0.23437 | 2.7288 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2011-01-18 | 32 | 20.3145 | 10.9345 | 31.2489 | 1.6987 | 0.76558 | 0.23231 | 2.6965 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-01-18 | 33 | 20.4964 | 11.3126 | 31.809 | 1.7601 | 0.76558 | 0.23647 | 2.7621 | 8.684% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-01-18 | 34 | 20.7344 | 11.4926 | 32.227 | 1.8067 | 0.76558 | 0.23958 | 2.8118 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-01-18 | 35 | 20.7666 | 11.8986 | 32.6652 | 1.8561 | 0.76558 | 0.24284 | 2.8645 | 8.769% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-01-18 | 36 | 21.5413 | 12.3485 | 33.8897 | 1.9979 | 0.76558 | 0.25194 | 3.0154 | 8.898% | 9.467% | 6.397% | 1.0977 | 1.1046 | 1.0683
2011-01-18 | 37 | 22.5411 | 12.3269 | 34.8681 | 2.1149 | 0.76558 | 0.25921 | 3.1397 | 9.004% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2011-01-18 | 38 | 23.0092 | 12.0895 | 35.0987 | 2.143 | 0.76558 | 0.26093 | 3.1695 | 9.03% | 9.608% | 6.493% | 1.0993 | 1.1063 | 1.0694
2011-01-18 | 39 | 22.7235 | 11.5885 | 34.312 | 2.048 | 0.76558 | 0.25508 | 3.0686 | 8.943% | 9.516% | 6.43% | 1.0982 | 1.1052 | 1.0687
2011-01-18 | 40 | 22.4377 | 11.0341 | 33.4718 | 1.9489 | 0.76558 | 0.24883 | 2.9633 | 8.853% | 9.42% | 6.365% | 1.0971 | 1.104 | 1.068
2011-01-18 | 41 | 21.8277 | 10.6767 | 32.5044 | 1.8379 | 0.76558 | 0.24164 | 2.8451 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-01-18 | 42 | 21.2439 | 10.3716 | 31.6155 | 1.7387 | 0.76558 | 0.23503 | 2.7393 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-18 | 43 | 20.6176 | 10.3827 | 31.0003 | 1.6717 | 0.76558 | 0.23046 | 2.6678 | 8.606% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2011-01-18 | 44 | 20.8017 | 10.4916 | 31.2933 | 1.7035 | 0.76558 | 0.23264 | 2.7017 | 8.633% | 9.186% | 6.207% | 1.0945 | 1.1012 | 1.0662
2011-01-18 | 45 | 20.3897 | 10.3953 | 30.7851 | 1.6486 | 0.76558 | 0.22886 | 2.643 | 8.585% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2011-01-18 | 46 | 18.8856 | 9.6749 | 28.5605 | 1.4189 | 0.76558 | 0.21232 | 2.3968 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2011-01-18 | 47 | 17.2715 | 9.2401 | 26.5116 | 1.2227 | 0.76558 | 0.19709 | 2.1853 | 8.243% | 8.77% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-01-18 | 48 | 15.8313 | 9.1068 | 24.9381 | 1.0818 | 0.76558 | 0.18539 | 2.0328 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2011-01-19 | 1 | 14.2333 | 8.2221 | 22.4553 | 0.87715 | 0.76558 | 0.16694 | 1.8097 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2011-01-19 | 2 | 12.9192 | 7.7986 | 20.7178 | 0.74666 | 0.76558 | 0.15402 | 1.6663 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-19 | 3 | 12.2774 | 7.312 | 19.5894 | 0.66754 | 0.76558 | 0.14563 | 1.5788 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-19 | 4 | 11.6615 | 7.0193 | 18.6809 | 0.60706 | 0.76558 | 0.13888 | 1.5115 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-01-19 | 5 | 11.4218 | 7.0568 | 18.4786 | 0.59398 | 0.76558 | 0.13737 | 1.4969 | 8.101% | 8.619% | 5.825% | 1.0881 | 1.0943 | 1.0618
2011-01-19 | 6 | 11.0541 | 7.0018 | 18.0559 | 0.56712 | 0.76558 | 0.13423 | 1.4669 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-01-19 | 7 | 10.9666 | 6.7754 | 17.742 | 0.54757 | 0.76558 | 0.1319 | 1.445 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-01-19 | 8 | 10.7367 | 6.6355 | 17.3722 | 0.52498 | 0.76558 | 0.12915 | 1.4197 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-01-19 | 9 | 11.0606 | 6.5199 | 17.5805 | 0.53765 | 0.76558 | 0.1307 | 1.4339 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-01-19 | 10 | 11.1787 | 6.4951 | 17.6738 | 0.54337 | 0.76558 | 0.13139 | 1.4403 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2011-01-19 | 11 | 11.3706 | 6.6808 | 18.0514 | 0.56683 | 0.76558 | 0.1342 | 1.4666 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-01-19 | 12 | 11.8502 | 7.0298 | 18.88 | 0.62007 | 0.76558 | 0.14036 | 1.526 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-01-19 | 13 | 12.9899 | 7.6012 | 20.5911 | 0.73755 | 0.76558 | 0.15308 | 1.6562 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-19 | 14 | 14.6114 | 8.4264 | 23.0378 | 0.92324 | 0.76558 | 0.17127 | 1.8601 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-19 | 15 | 17.4055 | 9.6873 | 27.0927 | 1.2769 | 0.76558 | 0.20141 | 2.2438 | 8.282% | 8.812% | 5.955% | 1.0903 | 1.0966 | 1.0633
2011-01-19 | 16 | 19.3534 | 10.9456 | 30.299 | 1.5969 | 0.76558 | 0.22525 | 2.5878 | 8.541% | 9.087% | 6.141% | 1.0934 | 1.1 | 1.0654
2011-01-19 | 17 | 21.1474 | 11.7588 | 32.9061 | 1.8836 | 0.76558 | 0.24463 | 2.8938 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-01-19 | 18 | 22.3195 | 11.9664 | 34.2859 | 2.0449 | 0.76558 | 0.25489 | 3.0653 | 8.941% | 9.513% | 6.428% | 1.0982 | 1.1051 | 1.0687
2011-01-19 | 19 | 22.9488 | 12.1096 | 35.0584 | 2.1381 | 0.76558 | 0.26063 | 3.1643 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2011-01-19 | 20 | 22.6887 | 12.074 | 34.7627 | 2.1021 | 0.76558 | 0.25843 | 3.1261 | 8.993% | 9.568% | 6.466% | 1.0988 | 1.1058 | 1.0691
2011-01-19 | 21 | 22.7746 | 11.734 | 34.5086 | 2.0715 | 0.76558 | 0.25654 | 3.0936 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2011-01-19 | 22 | 22.3486 | 11.9181 | 34.2667 | 2.0426 | 0.76558 | 0.25474 | 3.0629 | 8.938% | 9.51% | 6.427% | 1.0982 | 1.1051 | 1.0687
2011-01-19 | 23 | 21.9822 | 11.5339 | 33.5161 | 1.9541 | 0.76558 | 0.24916 | 2.9688 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2011-01-19 | 24 | 21.5822 | 11.6647 | 33.2469 | 1.9228 | 0.76558 | 0.24716 | 2.9356 | 8.83% | 9.395% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-01-19 | 25 | 21.312 | 11.8131 | 33.1251 | 1.9087 | 0.76558 | 0.24626 | 2.9206 | 8.817% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2011-01-19 | 26 | 21.144 | 11.563 | 32.7069 | 1.8609 | 0.76558 | 0.24315 | 2.8696 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-19 | 27 | 21.0674 | 11.7783 | 32.8457 | 1.8767 | 0.76558 | 0.24418 | 2.8864 | 8.788% | 9.35% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-01-19 | 28 | 20.9586 | 11.7585 | 32.7171 | 1.862 | 0.76558 | 0.24322 | 2.8708 | 8.775% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-01-19 | 29 | 20.4625 | 11.5445 | 32.007 | 1.7821 | 0.76558 | 0.23794 | 2.7856 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-01-19 | 30 | 20.1345 | 11.4843 | 31.6188 | 1.7391 | 0.76558 | 0.23506 | 2.7397 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-19 | 31 | 20.2064 | 11.4105 | 31.6169 | 1.7389 | 0.76558 | 0.23504 | 2.7395 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-19 | 32 | 20.1785 | 11.5607 | 31.7392 | 1.7524 | 0.76558 | 0.23595 | 2.7539 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-01-19 | 33 | 20.4007 | 12.0468 | 32.4476 | 1.8315 | 0.76558 | 0.24122 | 2.8383 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2011-01-19 | 34 | 20.4547 | 12.1095 | 32.5642 | 1.8447 | 0.76558 | 0.24209 | 2.8523 | 8.759% | 9.32% | 6.298% | 1.096 | 1.1028 | 1.0672
2011-01-19 | 35 | 20.5784 | 12.3191 | 32.8974 | 1.8826 | 0.76558 | 0.24456 | 2.8927 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-01-19 | 36 | 21.2503 | 12.4815 | 33.7318 | 1.9793 | 0.76558 | 0.25077 | 2.9957 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1044 | 1.0682
2011-01-19 | 37 | 21.6899 | 12.3711 | 34.061 | 2.0181 | 0.76558 | 0.25321 | 3.0369 | 8.916% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2011-01-19 | 38 | 22.1697 | 12.2836 | 34.4533 | 2.0649 | 0.76558 | 0.25613 | 3.0866 | 8.959% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2011-01-19 | 39 | 21.8379 | 11.954 | 33.7919 | 1.9864 | 0.76558 | 0.25121 | 3.0032 | 8.887% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2011-01-19 | 40 | 21.5323 | 11.7614 | 33.2936 | 1.9282 | 0.76558 | 0.24751 | 2.9413 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2011-01-19 | 41 | 21.1622 | 11.4654 | 32.6276 | 1.8518 | 0.76558 | 0.24256 | 2.86 | 8.766% | 9.327% | 6.302% | 1.0961 | 1.1029 | 1.0673
2011-01-19 | 42 | 21.2343 | 11.4066 | 32.6409 | 1.8534 | 0.76558 | 0.24266 | 2.8616 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-01-19 | 43 | 20.9186 | 11.3552 | 32.2739 | 1.8119 | 0.76558 | 0.23993 | 2.8174 | 8.73% | 9.288% | 6.277% | 1.0956 | 1.1024 | 1.067
2011-01-19 | 44 | 21.1554 | 11.1223 | 32.2777 | 1.8123 | 0.76558 | 0.23996 | 2.8179 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2011-01-19 | 45 | 20.8051 | 10.6212 | 31.4263 | 1.718 | 0.76558 | 0.23363 | 2.7172 | 8.646% | 9.2% | 6.217% | 1.0946 | 1.1013 | 1.0663
2011-01-19 | 46 | 19.4109 | 9.9819 | 29.3928 | 1.5029 | 0.76558 | 0.21851 | 2.4869 | 8.461% | 9.003% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-01-19 | 47 | 17.5329 | 9.5915 | 27.1244 | 1.2798 | 0.76558 | 0.20165 | 2.2471 | 8.284% | 8.814% | 5.956% | 1.0903 | 1.0967 | 1.0633
2011-01-19 | 48 | 15.9477 | 9.3684 | 25.3161 | 1.1149 | 0.76558 | 0.1882 | 2.0687 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-01-20 | 1 | 14.3201 | 8.5428 | 22.8629 | 0.90928 | 0.76558 | 0.16997 | 1.8448 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-01-20 | 2 | 13.17 | 7.9363 | 21.1063 | 0.77492 | 0.76558 | 0.15691 | 1.6974 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-20 | 3 | 12.5556 | 7.6822 | 20.2378 | 0.71246 | 0.76558 | 0.15045 | 1.6285 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-20 | 4 | 12.0631 | 7.4292 | 19.4924 | 0.66094 | 0.76558 | 0.14491 | 1.5714 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-01-20 | 5 | 11.6821 | 7.3943 | 19.0764 | 0.63303 | 0.76558 | 0.14182 | 1.5404 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-01-20 | 6 | 11.3381 | 7.0172 | 18.3553 | 0.58608 | 0.76558 | 0.13646 | 1.4881 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-01-20 | 7 | 11.0961 | 6.9796 | 18.0757 | 0.56836 | 0.76558 | 0.13438 | 1.4683 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-01-20 | 8 | 10.9522 | 6.7771 | 17.7293 | 0.54679 | 0.76558 | 0.1318 | 1.4442 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2011-01-20 | 9 | 11.0599 | 6.7055 | 17.7655 | 0.54902 | 0.76558 | 0.13207 | 1.4467 | 8.143% | 8.664% | 5.855% | 1.0887 | 1.0949 | 1.0622
2011-01-20 | 10 | 11.1441 | 6.9926 | 18.1366 | 0.5722 | 0.76558 | 0.13483 | 1.4726 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-01-20 | 11 | 11.5484 | 7.1391 | 18.6875 | 0.60749 | 0.76558 | 0.13893 | 1.512 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-01-20 | 12 | 11.8626 | 7.4637 | 19.3262 | 0.64972 | 0.76558 | 0.14367 | 1.559 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-01-20 | 13 | 12.8745 | 8.0103 | 20.8848 | 0.75875 | 0.76558 | 0.15526 | 1.6796 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-20 | 14 | 14.7408 | 8.9498 | 23.6906 | 0.97631 | 0.76558 | 0.17612 | 1.918 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-01-20 | 15 | 17.1069 | 9.7322 | 26.8391 | 1.2531 | 0.76558 | 0.19952 | 2.2182 | 8.265% | 8.794% | 5.942% | 1.0901 | 1.0964 | 1.0632
2011-01-20 | 16 | 19.3227 | 10.5271 | 29.8498 | 1.5499 | 0.76558 | 0.22191 | 2.5374 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2011-01-20 | 17 | 21.0305 | 11.0807 | 32.1112 | 1.7937 | 0.76558 | 0.23872 | 2.798 | 8.713% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2011-01-20 | 18 | 21.9486 | 11.5934 | 33.542 | 1.9571 | 0.76558 | 0.24936 | 2.972 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-01-20 | 19 | 22.6345 | 11.7006 | 34.3351 | 2.0507 | 0.76558 | 0.25525 | 3.0716 | 8.946% | 9.518% | 6.432% | 1.0982 | 1.1052 | 1.0687
2011-01-20 | 20 | 21.9864 | 11.8249 | 33.8113 | 1.9886 | 0.76558 | 0.25136 | 3.0056 | 8.889% | 9.458% | 6.391% | 1.0976 | 1.1045 | 1.0683
2011-01-20 | 21 | 22.1682 | 11.5062 | 33.6743 | 1.9726 | 0.76558 | 0.25034 | 2.9885 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-01-20 | 22 | 22.0541 | 11.5936 | 33.6477 | 1.9694 | 0.76558 | 0.25014 | 2.9852 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2011-01-20 | 23 | 21.5842 | 11.4185 | 33.0027 | 1.8947 | 0.76558 | 0.24535 | 2.9056 | 8.804% | 9.368% | 6.33% | 1.0965 | 1.1034 | 1.0676
2011-01-20 | 24 | 21.414 | 11.3165 | 32.7305 | 1.8635 | 0.76558 | 0.24332 | 2.8724 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0673
2011-01-20 | 25 | 21.2198 | 11.453 | 32.6728 | 1.857 | 0.76558 | 0.24289 | 2.8655 | 8.77% | 9.331% | 6.306% | 1.0961 | 1.1029 | 1.0673
2011-01-20 | 26 | 20.8957 | 11.2182 | 32.1139 | 1.794 | 0.76558 | 0.23874 | 2.7983 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2011-01-20 | 27 | 20.8717 | 11.486 | 32.3577 | 1.8213 | 0.76558 | 0.24055 | 2.8275 | 8.738% | 9.297% | 6.283% | 1.0957 | 1.1025 | 1.067
2011-01-20 | 28 | 20.4612 | 11.3335 | 31.7947 | 1.7585 | 0.76558 | 0.23637 | 2.7605 | 8.682% | 9.238% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-01-20 | 29 | 20.307 | 11.0696 | 31.3766 | 1.7126 | 0.76558 | 0.23326 | 2.7114 | 8.641% | 9.195% | 6.213% | 1.0946 | 1.1013 | 1.0662
2011-01-20 | 30 | 20.3307 | 11.0174 | 31.3481 | 1.7095 | 0.76558 | 0.23305 | 2.7081 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-01-20 | 31 | 20.5865 | 11.3557 | 31.9422 | 1.7749 | 0.76558 | 0.23746 | 2.7779 | 8.697% | 9.253% | 6.253% | 1.0953 | 1.102 | 1.0667
2011-01-20 | 32 | 20.3802 | 11.3336 | 31.7139 | 1.7496 | 0.76558 | 0.23576 | 2.7509 | 8.674% | 9.229% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-01-20 | 33 | 20.322 | 11.6675 | 31.9894 | 1.7801 | 0.76558 | 0.23781 | 2.7835 | 8.701% | 9.258% | 6.256% | 1.0953 | 1.102 | 1.0667
2011-01-20 | 34 | 20.4031 | 11.8762 | 32.2792 | 1.8125 | 0.76558 | 0.23997 | 2.8181 | 8.73% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2011-01-20 | 35 | 20.7191 | 11.9559 | 32.675 | 1.8572 | 0.76558 | 0.24291 | 2.8657 | 8.77% | 9.332% | 6.306% | 1.0961 | 1.1029 | 1.0673
2011-01-20 | 36 | 21.3428 | 12.1635 | 33.5063 | 1.9529 | 0.76558 | 0.24909 | 2.9676 | 8.857% | 9.424% | 6.368% | 1.0972 | 1.104 | 1.068
2011-01-20 | 37 | 22.0349 | 12.2418 | 34.2767 | 2.0438 | 0.76558 | 0.25482 | 3.0642 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2011-01-20 | 38 | 22.2389 | 12.0806 | 34.3195 | 2.0489 | 0.76558 | 0.25514 | 3.0696 | 8.944% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2011-01-20 | 39 | 21.9929 | 11.6802 | 33.6731 | 1.9724 | 0.76558 | 0.25033 | 2.9883 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-01-20 | 40 | 21.3929 | 11.0455 | 32.4384 | 1.8304 | 0.76558 | 0.24115 | 2.8372 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-01-20 | 41 | 20.919 | 10.5868 | 31.5059 | 1.7267 | 0.76558 | 0.23422 | 2.7265 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-01-20 | 42 | 21.0414 | 10.4332 | 31.4746 | 1.7233 | 0.76558 | 0.23399 | 2.7228 | 8.651% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2011-01-20 | 43 | 20.8155 | 10.412 | 31.2275 | 1.6963 | 0.76558 | 0.23215 | 2.6941 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-01-20 | 44 | 21.3338 | 10.8613 | 32.1951 | 1.8031 | 0.76558 | 0.23934 | 2.808 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2011-01-20 | 45 | 20.5121 | 10.6882 | 31.2004 | 1.6934 | 0.76558 | 0.23195 | 2.6909 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-01-20 | 46 | 18.9942 | 10.1409 | 29.1351 | 1.4766 | 0.76558 | 0.21659 | 2.4588 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0987 | 1.0646
2011-01-20 | 47 | 17.3642 | 9.6188 | 26.983 | 1.2665 | 0.76558 | 0.2006 | 2.2327 | 8.274% | 8.804% | 5.949% | 1.0902 | 1.0965 | 1.0633
2011-01-20 | 48 | 15.9481 | 9.421 | 25.3691 | 1.1196 | 0.76558 | 0.1886 | 2.0737 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-01-21 | 1 | 14.4119 | 8.4968 | 22.9087 | 0.91293 | 0.76558 | 0.17031 | 1.8488 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-01-21 | 2 | 13.2616 | 7.8508 | 21.1123 | 0.77537 | 0.76558 | 0.15695 | 1.6979 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-21 | 3 | 12.5617 | 7.3756 | 19.9373 | 0.69146 | 0.76558 | 0.14822 | 1.6053 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-21 | 4 | 12.0354 | 7.2381 | 19.2736 | 0.64619 | 0.76558 | 0.14328 | 1.555 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-21 | 5 | 11.7254 | 7.1173 | 18.8427 | 0.61762 | 0.76558 | 0.14008 | 1.5233 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-01-21 | 6 | 11.3563 | 7.1422 | 18.4985 | 0.59526 | 0.76558 | 0.13752 | 1.4984 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-01-21 | 7 | 11.2183 | 7.0053 | 18.2236 | 0.5777 | 0.76558 | 0.13548 | 1.4788 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-01-21 | 8 | 11.0764 | 6.8723 | 17.9487 | 0.56041 | 0.76558 | 0.13343 | 1.4594 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-01-21 | 9 | 11.1285 | 6.8625 | 17.991 | 0.56305 | 0.76558 | 0.13375 | 1.4624 | 8.128% | 8.649% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-01-21 | 10 | 11.2 | 6.7966 | 17.9967 | 0.5634 | 0.76558 | 0.13379 | 1.4628 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-01-21 | 11 | 11.5521 | 6.8784 | 18.4305 | 0.59089 | 0.76558 | 0.13701 | 1.4935 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2011-01-21 | 12 | 11.9355 | 7.4686 | 19.404 | 0.65497 | 0.76558 | 0.14425 | 1.5648 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-01-21 | 13 | 12.8773 | 7.9031 | 20.7804 | 0.75118 | 0.76558 | 0.15448 | 1.6712 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-21 | 14 | 14.5556 | 8.4397 | 22.9953 | 0.91984 | 0.76558 | 0.17095 | 1.8564 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-01-21 | 15 | 17.018 | 9.3665 | 26.3845 | 1.211 | 0.76558 | 0.19615 | 2.1727 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2011-01-21 | 16 | 19.224 | 10.1228 | 29.3468 | 1.4982 | 0.76558 | 0.21817 | 2.4819 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2011-01-21 | 17 | 20.9417 | 10.877 | 31.8187 | 1.7612 | 0.76558 | 0.23654 | 2.7633 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-01-21 | 18 | 21.7295 | 11.4702 | 33.1997 | 1.9174 | 0.76558 | 0.24681 | 2.9298 | 8.825% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2011-01-21 | 19 | 22.2876 | 11.7884 | 34.076 | 2.0199 | 0.76558 | 0.25333 | 3.0388 | 8.918% | 9.488% | 6.412% | 1.0979 | 1.1048 | 1.0685
2011-01-21 | 20 | 22.2574 | 11.8948 | 34.1523 | 2.029 | 0.76558 | 0.25389 | 3.0484 | 8.926% | 9.497% | 6.418% | 1.098 | 1.1049 | 1.0686
2011-01-21 | 21 | 21.956 | 11.8969 | 33.8529 | 1.9935 | 0.76558 | 0.25167 | 3.0108 | 8.894% | 9.463% | 6.395% | 1.0976 | 1.1045 | 1.0683
2011-01-21 | 22 | 21.7642 | 11.9567 | 33.7209 | 1.978 | 0.76558 | 0.25069 | 2.9943 | 8.88% | 9.448% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-01-21 | 23 | 21.2841 | 11.7795 | 33.0636 | 1.9017 | 0.76558 | 0.2458 | 2.913 | 8.81% | 9.374% | 6.335% | 1.0966 | 1.1034 | 1.0676
2011-01-21 | 24 | 21.2119 | 11.749 | 32.9609 | 1.8899 | 0.76558 | 0.24504 | 2.9005 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-01-21 | 25 | 20.9018 | 11.7495 | 32.6513 | 1.8545 | 0.76558 | 0.24273 | 2.8628 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2011-01-21 | 26 | 20.5736 | 11.5639 | 32.1376 | 1.7966 | 0.76558 | 0.23891 | 2.8011 | 8.716% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2011-01-21 | 27 | 20.3994 | 11.7812 | 32.1806 | 1.8015 | 0.76558 | 0.23923 | 2.8063 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-01-21 | 28 | 20.4573 | 11.9217 | 32.379 | 1.8237 | 0.76558 | 0.24071 | 2.83 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-01-21 | 29 | 20.1951 | 11.7731 | 31.9682 | 1.7778 | 0.76558 | 0.23766 | 2.781 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-01-21 | 30 | 19.8049 | 11.5468 | 31.3517 | 1.7098 | 0.76558 | 0.23307 | 2.7085 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-01-21 | 31 | 19.8071 | 11.5012 | 31.3084 | 1.7051 | 0.76558 | 0.23275 | 2.7034 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-01-21 | 32 | 20.2189 | 11.362 | 31.5809 | 1.7349 | 0.76558 | 0.23478 | 2.7353 | 8.661% | 9.216% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-01-21 | 33 | 20.2655 | 11.7115 | 31.9771 | 1.7787 | 0.76558 | 0.23772 | 2.782 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-01-21 | 34 | 20.577 | 11.7725 | 32.3495 | 1.8204 | 0.76558 | 0.24049 | 2.8265 | 8.737% | 9.297% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-01-21 | 35 | 20.593 | 11.939 | 32.532 | 1.841 | 0.76558 | 0.24185 | 2.8484 | 8.756% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2011-01-21 | 36 | 21.0064 | 12.3626 | 33.369 | 1.937 | 0.76558 | 0.24807 | 2.9506 | 8.842% | 9.408% | 6.358% | 1.097 | 1.1039 | 1.0679
2011-01-21 | 37 | 22.4361 | 12.3035 | 34.7396 | 2.0994 | 0.76558 | 0.25826 | 3.1232 | 8.99% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2011-01-21 | 38 | 23.1262 | 11.8894 | 35.0157 | 2.1328 | 0.76558 | 0.26031 | 3.1587 | 9.021% | 9.598% | 6.486% | 1.0992 | 1.1062 | 1.0694
2011-01-21 | 39 | 23.0527 | 11.7708 | 34.8234 | 2.1095 | 0.76558 | 0.25888 | 3.134 | 9% | 9.576% | 6.471% | 1.0989 | 1.1059 | 1.0692
2011-01-21 | 40 | 22.573 | 11.1897 | 33.7627 | 1.9829 | 0.76558 | 0.251 | 2.9995 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-01-21 | 41 | 21.9869 | 10.7271 | 32.7141 | 1.8617 | 0.76558 | 0.2432 | 2.8705 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-01-21 | 42 | 21.6005 | 10.3625 | 31.963 | 1.7772 | 0.76558 | 0.23762 | 2.7804 | 8.699% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2011-01-21 | 43 | 20.9707 | 10.4161 | 31.3868 | 1.7137 | 0.76558 | 0.23333 | 2.7126 | 8.642% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-01-21 | 44 | 20.9205 | 10.209 | 31.1295 | 1.6857 | 0.76558 | 0.23142 | 2.6827 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-01-21 | 45 | 20.0047 | 9.5018 | 29.5065 | 1.5145 | 0.76558 | 0.21935 | 2.4994 | 8.471% | 9.013% | 6.091% | 1.0925 | 1.0991 | 1.0649
2011-01-21 | 46 | 18.477 | 8.7748 | 27.2517 | 1.2919 | 0.76558 | 0.20259 | 2.2601 | 8.293% | 8.824% | 5.963% | 1.0904 | 1.0968 | 1.0634
2011-01-21 | 47 | 16.8953 | 8.4448 | 25.3401 | 1.117 | 0.76558 | 0.18838 | 2.071 | 8.173% | 8.696% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-01-21 | 48 | 15.6237 | 8.4702 | 24.0939 | 1.0098 | 0.76558 | 0.17912 | 1.9545 | 8.112% | 8.631% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-01-22 | 1 | 14.2456 | 7.6342 | 21.8798 | 0.83276 | 0.76558 | 0.16266 | 1.761 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-22 | 2 | 13.2097 | 7.1058 | 20.3155 | 0.71794 | 0.76558 | 0.15103 | 1.6345 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-22 | 3 | 12.3314 | 6.8303 | 19.1617 | 0.63871 | 0.76558 | 0.14245 | 1.5467 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-01-22 | 4 | 11.9429 | 6.581 | 18.5239 | 0.5969 | 0.76558 | 0.13771 | 1.5002 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-01-22 | 5 | 11.4807 | 6.3812 | 17.8619 | 0.555 | 0.76558 | 0.13279 | 1.4534 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-01-22 | 6 | 11.1417 | 6.212 | 17.3537 | 0.52387 | 0.76558 | 0.12901 | 1.4185 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-01-22 | 7 | 11.0259 | 6.1947 | 17.2206 | 0.51586 | 0.76558 | 0.12802 | 1.4095 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2011-01-22 | 8 | 10.9957 | 6.1427 | 17.1384 | 0.51095 | 0.76558 | 0.12741 | 1.4039 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2011-01-22 | 9 | 11.0042 | 6.2645 | 17.2687 | 0.51875 | 0.76558 | 0.12838 | 1.4127 | 8.181% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2011-01-22 | 10 | 11.4419 | 6.3129 | 17.7548 | 0.54836 | 0.76558 | 0.13199 | 1.4459 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2011-01-22 | 11 | 11.6937 | 6.6784 | 18.372 | 0.58715 | 0.76558 | 0.13658 | 1.4893 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-01-22 | 12 | 12.0161 | 6.8333 | 18.8494 | 0.61806 | 0.76558 | 0.14013 | 1.5238 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-01-22 | 13 | 13.096 | 7.2007 | 20.2967 | 0.71661 | 0.76558 | 0.15089 | 1.6331 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-22 | 14 | 14.69 | 7.946 | 22.636 | 0.89132 | 0.76558 | 0.16828 | 1.8252 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-22 | 15 | 17.1899 | 9.0142 | 26.204 | 1.1945 | 0.76558 | 0.1948 | 2.1548 | 8.223% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2011-01-22 | 16 | 19.3419 | 9.5953 | 28.9372 | 1.4566 | 0.76558 | 0.21512 | 2.4373 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-01-22 | 17 | 21.1219 | 10.1897 | 31.3116 | 1.7055 | 0.76558 | 0.23277 | 2.7038 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-01-22 | 18 | 21.9958 | 10.693 | 32.6887 | 1.8588 | 0.76558 | 0.24301 | 2.8674 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2011-01-22 | 19 | 22.7474 | 10.7963 | 33.5437 | 1.9573 | 0.76558 | 0.24937 | 2.9722 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-01-22 | 20 | 22.6689 | 10.7545 | 33.4235 | 1.9433 | 0.76558 | 0.24847 | 2.9573 | 8.848% | 9.414% | 6.362% | 1.0971 | 1.1039 | 1.0679
2011-01-22 | 21 | 22.6271 | 10.4758 | 33.1029 | 1.9062 | 0.76558 | 0.24609 | 2.9179 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-01-22 | 22 | 22.2898 | 10.6089 | 32.8987 | 1.8827 | 0.76558 | 0.24457 | 2.8929 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-01-22 | 23 | 22.0362 | 10.3327 | 32.3688 | 1.8226 | 0.76558 | 0.24063 | 2.8288 | 8.739% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.067
2011-01-22 | 24 | 21.7401 | 10.3886 | 32.1287 | 1.7956 | 0.76558 | 0.23885 | 2.8001 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2011-01-22 | 25 | 21.3761 | 10.3663 | 31.7423 | 1.7527 | 0.76558 | 0.23598 | 2.7543 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-01-22 | 26 | 20.8641 | 10.0267 | 30.8909 | 1.66 | 0.76558 | 0.22965 | 2.6552 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-01-22 | 27 | 20.6791 | 10.1641 | 30.8432 | 1.6548 | 0.76558 | 0.22929 | 2.6497 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-01-22 | 28 | 20.5126 | 9.9026 | 30.4152 | 1.6092 | 0.76558 | 0.22611 | 2.6009 | 8.551% | 9.099% | 6.148% | 1.0935 | 1.1001 | 1.0655
2011-01-22 | 29 | 20.1785 | 9.7419 | 29.9205 | 1.5573 | 0.76558 | 0.22243 | 2.5453 | 8.507% | 9.051% | 6.116% | 1.093 | 1.0995 | 1.0651
2011-01-22 | 30 | 19.7624 | 9.5366 | 29.299 | 1.4933 | 0.76558 | 0.21781 | 2.4767 | 8.453% | 8.994% | 6.078% | 1.0923 | 1.0988 | 1.0647
2011-01-22 | 31 | 19.7523 | 9.428 | 29.1803 | 1.4812 | 0.76558 | 0.21693 | 2.4637 | 8.443% | 8.983% | 6.071% | 1.0922 | 1.0987 | 1.0646
2011-01-22 | 32 | 19.8243 | 9.5067 | 29.331 | 1.4965 | 0.76558 | 0.21805 | 2.4802 | 8.456% | 8.997% | 6.08% | 1.0924 | 1.0989 | 1.0647
2011-01-22 | 33 | 20.1262 | 9.6634 | 29.7896 | 1.5437 | 0.76558 | 0.22146 | 2.5307 | 8.495% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2011-01-22 | 34 | 20.0003 | 9.5849 | 29.5851 | 1.5226 | 0.76558 | 0.21994 | 2.5081 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2011-01-22 | 35 | 20.1621 | 9.5629 | 29.725 | 1.537 | 0.76558 | 0.22098 | 2.5236 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2011-01-22 | 36 | 20.4698 | 9.7671 | 30.2369 | 1.5904 | 0.76558 | 0.22479 | 2.5808 | 8.535% | 9.081% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-01-22 | 37 | 21.2757 | 9.8276 | 31.1034 | 1.6829 | 0.76558 | 0.23123 | 2.6797 | 8.615% | 9.167% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-01-22 | 38 | 21.4535 | 9.7425 | 31.1959 | 1.6929 | 0.76558 | 0.23191 | 2.6904 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-01-22 | 39 | 21.3438 | 9.3333 | 30.6771 | 1.6371 | 0.76558 | 0.22806 | 2.6307 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-01-22 | 40 | 21.1236 | 9.1066 | 30.2301 | 1.5897 | 0.76558 | 0.22473 | 2.58 | 8.535% | 9.081% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-01-22 | 41 | 20.8295 | 8.6579 | 29.4874 | 1.5125 | 0.76558 | 0.21921 | 2.4973 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2011-01-22 | 42 | 20.5517 | 8.3692 | 28.9209 | 1.455 | 0.76558 | 0.215 | 2.4356 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0645
2011-01-22 | 43 | 20.0976 | 8.2478 | 28.3454 | 1.3977 | 0.76558 | 0.21072 | 2.374 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-01-22 | 44 | 20.2716 | 8.3801 | 28.6517 | 1.428 | 0.76558 | 0.213 | 2.4066 | 8.4% | 8.937% | 6.039% | 1.0917 | 1.0981 | 1.0643
2011-01-22 | 45 | 19.56 | 8.2595 | 27.8195 | 1.3463 | 0.76558 | 0.20681 | 2.3187 | 8.335% | 8.868% | 5.993% | 1.0909 | 1.0973 | 1.0637
2011-01-22 | 46 | 18.4965 | 7.7855 | 26.282 | 1.2016 | 0.76558 | 0.19538 | 2.1625 | 8.228% | 8.755% | 5.916% | 1.0897 | 1.0959 | 1.0629
2011-01-22 | 47 | 17.0122 | 7.4961 | 24.5082 | 1.0449 | 0.76558 | 0.1822 | 1.9926 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-01-22 | 48 | 15.6964 | 7.4899 | 23.1863 | 0.93519 | 0.76558 | 0.17237 | 1.8731 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-01-23 | 1 | 14.6103 | 6.6746 | 21.2849 | 0.78809 | 0.76558 | 0.15823 | 1.7119 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-23 | 2 | 13.5446 | 6.1489 | 19.6935 | 0.67465 | 0.76558 | 0.1464 | 1.5866 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-23 | 3 | 12.7445 | 5.6865 | 18.4311 | 0.59093 | 0.76558 | 0.13702 | 1.4935 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2011-01-23 | 4 | 12.0542 | 5.3852 | 17.4394 | 0.52905 | 0.76558 | 0.12965 | 1.4243 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-01-23 | 5 | 11.3902 | 5.2003 | 16.5904 | 0.4788 | 0.76558 | 0.12334 | 1.3677 | 8.244% | 8.772% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-01-23 | 6 | 11.1721 | 5.0975 | 16.2696 | 0.46046 | 0.76558 | 0.12095 | 1.347 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2011-01-23 | 7 | 10.7102 | 4.9972 | 15.7074 | 0.42918 | 0.76558 | 0.11677 | 1.3115 | 8.35% | 8.884% | 6.003% | 1.0911 | 1.0975 | 1.0639
2011-01-23 | 8 | 11.0341 | 4.9264 | 15.9605 | 0.44313 | 0.76558 | 0.11865 | 1.3274 | 8.317% | 8.849% | 5.98% | 1.0907 | 1.0971 | 1.0636
2011-01-23 | 9 | 11.1021 | 4.9366 | 16.0387 | 0.44748 | 0.76558 | 0.11923 | 1.3323 | 8.307% | 8.838% | 5.973% | 1.0906 | 1.097 | 1.0635
2011-01-23 | 10 | 11.2383 | 4.9785 | 16.2167 | 0.45747 | 0.76558 | 0.12056 | 1.3436 | 8.285% | 8.816% | 5.957% | 1.0903 | 1.0967 | 1.0633
2011-01-23 | 11 | 11.3362 | 5.1142 | 16.4504 | 0.47075 | 0.76558 | 0.12229 | 1.3586 | 8.259% | 8.787% | 5.938% | 1.09 | 1.0963 | 1.0631
2011-01-23 | 12 | 11.3363 | 5.3153 | 16.6516 | 0.48233 | 0.76558 | 0.12379 | 1.3717 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2011-01-23 | 13 | 11.934 | 5.5949 | 17.5289 | 0.5345 | 0.76558 | 0.13031 | 1.4304 | 8.16% | 8.682% | 5.867% | 1.0889 | 1.0951 | 1.0623
2011-01-23 | 14 | 12.9279 | 5.898 | 18.826 | 0.61652 | 0.76558 | 0.13995 | 1.5221 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-01-23 | 15 | 14.6341 | 6.6036 | 21.2377 | 0.7846 | 0.76558 | 0.15788 | 1.7081 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-23 | 16 | 16.238 | 7.3093 | 23.5473 | 0.96453 | 0.76558 | 0.17505 | 1.9052 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-01-23 | 17 | 18.1022 | 7.9528 | 26.0549 | 1.1809 | 0.76558 | 0.1937 | 2.1402 | 8.214% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2011-01-23 | 18 | 19.6922 | 8.7463 | 28.4385 | 1.4069 | 0.76558 | 0.21142 | 2.3838 | 8.382% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2011-01-23 | 19 | 21.0603 | 9.4914 | 30.5517 | 1.6237 | 0.76558 | 0.22713 | 2.6164 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2011-01-23 | 20 | 21.6264 | 9.8292 | 31.4556 | 1.7212 | 0.76558 | 0.23384 | 2.7206 | 8.649% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-01-23 | 21 | 22.0583 | 9.9343 | 31.9926 | 1.7805 | 0.76558 | 0.23784 | 2.7839 | 8.702% | 9.259% | 6.256% | 1.0953 | 1.102 | 1.0667
2011-01-23 | 22 | 22.0143 | 10.1176 | 32.1319 | 1.796 | 0.76558 | 0.23887 | 2.8005 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0669
2011-01-23 | 23 | 21.1603 | 9.8985 | 31.0588 | 1.678 | 0.76558 | 0.23089 | 2.6745 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-01-23 | 24 | 20.9337 | 9.764 | 30.6977 | 1.6393 | 0.76558 | 0.22821 | 2.633 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2011-01-23 | 25 | 20.4116 | 9.6381 | 30.0497 | 1.5708 | 0.76558 | 0.22339 | 2.5597 | 8.518% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2011-01-23 | 26 | 19.8755 | 9.1972 | 29.0727 | 1.4703 | 0.76558 | 0.21613 | 2.452 | 8.434% | 8.974% | 6.064% | 1.0921 | 1.0986 | 1.0646
2011-01-23 | 27 | 19.6535 | 9.1973 | 28.8507 | 1.4479 | 0.76558 | 0.21448 | 2.428 | 8.416% | 8.954% | 6.051% | 1.0919 | 1.0983 | 1.0644
2011-01-23 | 28 | 19.5373 | 9.0179 | 28.5552 | 1.4184 | 0.76558 | 0.21228 | 2.3963 | 8.392% | 8.929% | 6.034% | 1.0916 | 1.098 | 1.0642
2011-01-23 | 29 | 19.1672 | 8.6173 | 27.7845 | 1.3429 | 0.76558 | 0.20655 | 2.315 | 8.332% | 8.865% | 5.991% | 1.0909 | 1.0973 | 1.0637
2011-01-23 | 30 | 18.5597 | 8.4649 | 27.0246 | 1.2704 | 0.76558 | 0.2009 | 2.2369 | 8.277% | 8.807% | 5.951% | 1.0902 | 1.0966 | 1.0633
2011-01-23 | 31 | 18.4438 | 8.4819 | 26.9257 | 1.2612 | 0.76558 | 0.20017 | 2.2269 | 8.271% | 8.8% | 5.947% | 1.0902 | 1.0965 | 1.0632
2011-01-23 | 32 | 18.3098 | 8.2699 | 26.5798 | 1.229 | 0.76558 | 0.1976 | 2.1921 | 8.247% | 8.775% | 5.93% | 1.0899 | 1.0962 | 1.063
2011-01-23 | 33 | 18.3039 | 8.4853 | 26.7892 | 1.2484 | 0.76558 | 0.19915 | 2.2131 | 8.261% | 8.79% | 5.94% | 1.0901 | 1.0964 | 1.0631
2011-01-23 | 34 | 18.5098 | 8.4855 | 26.9953 | 1.2677 | 0.76558 | 0.20069 | 2.2339 | 8.275% | 8.805% | 5.95% | 1.0902 | 1.0966 | 1.0633
2011-01-23 | 35 | 18.8637 | 8.6909 | 27.5545 | 1.3208 | 0.76558 | 0.20484 | 2.2912 | 8.315% | 8.847% | 5.979% | 1.0907 | 1.0971 | 1.0636
2011-01-23 | 36 | 19.1636 | 8.9983 | 28.1619 | 1.3796 | 0.76558 | 0.20936 | 2.3546 | 8.361% | 8.896% | 6.011% | 1.0912 | 1.0976 | 1.064
2011-01-23 | 37 | 19.7555 | 9.1067 | 28.8622 | 1.4491 | 0.76558 | 0.21457 | 2.4292 | 8.417% | 8.955% | 6.052% | 1.0919 | 1.0984 | 1.0644
2011-01-23 | 38 | 19.7913 | 9.0662 | 28.8575 | 1.4486 | 0.76558 | 0.21453 | 2.4287 | 8.416% | 8.955% | 6.051% | 1.0919 | 1.0984 | 1.0644
2011-01-23 | 39 | 19.6269 | 8.9369 | 28.5638 | 1.4193 | 0.76558 | 0.21235 | 2.3972 | 8.392% | 8.93% | 6.034% | 1.0916 | 1.0981 | 1.0642
2011-01-23 | 40 | 19.741 | 8.7528 | 28.4938 | 1.4123 | 0.76558 | 0.21183 | 2.3897 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2011-01-23 | 41 | 19.3892 | 8.3702 | 27.7594 | 1.3405 | 0.76558 | 0.20637 | 2.3124 | 8.33% | 8.863% | 5.989% | 1.0909 | 1.0973 | 1.0637
2011-01-23 | 42 | 19.1613 | 8.2587 | 27.4201 | 1.3079 | 0.76558 | 0.20384 | 2.2773 | 8.305% | 8.837% | 5.971% | 1.0906 | 1.0969 | 1.0635
2011-01-23 | 43 | 19.1119 | 8.1736 | 27.2855 | 1.2951 | 0.76558 | 0.20284 | 2.2635 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2011-01-23 | 44 | 19.7242 | 8.355 | 28.0792 | 1.3715 | 0.76558 | 0.20874 | 2.3459 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2011-01-23 | 45 | 19.7486 | 8.1821 | 27.9306 | 1.3571 | 0.76558 | 0.20764 | 2.3303 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2011-01-23 | 46 | 18.7567 | 7.9259 | 26.6827 | 1.2385 | 0.76558 | 0.19836 | 2.2024 | 8.254% | 8.782% | 5.935% | 1.09 | 1.0963 | 1.0631
2011-01-23 | 47 | 17.6969 | 7.7607 | 25.4576 | 1.1274 | 0.76558 | 0.18925 | 2.0822 | 8.179% | 8.703% | 5.881% | 1.0891 | 1.0953 | 1.0625
2011-01-23 | 48 | 16.1367 | 7.7758 | 23.9125 | 0.99469 | 0.76558 | 0.17777 | 1.938 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-01-24 | 1 | 14.6885 | 6.8182 | 21.5067 | 0.8046 | 0.76558 | 0.15988 | 1.7301 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-24 | 2 | 13.6663 | 6.3366 | 20.0029 | 0.69602 | 0.76558 | 0.1487 | 1.6103 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-01-24 | 3 | 12.9923 | 6.089 | 19.0813 | 0.63336 | 0.76558 | 0.14185 | 1.5408 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-01-24 | 4 | 12.2465 | 5.855 | 18.1015 | 0.56999 | 0.76558 | 0.13457 | 1.4701 | 8.122% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-01-24 | 5 | 11.8024 | 5.7064 | 17.5089 | 0.53327 | 0.76558 | 0.13016 | 1.429 | 8.162% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2011-01-24 | 6 | 11.6002 | 5.4672 | 17.0674 | 0.50672 | 0.76558 | 0.12688 | 1.3992 | 8.198% | 8.723% | 5.894% | 1.0893 | 1.0956 | 1.0626
2011-01-24 | 7 | 11.0501 | 5.5333 | 16.5834 | 0.47839 | 0.76558 | 0.12328 | 1.3672 | 8.245% | 8.772% | 5.928% | 1.0899 | 1.0962 | 1.063
2011-01-24 | 8 | 10.778 | 5.4299 | 16.208 | 0.45697 | 0.76558 | 0.12049 | 1.343 | 8.286% | 8.817% | 5.958% | 1.0903 | 1.0967 | 1.0634
2011-01-24 | 9 | 10.8841 | 5.4805 | 16.3646 | 0.46585 | 0.76558 | 0.12166 | 1.3531 | 8.268% | 8.798% | 5.945% | 1.0901 | 1.0965 | 1.0632
2011-01-24 | 10 | 11.2861 | 5.4401 | 16.7262 | 0.48666 | 0.76558 | 0.12434 | 1.3766 | 8.23% | 8.757% | 5.917% | 1.0897 | 1.096 | 1.0629
2011-01-24 | 11 | 11.302 | 5.4626 | 16.7646 | 0.4889 | 0.76558 | 0.12463 | 1.3791 | 8.226% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2011-01-24 | 12 | 11.6138 | 5.5102 | 17.1239 | 0.51008 | 0.76558 | 0.1273 | 1.403 | 8.193% | 8.717% | 5.891% | 1.0892 | 1.0955 | 1.0626
2011-01-24 | 13 | 12.0718 | 5.6038 | 17.6756 | 0.54348 | 0.76558 | 0.1314 | 1.4405 | 8.149% | 8.671% | 5.859% | 1.0887 | 1.0949 | 1.0622
2011-01-24 | 14 | 12.3083 | 5.7512 | 18.0594 | 0.56734 | 0.76558 | 0.13426 | 1.4672 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-01-24 | 15 | 13.4682 | 6.1218 | 19.5901 | 0.66758 | 0.76558 | 0.14563 | 1.5788 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-24 | 16 | 14.9803 | 6.7508 | 21.7311 | 0.82149 | 0.76558 | 0.16155 | 1.7486 | 8.047% | 8.562% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-24 | 17 | 16.5961 | 7.5173 | 24.1133 | 1.0115 | 0.76558 | 0.17926 | 1.9563 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-01-24 | 18 | 18.148 | 8.436 | 26.584 | 1.2294 | 0.76558 | 0.19763 | 2.1926 | 8.248% | 8.776% | 5.93% | 1.0899 | 1.0962 | 1.063
2011-01-24 | 19 | 19.9919 | 9.0288 | 29.0207 | 1.465 | 0.76558 | 0.21574 | 2.4464 | 8.43% | 8.969% | 6.061% | 1.0921 | 1.0985 | 1.0645
2011-01-24 | 20 | 20.8561 | 9.4916 | 30.3478 | 1.6021 | 0.76558 | 0.22561 | 2.5933 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-01-24 | 21 | 21.7483 | 9.8405 | 31.5888 | 1.7358 | 0.76558 | 0.23483 | 2.7362 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-01-24 | 22 | 21.7482 | 9.9711 | 31.7194 | 1.7502 | 0.76558 | 0.23581 | 2.7516 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-01-24 | 23 | 21.3461 | 9.7607 | 31.1067 | 1.6832 | 0.76558 | 0.23125 | 2.6801 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-01-24 | 24 | 20.7036 | 9.4985 | 30.2022 | 1.5868 | 0.76558 | 0.22453 | 2.5769 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2011-01-24 | 25 | 20.4529 | 9.4769 | 29.9298 | 1.5583 | 0.76558 | 0.2225 | 2.5464 | 8.508% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2011-01-24 | 26 | 20.2028 | 9.0872 | 29.2899 | 1.4924 | 0.76558 | 0.21774 | 2.4757 | 8.452% | 8.993% | 6.077% | 1.0923 | 1.0988 | 1.0647
2011-01-24 | 27 | 19.9145 | 8.9497 | 28.8642 | 1.4493 | 0.76558 | 0.21458 | 2.4294 | 8.417% | 8.955% | 6.052% | 1.0919 | 1.0984 | 1.0644
2011-01-24 | 28 | 19.3165 | 8.6706 | 27.9871 | 1.3625 | 0.76558 | 0.20806 | 2.3362 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0638
2011-01-24 | 29 | 18.9947 | 8.2542 | 27.2488 | 1.2916 | 0.76558 | 0.20257 | 2.2598 | 8.293% | 8.824% | 5.963% | 1.0904 | 1.0968 | 1.0634
2011-01-24 | 30 | 18.6765 | 7.9641 | 26.6406 | 1.2346 | 0.76558 | 0.19805 | 2.1982 | 8.251% | 8.779% | 5.933% | 1.0899 | 1.0962 | 1.0631
2011-01-24 | 31 | 18.629 | 7.8557 | 26.4847 | 1.2202 | 0.76558 | 0.19689 | 2.1826 | 8.241% | 8.769% | 5.925% | 1.0898 | 1.0961 | 1.063
2011-01-24 | 32 | 18.2134 | 7.8603 | 26.0737 | 1.1826 | 0.76558 | 0.19384 | 2.142 | 8.215% | 8.741% | 5.907% | 1.0895 | 1.0958 | 1.0628
2011-01-24 | 33 | 18.1531 | 8.1042 | 26.2573 | 1.1993 | 0.76558 | 0.1952 | 2.1601 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2011-01-24 | 34 | 18.4709 | 7.9863 | 26.4572 | 1.2176 | 0.76558 | 0.19669 | 2.1799 | 8.239% | 8.767% | 5.924% | 1.0898 | 1.0961 | 1.063
2011-01-24 | 35 | 19.0525 | 8.3303 | 27.3828 | 1.3043 | 0.76558 | 0.20357 | 2.2735 | 8.303% | 8.834% | 5.97% | 1.0905 | 1.0969 | 1.0635
2011-01-24 | 36 | 19.5723 | 8.8199 | 28.3921 | 1.4023 | 0.76558 | 0.21107 | 2.3789 | 8.379% | 8.915% | 6.024% | 1.0915 | 1.0979 | 1.0641
2011-01-24 | 37 | 20.1863 | 8.9755 | 29.1618 | 1.4793 | 0.76558 | 0.21679 | 2.4617 | 8.442% | 8.982% | 6.069% | 1.0922 | 1.0987 | 1.0646
2011-01-24 | 38 | 20.6523 | 9.1084 | 29.7607 | 1.5407 | 0.76558 | 0.22124 | 2.5275 | 8.493% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-01-24 | 39 | 20.8644 | 9.0837 | 29.9481 | 1.5602 | 0.76558 | 0.22264 | 2.5484 | 8.509% | 9.054% | 6.118% | 1.093 | 1.0996 | 1.0652
2011-01-24 | 40 | 20.5608 | 8.6752 | 29.236 | 1.4869 | 0.76558 | 0.21734 | 2.4698 | 8.448% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2011-01-24 | 41 | 20.3845 | 8.3768 | 28.7613 | 1.439 | 0.76558 | 0.21381 | 2.4184 | 8.408% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0643
2011-01-24 | 42 | 20.2768 | 8.0945 | 28.3713 | 1.4002 | 0.76558 | 0.21092 | 2.3767 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2011-01-24 | 43 | 20.3148 | 8.0124 | 28.3272 | 1.3959 | 0.76558 | 0.21059 | 2.372 | 8.374% | 8.91% | 6.021% | 1.0914 | 1.0978 | 1.0641
2011-01-24 | 44 | 20.6606 | 8.1436 | 28.8042 | 1.4433 | 0.76558 | 0.21413 | 2.423 | 8.412% | 8.95% | 6.048% | 1.0918 | 1.0983 | 1.0644
2011-01-24 | 45 | 20.3347 | 7.7318 | 28.0665 | 1.3703 | 0.76558 | 0.20865 | 2.3445 | 8.353% | 8.888% | 6.006% | 1.0911 | 1.0976 | 1.0639
2011-01-24 | 46 | 19.0609 | 7.3301 | 26.3911 | 1.2116 | 0.76558 | 0.19619 | 2.1733 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2011-01-24 | 47 | 17.753 | 6.9808 | 24.7338 | 1.0642 | 0.76558 | 0.18387 | 2.0136 | 8.141% | 8.662% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-01-24 | 48 | 16.1609 | 6.9935 | 23.1544 | 0.93261 | 0.76558 | 0.17213 | 1.8703 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-01-25 | 1 | 14.4786 | 6.0474 | 20.526 | 0.7329 | 0.76558 | 0.15259 | 1.6511 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-25 | 2 | 13.1901 | 5.6003 | 18.7905 | 0.6142 | 0.76558 | 0.13969 | 1.5195 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-01-25 | 3 | 12.2904 | 5.2566 | 17.5471 | 0.5356 | 0.76558 | 0.13045 | 1.4316 | 8.159% | 8.681% | 5.866% | 1.0888 | 1.0951 | 1.0623
2011-01-25 | 4 | 11.8107 | 5.177 | 16.9877 | 0.502 | 0.76558 | 0.12629 | 1.3939 | 8.205% | 8.73% | 5.9% | 1.0894 | 1.0957 | 1.0627
2011-01-25 | 5 | 11.4828 | 5.1662 | 16.649 | 0.48218 | 0.76558 | 0.12377 | 1.3715 | 8.238% | 8.765% | 5.923% | 1.0898 | 1.0961 | 1.063
2011-01-25 | 6 | 11.4168 | 5.0543 | 16.4711 | 0.47193 | 0.76558 | 0.12245 | 1.36 | 8.257% | 8.785% | 5.937% | 1.09 | 1.0963 | 1.0631
2011-01-25 | 7 | 11.279 | 4.9922 | 16.2712 | 0.46055 | 0.76558 | 0.12096 | 1.3471 | 8.279% | 8.809% | 5.953% | 1.0903 | 1.0966 | 1.0633
2011-01-25 | 8 | 10.9647 | 4.9299 | 15.8947 | 0.43948 | 0.76558 | 0.11816 | 1.3232 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2011-01-25 | 9 | 10.9946 | 4.9592 | 15.9538 | 0.44275 | 0.76558 | 0.1186 | 1.3269 | 8.317% | 8.85% | 5.98% | 1.0907 | 1.0971 | 1.0636
2011-01-25 | 10 | 11.1927 | 5.0086 | 16.2013 | 0.4566 | 0.76558 | 0.12044 | 1.3426 | 8.287% | 8.817% | 5.958% | 1.0904 | 1.0967 | 1.0634
2011-01-25 | 11 | 11.6728 | 5.153 | 16.8258 | 0.49247 | 0.76558 | 0.12508 | 1.3831 | 8.22% | 8.746% | 5.91% | 1.0896 | 1.0958 | 1.0628
2011-01-25 | 12 | 12.2446 | 5.5484 | 17.7931 | 0.55073 | 0.76558 | 0.13228 | 1.4486 | 8.141% | 8.662% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-01-25 | 13 | 13.4206 | 6.1682 | 19.5889 | 0.6675 | 0.76558 | 0.14563 | 1.5787 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-25 | 14 | 14.9086 | 6.9182 | 21.8268 | 0.82874 | 0.76558 | 0.16226 | 1.7566 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-25 | 15 | 17.5448 | 8.068 | 25.6128 | 1.1412 | 0.76558 | 0.19041 | 2.0972 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2011-01-25 | 16 | 19.607 | 8.9058 | 28.5128 | 1.4142 | 0.76558 | 0.21197 | 2.3918 | 8.388% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2011-01-25 | 17 | 21.2085 | 9.6499 | 30.8585 | 1.6565 | 0.76558 | 0.22941 | 2.6515 | 8.592% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2011-01-25 | 18 | 21.6948 | 10.1941 | 31.8889 | 1.7689 | 0.76558 | 0.23707 | 2.7716 | 8.691% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2011-01-25 | 19 | 22.301 | 10.4827 | 32.7837 | 1.8696 | 0.76558 | 0.24372 | 2.8789 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-01-25 | 20 | 22.1456 | 10.2573 | 32.4029 | 1.8264 | 0.76558 | 0.24089 | 2.8329 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-01-25 | 21 | 22.1331 | 9.9091 | 32.0422 | 1.786 | 0.76558 | 0.23821 | 2.7898 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2011-01-25 | 22 | 21.7328 | 10.0545 | 31.7873 | 1.7577 | 0.76558 | 0.23631 | 2.7596 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-01-25 | 23 | 21.615 | 9.7539 | 31.3689 | 1.7117 | 0.76558 | 0.2332 | 2.7105 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2011-01-25 | 24 | 21.135 | 9.605 | 30.74 | 1.6438 | 0.76558 | 0.22853 | 2.6379 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-01-25 | 25 | 20.9753 | 9.7186 | 30.6939 | 1.6388 | 0.76558 | 0.22818 | 2.6326 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2011-01-25 | 26 | 20.4412 | 9.5089 | 29.9501 | 1.5604 | 0.76558 | 0.22265 | 2.5486 | 8.51% | 9.054% | 6.118% | 1.093 | 1.0996 | 1.0652
2011-01-25 | 27 | 20.2115 | 9.4723 | 29.6838 | 1.5328 | 0.76558 | 0.22067 | 2.519 | 8.486% | 9.029% | 6.102% | 1.0927 | 1.0993 | 1.065
2011-01-25 | 28 | 20.0038 | 8.8439 | 28.8477 | 1.4476 | 0.76558 | 0.21446 | 2.4277 | 8.415% | 8.954% | 6.051% | 1.0919 | 1.0983 | 1.0644
2011-01-25 | 29 | 19.724 | 8.7939 | 28.5179 | 1.4147 | 0.76558 | 0.21201 | 2.3923 | 8.389% | 8.926% | 6.032% | 1.0916 | 1.098 | 1.0642
2011-01-25 | 30 | 19.7679 | 9.0761 | 28.844 | 1.4473 | 0.76558 | 0.21443 | 2.4273 | 8.415% | 8.954% | 6.05% | 1.0919 | 1.0983 | 1.0644
2011-01-25 | 31 | 19.6846 | 9.0183 | 28.7029 | 1.4331 | 0.76558 | 0.21338 | 2.4121 | 8.404% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2011-01-25 | 32 | 19.5729 | 9.12 | 28.6929 | 1.4321 | 0.76558 | 0.21331 | 2.411 | 8.403% | 8.941% | 6.042% | 1.0917 | 1.0982 | 1.0643
2011-01-25 | 33 | 19.8534 | 9.4973 | 29.3507 | 1.4985 | 0.76558 | 0.2182 | 2.4823 | 8.457% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0647
2011-01-25 | 34 | 19.8316 | 9.5275 | 29.3591 | 1.4994 | 0.76558 | 0.21826 | 2.4832 | 8.458% | 9% | 6.081% | 1.0924 | 1.0989 | 1.0648
2011-01-25 | 35 | 20.0775 | 9.7646 | 29.8421 | 1.5492 | 0.76558 | 0.22185 | 2.5366 | 8.5% | 9.044% | 6.111% | 1.0929 | 1.0994 | 1.0651
2011-01-25 | 36 | 20.3894 | 10.0913 | 30.4807 | 1.6162 | 0.76558 | 0.2266 | 2.6083 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2011-01-25 | 37 | 21.041 | 10.2731 | 31.3141 | 1.7057 | 0.76558 | 0.23279 | 2.7041 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-01-25 | 38 | 21.1191 | 10.2805 | 31.3996 | 1.7151 | 0.76558 | 0.23343 | 2.7141 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-01-25 | 39 | 21.1231 | 9.8929 | 31.016 | 1.6734 | 0.76558 | 0.23058 | 2.6696 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-01-25 | 40 | 21.2096 | 9.6211 | 30.8307 | 1.6535 | 0.76558 | 0.2292 | 2.6483 | 8.59% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-01-25 | 41 | 21.0565 | 9.2497 | 30.3063 | 1.5977 | 0.76558 | 0.2253 | 2.5886 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2011-01-25 | 42 | 20.9509 | 9.16 | 30.1109 | 1.5772 | 0.76558 | 0.22385 | 2.5666 | 8.524% | 9.069% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-01-25 | 43 | 20.5432 | 9.0831 | 29.6262 | 1.5268 | 0.76558 | 0.22024 | 2.5126 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2011-01-25 | 44 | 21.1518 | 9.0728 | 30.2246 | 1.5891 | 0.76558 | 0.22469 | 2.5794 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-01-25 | 45 | 20.6501 | 8.5403 | 29.1904 | 1.4822 | 0.76558 | 0.21701 | 2.4648 | 8.444% | 8.984% | 6.071% | 1.0922 | 1.0987 | 1.0646
2011-01-25 | 46 | 19.0964 | 7.9061 | 27.0025 | 1.2684 | 0.76558 | 0.20074 | 2.2347 | 8.276% | 8.805% | 5.95% | 1.0902 | 1.0966 | 1.0633
2011-01-25 | 47 | 17.8447 | 7.5948 | 25.4395 | 1.1258 | 0.76558 | 0.18912 | 2.0805 | 8.178% | 8.702% | 5.88% | 1.0891 | 1.0953 | 1.0625
2011-01-25 | 48 | 16.109 | 7.5117 | 23.6207 | 0.97055 | 0.76558 | 0.1756 | 1.9117 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-26 | 1 | 14.7469 | 6.6281 | 21.3749 | 0.79478 | 0.76558 | 0.1589 | 1.7193 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-26 | 2 | 13.5392 | 6.151 | 19.6901 | 0.67442 | 0.76558 | 0.14638 | 1.5864 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-26 | 3 | 12.7514 | 5.7961 | 18.5475 | 0.59842 | 0.76558 | 0.13788 | 1.5019 | 8.097% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-01-26 | 4 | 12.3316 | 5.6064 | 17.938 | 0.55974 | 0.76558 | 0.13335 | 1.4587 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-01-26 | 5 | 11.7776 | 5.449 | 17.2266 | 0.51622 | 0.76558 | 0.12806 | 1.4099 | 8.184% | 8.708% | 5.884% | 1.0891 | 1.0954 | 1.0625
2011-01-26 | 6 | 11.3876 | 5.5159 | 16.9036 | 0.49704 | 0.76558 | 0.12566 | 1.3883 | 8.213% | 8.739% | 5.905% | 1.0895 | 1.0958 | 1.0628
2011-01-26 | 7 | 11.0694 | 5.5738 | 16.6431 | 0.48184 | 0.76558 | 0.12373 | 1.3711 | 8.239% | 8.766% | 5.923% | 1.0898 | 1.0961 | 1.063
2011-01-26 | 8 | 11.0158 | 5.5171 | 16.5329 | 0.47548 | 0.76558 | 0.12291 | 1.364 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2011-01-26 | 9 | 11.3637 | 5.6135 | 16.9773 | 0.50138 | 0.76558 | 0.12621 | 1.3932 | 8.206% | 8.731% | 5.9% | 1.0894 | 1.0957 | 1.0627
2011-01-26 | 10 | 11.4541 | 5.5355 | 16.9896 | 0.50211 | 0.76558 | 0.1263 | 1.394 | 8.205% | 8.73% | 5.899% | 1.0894 | 1.0957 | 1.0627
2011-01-26 | 11 | 11.638 | 5.7111 | 17.3491 | 0.52359 | 0.76558 | 0.12898 | 1.4181 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-01-26 | 12 | 12.1539 | 6.0564 | 18.2103 | 0.57686 | 0.76558 | 0.13538 | 1.4778 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-01-26 | 13 | 13.0375 | 6.494 | 19.5315 | 0.6636 | 0.76558 | 0.1452 | 1.5744 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-01-26 | 14 | 14.7616 | 7.3506 | 22.1122 | 0.85055 | 0.76558 | 0.16438 | 1.7805 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-01-26 | 15 | 17.3617 | 8.3504 | 25.7121 | 1.15 | 0.76558 | 0.19115 | 2.1068 | 8.194% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2011-01-26 | 16 | 19.5739 | 8.9389 | 28.5128 | 1.4142 | 0.76558 | 0.21197 | 2.3918 | 8.388% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2011-01-26 | 17 | 21.1905 | 9.5839 | 30.7744 | 1.6475 | 0.76558 | 0.22878 | 2.6418 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-01-26 | 18 | 21.8745 | 10.0658 | 31.9403 | 1.7746 | 0.76558 | 0.23745 | 2.7777 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2011-01-26 | 19 | 22.2626 | 10.1777 | 32.4403 | 1.8306 | 0.76558 | 0.24117 | 2.8374 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-01-26 | 20 | 22.1928 | 10.1342 | 32.327 | 1.8179 | 0.76558 | 0.24032 | 2.8238 | 8.735% | 9.294% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-01-26 | 21 | 22.1084 | 9.8941 | 32.0025 | 1.7816 | 0.76558 | 0.23791 | 2.7851 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-01-26 | 22 | 21.6859 | 10.0871 | 31.773 | 1.7561 | 0.76558 | 0.2362 | 2.7579 | 8.68% | 9.235% | 6.241% | 1.0951 | 1.1018 | 1.0666
2011-01-26 | 23 | 21.2577 | 9.9403 | 31.1981 | 1.6931 | 0.76558 | 0.23193 | 2.6906 | 8.624% | 9.176% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-01-26 | 24 | 21.1558 | 9.8321 | 30.9878 | 1.6704 | 0.76558 | 0.23037 | 2.6663 | 8.604% | 9.155% | 6.187% | 1.0941 | 1.1008 | 1.0659
2011-01-26 | 25 | 20.7659 | 9.9397 | 30.7057 | 1.6401 | 0.76558 | 0.22827 | 2.634 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-01-26 | 26 | 20.2643 | 9.8306 | 30.0949 | 1.5755 | 0.76558 | 0.22373 | 2.5648 | 8.522% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-01-26 | 27 | 20.1224 | 10.0664 | 30.1888 | 1.5854 | 0.76558 | 0.22443 | 2.5754 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-01-26 | 28 | 20.2822 | 9.9606 | 30.2428 | 1.591 | 0.76558 | 0.22483 | 2.5814 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-01-26 | 29 | 19.9542 | 9.8193 | 29.7735 | 1.542 | 0.76558 | 0.22134 | 2.529 | 8.494% | 9.038% | 6.107% | 1.0928 | 1.0994 | 1.065
2011-01-26 | 30 | 19.8402 | 9.8102 | 29.6504 | 1.5293 | 0.76558 | 0.22042 | 2.5153 | 8.483% | 9.026% | 6.099% | 1.0927 | 1.0992 | 1.065
2011-01-26 | 31 | 19.7386 | 9.7853 | 29.5239 | 1.5163 | 0.76558 | 0.21948 | 2.5014 | 8.472% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-01-26 | 32 | 19.6586 | 9.7991 | 29.4577 | 1.5095 | 0.76558 | 0.21899 | 2.4941 | 8.467% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2011-01-26 | 33 | 19.7889 | 10.1327 | 29.9215 | 1.5574 | 0.76558 | 0.22244 | 2.5454 | 8.507% | 9.051% | 6.117% | 1.093 | 1.0995 | 1.0652
2011-01-26 | 34 | 19.841 | 10.2317 | 30.0728 | 1.5732 | 0.76558 | 0.22356 | 2.5623 | 8.52% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2011-01-26 | 35 | 19.677 | 10.4595 | 30.1365 | 1.5799 | 0.76558 | 0.22404 | 2.5695 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2011-01-26 | 36 | 19.987 | 10.6861 | 30.6732 | 1.6366 | 0.76558 | 0.22803 | 2.6302 | 8.575% | 9.124% | 6.165% | 1.0938 | 1.1004 | 1.0657
2011-01-26 | 37 | 20.9989 | 10.9832 | 31.9822 | 1.7793 | 0.76558 | 0.23776 | 2.7826 | 8.701% | 9.257% | 6.256% | 1.0953 | 1.102 | 1.0667
2011-01-26 | 38 | 21.4268 | 11.3527 | 32.7795 | 1.8691 | 0.76558 | 0.24369 | 2.8784 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-01-26 | 39 | 21.5306 | 11.1199 | 32.6505 | 1.8544 | 0.76558 | 0.24273 | 2.8628 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2011-01-26 | 40 | 21.1166 | 10.6507 | 31.7674 | 1.7555 | 0.76558 | 0.23616 | 2.7572 | 8.679% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2011-01-26 | 41 | 20.787 | 9.8948 | 30.6818 | 1.6376 | 0.76558 | 0.22809 | 2.6312 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-01-26 | 42 | 20.5251 | 9.9035 | 30.4286 | 1.6106 | 0.76558 | 0.22621 | 2.6024 | 8.553% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-01-26 | 43 | 20.4956 | 9.979 | 30.4746 | 1.6155 | 0.76558 | 0.22655 | 2.6076 | 8.557% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2011-01-26 | 44 | 21.1737 | 10.0968 | 31.2704 | 1.701 | 0.76558 | 0.23247 | 2.699 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2011-01-26 | 45 | 20.4122 | 9.8117 | 30.2239 | 1.589 | 0.76558 | 0.22469 | 2.5793 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-01-26 | 46 | 19.1543 | 9.2234 | 28.3777 | 1.4008 | 0.76558 | 0.21096 | 2.3774 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2011-01-26 | 47 | 17.6963 | 8.5142 | 26.2105 | 1.195 | 0.76558 | 0.19485 | 2.1555 | 8.224% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2011-01-26 | 48 | 15.6082 | 8.2308 | 23.839 | 0.98858 | 0.76558 | 0.17722 | 1.9314 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-01-27 | 1 | 14.6429 | 7.396 | 22.0389 | 0.84491 | 0.76558 | 0.16384 | 1.7743 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-27 | 2 | 13.3405 | 6.8761 | 20.2166 | 0.71097 | 0.76558 | 0.15029 | 1.6268 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-01-27 | 3 | 12.3826 | 6.4473 | 18.83 | 0.61678 | 0.76558 | 0.13998 | 1.5223 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-01-27 | 4 | 11.8268 | 6.2065 | 18.0333 | 0.5657 | 0.76558 | 0.13406 | 1.4653 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-01-27 | 5 | 11.6368 | 6.2402 | 17.877 | 0.55593 | 0.76558 | 0.1329 | 1.4544 | 8.136% | 8.656% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-01-27 | 6 | 11.5048 | 6.1138 | 17.6186 | 0.53998 | 0.76558 | 0.13098 | 1.4365 | 8.154% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-01-27 | 7 | 11.2826 | 5.9879 | 17.2704 | 0.51885 | 0.76558 | 0.12839 | 1.4128 | 8.181% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2011-01-27 | 8 | 11.2347 | 5.9354 | 17.1701 | 0.51284 | 0.76558 | 0.12764 | 1.4061 | 8.189% | 8.713% | 5.888% | 1.0892 | 1.0954 | 1.0626
2011-01-27 | 9 | 11.1229 | 6.0257 | 17.1486 | 0.51155 | 0.76558 | 0.12748 | 1.4046 | 8.191% | 8.715% | 5.889% | 1.0892 | 1.0955 | 1.0626
2011-01-27 | 10 | 11.0947 | 6.1796 | 17.2742 | 0.51908 | 0.76558 | 0.12842 | 1.4131 | 8.18% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2011-01-27 | 11 | 11.3846 | 6.438 | 17.8226 | 0.55256 | 0.76558 | 0.1325 | 1.4506 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-01-27 | 12 | 12.0868 | 6.5583 | 18.6451 | 0.60473 | 0.76558 | 0.13861 | 1.5089 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-27 | 13 | 13.5847 | 7.1172 | 20.702 | 0.74552 | 0.76558 | 0.1539 | 1.665 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-27 | 14 | 14.9644 | 7.9187 | 22.883 | 0.91088 | 0.76558 | 0.17012 | 1.8466 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-01-27 | 15 | 17.6184 | 9.0189 | 26.6373 | 1.2343 | 0.76558 | 0.19802 | 2.1979 | 8.251% | 8.779% | 5.933% | 1.0899 | 1.0962 | 1.0631
2011-01-27 | 16 | 19.6746 | 10.0019 | 29.6765 | 1.532 | 0.76558 | 0.22062 | 2.5182 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0992 | 1.065
2011-01-27 | 17 | 21.2247 | 10.7416 | 31.9663 | 1.7775 | 0.76558 | 0.23764 | 2.7808 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-01-27 | 18 | 22.1547 | 11.4134 | 33.5681 | 1.9601 | 0.76558 | 0.24955 | 2.9753 | 8.863% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2011-01-27 | 19 | 22.105 | 11.4276 | 33.5326 | 1.956 | 0.76558 | 0.24929 | 2.9709 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-01-27 | 20 | 21.8673 | 11.5519 | 33.4192 | 1.9428 | 0.76558 | 0.24844 | 2.9568 | 8.848% | 9.414% | 6.361% | 1.0971 | 1.1039 | 1.0679
2011-01-27 | 21 | 21.5851 | 11.1838 | 32.7689 | 1.8679 | 0.76558 | 0.24361 | 2.8771 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.103 | 1.0674
2011-01-27 | 22 | 21.5209 | 11.291 | 32.8119 | 1.8728 | 0.76558 | 0.24393 | 2.8823 | 8.784% | 9.347% | 6.316% | 1.0963 | 1.1031 | 1.0674
2011-01-27 | 23 | 21.4685 | 10.9296 | 32.3981 | 1.8259 | 0.76558 | 0.24085 | 2.8323 | 8.742% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-01-27 | 24 | 20.9187 | 10.7028 | 31.6215 | 1.7394 | 0.76558 | 0.23508 | 2.7401 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-27 | 25 | 20.9003 | 10.6892 | 31.5895 | 1.7359 | 0.76558 | 0.23484 | 2.7363 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-01-27 | 26 | 20.3937 | 10.5138 | 30.9075 | 1.6617 | 0.76558 | 0.22977 | 2.6571 | 8.597% | 9.147% | 6.181% | 1.0941 | 1.1007 | 1.0659
2011-01-27 | 27 | 20.4219 | 10.7875 | 31.2094 | 1.6944 | 0.76558 | 0.23201 | 2.692 | 8.625% | 9.177% | 6.202% | 1.0944 | 1.101 | 1.0661
2011-01-27 | 28 | 20.2917 | 10.841 | 31.1328 | 1.686 | 0.76558 | 0.23144 | 2.6831 | 8.618% | 9.17% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-01-27 | 29 | 20.1457 | 10.7856 | 30.9313 | 1.6643 | 0.76558 | 0.22995 | 2.6598 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2011-01-27 | 30 | 19.82 | 10.9328 | 30.7528 | 1.6451 | 0.76558 | 0.22862 | 2.6393 | 8.582% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-01-27 | 31 | 19.594 | 11.0007 | 30.5947 | 1.6283 | 0.76558 | 0.22745 | 2.6213 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-01-27 | 32 | 19.838 | 11.0004 | 30.8384 | 1.6543 | 0.76558 | 0.22926 | 2.6491 | 8.59% | 9.14% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-01-27 | 33 | 20.044 | 11.0441 | 31.088 | 1.6812 | 0.76558 | 0.23111 | 2.6779 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2011-01-27 | 34 | 20.3122 | 11.0594 | 31.3716 | 1.712 | 0.76558 | 0.23322 | 2.7108 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2011-01-27 | 35 | 20.3322 | 11.1728 | 31.505 | 1.7266 | 0.76558 | 0.23421 | 2.7264 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-01-27 | 36 | 20.5082 | 11.2891 | 31.7973 | 1.7588 | 0.76558 | 0.23639 | 2.7608 | 8.682% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-01-27 | 37 | 21.2867 | 11.4198 | 32.7065 | 1.8608 | 0.76558 | 0.24314 | 2.8695 | 8.774% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-27 | 38 | 21.65 | 11.319 | 32.969 | 1.8908 | 0.76558 | 0.2451 | 2.9015 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-01-27 | 39 | 21.5703 | 11.1733 | 32.7435 | 1.865 | 0.76558 | 0.24342 | 2.874 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2011-01-27 | 40 | 21.0986 | 10.6759 | 31.7745 | 1.7563 | 0.76558 | 0.23622 | 2.7581 | 8.68% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2011-01-27 | 41 | 20.805 | 10.2543 | 31.0593 | 1.6781 | 0.76558 | 0.2309 | 2.6746 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-01-27 | 42 | 20.5451 | 9.9344 | 30.4795 | 1.616 | 0.76558 | 0.22659 | 2.6082 | 8.557% | 9.105% | 6.153% | 1.0936 | 1.1002 | 1.0656
2011-01-27 | 43 | 20.726 | 9.8702 | 30.5962 | 1.6284 | 0.76558 | 0.22746 | 2.6215 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-01-27 | 44 | 21.2719 | 10.2525 | 31.5245 | 1.7287 | 0.76558 | 0.23436 | 2.7287 | 8.656% | 9.21% | 6.223% | 1.0948 | 1.1014 | 1.0664
2011-01-27 | 45 | 20.8002 | 10.025 | 30.8252 | 1.6529 | 0.76558 | 0.22916 | 2.6476 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-01-27 | 46 | 19.1584 | 9.3378 | 28.4961 | 1.4126 | 0.76558 | 0.21184 | 2.39 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2011-01-27 | 47 | 17.4684 | 8.9476 | 26.416 | 1.2139 | 0.76558 | 0.19638 | 2.1758 | 8.237% | 8.764% | 5.922% | 1.0898 | 1.0961 | 1.063
2011-01-27 | 48 | 15.7685 | 8.9101 | 24.6786 | 1.0594 | 0.76558 | 0.18346 | 2.0085 | 8.139% | 8.659% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-01-28 | 1 | 14.2728 | 8.0995 | 22.3723 | 0.87068 | 0.76558 | 0.16632 | 1.8026 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-01-28 | 2 | 13.2349 | 7.5396 | 20.7745 | 0.75075 | 0.76558 | 0.15444 | 1.6708 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-28 | 3 | 12.5488 | 7.1835 | 19.7323 | 0.67731 | 0.76558 | 0.14669 | 1.5896 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-01-28 | 4 | 12.0327 | 6.9384 | 18.9711 | 0.62607 | 0.76558 | 0.14103 | 1.5327 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-01-28 | 5 | 11.7826 | 6.8522 | 18.6348 | 0.60407 | 0.76558 | 0.13853 | 1.5082 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-01-28 | 6 | 11.2187 | 6.7266 | 17.9453 | 0.56019 | 0.76558 | 0.13341 | 1.4592 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-01-28 | 7 | 10.8404 | 6.6088 | 17.4492 | 0.52965 | 0.76558 | 0.12972 | 1.4249 | 8.166% | 8.689% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-01-28 | 8 | 10.7782 | 6.3999 | 17.1781 | 0.51332 | 0.76558 | 0.1277 | 1.4066 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2011-01-28 | 9 | 10.9442 | 6.4195 | 17.3637 | 0.52447 | 0.76558 | 0.12908 | 1.4191 | 8.173% | 8.696% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-01-28 | 10 | 11.2903 | 6.5649 | 17.8552 | 0.55458 | 0.76558 | 0.13274 | 1.4529 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-01-28 | 11 | 11.5604 | 6.6539 | 18.2142 | 0.57711 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-01-28 | 12 | 12.1121 | 6.8554 | 18.9675 | 0.62583 | 0.76558 | 0.14101 | 1.5324 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-01-28 | 13 | 13.272 | 7.2614 | 20.5334 | 0.73343 | 0.76558 | 0.15265 | 1.6517 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-28 | 14 | 14.6878 | 7.993 | 22.6808 | 0.89486 | 0.76558 | 0.16861 | 1.829 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-01-28 | 15 | 17.4187 | 9.0662 | 26.4849 | 1.2202 | 0.76558 | 0.19689 | 2.1827 | 8.241% | 8.769% | 5.925% | 1.0898 | 1.0961 | 1.063
2011-01-28 | 16 | 19.7086 | 9.7358 | 29.4443 | 1.5081 | 0.76558 | 0.21889 | 2.4926 | 8.465% | 9.007% | 6.087% | 1.0925 | 1.099 | 1.0648
2011-01-28 | 17 | 21.2428 | 10.4365 | 31.6794 | 1.7458 | 0.76558 | 0.23551 | 2.7469 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-01-28 | 18 | 22.1707 | 10.7095 | 32.8802 | 1.8806 | 0.76558 | 0.24444 | 2.8906 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-01-28 | 19 | 22.6507 | 11.0539 | 33.7046 | 1.9761 | 0.76558 | 0.25056 | 2.9923 | 8.878% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-01-28 | 20 | 22.4369 | 11.0918 | 33.5286 | 1.9555 | 0.76558 | 0.24926 | 2.9704 | 8.859% | 9.426% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-01-28 | 21 | 22.3178 | 11.1576 | 33.4754 | 1.9493 | 0.76558 | 0.24886 | 2.9638 | 8.854% | 9.42% | 6.366% | 1.0971 | 1.104 | 1.068
2011-01-28 | 22 | 21.8586 | 11.358 | 33.2166 | 1.9193 | 0.76558 | 0.24694 | 2.9318 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2011-01-28 | 23 | 21.3657 | 11.223 | 32.5887 | 1.8474 | 0.76558 | 0.24227 | 2.8553 | 8.762% | 9.322% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-01-28 | 24 | 21.083 | 11.259 | 32.342 | 1.8196 | 0.76558 | 0.24043 | 2.8256 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-01-28 | 25 | 20.9829 | 11.2002 | 32.1831 | 1.8017 | 0.76558 | 0.23925 | 2.8066 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-01-28 | 26 | 20.7388 | 11.0193 | 31.7581 | 1.7545 | 0.76558 | 0.23609 | 2.7561 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-01-28 | 27 | 20.6928 | 11.1251 | 31.8179 | 1.7611 | 0.76558 | 0.23654 | 2.7632 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-01-28 | 28 | 20.3165 | 11.1994 | 31.5158 | 1.7278 | 0.76558 | 0.23429 | 2.7277 | 8.655% | 9.209% | 6.223% | 1.0947 | 1.1014 | 1.0664
2011-01-28 | 29 | 20.0326 | 11.0098 | 31.0424 | 1.6763 | 0.76558 | 0.23077 | 2.6726 | 8.61% | 9.161% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-01-28 | 30 | 20.0407 | 10.6937 | 30.7344 | 1.6432 | 0.76558 | 0.22848 | 2.6372 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-01-28 | 31 | 20.1827 | 10.5701 | 30.7528 | 1.6451 | 0.76558 | 0.22862 | 2.6393 | 8.582% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-01-28 | 32 | 20.1531 | 10.4228 | 30.5758 | 1.6263 | 0.76558 | 0.2273 | 2.6191 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-01-28 | 33 | 20.3471 | 10.7849 | 31.132 | 1.686 | 0.76558 | 0.23144 | 2.683 | 8.618% | 9.17% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-01-28 | 34 | 20.3151 | 10.7195 | 31.0346 | 1.6754 | 0.76558 | 0.23072 | 2.6717 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-01-28 | 35 | 20.5991 | 10.817 | 31.4161 | 1.7169 | 0.76558 | 0.23355 | 2.716 | 8.645% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-01-28 | 36 | 20.6632 | 11.4992 | 32.1624 | 1.7994 | 0.76558 | 0.2391 | 2.8041 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2011-01-28 | 37 | 21.185 | 11.6903 | 32.8753 | 1.8801 | 0.76558 | 0.2444 | 2.89 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-01-28 | 38 | 21.4492 | 11.5938 | 33.043 | 1.8993 | 0.76558 | 0.24565 | 2.9105 | 8.808% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2011-01-28 | 39 | 21.7289 | 11.564 | 33.2929 | 1.9281 | 0.76558 | 0.2475 | 2.9412 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1037 | 1.0678
2011-01-28 | 40 | 21.5651 | 11.17 | 32.7351 | 1.8641 | 0.76558 | 0.24336 | 2.873 | 8.777% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0674
2011-01-28 | 41 | 20.9076 | 10.6024 | 31.51 | 1.7272 | 0.76558 | 0.23425 | 2.727 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-01-28 | 42 | 20.5316 | 10.4232 | 30.9548 | 1.6668 | 0.76558 | 0.23012 | 2.6625 | 8.601% | 9.152% | 6.184% | 1.0941 | 1.1007 | 1.0659
2011-01-28 | 43 | 20.6956 | 10.3729 | 31.0685 | 1.6791 | 0.76558 | 0.23097 | 2.6756 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-01-28 | 44 | 21.6338 | 10.614 | 32.2478 | 1.809 | 0.76558 | 0.23973 | 2.8143 | 8.727% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.0669
2011-01-28 | 45 | 21.1658 | 10.454 | 31.6198 | 1.7392 | 0.76558 | 0.23507 | 2.7399 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-01-28 | 46 | 19.962 | 9.7762 | 29.7382 | 1.5384 | 0.76558 | 0.22108 | 2.525 | 8.491% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2011-01-28 | 47 | 18.2501 | 9.0412 | 27.2913 | 1.2956 | 0.76558 | 0.20289 | 2.2641 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2011-01-28 | 48 | 16.588 | 8.7839 | 25.3719 | 1.1198 | 0.76558 | 0.18862 | 2.074 | 8.174% | 8.698% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-01-29 | 1 | 14.714 | 7.7886 | 22.5026 | 0.88085 | 0.76558 | 0.16729 | 1.8137 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-01-29 | 2 | 13.7255 | 7.2769 | 21.0024 | 0.76731 | 0.76558 | 0.15613 | 1.689 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-01-29 | 3 | 12.8399 | 6.9501 | 19.79 | 0.68128 | 0.76558 | 0.14712 | 1.594 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-01-29 | 4 | 12.1897 | 6.6693 | 18.859 | 0.61869 | 0.76558 | 0.1402 | 1.5245 | 8.083% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-01-29 | 5 | 11.8258 | 6.5893 | 18.415 | 0.5899 | 0.76558 | 0.1369 | 1.4924 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-01-29 | 6 | 11.216 | 6.5313 | 17.7473 | 0.54789 | 0.76558 | 0.13194 | 1.4454 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-01-29 | 7 | 10.9605 | 6.4717 | 17.4322 | 0.52861 | 0.76558 | 0.12959 | 1.4238 | 8.168% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-01-29 | 8 | 10.7688 | 6.4697 | 17.2385 | 0.51693 | 0.76558 | 0.12815 | 1.4107 | 8.183% | 8.707% | 5.884% | 1.0891 | 1.0954 | 1.0625
2011-01-29 | 9 | 11.3089 | 6.7887 | 18.0976 | 0.56974 | 0.76558 | 0.13454 | 1.4699 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-01-29 | 10 | 11.3728 | 7.0748 | 18.4476 | 0.59199 | 0.76558 | 0.13714 | 1.4947 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-01-29 | 11 | 11.7647 | 7.2878 | 19.0526 | 0.63145 | 0.76558 | 0.14164 | 1.5387 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-01-29 | 12 | 12.1125 | 7.3534 | 19.4659 | 0.65915 | 0.76558 | 0.14471 | 1.5694 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-01-29 | 13 | 13.5263 | 7.777 | 21.3033 | 0.78946 | 0.76558 | 0.15837 | 1.7134 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-29 | 14 | 14.4743 | 8.5701 | 23.0444 | 0.92378 | 0.76558 | 0.17132 | 1.8607 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-29 | 15 | 17.1707 | 9.634 | 26.8048 | 1.2499 | 0.76558 | 0.19927 | 2.2147 | 8.262% | 8.791% | 5.941% | 1.0901 | 1.0964 | 1.0632
2011-01-29 | 16 | 19.6408 | 10.4507 | 30.0914 | 1.5751 | 0.76558 | 0.2237 | 2.5644 | 8.522% | 9.068% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-01-29 | 17 | 21.1928 | 11.2268 | 32.4196 | 1.8283 | 0.76558 | 0.24101 | 2.8349 | 8.744% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2011-01-29 | 18 | 22.1369 | 11.739 | 33.8759 | 1.9963 | 0.76558 | 0.25184 | 3.0137 | 8.896% | 9.466% | 6.396% | 1.0976 | 1.1046 | 1.0683
2011-01-29 | 19 | 22.663 | 11.8085 | 34.4716 | 2.0671 | 0.76558 | 0.25627 | 3.0889 | 8.961% | 9.534% | 6.443% | 1.0984 | 1.1054 | 1.0689
2011-01-29 | 20 | 22.5871 | 11.4371 | 34.0241 | 2.0138 | 0.76558 | 0.25294 | 3.0323 | 8.912% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2011-01-29 | 21 | 22.4343 | 11.0884 | 33.5227 | 1.9549 | 0.76558 | 0.24921 | 2.9696 | 8.859% | 9.426% | 6.369% | 1.0972 | 1.1041 | 1.068
2011-01-29 | 22 | 22.1099 | 11.2529 | 33.3628 | 1.9362 | 0.76558 | 0.24802 | 2.9498 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-01-29 | 23 | 21.4396 | 11.2717 | 32.7113 | 1.8614 | 0.76558 | 0.24318 | 2.8701 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-01-29 | 24 | 21.5296 | 11.1686 | 32.6981 | 1.8599 | 0.76558 | 0.24308 | 2.8685 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-01-29 | 25 | 21.2473 | 11.2542 | 32.5015 | 1.8376 | 0.76558 | 0.24162 | 2.8448 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-01-29 | 26 | 20.8272 | 10.9382 | 31.7653 | 1.7553 | 0.76558 | 0.23615 | 2.757 | 8.679% | 9.235% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-01-29 | 27 | 20.9371 | 10.9422 | 31.8793 | 1.7679 | 0.76558 | 0.23699 | 2.7705 | 8.69% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-01-29 | 28 | 20.9408 | 11.15 | 32.0909 | 1.7914 | 0.76558 | 0.23857 | 2.7956 | 8.711% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-01-29 | 29 | 20.5406 | 11.3698 | 31.9105 | 1.7713 | 0.76558 | 0.23723 | 2.7741 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2011-01-29 | 30 | 20.2847 | 11.9353 | 32.22 | 1.8059 | 0.76558 | 0.23953 | 2.811 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-01-29 | 31 | 20.2529 | 12.0743 | 32.3272 | 1.8179 | 0.76558 | 0.24032 | 2.8238 | 8.735% | 9.294% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-01-29 | 32 | 20.449 | 12.2622 | 32.7112 | 1.8613 | 0.76558 | 0.24318 | 2.8701 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-01-29 | 33 | 20.5366 | 12.6821 | 33.2187 | 1.9195 | 0.76558 | 0.24695 | 2.9321 | 8.827% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2011-01-29 | 34 | 20.6646 | 12.6325 | 33.2972 | 1.9286 | 0.76558 | 0.24754 | 2.9417 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2011-01-29 | 35 | 20.6325 | 12.6784 | 33.311 | 1.9302 | 0.76558 | 0.24764 | 2.9434 | 8.836% | 9.402% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-01-29 | 36 | 20.6469 | 12.7603 | 33.4072 | 1.9414 | 0.76558 | 0.24835 | 2.9553 | 8.846% | 9.413% | 6.361% | 1.097 | 1.1039 | 1.0679
2011-01-29 | 37 | 21.0466 | 12.9298 | 33.9764 | 2.0081 | 0.76558 | 0.25259 | 3.0263 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2011-01-29 | 38 | 21.2352 | 12.9944 | 34.2296 | 2.0382 | 0.76558 | 0.25447 | 3.0582 | 8.934% | 9.506% | 6.424% | 1.0981 | 1.105 | 1.0686
2011-01-29 | 39 | 21.1535 | 12.4735 | 33.627 | 1.967 | 0.76558 | 0.24999 | 2.9826 | 8.87% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-01-29 | 40 | 21.0859 | 11.5724 | 32.6583 | 1.8553 | 0.76558 | 0.24279 | 2.8637 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-01-29 | 41 | 20.4949 | 11.0054 | 31.5003 | 1.7261 | 0.76558 | 0.23418 | 2.7258 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-01-29 | 42 | 20.4776 | 10.6848 | 31.1624 | 1.6893 | 0.76558 | 0.23167 | 2.6865 | 8.621% | 9.173% | 6.198% | 1.0943 | 1.101 | 1.0661
2011-01-29 | 43 | 20.4537 | 10.3904 | 30.8441 | 1.6549 | 0.76558 | 0.2293 | 2.6498 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-01-29 | 44 | 20.6986 | 10.804 | 31.5026 | 1.7263 | 0.76558 | 0.23419 | 2.7261 | 8.654% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-01-29 | 45 | 20.4175 | 10.5702 | 30.9877 | 1.6704 | 0.76558 | 0.23037 | 2.6663 | 8.604% | 9.155% | 6.187% | 1.0941 | 1.1008 | 1.0659
2011-01-29 | 46 | 19.5116 | 10.07 | 29.5816 | 1.5222 | 0.76558 | 0.21991 | 2.5077 | 8.477% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2011-01-29 | 47 | 17.8797 | 9.7389 | 27.6186 | 1.3269 | 0.76558 | 0.20532 | 2.2978 | 8.32% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2011-01-29 | 48 | 16.6218 | 9.5734 | 26.1952 | 1.1937 | 0.76558 | 0.19474 | 2.154 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2011-01-30 | 1 | 14.6996 | 8.3129 | 23.0125 | 0.92122 | 0.76558 | 0.17108 | 1.8579 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-01-30 | 2 | 13.8875 | 7.6572 | 21.5447 | 0.80745 | 0.76558 | 0.16017 | 1.7332 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-30 | 3 | 13.1557 | 7.2888 | 20.4445 | 0.72709 | 0.76558 | 0.15199 | 1.6447 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-30 | 4 | 12.4397 | 6.9142 | 19.3539 | 0.65159 | 0.76558 | 0.14388 | 1.561 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-01-30 | 5 | 11.9864 | 6.8981 | 18.8844 | 0.62036 | 0.76558 | 0.14039 | 1.5263 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-01-30 | 6 | 11.6054 | 6.6915 | 18.297 | 0.58236 | 0.76558 | 0.13602 | 1.484 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-01-30 | 7 | 11.1839 | 6.6841 | 17.8679 | 0.55537 | 0.76558 | 0.13283 | 1.4538 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-01-30 | 8 | 10.8743 | 6.669 | 17.5433 | 0.53537 | 0.76558 | 0.13042 | 1.4314 | 8.159% | 8.681% | 5.866% | 1.0888 | 1.0951 | 1.0623
2011-01-30 | 9 | 10.9204 | 6.7428 | 17.6632 | 0.54272 | 0.76558 | 0.13131 | 1.4396 | 8.15% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0622
2011-01-30 | 10 | 11.2303 | 6.7453 | 17.9756 | 0.56208 | 0.76558 | 0.13363 | 1.4613 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-01-30 | 11 | 11.4205 | 6.7958 | 18.2163 | 0.57724 | 0.76558 | 0.13542 | 1.4782 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-01-30 | 12 | 11.7345 | 6.7931 | 18.5276 | 0.59714 | 0.76558 | 0.13774 | 1.5005 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-01-30 | 13 | 12.3823 | 6.8192 | 19.2015 | 0.64137 | 0.76558 | 0.14275 | 1.5497 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-01-30 | 14 | 13.161 | 6.9606 | 20.1215 | 0.7043 | 0.76558 | 0.14959 | 1.6195 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-01-30 | 15 | 14.495 | 7.5528 | 22.0478 | 0.8456 | 0.76558 | 0.16391 | 1.7751 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-01-30 | 16 | 16.0213 | 8.2978 | 24.3191 | 1.0288 | 0.76558 | 0.18079 | 1.9752 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-01-30 | 17 | 18.0594 | 8.9508 | 27.0102 | 1.2691 | 0.76558 | 0.2008 | 2.2355 | 8.276% | 8.806% | 5.951% | 1.0902 | 1.0966 | 1.0633
2011-01-30 | 18 | 20.1755 | 9.7513 | 29.9269 | 1.558 | 0.76558 | 0.22248 | 2.546 | 8.507% | 9.052% | 6.117% | 1.093 | 1.0995 | 1.0652
2011-01-30 | 19 | 21.8656 | 10.3619 | 32.2275 | 1.8067 | 0.76558 | 0.23958 | 2.8119 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-01-30 | 20 | 22.2352 | 10.8372 | 33.0724 | 1.9027 | 0.76558 | 0.24586 | 2.9141 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1035 | 1.0676
2011-01-30 | 21 | 22.6011 | 10.7547 | 33.3558 | 1.9354 | 0.76558 | 0.24797 | 2.949 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-01-30 | 22 | 22.461 | 10.6424 | 33.1034 | 1.9062 | 0.76558 | 0.24609 | 2.9179 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-01-30 | 23 | 21.9851 | 10.4525 | 32.4376 | 1.8303 | 0.76558 | 0.24115 | 2.8371 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-01-30 | 24 | 21.7873 | 10.4514 | 32.2386 | 1.808 | 0.76558 | 0.23967 | 2.8132 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1023 | 1.0669
2011-01-30 | 25 | 21.2411 | 10.5148 | 31.7559 | 1.7542 | 0.76558 | 0.23608 | 2.7559 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0665
2011-01-30 | 26 | 20.6111 | 10.2092 | 30.8203 | 1.6524 | 0.76558 | 0.22912 | 2.6471 | 8.589% | 9.138% | 6.175% | 1.094 | 1.1006 | 1.0658
2011-01-30 | 27 | 20.2586 | 10.1637 | 30.4222 | 1.61 | 0.76558 | 0.22616 | 2.6017 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-01-30 | 28 | 20.035 | 10.0046 | 30.0397 | 1.5697 | 0.76558 | 0.22332 | 2.5586 | 8.517% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-01-30 | 29 | 19.7468 | 9.6495 | 29.3964 | 1.5032 | 0.76558 | 0.21854 | 2.4873 | 8.461% | 9.003% | 6.084% | 1.0924 | 1.0989 | 1.0648
2011-01-30 | 30 | 19.3543 | 9.3898 | 28.744 | 1.4372 | 0.76558 | 0.21369 | 2.4165 | 8.407% | 8.945% | 6.045% | 1.0918 | 1.0982 | 1.0643
2011-01-30 | 31 | 19.2173 | 9.2889 | 28.5062 | 1.4136 | 0.76558 | 0.21192 | 2.3911 | 8.388% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2011-01-30 | 32 | 18.7659 | 9.2229 | 27.9888 | 1.3627 | 0.76558 | 0.20807 | 2.3364 | 8.347% | 8.882% | 6.002% | 1.0911 | 1.0975 | 1.0639
2011-01-30 | 33 | 18.9937 | 9.4512 | 28.4449 | 1.4075 | 0.76558 | 0.21146 | 2.3845 | 8.383% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2011-01-30 | 34 | 19.0756 | 9.4226 | 28.4982 | 1.4128 | 0.76558 | 0.21186 | 2.3902 | 8.387% | 8.924% | 6.03% | 1.0916 | 1.098 | 1.0642
2011-01-30 | 35 | 19.0119 | 9.4432 | 28.4551 | 1.4085 | 0.76558 | 0.21154 | 2.3856 | 8.384% | 8.92% | 6.028% | 1.0915 | 1.0979 | 1.0641
2011-01-30 | 36 | 19.5833 | 9.849 | 29.4323 | 1.5069 | 0.76558 | 0.2188 | 2.4913 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2011-01-30 | 37 | 20.5785 | 10.2342 | 30.8127 | 1.6516 | 0.76558 | 0.22907 | 2.6462 | 8.588% | 9.138% | 6.175% | 1.0939 | 1.1006 | 1.0658
2011-01-30 | 38 | 20.9402 | 10.4089 | 31.3491 | 1.7096 | 0.76558 | 0.23305 | 2.7082 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-01-30 | 39 | 20.9662 | 10.2232 | 31.1894 | 1.6922 | 0.76558 | 0.23187 | 2.6896 | 8.624% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-01-30 | 40 | 20.8524 | 10.1204 | 30.9727 | 1.6688 | 0.76558 | 0.23026 | 2.6646 | 8.603% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-01-30 | 41 | 20.712 | 9.9067 | 30.6187 | 1.6308 | 0.76558 | 0.22762 | 2.624 | 8.57% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2011-01-30 | 42 | 20.8244 | 9.8781 | 30.7025 | 1.6398 | 0.76558 | 0.22825 | 2.6336 | 8.578% | 9.127% | 6.167% | 1.0938 | 1.1004 | 1.0657
2011-01-30 | 43 | 20.9388 | 9.9473 | 30.8861 | 1.6594 | 0.76558 | 0.22961 | 2.6546 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-01-30 | 44 | 20.9115 | 10.0946 | 31.006 | 1.6723 | 0.76558 | 0.2305 | 2.6684 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2011-01-30 | 45 | 20.1656 | 9.871 | 30.0366 | 1.5694 | 0.76558 | 0.2233 | 2.5583 | 8.517% | 9.062% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-01-30 | 46 | 18.7856 | 9.3205 | 28.1062 | 1.3742 | 0.76558 | 0.20894 | 2.3487 | 8.356% | 8.891% | 6.008% | 1.0912 | 1.0976 | 1.0639
2011-01-30 | 47 | 17.694 | 9.0764 | 26.7705 | 1.2467 | 0.76558 | 0.19901 | 2.2112 | 8.26% | 8.789% | 5.939% | 1.09 | 1.0964 | 1.0631
2011-01-30 | 48 | 16.7496 | 9.0419 | 25.7915 | 1.1571 | 0.76558 | 0.19174 | 2.1145 | 8.198% | 8.723% | 5.895% | 1.0893 | 1.0956 | 1.0626
2011-01-31 | 1 | 15.3836 | 8.0942 | 23.4778 | 0.95884 | 0.76558 | 0.17454 | 1.899 | 8.088% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2011-01-31 | 2 | 14.0995 | 7.555 | 21.6545 | 0.8157 | 0.76558 | 0.16098 | 1.7423 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-01-31 | 3 | 13.1915 | 7.2002 | 20.3917 | 0.72334 | 0.76558 | 0.15159 | 1.6405 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-01-31 | 4 | 12.3571 | 6.9242 | 19.2813 | 0.64671 | 0.76558 | 0.14334 | 1.5556 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-31 | 5 | 11.8391 | 6.9275 | 18.7667 | 0.61265 | 0.76558 | 0.13951 | 1.5177 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-01-31 | 6 | 11.4011 | 6.7587 | 18.1598 | 0.57366 | 0.76558 | 0.135 | 1.4742 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-01-31 | 7 | 11.4171 | 6.6301 | 18.0472 | 0.56657 | 0.76558 | 0.13416 | 1.4663 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-01-31 | 8 | 11.285 | 6.5633 | 17.8482 | 0.55415 | 0.76558 | 0.13269 | 1.4524 | 8.138% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-01-31 | 9 | 11.3612 | 6.5142 | 17.8754 | 0.55584 | 0.76558 | 0.13289 | 1.4543 | 8.136% | 8.656% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-01-31 | 10 | 11.3489 | 6.6395 | 17.9884 | 0.56288 | 0.76558 | 0.13373 | 1.4622 | 8.129% | 8.649% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-01-31 | 11 | 11.2729 | 6.8365 | 18.1094 | 0.57048 | 0.76558 | 0.13463 | 1.4707 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-01-31 | 12 | 11.5528 | 6.7536 | 18.3064 | 0.58296 | 0.76558 | 0.13609 | 1.4846 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-01-31 | 13 | 12.5181 | 6.7757 | 19.2938 | 0.64755 | 0.76558 | 0.14343 | 1.5566 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-01-31 | 14 | 13.1041 | 6.6192 | 19.7234 | 0.6767 | 0.76558 | 0.14663 | 1.5889 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2011-01-31 | 15 | 14.4404 | 6.9756 | 21.416 | 0.79783 | 0.76558 | 0.15921 | 1.7226 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-01-31 | 16 | 16.014 | 7.5691 | 23.5831 | 0.96747 | 0.76558 | 0.17532 | 1.9084 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-01-31 | 17 | 17.9302 | 8.5658 | 26.496 | 1.2212 | 0.76558 | 0.19697 | 2.1838 | 8.242% | 8.769% | 5.926% | 1.0898 | 1.0961 | 1.063
2011-01-31 | 18 | 19.7157 | 9.2933 | 29.009 | 1.4639 | 0.76558 | 0.21566 | 2.4451 | 8.429% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-01-31 | 19 | 21.1979 | 9.7275 | 30.9254 | 1.6637 | 0.76558 | 0.2299 | 2.6591 | 8.599% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-01-31 | 20 | 22.0261 | 9.8691 | 31.8952 | 1.7696 | 0.76558 | 0.23711 | 2.7723 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-01-31 | 21 | 22.2698 | 10.0783 | 32.3481 | 1.8203 | 0.76558 | 0.24048 | 2.8263 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-01-31 | 22 | 22.091 | 10.1336 | 32.2246 | 1.8064 | 0.76558 | 0.23956 | 2.8115 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-01-31 | 23 | 21.3867 | 9.9994 | 31.3861 | 1.7136 | 0.76558 | 0.23333 | 2.7125 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-01-31 | 24 | 20.9328 | 9.9847 | 30.9175 | 1.6628 | 0.76558 | 0.22984 | 2.6582 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-01-31 | 25 | 20.3247 | 9.8748 | 30.1995 | 1.5865 | 0.76558 | 0.22451 | 2.5766 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2011-01-31 | 26 | 19.9783 | 9.6247 | 29.6029 | 1.5244 | 0.76558 | 0.22007 | 2.5101 | 8.479% | 9.022% | 6.096% | 1.0926 | 1.0992 | 1.0649
2011-01-31 | 27 | 19.4544 | 9.7603 | 29.2147 | 1.4847 | 0.76558 | 0.21719 | 2.4675 | 8.446% | 8.986% | 6.073% | 1.0923 | 1.0987 | 1.0647
2011-01-31 | 28 | 19.2457 | 9.7194 | 28.965 | 1.4594 | 0.76558 | 0.21533 | 2.4403 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2011-01-31 | 29 | 18.6839 | 9.4614 | 28.1453 | 1.378 | 0.76558 | 0.20924 | 2.3528 | 8.359% | 8.895% | 6.01% | 1.0912 | 1.0976 | 1.0639
2011-01-31 | 30 | 18.2788 | 9.3748 | 27.6536 | 1.3303 | 0.76558 | 0.20558 | 2.3014 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2011-01-31 | 31 | 18.299 | 9.1945 | 27.4936 | 1.3149 | 0.76558 | 0.20439 | 2.2849 | 8.311% | 8.842% | 5.975% | 1.0906 | 1.097 | 1.0636
2011-01-31 | 32 | 18.1692 | 9.0381 | 27.2073 | 1.2877 | 0.76558 | 0.20226 | 2.2555 | 8.29% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2011-01-31 | 33 | 18.2172 | 9.2185 | 27.4357 | 1.3094 | 0.76558 | 0.20396 | 2.2789 | 8.306% | 8.838% | 5.972% | 1.0906 | 1.0969 | 1.0635
2011-01-31 | 34 | 18.2215 | 9.3304 | 27.5519 | 1.3205 | 0.76558 | 0.20482 | 2.2909 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2011-01-31 | 35 | 18.5814 | 9.821 | 28.4024 | 1.4033 | 0.76558 | 0.21115 | 2.38 | 8.38% | 8.916% | 6.025% | 1.0915 | 1.0979 | 1.0641
2011-01-31 | 36 | 19.111 | 10.4799 | 29.5909 | 1.5232 | 0.76558 | 0.21998 | 2.5087 | 8.478% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2011-01-31 | 37 | 19.2847 | 10.8874 | 30.1722 | 1.5836 | 0.76558 | 0.2243 | 2.5735 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2011-01-31 | 38 | 20.1647 | 10.9265 | 31.0912 | 1.6815 | 0.76558 | 0.23114 | 2.6783 | 8.614% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-01-31 | 39 | 20.705 | 10.9992 | 31.7042 | 1.7485 | 0.76558 | 0.23569 | 2.7498 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-01-31 | 40 | 20.4205 | 10.6195 | 31.0399 | 1.676 | 0.76558 | 0.23075 | 2.6723 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-01-31 | 41 | 20.3602 | 10.2163 | 30.5765 | 1.6263 | 0.76558 | 0.22731 | 2.6192 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-01-31 | 42 | 20.2761 | 9.9459 | 30.2219 | 1.5888 | 0.76558 | 0.22467 | 2.5791 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-01-31 | 43 | 20.2306 | 9.8841 | 30.1147 | 1.5776 | 0.76558 | 0.22388 | 2.567 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-01-31 | 44 | 20.9887 | 10.0478 | 31.0365 | 1.6756 | 0.76558 | 0.23073 | 2.6719 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-01-31 | 45 | 20.4766 | 9.8348 | 30.3115 | 1.5983 | 0.76558 | 0.22534 | 2.5892 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2011-01-31 | 46 | 19.1586 | 8.8842 | 28.0428 | 1.368 | 0.76558 | 0.20847 | 2.342 | 8.352% | 8.886% | 6.005% | 1.0911 | 1.0975 | 1.0639
2011-01-31 | 47 | 17.531 | 8.5179 | 26.0489 | 1.1804 | 0.76558 | 0.19365 | 2.1396 | 8.214% | 8.739% | 5.906% | 1.0895 | 1.0958 | 1.0628
2011-01-31 | 48 | 15.9108 | 8.513 | 24.4238 | 1.0377 | 0.76558 | 0.18157 | 1.9848 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2011-02-01 | 1 | 14.3045 | 7.7161 | 22.0206 | 0.84352 | 0.76558 | 0.1637 | 1.7728 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-02-01 | 2 | 13.2848 | 7.2524 | 20.5373 | 0.7337 | 0.76558 | 0.15268 | 1.652 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-01 | 3 | 12.515 | 6.9665 | 19.4815 | 0.6602 | 0.76558 | 0.14483 | 1.5706 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-02-01 | 4 | 11.9347 | 6.714 | 18.6487 | 0.60497 | 0.76558 | 0.13864 | 1.5092 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-01 | 5 | 11.5765 | 6.658 | 18.2345 | 0.57839 | 0.76558 | 0.13556 | 1.4795 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-01 | 6 | 11.3144 | 6.6304 | 17.9448 | 0.56016 | 0.76558 | 0.1334 | 1.4591 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-01 | 7 | 10.72 | 6.5988 | 17.3188 | 0.52176 | 0.76558 | 0.12875 | 1.4161 | 8.177% | 8.7% | 5.879% | 1.089 | 1.0953 | 1.0625
2011-02-01 | 8 | 10.6701 | 6.5149 | 17.1851 | 0.51373 | 0.76558 | 0.12776 | 1.4071 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2011-02-01 | 9 | 10.896 | 6.5996 | 17.4956 | 0.53247 | 0.76558 | 0.13006 | 1.4281 | 8.163% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2011-02-01 | 10 | 11.2778 | 6.4784 | 17.7562 | 0.54845 | 0.76558 | 0.132 | 1.446 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2011-02-01 | 11 | 11.638 | 6.4749 | 18.113 | 0.57071 | 0.76558 | 0.13465 | 1.4709 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-01 | 12 | 11.9477 | 6.7989 | 18.7467 | 0.61134 | 0.76558 | 0.13936 | 1.5163 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-02-01 | 13 | 13.186 | 7.4207 | 20.6067 | 0.73867 | 0.76558 | 0.15319 | 1.6574 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-01 | 14 | 14.6901 | 8.0789 | 22.769 | 0.90183 | 0.76558 | 0.16927 | 1.8367 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-02-01 | 15 | 17.2522 | 9.2301 | 26.4823 | 1.22 | 0.76558 | 0.19687 | 2.1824 | 8.241% | 8.768% | 5.925% | 1.0898 | 1.0961 | 1.063
2011-02-01 | 16 | 19.0826 | 9.8799 | 28.9625 | 1.4592 | 0.76558 | 0.21531 | 2.4401 | 8.425% | 8.964% | 6.058% | 1.092 | 1.0985 | 1.0645
2011-02-01 | 17 | 21.0919 | 10.7209 | 31.8128 | 1.7605 | 0.76558 | 0.2365 | 2.7626 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-02-01 | 18 | 22.2069 | 11.1944 | 33.4013 | 1.9407 | 0.76558 | 0.24831 | 2.9546 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-02-01 | 19 | 22.5431 | 11.3578 | 33.9008 | 1.9992 | 0.76558 | 0.25202 | 3.0168 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2011-02-01 | 20 | 22.4189 | 11.3335 | 33.7524 | 1.9817 | 0.76558 | 0.25092 | 2.9982 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-02-01 | 21 | 22.2934 | 11.171 | 33.4644 | 1.9481 | 0.76558 | 0.24878 | 2.9624 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2011-02-01 | 22 | 21.8761 | 11.2695 | 33.1455 | 1.9111 | 0.76558 | 0.24641 | 2.9231 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1036 | 1.0677
2011-02-01 | 23 | 21.3443 | 11.0945 | 32.4387 | 1.8305 | 0.76558 | 0.24115 | 2.8372 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-02-01 | 24 | 21.1184 | 11.0889 | 32.2073 | 1.8044 | 0.76558 | 0.23943 | 2.8095 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-01 | 25 | 21.0706 | 11.0513 | 32.1219 | 1.7949 | 0.76558 | 0.2388 | 2.7993 | 8.714% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2011-02-01 | 26 | 20.7008 | 10.7976 | 31.4984 | 1.7259 | 0.76558 | 0.23416 | 2.7256 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-02-01 | 27 | 20.4393 | 10.8044 | 31.2436 | 1.6981 | 0.76558 | 0.23227 | 2.6959 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-02-01 | 28 | 20.3094 | 11.2689 | 31.5784 | 1.7347 | 0.76558 | 0.23476 | 2.735 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-02-01 | 29 | 20.0178 | 11.4011 | 31.4189 | 1.7172 | 0.76558 | 0.23357 | 2.7163 | 8.646% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-02-01 | 30 | 20.0822 | 11.4757 | 31.5579 | 1.7324 | 0.76558 | 0.23461 | 2.7326 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-02-01 | 31 | 20.0008 | 11.8002 | 31.801 | 1.7592 | 0.76558 | 0.23641 | 2.7612 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-02-01 | 32 | 19.9493 | 12.2707 | 32.22 | 1.8059 | 0.76558 | 0.23953 | 2.811 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-02-01 | 33 | 19.9558 | 13.0188 | 32.9746 | 1.8914 | 0.76558 | 0.24514 | 2.9022 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-02-01 | 34 | 20.2441 | 13.219 | 33.4631 | 1.9479 | 0.76558 | 0.24877 | 2.9622 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2011-02-01 | 35 | 20.1604 | 13.5304 | 33.6909 | 1.9745 | 0.76558 | 0.25046 | 2.9905 | 8.876% | 9.445% | 6.382% | 1.0974 | 1.1043 | 1.0682
2011-02-01 | 36 | 20.4748 | 13.9213 | 34.396 | 2.058 | 0.76558 | 0.2557 | 3.0793 | 8.953% | 9.525% | 6.437% | 1.0983 | 1.1053 | 1.0688
2011-02-01 | 37 | 20.9631 | 13.72 | 34.683 | 2.0925 | 0.76558 | 0.25784 | 3.1159 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2011-02-01 | 38 | 21.109 | 13.5667 | 34.6757 | 2.0916 | 0.76558 | 0.25778 | 3.115 | 8.983% | 9.558% | 6.459% | 1.0987 | 1.1057 | 1.069
2011-02-01 | 39 | 21.3368 | 13.4093 | 34.7461 | 2.1001 | 0.76558 | 0.25831 | 3.124 | 8.991% | 9.566% | 6.465% | 1.0988 | 1.1058 | 1.0691
2011-02-01 | 40 | 21.2208 | 12.7345 | 33.9553 | 2.0056 | 0.76558 | 0.25243 | 3.0236 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-02-01 | 41 | 20.8829 | 11.619 | 32.5019 | 1.8376 | 0.76558 | 0.24162 | 2.8448 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-02-01 | 42 | 20.7449 | 11.231 | 31.9759 | 1.7786 | 0.76558 | 0.23771 | 2.7819 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-02-01 | 43 | 20.3312 | 11.2239 | 31.5551 | 1.7321 | 0.76558 | 0.23458 | 2.7323 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-02-01 | 44 | 20.8114 | 11.1284 | 31.9398 | 1.7746 | 0.76558 | 0.23744 | 2.7776 | 8.696% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2011-02-01 | 45 | 20.679 | 10.9196 | 31.5986 | 1.7369 | 0.76558 | 0.23491 | 2.7374 | 8.663% | 9.217% | 6.229% | 1.0948 | 1.1015 | 1.0664
2011-02-01 | 46 | 19.2811 | 10.0566 | 29.3376 | 1.4972 | 0.76558 | 0.2181 | 2.4809 | 8.456% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2011-02-01 | 47 | 17.6413 | 9.5097 | 27.151 | 1.2824 | 0.76558 | 0.20184 | 2.2498 | 8.286% | 8.816% | 5.958% | 1.0903 | 1.0967 | 1.0634
2011-02-01 | 48 | 16.0072 | 8.9169 | 24.9241 | 1.0806 | 0.76558 | 0.18529 | 2.0315 | 8.151% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0623
2011-02-02 | 1 | 14.4369 | 8.1854 | 22.6223 | 0.89024 | 0.76558 | 0.16818 | 1.824 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-02-02 | 2 | 13.2909 | 7.8594 | 21.1504 | 0.77816 | 0.76558 | 0.15723 | 1.701 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-02 | 3 | 12.4668 | 7.5896 | 20.0564 | 0.69975 | 0.76558 | 0.1491 | 1.6144 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-02-02 | 4 | 11.7889 | 7.3835 | 19.1723 | 0.63942 | 0.76558 | 0.14253 | 1.5475 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-02-02 | 5 | 11.2024 | 7.313 | 18.5154 | 0.59635 | 0.76558 | 0.13765 | 1.4996 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-02 | 6 | 11.2268 | 7.162 | 18.3889 | 0.58823 | 0.76558 | 0.13671 | 1.4905 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-02 | 7 | 11.0708 | 7.2505 | 18.3213 | 0.58391 | 0.76558 | 0.1362 | 1.4857 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-02-02 | 8 | 11.0067 | 6.957 | 17.9637 | 0.56134 | 0.76558 | 0.13354 | 1.4605 | 8.13% | 8.65% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-02 | 9 | 11.1068 | 6.6755 | 17.7823 | 0.55006 | 0.76558 | 0.1322 | 1.4478 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-02-02 | 10 | 11.1687 | 6.8252 | 17.9939 | 0.56323 | 0.76558 | 0.13377 | 1.4626 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-02 | 11 | 11.2767 | 7.1018 | 18.3785 | 0.58756 | 0.76558 | 0.13663 | 1.4898 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-02 | 12 | 11.5062 | 7.4601 | 18.9664 | 0.62575 | 0.76558 | 0.141 | 1.5323 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-02 | 13 | 13.0621 | 7.8468 | 20.909 | 0.7605 | 0.76558 | 0.15544 | 1.6815 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-02 | 14 | 14.7902 | 8.5205 | 23.3107 | 0.94525 | 0.76558 | 0.17329 | 1.8841 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-02-02 | 15 | 17.4003 | 9.8732 | 27.2735 | 1.2939 | 0.76558 | 0.20275 | 2.2623 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2011-02-02 | 16 | 19.3507 | 10.9945 | 30.3452 | 1.6018 | 0.76558 | 0.22559 | 2.593 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-02-02 | 17 | 20.7948 | 11.4446 | 32.2395 | 1.8081 | 0.76558 | 0.23967 | 2.8133 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1024 | 1.0669
2011-02-02 | 18 | 21.6166 | 11.4326 | 33.0492 | 1.9 | 0.76558 | 0.24569 | 2.9113 | 8.809% | 9.373% | 6.334% | 1.0966 | 1.1034 | 1.0676
2011-02-02 | 19 | 22.0167 | 11.44 | 33.4568 | 1.9472 | 0.76558 | 0.24872 | 2.9615 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-02-02 | 20 | 21.7707 | 11.4164 | 33.1871 | 1.9159 | 0.76558 | 0.24672 | 2.9282 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2011-02-02 | 21 | 21.7342 | 11.4878 | 33.222 | 1.9199 | 0.76558 | 0.24698 | 2.9325 | 8.827% | 9.392% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-02-02 | 22 | 21.4439 | 11.6471 | 33.091 | 1.9048 | 0.76558 | 0.246 | 2.9164 | 8.813% | 9.377% | 6.337% | 1.0967 | 1.1035 | 1.0677
2011-02-02 | 23 | 21.1458 | 11.7843 | 32.9302 | 1.8864 | 0.76558 | 0.24481 | 2.8967 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2011-02-02 | 24 | 21.0058 | 11.8796 | 32.8854 | 1.8812 | 0.76558 | 0.24447 | 2.8913 | 8.792% | 9.355% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-02-02 | 25 | 20.8237 | 11.8978 | 32.7215 | 1.8625 | 0.76558 | 0.24326 | 2.8714 | 8.775% | 9.337% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-02-02 | 26 | 20.5105 | 11.7354 | 32.2459 | 1.8088 | 0.76558 | 0.23972 | 2.8141 | 8.727% | 9.285% | 6.275% | 1.0956 | 1.1024 | 1.0669
2011-02-02 | 27 | 20.4949 | 12.4343 | 32.9292 | 1.8862 | 0.76558 | 0.2448 | 2.8966 | 8.797% | 9.359% | 6.325% | 1.0964 | 1.1033 | 1.0675
2011-02-02 | 28 | 20.2747 | 12.9901 | 33.2648 | 1.9249 | 0.76558 | 0.24729 | 2.9378 | 8.831% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-02-02 | 29 | 20.1504 | 12.9375 | 33.0879 | 1.9045 | 0.76558 | 0.24598 | 2.916 | 8.813% | 9.377% | 6.337% | 1.0966 | 1.1035 | 1.0677
2011-02-02 | 30 | 19.9945 | 12.9827 | 32.9772 | 1.8917 | 0.76558 | 0.24516 | 2.9025 | 8.801% | 9.365% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-02-02 | 31 | 20.2262 | 13.4817 | 33.7079 | 1.9765 | 0.76558 | 0.25059 | 2.9927 | 8.878% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-02-02 | 32 | 20.0323 | 13.7091 | 33.7414 | 1.9804 | 0.76558 | 0.25084 | 2.9969 | 8.882% | 9.45% | 6.386% | 1.0975 | 1.1044 | 1.0682
2011-02-02 | 33 | 20.2604 | 14.087 | 34.3474 | 2.0522 | 0.76558 | 0.25534 | 3.0731 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2011-02-02 | 34 | 20.5182 | 14.2391 | 34.7573 | 2.1015 | 0.76558 | 0.25839 | 3.1255 | 8.992% | 9.568% | 6.465% | 1.0988 | 1.1058 | 1.0691
2011-02-02 | 35 | 20.4307 | 14.1914 | 34.6222 | 2.0852 | 0.76558 | 0.25739 | 3.1081 | 8.977% | 9.552% | 6.455% | 1.0986 | 1.1056 | 1.069
2011-02-02 | 36 | 20.8863 | 13.7021 | 34.5884 | 2.0811 | 0.76558 | 0.25713 | 3.1038 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2011-02-02 | 37 | 21.2162 | 13.8343 | 35.0506 | 2.1371 | 0.76558 | 0.26057 | 3.1632 | 9.025% | 9.602% | 6.489% | 1.0992 | 1.1062 | 1.0694
2011-02-02 | 38 | 21.4062 | 13.7292 | 35.1354 | 2.1475 | 0.76558 | 0.2612 | 3.1742 | 9.034% | 9.612% | 6.496% | 1.0993 | 1.1063 | 1.0695
2011-02-02 | 39 | 21.3958 | 13.3117 | 34.7075 | 2.0955 | 0.76558 | 0.25802 | 3.1191 | 8.987% | 9.562% | 6.461% | 1.0987 | 1.1057 | 1.0691
2011-02-02 | 40 | 21.0553 | 12.5031 | 33.5584 | 1.959 | 0.76558 | 0.24948 | 2.9741 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2011-02-02 | 41 | 20.4872 | 11.5337 | 32.021 | 1.7836 | 0.76558 | 0.23805 | 2.7873 | 8.704% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2011-02-02 | 42 | 20.5754 | 11.5698 | 32.1451 | 1.7975 | 0.76558 | 0.23897 | 2.802 | 8.717% | 9.275% | 6.267% | 1.0955 | 1.1022 | 1.0669
2011-02-02 | 43 | 20.7914 | 11.4175 | 32.2089 | 1.8046 | 0.76558 | 0.23944 | 2.8096 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-02 | 44 | 21.4098 | 11.4909 | 32.9006 | 1.883 | 0.76558 | 0.24459 | 2.8931 | 8.794% | 9.356% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-02-02 | 45 | 20.6679 | 11.047 | 31.7148 | 1.7497 | 0.76558 | 0.23577 | 2.751 | 8.674% | 9.229% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-02 | 46 | 19.3517 | 10.0907 | 29.4424 | 1.5079 | 0.76558 | 0.21888 | 2.4924 | 8.465% | 9.007% | 6.087% | 1.0925 | 1.099 | 1.0648
2011-02-02 | 47 | 17.5915 | 9.5809 | 27.1724 | 1.2844 | 0.76558 | 0.202 | 2.252 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2011-02-02 | 48 | 15.9814 | 9.4339 | 25.4153 | 1.1236 | 0.76558 | 0.18894 | 2.0782 | 8.177% | 8.7% | 5.879% | 1.089 | 1.0953 | 1.0625
2011-02-03 | 1 | 14.3036 | 8.4949 | 22.7985 | 0.90416 | 0.76558 | 0.16949 | 1.8392 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2011-02-03 | 2 | 13.1881 | 7.9213 | 21.1094 | 0.77515 | 0.76558 | 0.15693 | 1.6977 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-03 | 3 | 12.0742 | 7.5269 | 19.601 | 0.66833 | 0.76558 | 0.14572 | 1.5796 | 8.059% | 8.575% | 5.794% | 1.0877 | 1.0938 | 1.0615
2011-02-03 | 4 | 11.6081 | 7.216 | 18.824 | 0.6164 | 0.76558 | 0.13994 | 1.5219 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-03 | 5 | 11.4501 | 7.2156 | 18.6657 | 0.60607 | 0.76558 | 0.13876 | 1.5104 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-02-03 | 6 | 11.3202 | 7.1268 | 18.447 | 0.59195 | 0.76558 | 0.13714 | 1.4947 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-02-03 | 7 | 11.4061 | 7.1399 | 18.5459 | 0.59832 | 0.76558 | 0.13787 | 1.5018 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-03 | 8 | 11.258 | 7.0747 | 18.3327 | 0.58464 | 0.76558 | 0.13629 | 1.4865 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-02-03 | 9 | 11.1796 | 7.1231 | 18.3027 | 0.58273 | 0.76558 | 0.13606 | 1.4844 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-03 | 10 | 11.2036 | 7.1427 | 18.3463 | 0.58551 | 0.76558 | 0.13639 | 1.4875 | 8.108% | 8.627% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-02-03 | 11 | 11.1355 | 7.3713 | 18.5068 | 0.59579 | 0.76558 | 0.13758 | 1.499 | 8.099% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-02-03 | 12 | 11.5856 | 7.5096 | 19.0952 | 0.63429 | 0.76558 | 0.14196 | 1.5418 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-02-03 | 13 | 13.1193 | 7.9598 | 21.0791 | 0.77293 | 0.76558 | 0.1567 | 1.6952 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-03 | 14 | 14.6491 | 8.7201 | 23.3692 | 0.95 | 0.76558 | 0.17373 | 1.8893 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-03 | 15 | 17.1736 | 10.001 | 27.1746 | 1.2846 | 0.76558 | 0.20202 | 2.2522 | 8.288% | 8.818% | 5.959% | 1.0904 | 1.0967 | 1.0634
2011-02-03 | 16 | 19.2597 | 10.9132 | 30.1729 | 1.5837 | 0.76558 | 0.22431 | 2.5736 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2011-02-03 | 17 | 20.8843 | 11.4936 | 32.3779 | 1.8236 | 0.76558 | 0.2407 | 2.8299 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-02-03 | 18 | 21.7486 | 11.6165 | 33.3651 | 1.9365 | 0.76558 | 0.24804 | 2.9501 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-02-03 | 19 | 21.718 | 11.4992 | 33.2172 | 1.9194 | 0.76558 | 0.24694 | 2.9319 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2011-02-03 | 20 | 21.4241 | 11.4972 | 32.9213 | 1.8853 | 0.76558 | 0.24474 | 2.8957 | 8.796% | 9.359% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-02-03 | 21 | 21.4717 | 11.4087 | 32.8804 | 1.8806 | 0.76558 | 0.24444 | 2.8907 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-02-03 | 22 | 21.5989 | 11.5463 | 33.1452 | 1.9111 | 0.76558 | 0.24641 | 2.9231 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2011-02-03 | 23 | 21.4086 | 11.34 | 32.7486 | 1.8656 | 0.76558 | 0.24346 | 2.8746 | 8.778% | 9.34% | 6.311% | 1.0962 | 1.103 | 1.0674
2011-02-03 | 24 | 21.4543 | 11.2122 | 32.6665 | 1.8563 | 0.76558 | 0.24285 | 2.8647 | 8.77% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-02-03 | 25 | 21.1661 | 11.2721 | 32.4382 | 1.8304 | 0.76558 | 0.24115 | 2.8371 | 8.746% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-02-03 | 26 | 20.9377 | 11.2043 | 32.142 | 1.7971 | 0.76558 | 0.23895 | 2.8017 | 8.717% | 9.274% | 6.267% | 1.0955 | 1.1022 | 1.0669
2011-02-03 | 27 | 20.8555 | 11.7419 | 32.5974 | 1.8484 | 0.76558 | 0.24233 | 2.8563 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-02-03 | 28 | 20.8254 | 12.4682 | 33.2936 | 1.9282 | 0.76558 | 0.24751 | 2.9413 | 8.834% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2011-02-03 | 29 | 20.9455 | 12.2046 | 33.1501 | 1.9116 | 0.76558 | 0.24644 | 2.9237 | 8.819% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2011-02-03 | 30 | 20.8875 | 12.3492 | 33.2367 | 1.9216 | 0.76558 | 0.24709 | 2.9343 | 8.828% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-02-03 | 31 | 20.7469 | 12.4596 | 33.2065 | 1.9181 | 0.76558 | 0.24686 | 2.9306 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0678
2011-02-03 | 32 | 20.9354 | 12.5925 | 33.5279 | 1.9555 | 0.76558 | 0.24925 | 2.9703 | 8.859% | 9.426% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-02-03 | 33 | 21.0151 | 12.9948 | 34.0099 | 2.0121 | 0.76558 | 0.25283 | 3.0305 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2011-02-03 | 34 | 21.6284 | 13.2043 | 34.8327 | 2.1106 | 0.76558 | 0.25895 | 3.1351 | 9.001% | 9.577% | 6.471% | 1.0989 | 1.1059 | 1.0692
2011-02-03 | 35 | 21.4561 | 13.4533 | 34.9094 | 2.1199 | 0.76558 | 0.25952 | 3.145 | 9.009% | 9.586% | 6.478% | 1.099 | 1.106 | 1.0693
2011-02-03 | 36 | 21.7259 | 13.541 | 35.2669 | 2.1636 | 0.76558 | 0.26218 | 3.1913 | 9.049% | 9.628% | 6.506% | 1.0995 | 1.1065 | 1.0696
2011-02-03 | 37 | 22.2058 | 13.358 | 35.5638 | 2.2001 | 0.76558 | 0.26439 | 3.2301 | 9.083% | 9.664% | 6.53% | 1.0999 | 1.107 | 1.0699
2011-02-03 | 38 | 22.1016 | 13.1348 | 35.2363 | 2.1598 | 0.76558 | 0.26195 | 3.1873 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2011-02-03 | 39 | 22.2574 | 12.5858 | 34.8432 | 2.1119 | 0.76558 | 0.25903 | 3.1365 | 9.002% | 9.578% | 6.472% | 1.0989 | 1.1059 | 1.0692
2011-02-03 | 40 | 22.0283 | 11.9245 | 33.9528 | 2.0053 | 0.76558 | 0.25241 | 3.0233 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-02-03 | 41 | 21.5705 | 11.6658 | 33.2363 | 1.9216 | 0.76558 | 0.24708 | 2.9343 | 8.828% | 9.393% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-02-03 | 42 | 21.0929 | 11.3504 | 32.4433 | 1.831 | 0.76558 | 0.24119 | 2.8378 | 8.747% | 9.307% | 6.289% | 1.0959 | 1.1026 | 1.0671
2011-02-03 | 43 | 21.0486 | 11.3314 | 32.3799 | 1.8238 | 0.76558 | 0.24072 | 2.8301 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-02-03 | 44 | 21.4984 | 11.4748 | 32.9731 | 1.8913 | 0.76558 | 0.24513 | 2.902 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-02-03 | 45 | 20.7245 | 11.1538 | 31.8783 | 1.7678 | 0.76558 | 0.23699 | 2.7703 | 8.69% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-02-03 | 46 | 19.1644 | 10.2158 | 29.3802 | 1.5016 | 0.76558 | 0.21842 | 2.4856 | 8.46% | 9.001% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-02-03 | 47 | 17.7203 | 9.7568 | 27.4771 | 1.3133 | 0.76558 | 0.20427 | 2.2832 | 8.309% | 8.841% | 5.974% | 1.0906 | 1.097 | 1.0635
2011-02-03 | 48 | 16.1428 | 9.5859 | 25.7287 | 1.1515 | 0.76558 | 0.19127 | 2.1084 | 8.195% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2011-02-04 | 1 | 14.6009 | 8.6902 | 23.2911 | 0.94366 | 0.76558 | 0.17315 | 1.8824 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-02-04 | 2 | 13.3629 | 8.222 | 21.5849 | 0.81046 | 0.76558 | 0.16046 | 1.7365 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-04 | 3 | 12.6611 | 7.9311 | 20.5922 | 0.73763 | 0.76558 | 0.15309 | 1.6563 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-04 | 4 | 12.1212 | 7.8656 | 19.9867 | 0.69489 | 0.76558 | 0.14858 | 1.6091 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-02-04 | 5 | 11.5268 | 7.7711 | 19.2979 | 0.64782 | 0.76558 | 0.14346 | 1.5569 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-04 | 6 | 11.3212 | 7.4954 | 18.8166 | 0.61591 | 0.76558 | 0.13988 | 1.5214 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-04 | 7 | 11.4993 | 7.3796 | 18.8789 | 0.62 | 0.76558 | 0.14035 | 1.5259 | 8.083% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-02-04 | 8 | 11.3194 | 7.2394 | 18.5588 | 0.59915 | 0.76558 | 0.13797 | 1.5027 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-04 | 9 | 11.1475 | 7.2979 | 18.4454 | 0.59185 | 0.76558 | 0.13713 | 1.4946 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-02-04 | 10 | 11.4398 | 7.3825 | 18.8223 | 0.61628 | 0.76558 | 0.13993 | 1.5218 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-04 | 11 | 11.6515 | 7.4233 | 19.0749 | 0.63293 | 0.76558 | 0.1418 | 1.5403 | 8.075% | 8.592% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-02-04 | 12 | 11.7818 | 7.7117 | 19.4934 | 0.66102 | 0.76558 | 0.14492 | 1.5715 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-04 | 13 | 13.1213 | 8.4121 | 21.5334 | 0.8066 | 0.76558 | 0.16008 | 1.7323 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-04 | 14 | 14.931 | 9.3786 | 24.3096 | 1.028 | 0.76558 | 0.18072 | 1.9743 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-04 | 15 | 17.779 | 10.7152 | 28.4941 | 1.4124 | 0.76558 | 0.21183 | 2.3898 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2011-02-04 | 16 | 19.8372 | 11.4952 | 31.3324 | 1.7077 | 0.76558 | 0.23293 | 2.7062 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2011-02-04 | 17 | 20.9593 | 11.6725 | 32.6318 | 1.8523 | 0.76558 | 0.24259 | 2.8605 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-02-04 | 18 | 21.3594 | 11.7359 | 33.0953 | 1.9053 | 0.76558 | 0.24603 | 2.9169 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2011-02-04 | 19 | 21.4494 | 11.6339 | 33.0832 | 1.9039 | 0.76558 | 0.24594 | 2.9155 | 8.812% | 9.376% | 6.336% | 1.0966 | 1.1035 | 1.0676
2011-02-04 | 20 | 21.5694 | 11.6263 | 33.1957 | 1.9169 | 0.76558 | 0.24678 | 2.9293 | 8.824% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2011-02-04 | 21 | 21.6308 | 11.6776 | 33.3084 | 1.9299 | 0.76558 | 0.24762 | 2.9431 | 8.836% | 9.402% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-02-04 | 22 | 21.4566 | 11.8398 | 33.2964 | 1.9285 | 0.76558 | 0.24753 | 2.9417 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2011-02-04 | 23 | 21.3025 | 11.8968 | 33.1993 | 1.9173 | 0.76558 | 0.24681 | 2.9297 | 8.825% | 9.389% | 6.345% | 1.0968 | 1.1036 | 1.0677
2011-02-04 | 24 | 21.2367 | 11.9834 | 33.2201 | 1.9197 | 0.76558 | 0.24696 | 2.9322 | 8.827% | 9.392% | 6.346% | 1.0968 | 1.1037 | 1.0678
2011-02-04 | 25 | 20.9865 | 12.0464 | 33.0329 | 1.8981 | 0.76558 | 0.24557 | 2.9093 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2011-02-04 | 26 | 20.9881 | 11.8798 | 32.8679 | 1.8792 | 0.76558 | 0.24434 | 2.8891 | 8.79% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-02-04 | 27 | 20.9756 | 12.3197 | 33.2953 | 1.9284 | 0.76558 | 0.24752 | 2.9415 | 8.835% | 9.4% | 6.352% | 1.0969 | 1.1038 | 1.0678
2011-02-04 | 28 | 21.1216 | 12.6371 | 33.7586 | 1.9825 | 0.76558 | 0.25097 | 2.999 | 8.884% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-02-04 | 29 | 21.0854 | 12.6618 | 33.7472 | 1.9811 | 0.76558 | 0.25088 | 2.9976 | 8.882% | 9.451% | 6.386% | 1.0975 | 1.1044 | 1.0682
2011-02-04 | 30 | 20.8817 | 12.8889 | 33.7706 | 1.9839 | 0.76558 | 0.25105 | 3.0005 | 8.885% | 9.454% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-02-04 | 31 | 20.9057 | 13.0466 | 33.9523 | 2.0053 | 0.76558 | 0.25241 | 3.0233 | 8.904% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-02-04 | 32 | 21.1791 | 13.3788 | 34.5579 | 2.0774 | 0.76558 | 0.25691 | 3.0999 | 8.97% | 9.544% | 6.45% | 1.0985 | 1.1055 | 1.0689
2011-02-04 | 33 | 21.3945 | 13.9383 | 35.3328 | 2.1716 | 0.76558 | 0.26267 | 3.1999 | 9.056% | 9.636% | 6.512% | 1.0996 | 1.1066 | 1.0697
2011-02-04 | 34 | 21.5146 | 13.4983 | 35.0129 | 2.1325 | 0.76558 | 0.26029 | 3.1584 | 9.021% | 9.598% | 6.486% | 1.0992 | 1.1062 | 1.0694
2011-02-04 | 35 | 21.3407 | 13.4235 | 34.7642 | 2.1023 | 0.76558 | 0.25844 | 3.1263 | 8.993% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2011-02-04 | 36 | 21.4805 | 13.484 | 34.9644 | 2.1266 | 0.76558 | 0.25993 | 3.1521 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-02-04 | 37 | 22.0883 | 13.717 | 35.8053 | 2.2301 | 0.76558 | 0.26618 | 3.2619 | 9.11% | 9.693% | 6.55% | 1.1002 | 1.1073 | 1.0701
2011-02-04 | 38 | 22.5082 | 13.5727 | 36.0809 | 2.2646 | 0.76558 | 0.26823 | 3.2984 | 9.142% | 9.727% | 6.573% | 1.1006 | 1.1077 | 1.0704
2011-02-04 | 39 | 22.2764 | 13.2228 | 35.4992 | 2.1922 | 0.76558 | 0.26391 | 3.2216 | 9.075% | 9.656% | 6.525% | 1.0998 | 1.1069 | 1.0698
2011-02-04 | 40 | 21.8228 | 12.565 | 34.3878 | 2.057 | 0.76558 | 0.25564 | 3.0783 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-02-04 | 41 | 21.3087 | 12.0413 | 33.35 | 1.9348 | 0.76558 | 0.24793 | 2.9483 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-02-04 | 42 | 20.7743 | 11.8707 | 32.645 | 1.8538 | 0.76558 | 0.24269 | 2.8621 | 8.767% | 9.328% | 6.304% | 1.0961 | 1.1029 | 1.0673
2011-02-04 | 43 | 20.7764 | 11.7295 | 32.5059 | 1.8381 | 0.76558 | 0.24165 | 2.8453 | 8.753% | 9.313% | 6.294% | 1.0959 | 1.1027 | 1.0672
2011-02-04 | 44 | 21.2766 | 11.736 | 33.0126 | 1.8958 | 0.76558 | 0.24542 | 2.9068 | 8.805% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2011-02-04 | 45 | 20.7891 | 11.2361 | 32.0252 | 1.7841 | 0.76558 | 0.23808 | 2.7877 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2011-02-04 | 46 | 19.4471 | 10.4568 | 29.9039 | 1.5556 | 0.76558 | 0.22231 | 2.5435 | 8.505% | 9.05% | 6.115% | 1.093 | 1.0995 | 1.0651
2011-02-04 | 47 | 17.7392 | 10.0193 | 27.7585 | 1.3404 | 0.76558 | 0.20636 | 2.3123 | 8.33% | 8.863% | 5.989% | 1.0909 | 1.0973 | 1.0637
2011-02-04 | 48 | 16.1834 | 10.054 | 26.2374 | 1.1975 | 0.76558 | 0.19505 | 2.1581 | 8.225% | 8.752% | 5.914% | 1.0896 | 1.0959 | 1.0629
2011-02-05 | 1 | 14.7203 | 9.1372 | 23.8575 | 0.99011 | 0.76558 | 0.17736 | 1.933 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-02-05 | 2 | 13.4281 | 8.5162 | 21.9443 | 0.83768 | 0.76558 | 0.16314 | 1.7664 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-02-05 | 3 | 12.5918 | 8.1743 | 20.7662 | 0.75015 | 0.76558 | 0.15438 | 1.6701 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-05 | 4 | 12.17 | 7.897 | 20.0671 | 0.70049 | 0.76558 | 0.14918 | 1.6152 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-05 | 5 | 12.0702 | 7.8846 | 19.9548 | 0.69267 | 0.76558 | 0.14835 | 1.6066 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-02-05 | 6 | 11.736 | 7.7984 | 19.5344 | 0.6638 | 0.76558 | 0.14522 | 1.5746 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-05 | 7 | 11.5661 | 7.8432 | 19.4093 | 0.65532 | 0.76558 | 0.14429 | 1.5652 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-02-05 | 8 | 11.368 | 7.7707 | 19.1386 | 0.63717 | 0.76558 | 0.14228 | 1.545 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-02-05 | 9 | 11.4461 | 7.971 | 19.4171 | 0.65585 | 0.76558 | 0.14435 | 1.5658 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-02-05 | 10 | 11.3799 | 7.9819 | 19.3618 | 0.65212 | 0.76558 | 0.14394 | 1.5616 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-02-05 | 11 | 11.578 | 8.1539 | 19.7319 | 0.67729 | 0.76558 | 0.14669 | 1.5896 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-02-05 | 12 | 12.1761 | 8.1944 | 20.3705 | 0.72184 | 0.76558 | 0.15144 | 1.6389 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-05 | 13 | 13.3303 | 8.7182 | 22.0485 | 0.84565 | 0.76558 | 0.16391 | 1.7751 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-02-05 | 14 | 14.9164 | 9.4492 | 24.3656 | 1.0327 | 0.76558 | 0.18114 | 1.9795 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-02-05 | 15 | 17.7806 | 10.5653 | 28.3459 | 1.3977 | 0.76558 | 0.21073 | 2.374 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-02-05 | 16 | 19.9587 | 11.4963 | 31.4551 | 1.7211 | 0.76558 | 0.23384 | 2.7206 | 8.649% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-02-05 | 17 | 21.2548 | 11.9484 | 33.2032 | 1.9178 | 0.76558 | 0.24684 | 2.9302 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0678
2011-02-05 | 18 | 21.6384 | 12.153 | 33.7914 | 1.9863 | 0.76558 | 0.25121 | 3.0031 | 8.887% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2011-02-05 | 19 | 21.7423 | 12.3921 | 34.1344 | 2.0268 | 0.76558 | 0.25376 | 3.0462 | 8.924% | 9.495% | 6.416% | 1.098 | 1.1049 | 1.0686
2011-02-05 | 20 | 21.6364 | 12.4167 | 34.0531 | 2.0172 | 0.76558 | 0.25316 | 3.0359 | 8.915% | 9.486% | 6.41% | 1.0979 | 1.1048 | 1.0685
2011-02-05 | 21 | 21.6651 | 12.0676 | 33.7327 | 1.9794 | 0.76558 | 0.25077 | 2.9958 | 8.881% | 9.449% | 6.385% | 1.0975 | 1.1044 | 1.0682
2011-02-05 | 22 | 21.4458 | 12.3492 | 33.795 | 1.9867 | 0.76558 | 0.25124 | 3.0036 | 8.888% | 9.456% | 6.39% | 1.0975 | 1.1044 | 1.0683
2011-02-05 | 23 | 21.3356 | 12.1786 | 33.5142 | 1.9539 | 0.76558 | 0.24915 | 2.9686 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2011-02-05 | 24 | 21.3821 | 12.1309 | 33.5129 | 1.9537 | 0.76558 | 0.24914 | 2.9684 | 8.858% | 9.424% | 6.369% | 1.0972 | 1.1041 | 1.068
2011-02-05 | 25 | 21.2597 | 12.0865 | 33.3462 | 1.9343 | 0.76558 | 0.2479 | 2.9478 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-02-05 | 26 | 21.0598 | 11.8192 | 32.879 | 1.8805 | 0.76558 | 0.24443 | 2.8905 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-02-05 | 27 | 21.1016 | 12.2574 | 33.359 | 1.9358 | 0.76558 | 0.248 | 2.9494 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-02-05 | 28 | 21.2694 | 12.794 | 34.0634 | 2.0184 | 0.76558 | 0.25323 | 3.0372 | 8.916% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2011-02-05 | 29 | 20.9526 | 12.9379 | 33.8904 | 1.998 | 0.76558 | 0.25195 | 3.0155 | 8.898% | 9.467% | 6.397% | 1.0977 | 1.1046 | 1.0683
2011-02-05 | 30 | 20.806 | 12.9718 | 33.7779 | 1.9847 | 0.76558 | 0.25111 | 3.0014 | 8.886% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-02-05 | 31 | 20.8568 | 13.3311 | 34.1879 | 2.0332 | 0.76558 | 0.25416 | 3.0529 | 8.93% | 9.501% | 6.421% | 1.0981 | 1.105 | 1.0686
2011-02-05 | 32 | 20.8466 | 13.7276 | 34.5742 | 2.0794 | 0.76558 | 0.25703 | 3.102 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2011-02-05 | 33 | 21.066 | 14.0466 | 35.1126 | 2.1447 | 0.76558 | 0.26103 | 3.1713 | 9.032% | 9.61% | 6.494% | 1.0993 | 1.1063 | 1.0694
2011-02-05 | 34 | 21.1614 | 14.0022 | 35.1636 | 2.1509 | 0.76558 | 0.26141 | 3.1779 | 9.037% | 9.616% | 6.498% | 1.0994 | 1.1064 | 1.0695
2011-02-05 | 35 | 21.0641 | 13.8068 | 34.8709 | 2.1152 | 0.76558 | 0.25923 | 3.1401 | 9.005% | 9.581% | 6.474% | 1.099 | 1.106 | 1.0692
2011-02-05 | 36 | 21.1094 | 13.3403 | 34.4497 | 2.0645 | 0.76558 | 0.2561 | 3.0861 | 8.958% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2011-02-05 | 37 | 21.5403 | 13.0913 | 34.6316 | 2.0863 | 0.76558 | 0.25746 | 3.1093 | 8.978% | 9.553% | 6.455% | 1.0986 | 1.1056 | 1.069
2011-02-05 | 38 | 21.3956 | 12.5032 | 33.8988 | 1.999 | 0.76558 | 0.25201 | 3.0165 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2011-02-05 | 39 | 21.0541 | 11.9632 | 33.0173 | 1.8963 | 0.76558 | 0.24545 | 2.9074 | 8.806% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2011-02-05 | 40 | 20.6575 | 11.3625 | 32.02 | 1.7835 | 0.76558 | 0.23804 | 2.7871 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-02-05 | 41 | 20.3305 | 11.1716 | 31.5022 | 1.7263 | 0.76558 | 0.23419 | 2.7261 | 8.654% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-02-05 | 42 | 19.7164 | 10.9922 | 30.7086 | 1.6404 | 0.76558 | 0.22829 | 2.6343 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-02-05 | 43 | 19.6733 | 10.9568 | 30.6301 | 1.632 | 0.76558 | 0.22771 | 2.6253 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2011-02-05 | 44 | 20.5105 | 10.9981 | 31.5086 | 1.727 | 0.76558 | 0.23424 | 2.7268 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-02-05 | 45 | 20.2908 | 10.5807 | 30.8714 | 1.6579 | 0.76558 | 0.2295 | 2.6529 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-05 | 46 | 18.8834 | 10.0535 | 28.9368 | 1.4566 | 0.76558 | 0.21512 | 2.4373 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-02-05 | 47 | 17.5643 | 9.7171 | 27.2814 | 1.2947 | 0.76558 | 0.20281 | 2.2631 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2011-02-05 | 48 | 16.1743 | 9.6874 | 25.8617 | 1.1635 | 0.76558 | 0.19226 | 2.1213 | 8.202% | 8.727% | 5.898% | 1.0894 | 1.0956 | 1.0627
2011-02-06 | 1 | 14.7123 | 8.8679 | 23.5802 | 0.96723 | 0.76558 | 0.1753 | 1.9081 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-02-06 | 2 | 13.6571 | 8.252 | 21.9091 | 0.835 | 0.76558 | 0.16288 | 1.7635 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-06 | 3 | 12.7879 | 7.8299 | 20.6178 | 0.73947 | 0.76558 | 0.15328 | 1.6583 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-06 | 4 | 12.0963 | 7.6152 | 19.7114 | 0.67588 | 0.76558 | 0.14654 | 1.588 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2011-02-06 | 5 | 11.6896 | 7.6226 | 19.3122 | 0.64878 | 0.76558 | 0.14357 | 1.5579 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-02-06 | 6 | 11.6279 | 7.4294 | 19.0573 | 0.63177 | 0.76558 | 0.14167 | 1.539 | 8.076% | 8.593% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-02-06 | 7 | 11.5307 | 7.2376 | 18.7683 | 0.61275 | 0.76558 | 0.13953 | 1.5179 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-02-06 | 8 | 11.197 | 7.098 | 18.2951 | 0.58224 | 0.76558 | 0.13601 | 1.4838 | 8.111% | 8.63% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-06 | 9 | 11.2807 | 7.1707 | 18.4514 | 0.59223 | 0.76558 | 0.13717 | 1.495 | 8.102% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-02-06 | 10 | 11.2228 | 7.2553 | 18.4781 | 0.59395 | 0.76558 | 0.13737 | 1.4969 | 8.101% | 8.619% | 5.825% | 1.0882 | 1.0943 | 1.0618
2011-02-06 | 11 | 11.2207 | 7.2871 | 18.5078 | 0.59586 | 0.76558 | 0.13759 | 1.499 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-06 | 12 | 11.2571 | 7.2561 | 18.5132 | 0.59621 | 0.76558 | 0.13763 | 1.4994 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-06 | 13 | 12.0778 | 7.443 | 19.5208 | 0.66287 | 0.76558 | 0.14512 | 1.5736 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-06 | 14 | 12.8731 | 7.6558 | 20.5289 | 0.7331 | 0.76558 | 0.15261 | 1.6513 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-06 | 15 | 14.4077 | 8.1248 | 22.5325 | 0.88319 | 0.76558 | 0.16751 | 1.8163 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-06 | 16 | 15.7871 | 8.8654 | 24.6525 | 1.0572 | 0.76558 | 0.18327 | 2.006 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-02-06 | 17 | 17.1962 | 9.741 | 26.9372 | 1.2622 | 0.76558 | 0.20025 | 2.2281 | 8.271% | 8.801% | 5.947% | 1.0902 | 1.0965 | 1.0632
2011-02-06 | 18 | 18.9018 | 10.4664 | 29.3682 | 1.5003 | 0.76558 | 0.21833 | 2.4842 | 8.459% | 9% | 6.082% | 1.0924 | 1.0989 | 1.0648
2011-02-06 | 19 | 20.1022 | 11.0686 | 31.1708 | 1.6902 | 0.76558 | 0.23173 | 2.6875 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-02-06 | 20 | 20.8303 | 11.2029 | 32.0332 | 1.785 | 0.76558 | 0.23814 | 2.7887 | 8.706% | 9.263% | 6.259% | 1.0954 | 1.1021 | 1.0668
2011-02-06 | 21 | 21.0916 | 11.2807 | 32.3723 | 1.823 | 0.76558 | 0.24066 | 2.8292 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-02-06 | 22 | 21.2629 | 11.5622 | 32.8251 | 1.8743 | 0.76558 | 0.24403 | 2.8839 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-02-06 | 23 | 20.7116 | 11.2854 | 31.997 | 1.781 | 0.76558 | 0.23787 | 2.7844 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-02-06 | 24 | 20.1186 | 11.1858 | 31.3044 | 1.7047 | 0.76558 | 0.23272 | 2.703 | 8.635% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-02-06 | 25 | 19.8702 | 11.0017 | 30.8719 | 1.6579 | 0.76558 | 0.22951 | 2.653 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-06 | 26 | 19.6361 | 10.709 | 30.3451 | 1.6018 | 0.76558 | 0.22559 | 2.593 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-02-06 | 27 | 19.5302 | 11.1971 | 30.7273 | 1.6424 | 0.76558 | 0.22843 | 2.6364 | 8.58% | 9.129% | 6.169% | 1.0939 | 1.1005 | 1.0657
2011-02-06 | 28 | 19.2673 | 11.61 | 30.8773 | 1.6585 | 0.76558 | 0.22955 | 2.6536 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-06 | 29 | 19.0978 | 11.7384 | 30.8362 | 1.6541 | 0.76558 | 0.22924 | 2.6489 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-02-06 | 30 | 18.7169 | 12.0514 | 30.7683 | 1.6468 | 0.76558 | 0.22874 | 2.6411 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-02-06 | 31 | 18.7819 | 12.3921 | 31.174 | 1.6905 | 0.76558 | 0.23175 | 2.6879 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-02-06 | 32 | 18.6562 | 12.3697 | 31.026 | 1.6745 | 0.76558 | 0.23065 | 2.6707 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-02-06 | 33 | 18.9213 | 12.6977 | 31.619 | 1.7391 | 0.76558 | 0.23506 | 2.7398 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-02-06 | 34 | 19.1154 | 12.1355 | 31.2509 | 1.6989 | 0.76558 | 0.23232 | 2.6968 | 8.629% | 9.182% | 6.205% | 1.0944 | 1.1011 | 1.0661
2011-02-06 | 35 | 19.1861 | 12.3101 | 31.4962 | 1.7256 | 0.76558 | 0.23415 | 2.7254 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-02-06 | 36 | 19.6988 | 12.6893 | 32.3881 | 1.8248 | 0.76558 | 0.24078 | 2.8311 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2011-02-06 | 37 | 20.0084 | 12.7597 | 32.7681 | 1.8678 | 0.76558 | 0.2436 | 2.877 | 8.78% | 9.342% | 6.313% | 1.0962 | 1.103 | 1.0674
2011-02-06 | 38 | 20.0678 | 12.1373 | 32.2051 | 1.8042 | 0.76558 | 0.23942 | 2.8092 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-06 | 39 | 19.9982 | 11.3592 | 31.3575 | 1.7105 | 0.76558 | 0.23312 | 2.7092 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2011-02-06 | 40 | 19.9925 | 11.198 | 31.1905 | 1.6923 | 0.76558 | 0.23187 | 2.6898 | 8.624% | 9.176% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-02-06 | 41 | 19.787 | 10.7096 | 30.4966 | 1.6178 | 0.76558 | 0.22672 | 2.6101 | 8.559% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2011-02-06 | 42 | 19.3194 | 10.4621 | 29.7814 | 1.5429 | 0.76558 | 0.2214 | 2.5298 | 8.495% | 9.038% | 6.108% | 1.0928 | 1.0994 | 1.065
2011-02-06 | 43 | 19.3166 | 10.5607 | 29.8773 | 1.5528 | 0.76558 | 0.22211 | 2.5405 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-02-06 | 44 | 19.7174 | 10.6925 | 30.4098 | 1.6087 | 0.76558 | 0.22607 | 2.6003 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2011-02-06 | 45 | 19.4565 | 10.6024 | 30.0589 | 1.5717 | 0.76558 | 0.22346 | 2.5608 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2011-02-06 | 46 | 18.2948 | 10.002 | 28.2967 | 1.3929 | 0.76558 | 0.21036 | 2.3688 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2011-02-06 | 47 | 17.0619 | 9.7364 | 26.7983 | 1.2492 | 0.76558 | 0.19922 | 2.214 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2011-02-06 | 48 | 15.7198 | 9.6943 | 25.4141 | 1.1235 | 0.76558 | 0.18893 | 2.078 | 8.177% | 8.7% | 5.879% | 1.089 | 1.0953 | 1.0625
2011-02-07 | 1 | 14.4678 | 8.7874 | 23.2552 | 0.94075 | 0.76558 | 0.17288 | 1.8792 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-02-07 | 2 | 13.5072 | 8.1583 | 21.6655 | 0.81653 | 0.76558 | 0.16106 | 1.7432 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-07 | 3 | 12.6517 | 7.8758 | 20.5275 | 0.73301 | 0.76558 | 0.1526 | 1.6512 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-07 | 4 | 11.9994 | 7.5301 | 19.5295 | 0.66346 | 0.76558 | 0.14518 | 1.5742 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-07 | 5 | 11.74 | 7.4683 | 19.2083 | 0.64182 | 0.76558 | 0.1428 | 1.5502 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-02-07 | 6 | 11.5441 | 7.3265 | 18.8706 | 0.61945 | 0.76558 | 0.14029 | 1.5253 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-02-07 | 7 | 11.4667 | 7.141 | 18.6077 | 0.60231 | 0.76558 | 0.13833 | 1.5062 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-02-07 | 8 | 11.2821 | 7.0228 | 18.3049 | 0.58287 | 0.76558 | 0.13608 | 1.4845 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-07 | 9 | 11.2446 | 6.949 | 18.1936 | 0.5758 | 0.76558 | 0.13525 | 1.4766 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-02-07 | 10 | 11.2311 | 6.9868 | 18.218 | 0.57734 | 0.76558 | 0.13543 | 1.4784 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-07 | 11 | 11.1828 | 6.9782 | 18.161 | 0.57374 | 0.76558 | 0.13501 | 1.4743 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-02-07 | 12 | 11.3062 | 7.059 | 18.3652 | 0.58671 | 0.76558 | 0.13653 | 1.4888 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-02-07 | 13 | 12.3543 | 7.1287 | 19.483 | 0.66031 | 0.76558 | 0.14484 | 1.5707 | 8.062% | 8.578% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-02-07 | 14 | 12.6983 | 7.0795 | 19.7778 | 0.68044 | 0.76558 | 0.14703 | 1.593 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-07 | 15 | 13.6188 | 7.498 | 21.1168 | 0.7757 | 0.76558 | 0.15699 | 1.6983 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-07 | 16 | 14.9479 | 7.9163 | 22.8642 | 0.90938 | 0.76558 | 0.16998 | 1.8449 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-02-07 | 17 | 16.611 | 8.7192 | 25.3302 | 1.1161 | 0.76558 | 0.18831 | 2.07 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-02-07 | 18 | 17.6818 | 9.6088 | 27.2907 | 1.2956 | 0.76558 | 0.20288 | 2.264 | 8.296% | 8.827% | 5.965% | 1.0905 | 1.0968 | 1.0634
2011-02-07 | 19 | 19.1887 | 10.433 | 29.6217 | 1.5263 | 0.76558 | 0.22021 | 2.5121 | 8.481% | 9.024% | 6.098% | 1.0927 | 1.0992 | 1.0649
2011-02-07 | 20 | 19.9496 | 10.7603 | 30.7099 | 1.6406 | 0.76558 | 0.2283 | 2.6344 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-02-07 | 21 | 20.6892 | 11.031 | 31.7202 | 1.7503 | 0.76558 | 0.23581 | 2.7517 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-07 | 22 | 20.643 | 11.3506 | 31.9936 | 1.7806 | 0.76558 | 0.23784 | 2.784 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-02-07 | 23 | 20.6369 | 11.0612 | 31.6981 | 1.7478 | 0.76558 | 0.23565 | 2.7491 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-02-07 | 24 | 20.46 | 10.9035 | 31.3635 | 1.7111 | 0.76558 | 0.23316 | 2.7099 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2011-02-07 | 25 | 20.1536 | 10.9474 | 31.101 | 1.6826 | 0.76558 | 0.23121 | 2.6794 | 8.615% | 9.167% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-02-07 | 26 | 20.0244 | 10.848 | 30.8724 | 1.658 | 0.76558 | 0.22951 | 2.653 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-07 | 27 | 19.8844 | 10.8267 | 30.7111 | 1.6407 | 0.76558 | 0.22831 | 2.6346 | 8.579% | 9.128% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-02-07 | 28 | 19.745 | 10.6315 | 30.3764 | 1.6051 | 0.76558 | 0.22582 | 2.5965 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2011-02-07 | 29 | 19.6064 | 10.0047 | 29.6111 | 1.5253 | 0.76558 | 0.22013 | 2.511 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2011-02-07 | 30 | 19.0187 | 9.7149 | 28.7336 | 1.4362 | 0.76558 | 0.21361 | 2.4154 | 8.406% | 8.944% | 6.044% | 1.0918 | 1.0982 | 1.0643
2011-02-07 | 31 | 18.8485 | 9.6171 | 28.4655 | 1.4095 | 0.76558 | 0.21162 | 2.3867 | 8.385% | 8.921% | 6.029% | 1.0915 | 1.098 | 1.0642
2011-02-07 | 32 | 18.6147 | 9.5401 | 28.1549 | 1.3789 | 0.76558 | 0.20931 | 2.3538 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2011-02-07 | 33 | 18.5857 | 9.9557 | 28.5414 | 1.4171 | 0.76558 | 0.21218 | 2.3948 | 8.391% | 8.928% | 6.033% | 1.0916 | 1.098 | 1.0642
2011-02-07 | 34 | 19.0669 | 9.9456 | 29.0125 | 1.4642 | 0.76558 | 0.21568 | 2.4455 | 8.429% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-02-07 | 35 | 19.2535 | 10.4492 | 29.7027 | 1.5347 | 0.76558 | 0.22081 | 2.5211 | 8.488% | 9.031% | 6.103% | 1.0928 | 1.0993 | 1.065
2011-02-07 | 36 | 19.853 | 11.1089 | 30.9619 | 1.6676 | 0.76558 | 0.23017 | 2.6633 | 8.602% | 9.153% | 6.185% | 1.0941 | 1.1007 | 1.0659
2011-02-07 | 37 | 20.558 | 11.4673 | 32.0253 | 1.7841 | 0.76558 | 0.23808 | 2.7878 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2011-02-07 | 38 | 21.0697 | 11.5362 | 32.6059 | 1.8494 | 0.76558 | 0.2424 | 2.8574 | 8.763% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2011-02-07 | 39 | 21.2492 | 11.264 | 32.5132 | 1.8389 | 0.76558 | 0.24171 | 2.8462 | 8.754% | 9.314% | 6.294% | 1.0959 | 1.1027 | 1.0672
2011-02-07 | 40 | 21.2997 | 11.1301 | 32.4299 | 1.8295 | 0.76558 | 0.24109 | 2.8361 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2011-02-07 | 41 | 20.9214 | 10.9707 | 31.8921 | 1.7693 | 0.76558 | 0.23709 | 2.772 | 8.692% | 9.248% | 6.249% | 1.0952 | 1.1019 | 1.0667
2011-02-07 | 42 | 20.4953 | 10.9472 | 31.4425 | 1.7198 | 0.76558 | 0.23375 | 2.7191 | 8.648% | 9.201% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-02-07 | 43 | 20.5629 | 10.7883 | 31.3512 | 1.7098 | 0.76558 | 0.23307 | 2.7084 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-02-07 | 44 | 20.5954 | 10.552 | 31.1475 | 1.6876 | 0.76558 | 0.23155 | 2.6848 | 8.62% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-02-07 | 45 | 19.7454 | 10.0722 | 29.8177 | 1.5466 | 0.76558 | 0.22167 | 2.5339 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-02-07 | 46 | 17.9286 | 9.3529 | 27.2814 | 1.2947 | 0.76558 | 0.20281 | 2.2631 | 8.295% | 8.826% | 5.964% | 1.0905 | 1.0968 | 1.0634
2011-02-07 | 47 | 16.1748 | 8.9489 | 25.1237 | 1.098 | 0.76558 | 0.18677 | 2.0503 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2011-02-07 | 48 | 14.9031 | 9.1404 | 24.0435 | 1.0056 | 0.76558 | 0.17874 | 1.9499 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-08 | 1 | 13.5875 | 8.3796 | 21.9671 | 0.83942 | 0.76558 | 0.16331 | 1.7683 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-02-08 | 2 | 12.8816 | 7.8354 | 20.717 | 0.7466 | 0.76558 | 0.15401 | 1.6662 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-08 | 3 | 12.1865 | 7.4997 | 19.6862 | 0.67415 | 0.76558 | 0.14635 | 1.5861 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-02-08 | 4 | 11.7966 | 7.2456 | 19.0422 | 0.63076 | 0.76558 | 0.14156 | 1.5379 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-02-08 | 5 | 11.503 | 7.2014 | 18.7044 | 0.60859 | 0.76558 | 0.13905 | 1.5132 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-08 | 6 | 10.9473 | 7.1622 | 18.1095 | 0.57049 | 0.76558 | 0.13463 | 1.4707 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-08 | 7 | 10.8593 | 7.1982 | 18.0574 | 0.56721 | 0.76558 | 0.13424 | 1.467 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-02-08 | 8 | 10.7375 | 7.2191 | 17.9566 | 0.5609 | 0.76558 | 0.13349 | 1.46 | 8.131% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-08 | 9 | 10.9696 | 7.2449 | 18.2145 | 0.57712 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-08 | 10 | 11.2717 | 7.2381 | 18.5098 | 0.59599 | 0.76558 | 0.1376 | 1.4992 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-08 | 11 | 11.4037 | 7.3097 | 18.7134 | 0.60917 | 0.76558 | 0.13912 | 1.5139 | 8.09% | 8.607% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-08 | 12 | 11.9458 | 7.689 | 19.6348 | 0.67064 | 0.76558 | 0.14597 | 1.5822 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-02-08 | 13 | 13.1557 | 8.3438 | 21.4995 | 0.80406 | 0.76558 | 0.15983 | 1.7295 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-08 | 14 | 14.7873 | 9.2801 | 24.0674 | 1.0076 | 0.76558 | 0.17892 | 1.9521 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-02-08 | 15 | 17.4677 | 10.7333 | 28.2009 | 1.3834 | 0.76558 | 0.20965 | 2.3587 | 8.364% | 8.899% | 6.014% | 1.0913 | 1.0977 | 1.064
2011-02-08 | 16 | 20.0761 | 11.651 | 31.7271 | 1.751 | 0.76558 | 0.23586 | 2.7525 | 8.675% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-02-08 | 17 | 21.4196 | 12.1471 | 33.5667 | 1.96 | 0.76558 | 0.24954 | 2.9751 | 8.863% | 9.43% | 6.373% | 1.0973 | 1.1041 | 1.0681
2011-02-08 | 18 | 21.6599 | 12.0512 | 33.7112 | 1.9769 | 0.76558 | 0.25061 | 2.9931 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-02-08 | 19 | 21.8904 | 11.9116 | 33.802 | 1.9876 | 0.76558 | 0.25129 | 3.0044 | 8.888% | 9.457% | 6.391% | 1.0976 | 1.1044 | 1.0683
2011-02-08 | 20 | 21.6192 | 11.8056 | 33.4249 | 1.9435 | 0.76558 | 0.24848 | 2.9575 | 8.848% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2011-02-08 | 21 | 21.5294 | 11.4274 | 32.9568 | 1.8894 | 0.76558 | 0.245 | 2.9 | 8.799% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-02-08 | 22 | 21.3052 | 11.1949 | 32.5 | 1.8374 | 0.76558 | 0.24161 | 2.8446 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-02-08 | 23 | 20.8829 | 11.1881 | 32.071 | 1.7892 | 0.76558 | 0.23842 | 2.7932 | 8.709% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2011-02-08 | 24 | 20.7111 | 11.132 | 31.843 | 1.7639 | 0.76558 | 0.23672 | 2.7662 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-02-08 | 25 | 20.4889 | 11.041 | 31.5299 | 1.7293 | 0.76558 | 0.2344 | 2.7293 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2011-02-08 | 26 | 20.3299 | 10.7871 | 31.117 | 1.6843 | 0.76558 | 0.23133 | 2.6812 | 8.617% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-02-08 | 27 | 20.1996 | 11.0697 | 31.2693 | 1.7009 | 0.76558 | 0.23246 | 2.6989 | 8.631% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2011-02-08 | 28 | 20.2818 | 11.2277 | 31.5095 | 1.7271 | 0.76558 | 0.23425 | 2.7269 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-02-08 | 29 | 20.0723 | 11.2484 | 31.3207 | 1.7065 | 0.76558 | 0.23284 | 2.7049 | 8.636% | 9.189% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-02-08 | 30 | 20.0187 | 11.3539 | 31.3727 | 1.7121 | 0.76558 | 0.23323 | 2.7109 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2011-02-08 | 31 | 19.8589 | 11.2106 | 31.0696 | 1.6792 | 0.76558 | 0.23097 | 2.6758 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-02-08 | 32 | 20.1011 | 11.2978 | 31.3989 | 1.715 | 0.76558 | 0.23342 | 2.714 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-02-08 | 33 | 20.0675 | 11.5472 | 31.6147 | 1.7387 | 0.76558 | 0.23503 | 2.7393 | 8.665% | 9.219% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-02-08 | 34 | 20.1528 | 11.683 | 31.8357 | 1.763 | 0.76558 | 0.23667 | 2.7653 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2011-02-08 | 35 | 20.2689 | 12.0045 | 32.2734 | 1.8119 | 0.76558 | 0.23992 | 2.8174 | 8.73% | 9.288% | 6.277% | 1.0956 | 1.1024 | 1.067
2011-02-08 | 36 | 20.6741 | 12.3295 | 33.0035 | 1.8948 | 0.76558 | 0.24535 | 2.9057 | 8.804% | 9.368% | 6.33% | 1.0965 | 1.1034 | 1.0676
2011-02-08 | 37 | 21.1398 | 12.5618 | 33.7016 | 1.9758 | 0.76558 | 0.25054 | 2.9919 | 8.878% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-02-08 | 38 | 21.4231 | 12.5942 | 34.0173 | 2.013 | 0.76558 | 0.25289 | 3.0314 | 8.911% | 9.482% | 6.407% | 1.0978 | 1.1047 | 1.0685
2011-02-08 | 39 | 21.6644 | 12.021 | 33.6854 | 1.9739 | 0.76558 | 0.25042 | 2.9899 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2011-02-08 | 40 | 21.4212 | 11.852 | 33.2732 | 1.9259 | 0.76558 | 0.24736 | 2.9388 | 8.832% | 9.398% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-02-08 | 41 | 21.1037 | 11.285 | 32.3887 | 1.8248 | 0.76558 | 0.24078 | 2.8312 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2011-02-08 | 42 | 20.9187 | 11.1813 | 32.1 | 1.7924 | 0.76558 | 0.23864 | 2.7967 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-02-08 | 43 | 21.1318 | 11.5703 | 32.702 | 1.8603 | 0.76558 | 0.24311 | 2.869 | 8.773% | 9.335% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-02-08 | 44 | 21.7109 | 11.7112 | 33.4221 | 1.9431 | 0.76558 | 0.24846 | 2.9572 | 8.848% | 9.414% | 6.362% | 1.0971 | 1.1039 | 1.0679
2011-02-08 | 45 | 20.666 | 11.2706 | 31.9366 | 1.7742 | 0.76558 | 0.23742 | 2.7772 | 8.696% | 9.253% | 6.252% | 1.0952 | 1.102 | 1.0667
2011-02-08 | 46 | 18.8184 | 10.4419 | 29.2603 | 1.4893 | 0.76558 | 0.21752 | 2.4724 | 8.45% | 8.991% | 6.075% | 1.0923 | 1.0988 | 1.0647
2011-02-08 | 47 | 17.01 | 9.7921 | 26.8022 | 1.2496 | 0.76558 | 0.19925 | 2.2144 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2011-02-08 | 48 | 15.569 | 9.5144 | 25.0834 | 1.0945 | 0.76558 | 0.18647 | 2.0465 | 8.159% | 8.681% | 5.866% | 1.0888 | 1.0951 | 1.0623
2011-02-09 | 1 | 13.9893 | 8.6625 | 22.6518 | 0.89256 | 0.76558 | 0.1684 | 1.8265 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2011-02-09 | 2 | 12.9172 | 8.0858 | 21.003 | 0.76736 | 0.76558 | 0.15614 | 1.6891 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-09 | 3 | 12.128 | 7.6683 | 19.7963 | 0.68172 | 0.76558 | 0.14717 | 1.5945 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-09 | 4 | 11.6704 | 7.6111 | 19.2816 | 0.64673 | 0.76558 | 0.14334 | 1.5556 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-09 | 5 | 11.3462 | 7.4785 | 18.8247 | 0.61644 | 0.76558 | 0.13995 | 1.522 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-09 | 6 | 11.2224 | 7.6241 | 18.8465 | 0.61787 | 0.76558 | 0.14011 | 1.5236 | 8.084% | 8.601% | 5.812% | 1.088 | 1.0941 | 1.0617
2011-02-09 | 7 | 11.0808 | 7.874 | 18.9548 | 0.62499 | 0.76558 | 0.14091 | 1.5315 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-02-09 | 8 | 11.103 | 7.8327 | 18.9357 | 0.62373 | 0.76558 | 0.14077 | 1.5301 | 8.08% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-02-09 | 9 | 10.8257 | 7.8612 | 18.6869 | 0.60745 | 0.76558 | 0.13892 | 1.5119 | 8.091% | 8.609% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-09 | 10 | 10.7973 | 7.7538 | 18.5512 | 0.59866 | 0.76558 | 0.13791 | 1.5021 | 8.097% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-09 | 11 | 11.5541 | 7.9773 | 19.5314 | 0.66359 | 0.76558 | 0.1452 | 1.5744 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-09 | 12 | 11.8953 | 8.4145 | 20.3097 | 0.71754 | 0.76558 | 0.15099 | 1.6341 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-09 | 13 | 13.2985 | 8.8791 | 22.1777 | 0.85559 | 0.76558 | 0.16487 | 1.786 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-02-09 | 14 | 14.9936 | 9.5129 | 24.5065 | 1.0447 | 0.76558 | 0.18218 | 1.9925 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-09 | 15 | 17.9355 | 10.8963 | 28.8318 | 1.446 | 0.76558 | 0.21434 | 2.4259 | 8.414% | 8.953% | 6.05% | 1.0919 | 1.0983 | 1.0644
2011-02-09 | 16 | 20.4598 | 12.0248 | 32.4845 | 1.8356 | 0.76558 | 0.24149 | 2.8427 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-02-09 | 17 | 21.9729 | 12.7118 | 34.6848 | 2.0927 | 0.76558 | 0.25785 | 3.1162 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2011-02-09 | 18 | 22.0475 | 12.4051 | 34.4526 | 2.0648 | 0.76558 | 0.25612 | 3.0865 | 8.959% | 9.532% | 6.441% | 1.0984 | 1.1054 | 1.0688
2011-02-09 | 19 | 21.911 | 12.2072 | 34.1182 | 2.0249 | 0.76558 | 0.25364 | 3.0441 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2011-02-09 | 20 | 21.4609 | 11.6471 | 33.108 | 1.9068 | 0.76558 | 0.24613 | 2.9185 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-02-09 | 21 | 21.2183 | 11.4609 | 32.6792 | 1.8577 | 0.76558 | 0.24294 | 2.8662 | 8.771% | 9.332% | 6.306% | 1.0961 | 1.1029 | 1.0673
2011-02-09 | 22 | 20.9947 | 11.6064 | 32.6011 | 1.8488 | 0.76558 | 0.24236 | 2.8568 | 8.763% | 9.324% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-02-09 | 23 | 20.6586 | 11.4383 | 32.0969 | 1.7921 | 0.76558 | 0.23861 | 2.7963 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-02-09 | 24 | 20.4255 | 11.5028 | 31.9284 | 1.7733 | 0.76558 | 0.23736 | 2.7763 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.1019 | 1.0667
2011-02-09 | 25 | 20.2207 | 11.6371 | 31.8578 | 1.7655 | 0.76558 | 0.23683 | 2.7679 | 8.688% | 9.244% | 6.247% | 1.0952 | 1.1019 | 1.0666
2011-02-09 | 26 | 19.8052 | 11.3102 | 31.1154 | 1.6842 | 0.76558 | 0.23132 | 2.6811 | 8.617% | 9.168% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-02-09 | 27 | 19.9565 | 11.517 | 31.4735 | 1.7232 | 0.76558 | 0.23398 | 2.7227 | 8.651% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2011-02-09 | 28 | 20.0519 | 11.6392 | 31.691 | 1.7471 | 0.76558 | 0.2356 | 2.7482 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2011-02-09 | 29 | 19.7885 | 11.2779 | 31.0664 | 1.6789 | 0.76558 | 0.23095 | 2.6754 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-02-09 | 30 | 19.5824 | 11.0795 | 30.6619 | 1.6354 | 0.76558 | 0.22794 | 2.629 | 8.574% | 9.123% | 6.165% | 1.0938 | 1.1004 | 1.0657
2011-02-09 | 31 | 19.6617 | 11.2112 | 30.8729 | 1.658 | 0.76558 | 0.22951 | 2.6531 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-09 | 32 | 19.6697 | 11.5491 | 31.2189 | 1.6954 | 0.76558 | 0.23208 | 2.6931 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2011-02-09 | 33 | 19.94 | 11.9389 | 31.8789 | 1.7678 | 0.76558 | 0.23699 | 2.7704 | 8.69% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-02-09 | 34 | 20.2615 | 12.1178 | 32.3793 | 1.8238 | 0.76558 | 0.24071 | 2.8301 | 8.74% | 9.3% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-02-09 | 35 | 20.7025 | 12.4198 | 33.1223 | 1.9084 | 0.76558 | 0.24624 | 2.9202 | 8.817% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2011-02-09 | 36 | 21.0725 | 12.518 | 33.5905 | 1.9628 | 0.76558 | 0.24972 | 2.9781 | 8.866% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2011-02-09 | 37 | 21.6807 | 12.798 | 34.4787 | 2.0679 | 0.76558 | 0.25632 | 3.0898 | 8.962% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2011-02-09 | 38 | 21.552 | 12.6503 | 34.2023 | 2.0349 | 0.76558 | 0.25426 | 3.0548 | 8.931% | 9.503% | 6.422% | 1.0981 | 1.105 | 1.0686
2011-02-09 | 39 | 21.8362 | 12.5515 | 34.3876 | 2.057 | 0.76558 | 0.25564 | 3.0782 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-02-09 | 40 | 21.7173 | 12.1675 | 33.8848 | 1.9973 | 0.76558 | 0.2519 | 3.0148 | 8.897% | 9.467% | 6.397% | 1.0977 | 1.1046 | 1.0683
2011-02-09 | 41 | 21.2037 | 11.6512 | 32.8549 | 1.8777 | 0.76558 | 0.24425 | 2.8876 | 8.789% | 9.351% | 6.319% | 1.0964 | 1.1032 | 1.0675
2011-02-09 | 42 | 21.6004 | 11.4111 | 33.0115 | 1.8957 | 0.76558 | 0.24541 | 2.9067 | 8.805% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2011-02-09 | 43 | 21.6566 | 11.6697 | 33.3263 | 1.932 | 0.76558 | 0.24775 | 2.9453 | 8.838% | 9.404% | 6.354% | 1.0969 | 1.1038 | 1.0679
2011-02-09 | 44 | 21.6578 | 11.59 | 33.2478 | 1.9229 | 0.76558 | 0.24717 | 2.9357 | 8.83% | 9.395% | 6.349% | 1.0968 | 1.1037 | 1.0678
2011-02-09 | 45 | 20.1945 | 10.9537 | 31.1483 | 1.6877 | 0.76558 | 0.23156 | 2.6849 | 8.62% | 9.171% | 6.198% | 1.0943 | 1.101 | 1.0661
2011-02-09 | 46 | 18.6405 | 10.1285 | 28.769 | 1.4397 | 0.76558 | 0.21387 | 2.4192 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2011-02-09 | 47 | 16.8005 | 9.5263 | 26.3268 | 1.2057 | 0.76558 | 0.19572 | 2.167 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2011-02-09 | 48 | 15.4011 | 9.6294 | 25.0305 | 1.0899 | 0.76558 | 0.18608 | 2.0415 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-02-10 | 1 | 13.9192 | 8.6141 | 22.5333 | 0.88325 | 0.76558 | 0.16752 | 1.8163 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-10 | 2 | 12.835 | 8.0376 | 20.8726 | 0.75786 | 0.76558 | 0.15517 | 1.6786 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-10 | 3 | 12.3751 | 7.6882 | 20.0634 | 0.70023 | 0.76558 | 0.14915 | 1.615 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-10 | 4 | 11.7902 | 7.476 | 19.2662 | 0.64569 | 0.76558 | 0.14323 | 1.5545 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-10 | 5 | 11.4723 | 7.4689 | 18.9412 | 0.62409 | 0.76558 | 0.14081 | 1.5305 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-02-10 | 6 | 11.2246 | 7.4814 | 18.706 | 0.60869 | 0.76558 | 0.13906 | 1.5133 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-10 | 7 | 11.0156 | 7.3383 | 18.3539 | 0.58599 | 0.76558 | 0.13645 | 1.488 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-02-10 | 8 | 10.8778 | 7.2417 | 18.1195 | 0.57112 | 0.76558 | 0.1347 | 1.4714 | 8.121% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-10 | 9 | 10.7543 | 7.24 | 17.9943 | 0.56325 | 0.76558 | 0.13377 | 1.4626 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-10 | 10 | 11.2044 | 7.2975 | 18.5019 | 0.59548 | 0.76558 | 0.13755 | 1.4986 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-02-10 | 11 | 11.5273 | 7.5096 | 19.0369 | 0.63041 | 0.76558 | 0.14152 | 1.5375 | 8.077% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0617
2011-02-10 | 12 | 11.7653 | 7.8198 | 19.5851 | 0.66725 | 0.76558 | 0.1456 | 1.5784 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-10 | 13 | 13.346 | 8.4574 | 21.8034 | 0.82696 | 0.76558 | 0.16209 | 1.7546 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-10 | 14 | 15.1576 | 9.3778 | 24.5354 | 1.0472 | 0.76558 | 0.1824 | 1.9952 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-02-10 | 15 | 18.2891 | 10.9411 | 29.2302 | 1.4863 | 0.76558 | 0.2173 | 2.4692 | 8.447% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2011-02-10 | 16 | 20.7494 | 12.0445 | 32.7939 | 1.8708 | 0.76558 | 0.24379 | 2.8801 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2011-02-10 | 17 | 21.7316 | 12.4497 | 34.1813 | 2.0324 | 0.76558 | 0.25411 | 3.0521 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2011-02-10 | 18 | 21.9221 | 12.3145 | 34.2367 | 2.039 | 0.76558 | 0.25452 | 3.0591 | 8.935% | 9.507% | 6.424% | 1.0981 | 1.1051 | 1.0687
2011-02-10 | 19 | 21.899 | 12.1022 | 34.0012 | 2.0111 | 0.76558 | 0.25277 | 3.0294 | 8.91% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2011-02-10 | 20 | 21.5214 | 12.2533 | 33.7747 | 1.9843 | 0.76558 | 0.25109 | 3.001 | 8.885% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-02-10 | 21 | 21.3661 | 11.8788 | 33.2449 | 1.9226 | 0.76558 | 0.24715 | 2.9353 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-02-10 | 22 | 21.0138 | 11.652 | 32.6657 | 1.8562 | 0.76558 | 0.24284 | 2.8646 | 8.769% | 9.331% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-02-10 | 23 | 20.9842 | 11.3685 | 32.3527 | 1.8208 | 0.76558 | 0.24051 | 2.8269 | 8.738% | 9.297% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-02-10 | 24 | 20.7383 | 11.3433 | 32.0816 | 1.7904 | 0.76558 | 0.2385 | 2.7945 | 8.71% | 9.268% | 6.263% | 1.0954 | 1.1021 | 1.0668
2011-02-10 | 25 | 20.5111 | 11.4191 | 31.9301 | 1.7735 | 0.76558 | 0.23737 | 2.7765 | 8.695% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2011-02-10 | 26 | 20.2294 | 10.7373 | 30.9667 | 1.6681 | 0.76558 | 0.23021 | 2.6639 | 8.602% | 9.153% | 6.185% | 1.0941 | 1.1008 | 1.0659
2011-02-10 | 27 | 20.2138 | 10.5472 | 30.761 | 1.646 | 0.76558 | 0.22868 | 2.6403 | 8.583% | 9.133% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-02-10 | 28 | 20.1964 | 10.3675 | 30.5639 | 1.625 | 0.76558 | 0.22722 | 2.6178 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2011-02-10 | 29 | 19.9253 | 10.1541 | 30.0794 | 1.5739 | 0.76558 | 0.22361 | 2.5631 | 8.521% | 9.066% | 6.127% | 1.0931 | 1.0997 | 1.0653
2011-02-10 | 30 | 19.4042 | 10.0251 | 29.4293 | 1.5066 | 0.76558 | 0.21878 | 2.4909 | 8.464% | 9.006% | 6.086% | 1.0925 | 1.099 | 1.0648
2011-02-10 | 31 | 19.2922 | 9.9678 | 29.2599 | 1.4893 | 0.76558 | 0.21752 | 2.4724 | 8.45% | 8.991% | 6.075% | 1.0923 | 1.0988 | 1.0647
2011-02-10 | 32 | 19.8057 | 9.9848 | 29.7905 | 1.5438 | 0.76558 | 0.22147 | 2.5308 | 8.495% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2011-02-10 | 33 | 19.9509 | 10.2603 | 30.2112 | 1.5877 | 0.76558 | 0.22459 | 2.5779 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2011-02-10 | 34 | 20.31 | 10.2932 | 30.6032 | 1.6292 | 0.76558 | 0.22751 | 2.6223 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2011-02-10 | 35 | 20.249 | 10.6758 | 30.9249 | 1.6636 | 0.76558 | 0.2299 | 2.6591 | 8.599% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-02-10 | 36 | 20.6247 | 10.8405 | 31.4653 | 1.7223 | 0.76558 | 0.23392 | 2.7217 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-02-10 | 37 | 21.1003 | 10.8704 | 31.9707 | 1.778 | 0.76558 | 0.23767 | 2.7813 | 8.699% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-02-10 | 38 | 21.4262 | 10.7807 | 32.2069 | 1.8044 | 0.76558 | 0.23943 | 2.8094 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-10 | 39 | 21.4074 | 10.7175 | 32.1248 | 1.7952 | 0.76558 | 0.23882 | 2.7996 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0668
2011-02-10 | 40 | 21.0828 | 10.5449 | 31.6277 | 1.7401 | 0.76558 | 0.23512 | 2.7408 | 8.666% | 9.22% | 6.231% | 1.0949 | 1.1016 | 1.0664
2011-02-10 | 41 | 20.4473 | 10.2326 | 30.6799 | 1.6374 | 0.76558 | 0.22808 | 2.631 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-02-10 | 42 | 20.3689 | 10.3687 | 30.7376 | 1.6435 | 0.76558 | 0.22851 | 2.6376 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-02-10 | 43 | 21.0588 | 10.4485 | 31.5073 | 1.7269 | 0.76558 | 0.23423 | 2.7267 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-02-10 | 44 | 21.6493 | 10.3526 | 32.0019 | 1.7815 | 0.76558 | 0.23791 | 2.785 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-02-10 | 45 | 20.8026 | 10.0072 | 30.8098 | 1.6513 | 0.76558 | 0.22904 | 2.6459 | 8.588% | 9.137% | 6.175% | 1.0939 | 1.1006 | 1.0658
2011-02-10 | 46 | 19.1067 | 9.1274 | 28.2341 | 1.3867 | 0.76558 | 0.2099 | 2.3622 | 8.366% | 8.902% | 6.015% | 1.0913 | 1.0977 | 1.064
2011-02-10 | 47 | 17.1264 | 8.6991 | 25.8255 | 1.1602 | 0.76558 | 0.19199 | 2.1178 | 8.2% | 8.725% | 5.896% | 1.0893 | 1.0956 | 1.0627
2011-02-10 | 48 | 15.6539 | 8.6963 | 24.3502 | 1.0314 | 0.76558 | 0.18102 | 1.978 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-02-11 | 1 | 14.2405 | 7.7781 | 22.0186 | 0.84336 | 0.76558 | 0.16369 | 1.7726 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-02-11 | 2 | 13.0449 | 7.2597 | 20.3047 | 0.71718 | 0.76558 | 0.15095 | 1.6337 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-11 | 3 | 12.4184 | 7.0061 | 19.4245 | 0.65635 | 0.76558 | 0.1444 | 1.5663 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0938 | 1.0615
2011-02-11 | 4 | 11.8647 | 6.772 | 18.6368 | 0.60419 | 0.76558 | 0.13855 | 1.5083 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-11 | 5 | 11.5711 | 6.6194 | 18.1905 | 0.57561 | 0.76558 | 0.13523 | 1.4764 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-02-11 | 6 | 11.2634 | 6.7217 | 17.9851 | 0.56268 | 0.76558 | 0.1337 | 1.462 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-11 | 7 | 10.792 | 6.6858 | 17.4778 | 0.53138 | 0.76558 | 0.12993 | 1.4269 | 8.164% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-02-11 | 8 | 10.8638 | 6.6411 | 17.5049 | 0.53303 | 0.76558 | 0.13013 | 1.4287 | 8.162% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2011-02-11 | 9 | 11.1662 | 6.6893 | 17.8555 | 0.5546 | 0.76558 | 0.13274 | 1.4529 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-02-11 | 10 | 11.5557 | 6.6502 | 18.2059 | 0.57658 | 0.76558 | 0.13535 | 1.4775 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-11 | 11 | 11.4696 | 6.8336 | 18.3032 | 0.58276 | 0.76558 | 0.13607 | 1.4844 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-11 | 12 | 11.7635 | 7.1998 | 18.9633 | 0.62555 | 0.76558 | 0.14098 | 1.5321 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-11 | 13 | 13.3568 | 7.7765 | 21.1333 | 0.77691 | 0.76558 | 0.15711 | 1.6996 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-11 | 14 | 15.1329 | 8.5548 | 23.6876 | 0.97606 | 0.76558 | 0.1761 | 1.9177 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-02-11 | 15 | 18.1929 | 10.0498 | 28.2427 | 1.3875 | 0.76558 | 0.20996 | 2.3631 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2011-02-11 | 16 | 20.6774 | 11.0024 | 31.6798 | 1.7458 | 0.76558 | 0.23551 | 2.7469 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-02-11 | 17 | 22.1064 | 11.6665 | 33.7729 | 1.9841 | 0.76558 | 0.25107 | 3.0008 | 8.885% | 9.454% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-02-11 | 18 | 22.4461 | 11.5679 | 34.014 | 2.0126 | 0.76558 | 0.25286 | 3.031 | 8.911% | 9.481% | 6.407% | 1.0978 | 1.1047 | 1.0685
2011-02-11 | 19 | 21.9538 | 11.5128 | 33.4666 | 1.9483 | 0.76558 | 0.2488 | 2.9627 | 8.853% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2011-02-11 | 20 | 21.8062 | 11.0294 | 32.8356 | 1.8755 | 0.76558 | 0.2441 | 2.8852 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-02-11 | 21 | 21.418 | 10.8872 | 32.3052 | 1.8154 | 0.76558 | 0.24016 | 2.8212 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2011-02-11 | 22 | 21.1452 | 10.8769 | 32.0221 | 1.7838 | 0.76558 | 0.23806 | 2.7874 | 8.705% | 9.262% | 6.259% | 1.0953 | 1.1021 | 1.0668
2011-02-11 | 23 | 20.8991 | 10.6603 | 31.5594 | 1.7326 | 0.76558 | 0.23462 | 2.7328 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-02-11 | 24 | 20.6344 | 10.7535 | 31.3879 | 1.7138 | 0.76558 | 0.23334 | 2.7127 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-02-11 | 25 | 20.5963 | 10.6697 | 31.266 | 1.7005 | 0.76558 | 0.23243 | 2.6985 | 8.631% | 9.183% | 6.206% | 1.0945 | 1.1011 | 1.0662
2011-02-11 | 26 | 20.0831 | 10.4335 | 30.5166 | 1.62 | 0.76558 | 0.22686 | 2.6124 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-02-11 | 27 | 20.1109 | 10.6311 | 30.742 | 1.644 | 0.76558 | 0.22854 | 2.6381 | 8.581% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-02-11 | 28 | 19.9674 | 10.7343 | 30.7017 | 1.6397 | 0.76558 | 0.22824 | 2.6335 | 8.578% | 9.127% | 6.167% | 1.0938 | 1.1004 | 1.0657
2011-02-11 | 29 | 19.9829 | 10.5387 | 30.5217 | 1.6205 | 0.76558 | 0.2269 | 2.613 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-02-11 | 30 | 19.7187 | 10.5657 | 30.2845 | 1.5954 | 0.76558 | 0.22514 | 2.5861 | 8.539% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-02-11 | 31 | 19.6816 | 10.4383 | 30.1199 | 1.5781 | 0.76558 | 0.22391 | 2.5676 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-02-11 | 32 | 19.626 | 10.4143 | 30.0403 | 1.5698 | 0.76558 | 0.22332 | 2.5587 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-02-11 | 33 | 19.637 | 10.7994 | 30.4363 | 1.6115 | 0.76558 | 0.22627 | 2.6033 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-02-11 | 34 | 20.0984 | 10.7804 | 30.8789 | 1.6587 | 0.76558 | 0.22956 | 2.6538 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-11 | 35 | 20.3927 | 11.0384 | 31.4311 | 1.7185 | 0.76558 | 0.23366 | 2.7178 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2011-02-11 | 36 | 20.6205 | 11.1949 | 31.8154 | 1.7608 | 0.76558 | 0.23652 | 2.7629 | 8.684% | 9.24% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-02-11 | 37 | 21.1758 | 11.3539 | 32.5298 | 1.8408 | 0.76558 | 0.24183 | 2.8482 | 8.756% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2011-02-11 | 38 | 21.4235 | 11.453 | 32.8765 | 1.8802 | 0.76558 | 0.24441 | 2.8902 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-02-11 | 39 | 21.5867 | 11.3229 | 32.9096 | 1.884 | 0.76558 | 0.24465 | 2.8942 | 8.794% | 9.357% | 6.323% | 1.0964 | 1.1032 | 1.0675
2011-02-11 | 40 | 21.1196 | 10.9415 | 32.0612 | 1.7881 | 0.76558 | 0.23835 | 2.792 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-11 | 41 | 20.7419 | 10.5632 | 31.3051 | 1.7048 | 0.76558 | 0.23273 | 2.7031 | 8.635% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-02-11 | 42 | 20.8308 | 10.541 | 31.3718 | 1.712 | 0.76558 | 0.23322 | 2.7108 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1012 | 1.0662
2011-02-11 | 43 | 21.3498 | 10.7997 | 32.1495 | 1.798 | 0.76558 | 0.239 | 2.8026 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-02-11 | 44 | 21.5283 | 10.9617 | 32.49 | 1.8363 | 0.76558 | 0.24153 | 2.8434 | 8.752% | 9.312% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-02-11 | 45 | 20.3807 | 10.6598 | 31.0406 | 1.6761 | 0.76558 | 0.23076 | 2.6724 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-02-11 | 46 | 18.9534 | 9.988 | 28.9414 | 1.457 | 0.76558 | 0.21515 | 2.4378 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-02-11 | 47 | 17.0527 | 9.4881 | 26.5408 | 1.2254 | 0.76558 | 0.19731 | 2.1882 | 8.245% | 8.772% | 5.928% | 1.0899 | 1.0962 | 1.063
2011-02-11 | 48 | 15.5718 | 9.1616 | 24.7334 | 1.0642 | 0.76558 | 0.18387 | 2.0136 | 8.141% | 8.662% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-02-12 | 1 | 14.057 | 8.3504 | 22.4074 | 0.87341 | 0.76558 | 0.16658 | 1.8056 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-02-12 | 2 | 13.0455 | 7.9313 | 20.9768 | 0.76544 | 0.76558 | 0.15594 | 1.687 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-12 | 3 | 12.4314 | 7.681 | 20.1124 | 0.70366 | 0.76558 | 0.14952 | 1.6188 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-12 | 4 | 11.9979 | 7.4016 | 19.3995 | 0.65466 | 0.76558 | 0.14422 | 1.5645 | 8.064% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-02-12 | 5 | 11.6819 | 7.4069 | 19.0888 | 0.63386 | 0.76558 | 0.14191 | 1.5413 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-02-12 | 6 | 11.47 | 7.4234 | 18.8934 | 0.62095 | 0.76558 | 0.14046 | 1.527 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-02-12 | 7 | 11.1828 | 7.5887 | 18.7715 | 0.61296 | 0.76558 | 0.13955 | 1.5181 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0941 | 1.0617
2011-02-12 | 8 | 11.0252 | 7.2685 | 18.2937 | 0.58215 | 0.76558 | 0.136 | 1.4837 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0944 | 1.0619
2011-02-12 | 9 | 11.0115 | 7.1228 | 18.1343 | 0.57205 | 0.76558 | 0.13481 | 1.4724 | 8.12% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-02-12 | 10 | 11.0433 | 7.1038 | 18.147 | 0.57286 | 0.76558 | 0.13491 | 1.4733 | 8.119% | 8.639% | 5.837% | 1.0884 | 1.0946 | 1.062
2011-02-12 | 11 | 11.2856 | 7.3776 | 18.6632 | 0.60591 | 0.76558 | 0.13874 | 1.5102 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-02-12 | 12 | 12.0002 | 7.6477 | 19.6478 | 0.67153 | 0.76558 | 0.14606 | 1.5832 | 8.058% | 8.573% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-02-12 | 13 | 13.515 | 8.1321 | 21.6471 | 0.81514 | 0.76558 | 0.16093 | 1.7416 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-12 | 14 | 15.2088 | 8.9309 | 24.1397 | 1.0137 | 0.76558 | 0.17946 | 1.9587 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-12 | 15 | 18.295 | 10.5265 | 28.8214 | 1.445 | 0.76558 | 0.21426 | 2.4248 | 8.413% | 8.952% | 6.049% | 1.0919 | 1.0983 | 1.0644
2011-02-12 | 16 | 20.7384 | 11.4658 | 32.2042 | 1.8041 | 0.76558 | 0.23941 | 2.8091 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-12 | 17 | 22.1686 | 12.1152 | 34.2838 | 2.0446 | 0.76558 | 0.25487 | 3.0651 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2011-02-12 | 18 | 22.4828 | 12.343 | 34.8258 | 2.1098 | 0.76558 | 0.2589 | 3.1343 | 9% | 9.576% | 6.471% | 1.0989 | 1.1059 | 1.0692
2011-02-12 | 19 | 22.143 | 12.3136 | 34.4565 | 2.0653 | 0.76558 | 0.25615 | 3.087 | 8.959% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2011-02-12 | 20 | 21.7229 | 12.0815 | 33.8045 | 1.9878 | 0.76558 | 0.25131 | 3.0047 | 8.889% | 9.457% | 6.391% | 1.0976 | 1.1045 | 1.0683
2011-02-12 | 21 | 21.4545 | 11.6991 | 33.1537 | 1.912 | 0.76558 | 0.24647 | 2.9241 | 8.82% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2011-02-12 | 22 | 21.2743 | 11.572 | 32.8463 | 1.8768 | 0.76558 | 0.24418 | 2.8865 | 8.788% | 9.35% | 6.319% | 1.0963 | 1.1031 | 1.0674
2011-02-12 | 23 | 20.9016 | 11.3124 | 32.214 | 1.8052 | 0.76558 | 0.23948 | 2.8103 | 8.724% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-12 | 24 | 20.4965 | 11.42 | 31.9165 | 1.772 | 0.76558 | 0.23727 | 2.7749 | 8.694% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2011-02-12 | 25 | 20.526 | 11.6486 | 32.1745 | 1.8008 | 0.76558 | 0.23919 | 2.8055 | 8.72% | 9.278% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-02-12 | 26 | 20.3521 | 11.4027 | 31.7548 | 1.7541 | 0.76558 | 0.23607 | 2.7557 | 8.678% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0665
2011-02-12 | 27 | 20.4436 | 11.6062 | 32.0498 | 1.7868 | 0.76558 | 0.23826 | 2.7907 | 8.707% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-12 | 28 | 20.5858 | 11.3634 | 31.9492 | 1.7756 | 0.76558 | 0.23751 | 2.7787 | 8.697% | 9.254% | 6.253% | 1.0953 | 1.102 | 1.0667
2011-02-12 | 29 | 20.1658 | 11.3364 | 31.5022 | 1.7263 | 0.76558 | 0.23419 | 2.7261 | 8.654% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-02-12 | 30 | 20.0188 | 11.4611 | 31.4799 | 1.7239 | 0.76558 | 0.23403 | 2.7235 | 8.651% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2011-02-12 | 31 | 20.1709 | 11.3391 | 31.51 | 1.7272 | 0.76558 | 0.23425 | 2.727 | 8.654% | 9.208% | 6.222% | 1.0947 | 1.1014 | 1.0664
2011-02-12 | 32 | 19.9823 | 11.2373 | 31.2196 | 1.6955 | 0.76558 | 0.23209 | 2.6931 | 8.626% | 9.179% | 6.202% | 1.0944 | 1.1011 | 1.0661
2011-02-12 | 33 | 20.2536 | 11.4619 | 31.7155 | 1.7498 | 0.76558 | 0.23578 | 2.7511 | 8.674% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-12 | 34 | 20.5784 | 11.2127 | 31.791 | 1.7581 | 0.76558 | 0.23634 | 2.76 | 8.682% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-02-12 | 35 | 20.537 | 11.3367 | 31.8737 | 1.7673 | 0.76558 | 0.23695 | 2.7698 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-02-12 | 36 | 20.9575 | 11.5923 | 32.5498 | 1.843 | 0.76558 | 0.24198 | 2.8506 | 8.758% | 9.318% | 6.297% | 1.096 | 1.1028 | 1.0672
2011-02-12 | 37 | 21.7093 | 11.5328 | 33.2421 | 1.9223 | 0.76558 | 0.24713 | 2.935 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-02-12 | 38 | 21.9958 | 11.6102 | 33.606 | 1.9646 | 0.76558 | 0.24983 | 2.98 | 8.867% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2011-02-12 | 39 | 22.0372 | 11.4684 | 33.5056 | 1.9529 | 0.76558 | 0.24908 | 2.9675 | 8.857% | 9.424% | 6.368% | 1.0972 | 1.104 | 1.068
2011-02-12 | 40 | 21.9978 | 11.3742 | 33.372 | 1.9373 | 0.76558 | 0.24809 | 2.951 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2011-02-12 | 41 | 21.4684 | 11.2568 | 32.7252 | 1.8629 | 0.76558 | 0.24328 | 2.8718 | 8.776% | 9.337% | 6.31% | 1.0962 | 1.103 | 1.0673
2011-02-12 | 42 | 21.1555 | 10.9911 | 32.1466 | 1.7976 | 0.76558 | 0.23898 | 2.8022 | 8.717% | 9.275% | 6.267% | 1.0955 | 1.1022 | 1.0669
2011-02-12 | 43 | 20.9624 | 10.7742 | 31.7366 | 1.7521 | 0.76558 | 0.23593 | 2.7536 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-02-12 | 44 | 20.6606 | 10.7489 | 31.4095 | 1.7162 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-02-12 | 45 | 19.8322 | 10.2378 | 30.07 | 1.5729 | 0.76558 | 0.22354 | 2.562 | 8.52% | 9.065% | 6.126% | 1.0931 | 1.0997 | 1.0653
2011-02-12 | 46 | 18.2103 | 9.6728 | 27.8831 | 1.3524 | 0.76558 | 0.20729 | 2.3253 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2011-02-12 | 47 | 16.8468 | 9.4095 | 26.2564 | 1.1992 | 0.76558 | 0.19519 | 2.16 | 8.227% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2011-02-12 | 48 | 15.661 | 9.3496 | 25.0106 | 1.0881 | 0.76558 | 0.18593 | 2.0396 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-02-13 | 1 | 14.2742 | 8.5926 | 22.8668 | 0.90959 | 0.76558 | 0.16999 | 1.8452 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-02-13 | 2 | 13.4322 | 8.171 | 21.6031 | 0.81184 | 0.76558 | 0.1606 | 1.738 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-13 | 3 | 12.8905 | 8.0009 | 20.8914 | 0.75922 | 0.76558 | 0.15531 | 1.6801 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-13 | 4 | 12.2697 | 7.7191 | 19.9888 | 0.69504 | 0.76558 | 0.1486 | 1.6092 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-02-13 | 5 | 11.7581 | 7.6807 | 19.4388 | 0.65731 | 0.76558 | 0.14451 | 1.5674 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-02-13 | 6 | 11.1893 | 7.5213 | 18.7106 | 0.60899 | 0.76558 | 0.1391 | 1.5137 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-13 | 7 | 11.0137 | 7.2374 | 18.2511 | 0.57944 | 0.76558 | 0.13568 | 1.4807 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-02-13 | 8 | 11.1282 | 7.1251 | 18.2532 | 0.57958 | 0.76558 | 0.1357 | 1.4809 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-02-13 | 9 | 11.102 | 7.1131 | 18.2152 | 0.57717 | 0.76558 | 0.13541 | 1.4782 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-13 | 10 | 11.3499 | 7.1668 | 18.5167 | 0.59643 | 0.76558 | 0.13766 | 1.4997 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-13 | 11 | 11.3487 | 7.2708 | 18.6195 | 0.60308 | 0.76558 | 0.13842 | 1.5071 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-02-13 | 12 | 11.9479 | 7.4483 | 19.3962 | 0.65444 | 0.76558 | 0.14419 | 1.5642 | 8.065% | 8.581% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-02-13 | 13 | 12.5119 | 7.7882 | 20.3001 | 0.71686 | 0.76558 | 0.15091 | 1.6333 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-02-13 | 14 | 13.1929 | 7.9271 | 21.1199 | 0.77593 | 0.76558 | 0.15701 | 1.6985 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-13 | 15 | 14.7556 | 8.2897 | 23.0452 | 0.92384 | 0.76558 | 0.17132 | 1.8607 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-02-13 | 16 | 16.3339 | 8.645 | 24.9788 | 1.0854 | 0.76558 | 0.1857 | 2.0366 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-13 | 17 | 18.1799 | 9.3121 | 27.492 | 1.3148 | 0.76558 | 0.20438 | 2.2847 | 8.31% | 8.842% | 5.975% | 1.0906 | 1.097 | 1.0635
2011-02-13 | 18 | 19.7303 | 9.9711 | 29.7014 | 1.5346 | 0.76558 | 0.2208 | 2.521 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2011-02-13 | 19 | 21.3762 | 10.7472 | 32.1234 | 1.7951 | 0.76558 | 0.23881 | 2.7994 | 8.715% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2011-02-13 | 20 | 21.8956 | 11.0986 | 32.9941 | 1.8937 | 0.76558 | 0.24528 | 2.9045 | 8.803% | 9.367% | 6.33% | 1.0965 | 1.1033 | 1.0676
2011-02-13 | 21 | 22.0968 | 11.4128 | 33.5095 | 1.9533 | 0.76558 | 0.24911 | 2.968 | 8.857% | 9.424% | 6.368% | 1.0972 | 1.104 | 1.068
2011-02-13 | 22 | 22.2159 | 11.6974 | 33.9133 | 2.0007 | 0.76558 | 0.25212 | 3.0184 | 8.9% | 9.47% | 6.399% | 1.0977 | 1.1046 | 1.0684
2011-02-13 | 23 | 21.7515 | 11.4806 | 33.232 | 1.9211 | 0.76558 | 0.24705 | 2.9337 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-02-13 | 24 | 21.3652 | 11.3651 | 32.7302 | 1.8635 | 0.76558 | 0.24332 | 2.8724 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0673
2011-02-13 | 25 | 20.8693 | 11.1902 | 32.0595 | 1.7879 | 0.76558 | 0.23833 | 2.7918 | 8.708% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-13 | 26 | 20.2542 | 10.8111 | 31.0653 | 1.6788 | 0.76558 | 0.23094 | 2.6753 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-02-13 | 27 | 19.8343 | 10.7274 | 30.5616 | 1.6248 | 0.76558 | 0.2272 | 2.6175 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2011-02-13 | 28 | 19.8368 | 10.4508 | 30.2876 | 1.5958 | 0.76558 | 0.22516 | 2.5865 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-02-13 | 29 | 19.4678 | 9.9215 | 29.3893 | 1.5025 | 0.76558 | 0.21848 | 2.4866 | 8.461% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-02-13 | 30 | 19.1129 | 9.5058 | 28.6187 | 1.4247 | 0.76558 | 0.21276 | 2.4031 | 8.397% | 8.934% | 6.037% | 1.0917 | 1.0981 | 1.0643
2011-02-13 | 31 | 18.8516 | 9.3907 | 28.2423 | 1.3875 | 0.76558 | 0.20996 | 2.363 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2011-02-13 | 32 | 18.769 | 9.02 | 27.789 | 1.3433 | 0.76558 | 0.20659 | 2.3155 | 8.332% | 8.866% | 5.991% | 1.0909 | 1.0973 | 1.0637
2011-02-13 | 33 | 18.6708 | 9.2146 | 27.8854 | 1.3527 | 0.76558 | 0.2073 | 2.3255 | 8.34% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2011-02-13 | 34 | 18.7721 | 9.3084 | 28.0806 | 1.3717 | 0.76558 | 0.20875 | 2.346 | 8.355% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2011-02-13 | 35 | 19.1033 | 9.5709 | 28.6743 | 1.4303 | 0.76558 | 0.21317 | 2.409 | 8.401% | 8.939% | 6.041% | 1.0917 | 1.0982 | 1.0643
2011-02-13 | 36 | 19.5832 | 10.0373 | 29.6205 | 1.5262 | 0.76558 | 0.2202 | 2.512 | 8.481% | 9.023% | 6.098% | 1.0927 | 1.0992 | 1.0649
2011-02-13 | 37 | 20.489 | 10.2104 | 30.6995 | 1.6394 | 0.76558 | 0.22822 | 2.6332 | 8.577% | 9.126% | 6.167% | 1.0938 | 1.1004 | 1.0657
2011-02-13 | 38 | 20.7878 | 10.1893 | 30.9771 | 1.6692 | 0.76558 | 0.23029 | 2.6651 | 8.603% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-02-13 | 39 | 21.1408 | 10.06 | 31.2008 | 1.6934 | 0.76558 | 0.23195 | 2.691 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-02-13 | 40 | 20.7058 | 9.7277 | 30.4335 | 1.6112 | 0.76558 | 0.22625 | 2.603 | 8.553% | 9.1% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-02-13 | 41 | 20.4656 | 9.4418 | 29.9074 | 1.5559 | 0.76558 | 0.22234 | 2.5439 | 8.506% | 9.05% | 6.116% | 1.093 | 1.0995 | 1.0651
2011-02-13 | 42 | 20.2295 | 9.3358 | 29.5652 | 1.5205 | 0.76558 | 0.21979 | 2.5059 | 8.476% | 9.018% | 6.094% | 1.0926 | 1.0991 | 1.0649
2011-02-13 | 43 | 20.8874 | 9.4916 | 30.3789 | 1.6054 | 0.76558 | 0.22584 | 2.5968 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1001 | 1.0655
2011-02-13 | 44 | 20.6494 | 9.506 | 30.1554 | 1.5819 | 0.76558 | 0.22418 | 2.5716 | 8.528% | 9.074% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-02-13 | 45 | 19.8413 | 9.1055 | 28.9468 | 1.4576 | 0.76558 | 0.21519 | 2.4384 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2011-02-13 | 46 | 18.6112 | 8.4903 | 27.1015 | 1.2777 | 0.76558 | 0.20148 | 2.2447 | 8.283% | 8.813% | 5.955% | 1.0903 | 1.0966 | 1.0633
2011-02-13 | 47 | 17.5551 | 8.3864 | 25.9415 | 1.1706 | 0.76558 | 0.19285 | 2.1291 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2011-02-13 | 48 | 16.439 | 8.5131 | 24.9521 | 1.0831 | 0.76558 | 0.1855 | 2.0341 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2011-02-14 | 1 | 14.9873 | 7.8318 | 22.8191 | 0.9058 | 0.76558 | 0.16964 | 1.841 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-14 | 2 | 13.8754 | 7.2668 | 21.1422 | 0.77756 | 0.76558 | 0.15717 | 1.7003 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-14 | 3 | 12.9495 | 6.7986 | 19.7481 | 0.6784 | 0.76558 | 0.14681 | 1.5908 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-02-14 | 4 | 12.2035 | 6.6703 | 18.8738 | 0.61966 | 0.76558 | 0.14031 | 1.5255 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-02-14 | 5 | 11.6581 | 6.7667 | 18.4248 | 0.59053 | 0.76558 | 0.13697 | 1.4931 | 8.104% | 8.622% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-02-14 | 6 | 11.3778 | 6.6226 | 18.0004 | 0.56363 | 0.76558 | 0.13382 | 1.463 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-14 | 7 | 11.4698 | 6.6112 | 18.081 | 0.56869 | 0.76558 | 0.13442 | 1.4687 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-02-14 | 8 | 11.3817 | 6.4966 | 17.8783 | 0.55602 | 0.76558 | 0.13291 | 1.4545 | 8.136% | 8.656% | 5.849% | 1.0886 | 1.0948 | 1.0621
2011-02-14 | 9 | 11.4991 | 6.3549 | 17.854 | 0.5545 | 0.76558 | 0.13273 | 1.4528 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-02-14 | 10 | 11.5006 | 6.3505 | 17.8511 | 0.55433 | 0.76558 | 0.13271 | 1.4526 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-02-14 | 11 | 11.7235 | 6.5628 | 18.2863 | 0.58168 | 0.76558 | 0.13594 | 1.4832 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-02-14 | 12 | 11.8126 | 6.6633 | 18.4759 | 0.59381 | 0.76558 | 0.13735 | 1.4967 | 8.101% | 8.619% | 5.825% | 1.0882 | 1.0943 | 1.0618
2011-02-14 | 13 | 12.5229 | 6.8261 | 19.3491 | 0.65126 | 0.76558 | 0.14384 | 1.5607 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-02-14 | 14 | 13.2486 | 6.9006 | 20.1491 | 0.70623 | 0.76558 | 0.14979 | 1.6216 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0936 | 1.0614
2011-02-14 | 15 | 14.7886 | 7.2462 | 22.0348 | 0.8446 | 0.76558 | 0.16381 | 1.774 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-02-14 | 16 | 16.2559 | 7.9698 | 24.2256 | 1.0209 | 0.76558 | 0.1801 | 1.9666 | 8.118% | 8.637% | 5.837% | 1.0883 | 1.0945 | 1.062
2011-02-14 | 17 | 18.3566 | 8.8563 | 27.2129 | 1.2882 | 0.76558 | 0.2023 | 2.2561 | 8.29% | 8.821% | 5.961% | 1.0904 | 1.0967 | 1.0634
2011-02-14 | 18 | 20.0096 | 9.5923 | 29.6019 | 1.5243 | 0.76558 | 0.22006 | 2.51 | 8.479% | 9.022% | 6.096% | 1.0926 | 1.0992 | 1.0649
2011-02-14 | 19 | 21.2781 | 10.3093 | 31.5875 | 1.7357 | 0.76558 | 0.23483 | 2.7361 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-02-14 | 20 | 21.9991 | 10.4743 | 32.4734 | 1.8344 | 0.76558 | 0.24141 | 2.8414 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-02-14 | 21 | 22.3958 | 10.5903 | 32.9861 | 1.8928 | 0.76558 | 0.24522 | 2.9036 | 8.802% | 9.366% | 6.329% | 1.0965 | 1.1033 | 1.0676
2011-02-14 | 22 | 22.1399 | 10.7416 | 32.8814 | 1.8808 | 0.76558 | 0.24444 | 2.8908 | 8.792% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-02-14 | 23 | 21.5113 | 10.7004 | 32.2116 | 1.8049 | 0.76558 | 0.23947 | 2.81 | 8.723% | 9.282% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-02-14 | 24 | 20.9766 | 10.5354 | 31.512 | 1.7274 | 0.76558 | 0.23426 | 2.7272 | 8.655% | 9.208% | 6.223% | 1.0947 | 1.1014 | 1.0664
2011-02-14 | 25 | 20.6643 | 10.597 | 31.2613 | 1.7 | 0.76558 | 0.2324 | 2.698 | 8.63% | 9.183% | 6.205% | 1.0945 | 1.1011 | 1.0662
2011-02-14 | 26 | 20.4256 | 10.2622 | 30.6877 | 1.6382 | 0.76558 | 0.22814 | 2.6319 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-02-14 | 27 | 20.155 | 10.1743 | 30.3293 | 1.6001 | 0.76558 | 0.22547 | 2.5912 | 8.544% | 9.09% | 6.143% | 1.0934 | 1.1 | 1.0654
2011-02-14 | 28 | 19.5726 | 10.1221 | 29.6946 | 1.5339 | 0.76558 | 0.22075 | 2.5202 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2011-02-14 | 29 | 19.5118 | 9.7164 | 29.2282 | 1.4861 | 0.76558 | 0.21729 | 2.4689 | 8.447% | 8.988% | 6.073% | 1.0923 | 1.0988 | 1.0647
2011-02-14 | 30 | 19.0905 | 9.3922 | 28.4827 | 1.4112 | 0.76558 | 0.21174 | 2.3885 | 8.386% | 8.923% | 6.03% | 1.0915 | 1.098 | 1.0642
2011-02-14 | 31 | 19.1743 | 9.2852 | 28.4595 | 1.4089 | 0.76558 | 0.21157 | 2.3861 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2011-02-14 | 32 | 19.0961 | 9.3011 | 28.3972 | 1.4028 | 0.76558 | 0.21111 | 2.3795 | 8.379% | 8.915% | 6.025% | 1.0915 | 1.0979 | 1.0641
2011-02-14 | 33 | 19.097 | 9.6803 | 28.7773 | 1.4406 | 0.76558 | 0.21393 | 2.4201 | 8.41% | 8.948% | 6.047% | 1.0918 | 1.0983 | 1.0644
2011-02-14 | 34 | 19.2086 | 9.688 | 28.8967 | 1.4525 | 0.76558 | 0.21482 | 2.4329 | 8.419% | 8.958% | 6.054% | 1.0919 | 1.0984 | 1.0644
2011-02-14 | 35 | 19.64 | 10.0603 | 29.7003 | 1.5345 | 0.76558 | 0.2208 | 2.5208 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2011-02-14 | 36 | 20.4812 | 10.5474 | 31.0286 | 1.6748 | 0.76558 | 0.23067 | 2.671 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-02-14 | 37 | 21.5927 | 10.8236 | 32.4163 | 1.8279 | 0.76558 | 0.24099 | 2.8345 | 8.744% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2011-02-14 | 38 | 21.5267 | 10.9695 | 32.4962 | 1.837 | 0.76558 | 0.24158 | 2.8441 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-02-14 | 39 | 21.7108 | 11.0018 | 32.7127 | 1.8615 | 0.76558 | 0.24319 | 2.8703 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-02-14 | 40 | 21.3839 | 10.6894 | 32.0733 | 1.7895 | 0.76558 | 0.23844 | 2.7935 | 8.71% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2011-02-14 | 41 | 21.2356 | 10.5245 | 31.7601 | 1.7547 | 0.76558 | 0.23611 | 2.7564 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-02-14 | 42 | 21.3585 | 10.4131 | 31.7716 | 1.756 | 0.76558 | 0.23619 | 2.7577 | 8.68% | 9.235% | 6.241% | 1.095 | 1.1018 | 1.0666
2011-02-14 | 43 | 21.7028 | 10.4848 | 32.1876 | 1.8022 | 0.76558 | 0.23929 | 2.8071 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-02-14 | 44 | 21.7027 | 10.1362 | 31.8389 | 1.7634 | 0.76558 | 0.23669 | 2.7657 | 8.686% | 9.242% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-02-14 | 45 | 20.3245 | 9.1986 | 29.5231 | 1.5162 | 0.76558 | 0.21948 | 2.5013 | 8.472% | 9.014% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-02-14 | 46 | 18.7241 | 8.5445 | 27.2685 | 1.2935 | 0.76558 | 0.20272 | 2.2618 | 8.294% | 8.825% | 5.964% | 1.0904 | 1.0968 | 1.0634
2011-02-14 | 47 | 17.0207 | 8.2826 | 25.3033 | 1.1138 | 0.76558 | 0.18811 | 2.0674 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-02-14 | 48 | 15.756 | 8.4039 | 24.16 | 1.0154 | 0.76558 | 0.17961 | 1.9606 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-15 | 1 | 14.2626 | 7.7647 | 22.0273 | 0.84403 | 0.76558 | 0.16375 | 1.7734 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-02-15 | 2 | 13.2586 | 7.2309 | 20.4895 | 0.73029 | 0.76558 | 0.15232 | 1.6482 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-15 | 3 | 12.8151 | 6.9917 | 19.8068 | 0.68244 | 0.76558 | 0.14725 | 1.5953 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-15 | 4 | 12.0036 | 6.9385 | 18.9421 | 0.62415 | 0.76558 | 0.14082 | 1.5305 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-02-15 | 5 | 11.5214 | 7.0887 | 18.6101 | 0.60246 | 0.76558 | 0.13835 | 1.5064 | 8.094% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-02-15 | 6 | 11.0897 | 6.9256 | 18.0153 | 0.56457 | 0.76558 | 0.13393 | 1.4641 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2011-02-15 | 7 | 11.1123 | 6.7865 | 17.8988 | 0.55729 | 0.76558 | 0.13306 | 1.4559 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0947 | 1.0621
2011-02-15 | 8 | 11.0959 | 6.6782 | 17.7741 | 0.54955 | 0.76558 | 0.13213 | 1.4473 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2011-02-15 | 9 | 11.3919 | 6.8345 | 18.2264 | 0.57788 | 0.76558 | 0.1355 | 1.479 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-15 | 10 | 11.3964 | 6.8881 | 18.2845 | 0.58157 | 0.76558 | 0.13593 | 1.4831 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-02-15 | 11 | 11.8421 | 6.9689 | 18.811 | 0.61554 | 0.76558 | 0.13984 | 1.521 | 8.086% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-15 | 12 | 12.1789 | 7.2701 | 19.449 | 0.65801 | 0.76558 | 0.14459 | 1.5682 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-02-15 | 13 | 13.6004 | 7.7886 | 21.389 | 0.79582 | 0.76558 | 0.15901 | 1.7204 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-15 | 14 | 15.7521 | 8.8022 | 24.5543 | 1.0488 | 0.76558 | 0.18254 | 1.9969 | 8.133% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-02-15 | 15 | 19.0746 | 10.4132 | 29.4878 | 1.5126 | 0.76558 | 0.21922 | 2.4974 | 8.469% | 9.011% | 6.089% | 1.0925 | 1.099 | 1.0648
2011-02-15 | 16 | 21.996 | 11.4166 | 33.4126 | 1.942 | 0.76558 | 0.24839 | 2.956 | 8.847% | 9.413% | 6.361% | 1.0971 | 1.1039 | 1.0679
2011-02-15 | 17 | 23.2476 | 12.3654 | 35.613 | 2.2062 | 0.76558 | 0.26475 | 3.2366 | 9.088% | 9.67% | 6.534% | 1.1 | 1.107 | 1.0699
2011-02-15 | 18 | 23.2837 | 12.4515 | 35.7353 | 2.2214 | 0.76558 | 0.26566 | 3.2526 | 9.102% | 9.685% | 6.544% | 1.1001 | 1.1072 | 1.07
2011-02-15 | 19 | 23.2655 | 12.3078 | 35.5732 | 2.2013 | 0.76558 | 0.26446 | 3.2313 | 9.084% | 9.665% | 6.531% | 1.0999 | 1.107 | 1.0699
2011-02-15 | 20 | 22.7967 | 12.1756 | 34.9723 | 2.1276 | 0.76558 | 0.25999 | 3.1531 | 9.016% | 9.593% | 6.483% | 1.0991 | 1.1061 | 1.0693
2011-02-15 | 21 | 22.5683 | 11.8091 | 34.3774 | 2.0558 | 0.76558 | 0.25557 | 3.0769 | 8.95% | 9.523% | 6.435% | 1.0983 | 1.1053 | 1.0688
2011-02-15 | 22 | 22.1427 | 11.6157 | 33.7583 | 1.9824 | 0.76558 | 0.25096 | 2.999 | 8.884% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-02-15 | 23 | 21.4955 | 11.2602 | 32.7557 | 1.8664 | 0.76558 | 0.24351 | 2.8755 | 8.779% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2011-02-15 | 24 | 21.2642 | 11.0496 | 32.3138 | 1.8164 | 0.76558 | 0.24023 | 2.8222 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2011-02-15 | 25 | 20.8541 | 11.0298 | 31.884 | 1.7684 | 0.76558 | 0.23703 | 2.771 | 8.691% | 9.247% | 6.249% | 1.0952 | 1.1019 | 1.0667
2011-02-15 | 26 | 20.7178 | 10.4136 | 31.1313 | 1.6859 | 0.76558 | 0.23143 | 2.6829 | 8.618% | 9.17% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-02-15 | 27 | 20.4346 | 10.6946 | 31.1293 | 1.6857 | 0.76558 | 0.23142 | 2.6827 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.101 | 1.0661
2011-02-15 | 28 | 20.2835 | 10.8931 | 31.1766 | 1.6908 | 0.76558 | 0.23177 | 2.6881 | 8.622% | 9.174% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-02-15 | 29 | 20.1522 | 10.5813 | 30.7335 | 1.6431 | 0.76558 | 0.22848 | 2.6371 | 8.581% | 9.13% | 6.169% | 1.0939 | 1.1005 | 1.0658
2011-02-15 | 30 | 19.7767 | 10.5745 | 30.3512 | 1.6025 | 0.76558 | 0.22563 | 2.5937 | 8.546% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-02-15 | 31 | 19.6377 | 10.4469 | 30.0846 | 1.5744 | 0.76558 | 0.22365 | 2.5637 | 8.522% | 9.067% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-02-15 | 32 | 19.5564 | 10.6322 | 30.1886 | 1.5853 | 0.76558 | 0.22443 | 2.5753 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-02-15 | 33 | 19.9915 | 10.7784 | 30.77 | 1.647 | 0.76558 | 0.22875 | 2.6413 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-02-15 | 34 | 20.1264 | 10.7346 | 30.861 | 1.6567 | 0.76558 | 0.22942 | 2.6517 | 8.593% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2011-02-15 | 35 | 20.4559 | 11.0367 | 31.4926 | 1.7253 | 0.76558 | 0.23412 | 2.7249 | 8.653% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-02-15 | 36 | 20.8868 | 11.4551 | 32.3419 | 1.8196 | 0.76558 | 0.24043 | 2.8256 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-02-15 | 37 | 21.7479 | 11.5944 | 33.3423 | 1.9339 | 0.76558 | 0.24787 | 2.9473 | 8.84% | 9.405% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-02-15 | 38 | 22.1946 | 11.423 | 33.6177 | 1.9659 | 0.76558 | 0.24992 | 2.9814 | 8.869% | 9.436% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-02-15 | 39 | 21.945 | 11.094 | 33.039 | 1.8988 | 0.76558 | 0.24562 | 2.91 | 8.808% | 9.372% | 6.333% | 1.0966 | 1.1034 | 1.0676
2011-02-15 | 40 | 21.3838 | 10.6663 | 32.0501 | 1.7869 | 0.76558 | 0.23826 | 2.7907 | 8.707% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-15 | 41 | 20.9789 | 10.4662 | 31.4451 | 1.72 | 0.76558 | 0.23377 | 2.7194 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-02-15 | 42 | 21.378 | 10.519 | 31.897 | 1.7698 | 0.76558 | 0.23713 | 2.7725 | 8.692% | 9.248% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-02-15 | 43 | 22.0564 | 10.8328 | 32.8892 | 1.8817 | 0.76558 | 0.2445 | 2.8917 | 8.792% | 9.355% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-02-15 | 44 | 22.2751 | 10.6581 | 32.9332 | 1.8867 | 0.76558 | 0.24483 | 2.8971 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2011-02-15 | 45 | 21.494 | 10.0577 | 31.5518 | 1.7317 | 0.76558 | 0.23456 | 2.7319 | 8.658% | 9.213% | 6.225% | 1.0948 | 1.1015 | 1.0664
2011-02-15 | 46 | 19.6994 | 9.3307 | 29.0301 | 1.466 | 0.76558 | 0.21581 | 2.4474 | 8.431% | 8.97% | 6.062% | 1.0921 | 1.0985 | 1.0645
2011-02-15 | 47 | 17.9603 | 8.9174 | 26.8776 | 1.2567 | 0.76558 | 0.19981 | 2.222 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2011-02-15 | 48 | 16.2048 | 8.7678 | 24.9726 | 1.0848 | 0.76558 | 0.18565 | 2.0361 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-16 | 1 | 14.6324 | 7.9455 | 22.578 | 0.88676 | 0.76558 | 0.16785 | 1.8202 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-16 | 2 | 13.429 | 7.5277 | 20.9566 | 0.76397 | 0.76558 | 0.15579 | 1.6853 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-16 | 3 | 12.6191 | 7.1433 | 19.7624 | 0.67938 | 0.76558 | 0.14692 | 1.5919 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-02-16 | 4 | 12.0295 | 6.9462 | 18.9757 | 0.62637 | 0.76558 | 0.14107 | 1.533 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-16 | 5 | 11.502 | 6.974 | 18.476 | 0.59381 | 0.76558 | 0.13735 | 1.4967 | 8.101% | 8.619% | 5.825% | 1.0882 | 1.0943 | 1.0618
2011-02-16 | 6 | 11.4334 | 6.8858 | 18.3191 | 0.58377 | 0.76558 | 0.13619 | 1.4855 | 8.109% | 8.628% | 5.831% | 1.0882 | 1.0944 | 1.0619
2011-02-16 | 7 | 11.4466 | 6.9247 | 18.3713 | 0.5871 | 0.76558 | 0.13657 | 1.4893 | 8.106% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-02-16 | 8 | 11.3694 | 7.012 | 18.3814 | 0.58775 | 0.76558 | 0.13665 | 1.49 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-16 | 9 | 11.514 | 6.9565 | 18.4705 | 0.59346 | 0.76558 | 0.13731 | 1.4964 | 8.101% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-02-16 | 10 | 11.7992 | 6.8318 | 18.631 | 0.60382 | 0.76558 | 0.1385 | 1.5079 | 8.094% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-16 | 11 | 12.1045 | 7.1271 | 19.2316 | 0.64338 | 0.76558 | 0.14297 | 1.5519 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-02-16 | 12 | 12.6524 | 7.4736 | 20.126 | 0.70461 | 0.76558 | 0.14962 | 1.6198 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-16 | 13 | 14.2767 | 8.0815 | 22.3582 | 0.86958 | 0.76558 | 0.16621 | 1.8014 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-02-16 | 14 | 16.3909 | 9.0976 | 25.4885 | 1.1301 | 0.76558 | 0.18948 | 2.0852 | 8.181% | 8.704% | 5.882% | 1.0891 | 1.0953 | 1.0625
2011-02-16 | 15 | 20.0172 | 10.8398 | 30.857 | 1.6563 | 0.76558 | 0.22939 | 2.6513 | 8.592% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2011-02-16 | 16 | 21.4671 | 11.0547 | 32.5218 | 1.8399 | 0.76558 | 0.24177 | 2.8472 | 8.755% | 9.315% | 6.295% | 1.0959 | 1.1027 | 1.0672
2011-02-16 | 17 | 20.4675 | 10.6779 | 31.1454 | 1.6874 | 0.76558 | 0.23154 | 2.6845 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-02-16 | 18 | 21.9081 | 11.3218 | 33.2299 | 1.9208 | 0.76558 | 0.24704 | 2.9335 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-02-16 | 19 | 25.1899 | 12.9905 | 38.1804 | 2.5358 | 0.76558 | 0.28384 | 3.5852 | 9.39% | 9.991% | 6.752% | 1.1036 | 1.111 | 1.0724
2011-02-16 | 20 | 25.0375 | 12.7978 | 37.8352 | 2.4902 | 0.76558 | 0.28127 | 3.537 | 9.348% | 9.947% | 6.722% | 1.1031 | 1.1105 | 1.0721
2011-02-16 | 21 | 23.5359 | 11.7885 | 35.3244 | 2.1706 | 0.76558 | 0.26261 | 3.1988 | 9.056% | 9.635% | 6.511% | 1.0996 | 1.1066 | 1.0696
2011-02-16 | 22 | 22.4733 | 11.4823 | 33.9556 | 2.0057 | 0.76558 | 0.25243 | 3.0237 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-02-16 | 23 | 21.2846 | 11.0403 | 32.3249 | 1.8176 | 0.76558 | 0.24031 | 2.8235 | 8.735% | 9.294% | 6.28% | 1.0957 | 1.1025 | 1.067
2011-02-16 | 24 | 20.7236 | 10.7139 | 31.4375 | 1.7192 | 0.76558 | 0.23371 | 2.7185 | 8.647% | 9.201% | 6.217% | 1.0947 | 1.1013 | 1.0663
2011-02-16 | 25 | 20.3826 | 10.5005 | 30.8831 | 1.6591 | 0.76558 | 0.22959 | 2.6543 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-02-16 | 26 | 20.077 | 10.2006 | 30.2776 | 1.5947 | 0.76558 | 0.22509 | 2.5854 | 8.539% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2011-02-16 | 27 | 20.1215 | 10.4604 | 30.5819 | 1.6269 | 0.76558 | 0.22735 | 2.6198 | 8.567% | 9.115% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-02-16 | 28 | 19.9108 | 10.6875 | 30.5983 | 1.6287 | 0.76558 | 0.22747 | 2.6217 | 8.568% | 9.117% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-02-16 | 29 | 19.8025 | 10.4842 | 30.2867 | 1.5957 | 0.76558 | 0.22515 | 2.5864 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-02-16 | 30 | 19.7255 | 10.2529 | 29.9784 | 1.5633 | 0.76558 | 0.22286 | 2.5518 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-02-16 | 31 | 19.815 | 10.0921 | 29.9071 | 1.5559 | 0.76558 | 0.22233 | 2.5438 | 8.506% | 9.05% | 6.116% | 1.093 | 1.0995 | 1.0651
2011-02-16 | 32 | 19.8083 | 10.2332 | 30.0414 | 1.5699 | 0.76558 | 0.22333 | 2.5588 | 8.518% | 9.063% | 6.124% | 1.0931 | 1.0997 | 1.0652
2011-02-16 | 33 | 20.1732 | 10.5681 | 30.7413 | 1.6439 | 0.76558 | 0.22853 | 2.638 | 8.581% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-02-16 | 34 | 20.1689 | 10.5711 | 30.74 | 1.6438 | 0.76558 | 0.22852 | 2.6379 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-02-16 | 35 | 20.5819 | 10.7994 | 31.3813 | 1.7131 | 0.76558 | 0.23329 | 2.7119 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-02-16 | 36 | 20.8475 | 10.957 | 31.8045 | 1.7596 | 0.76558 | 0.23644 | 2.7616 | 8.683% | 9.239% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-02-16 | 37 | 21.5557 | 11.2746 | 32.8303 | 1.8749 | 0.76558 | 0.24406 | 2.8846 | 8.786% | 9.349% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-02-16 | 38 | 22.0739 | 11.1001 | 33.1739 | 1.9144 | 0.76558 | 0.24662 | 2.9266 | 8.822% | 9.387% | 6.343% | 1.0968 | 1.1036 | 1.0677
2011-02-16 | 39 | 21.973 | 10.8718 | 32.8448 | 1.8766 | 0.76558 | 0.24417 | 2.8863 | 8.788% | 9.35% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-02-16 | 40 | 21.8962 | 10.6267 | 32.5229 | 1.84 | 0.76558 | 0.24178 | 2.8473 | 8.755% | 9.315% | 6.295% | 1.0959 | 1.1027 | 1.0672
2011-02-16 | 41 | 21.4946 | 10.1768 | 31.6714 | 1.7449 | 0.76558 | 0.23545 | 2.7459 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-02-16 | 42 | 21.5518 | 10.1642 | 31.716 | 1.7498 | 0.76558 | 0.23578 | 2.7512 | 8.674% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-16 | 43 | 22.0507 | 10.5623 | 32.613 | 1.8502 | 0.76558 | 0.24245 | 2.8582 | 8.764% | 9.325% | 6.301% | 1.0961 | 1.1028 | 1.0673
2011-02-16 | 44 | 22.0932 | 10.4407 | 32.5338 | 1.8412 | 0.76558 | 0.24186 | 2.8487 | 8.756% | 9.316% | 6.296% | 1.096 | 1.1027 | 1.0672
2011-02-16 | 45 | 21.1909 | 9.7379 | 30.9287 | 1.664 | 0.76558 | 0.22993 | 2.6595 | 8.599% | 9.149% | 6.183% | 1.0941 | 1.1007 | 1.0659
2011-02-16 | 46 | 19.5652 | 8.932 | 28.4971 | 1.4127 | 0.76558 | 0.21185 | 2.3901 | 8.387% | 8.924% | 6.03% | 1.0915 | 1.098 | 1.0642
2011-02-16 | 47 | 17.7554 | 8.5531 | 26.3085 | 1.204 | 0.76558 | 0.19558 | 2.1652 | 8.23% | 8.757% | 5.917% | 1.0897 | 1.096 | 1.0629
2011-02-16 | 48 | 16.1723 | 8.4993 | 24.6715 | 1.0588 | 0.76558 | 0.18341 | 2.0078 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0622
2011-02-17 | 1 | 14.3621 | 7.763 | 22.125 | 0.85154 | 0.76558 | 0.16448 | 1.7816 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-02-17 | 2 | 13.4016 | 7.2497 | 20.6513 | 0.74187 | 0.76558 | 0.15352 | 1.661 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-17 | 3 | 12.2889 | 6.9811 | 19.27 | 0.64595 | 0.76558 | 0.14326 | 1.5548 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-17 | 4 | 12.3037 | 6.7176 | 19.0213 | 0.62938 | 0.76558 | 0.14141 | 1.5364 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2011-02-17 | 5 | 11.6637 | 6.8462 | 18.51 | 0.596 | 0.76558 | 0.13761 | 1.4992 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-17 | 6 | 11.4019 | 6.754 | 18.156 | 0.57342 | 0.76558 | 0.13497 | 1.474 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-02-17 | 7 | 11.1783 | 6.6835 | 17.8617 | 0.55499 | 0.76558 | 0.13279 | 1.4534 | 8.137% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-02-17 | 8 | 11.2899 | 6.7175 | 18.0074 | 0.56407 | 0.76558 | 0.13387 | 1.4635 | 8.127% | 8.647% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-17 | 9 | 11.094 | 6.9304 | 18.0244 | 0.56514 | 0.76558 | 0.134 | 1.4647 | 8.126% | 8.646% | 5.843% | 1.0885 | 1.0946 | 1.0621
2011-02-17 | 10 | 11.2709 | 7.035 | 18.3058 | 0.58293 | 0.76558 | 0.13609 | 1.4846 | 8.11% | 8.629% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-02-17 | 11 | 11.5522 | 7.2621 | 18.8143 | 0.61576 | 0.76558 | 0.13987 | 1.5212 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-17 | 12 | 12.1431 | 7.4176 | 19.5607 | 0.66558 | 0.76558 | 0.14542 | 1.5766 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-17 | 13 | 13.8103 | 8.0396 | 21.8499 | 0.83049 | 0.76558 | 0.16243 | 1.7585 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-17 | 14 | 15.7355 | 9.1689 | 24.9044 | 1.0789 | 0.76558 | 0.18514 | 2.0296 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2011-02-17 | 15 | 19.0988 | 10.6275 | 29.7263 | 1.5372 | 0.76558 | 0.22099 | 2.5237 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2011-02-17 | 16 | 21.8191 | 11.7312 | 33.5503 | 1.9581 | 0.76558 | 0.24942 | 2.9731 | 8.862% | 9.429% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-02-17 | 17 | 23.2892 | 12.3823 | 35.6716 | 2.2135 | 0.76558 | 0.26519 | 3.2443 | 9.095% | 9.677% | 6.539% | 1.1 | 1.1071 | 1.07
2011-02-17 | 18 | 23.3432 | 12.5331 | 35.8763 | 2.239 | 0.76558 | 0.26671 | 3.2713 | 9.118% | 9.702% | 6.556% | 1.1003 | 1.1074 | 1.0702
2011-02-17 | 19 | 22.6938 | 12.2269 | 34.9207 | 2.1213 | 0.76558 | 0.2596 | 3.1465 | 9.01% | 9.587% | 6.478% | 1.099 | 1.106 | 1.0693
2011-02-17 | 20 | 21.9847 | 12.0825 | 34.0672 | 2.0189 | 0.76558 | 0.25326 | 3.0377 | 8.917% | 9.487% | 6.411% | 1.0979 | 1.1048 | 1.0685
2011-02-17 | 21 | 21.6894 | 11.8977 | 33.5871 | 1.9624 | 0.76558 | 0.24969 | 2.9776 | 8.865% | 9.433% | 6.374% | 1.0973 | 1.1042 | 1.0681
2011-02-17 | 22 | 21.1285 | 11.7698 | 32.8982 | 1.8827 | 0.76558 | 0.24457 | 2.8928 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-02-17 | 23 | 20.7673 | 11.2906 | 32.0578 | 1.7877 | 0.76558 | 0.23832 | 2.7916 | 8.708% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-17 | 24 | 20.4469 | 11.2386 | 31.6855 | 1.7464 | 0.76558 | 0.23555 | 2.7476 | 8.671% | 9.226% | 6.235% | 1.0949 | 1.1016 | 1.0665
2011-02-17 | 25 | 20.7449 | 11.0555 | 31.8004 | 1.7591 | 0.76558 | 0.23641 | 2.7611 | 8.683% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-02-17 | 26 | 20.501 | 10.6192 | 31.1202 | 1.6847 | 0.76558 | 0.23135 | 2.6816 | 8.617% | 9.168% | 6.196% | 1.0943 | 1.1009 | 1.066
2011-02-17 | 27 | 20.2605 | 10.8809 | 31.1414 | 1.687 | 0.76558 | 0.23151 | 2.6841 | 8.619% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-02-17 | 28 | 20.1776 | 11.0713 | 31.2489 | 1.6987 | 0.76558 | 0.23231 | 2.6965 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-02-17 | 29 | 19.895 | 10.6101 | 30.5051 | 1.6187 | 0.76558 | 0.22678 | 2.6111 | 8.56% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2011-02-17 | 30 | 19.7816 | 10.3578 | 30.1394 | 1.5802 | 0.76558 | 0.22406 | 2.5698 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2011-02-17 | 31 | 19.5143 | 10.4663 | 29.9807 | 1.5636 | 0.76558 | 0.22288 | 2.552 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-02-17 | 32 | 19.4171 | 10.6395 | 30.0566 | 1.5715 | 0.76558 | 0.22344 | 2.5605 | 8.519% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2011-02-17 | 33 | 19.8815 | 10.9951 | 30.8766 | 1.6584 | 0.76558 | 0.22954 | 2.6535 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-17 | 34 | 20.2265 | 11.0476 | 31.2741 | 1.7014 | 0.76558 | 0.2325 | 2.6995 | 8.632% | 9.184% | 6.206% | 1.0945 | 1.1011 | 1.0662
2011-02-17 | 35 | 20.5066 | 11.4656 | 31.9722 | 1.7782 | 0.76558 | 0.23769 | 2.7815 | 8.7% | 9.256% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-02-17 | 36 | 21.1241 | 11.8355 | 32.9595 | 1.8897 | 0.76558 | 0.24503 | 2.9003 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-02-17 | 37 | 22.1061 | 11.992 | 34.0981 | 2.0225 | 0.76558 | 0.25349 | 3.0416 | 8.92% | 9.491% | 6.414% | 1.0979 | 1.1049 | 1.0685
2011-02-17 | 38 | 22.4393 | 11.88 | 34.3194 | 2.0489 | 0.76558 | 0.25513 | 3.0696 | 8.944% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2011-02-17 | 39 | 22.5054 | 11.5715 | 34.0769 | 2.02 | 0.76558 | 0.25333 | 3.0389 | 8.918% | 9.489% | 6.412% | 1.0979 | 1.1048 | 1.0685
2011-02-17 | 40 | 22.1742 | 11.3419 | 33.516 | 1.9541 | 0.76558 | 0.24916 | 2.9688 | 8.858% | 9.425% | 6.369% | 1.0972 | 1.1041 | 1.068
2011-02-17 | 41 | 21.7693 | 11.0562 | 32.8255 | 1.8744 | 0.76558 | 0.24403 | 2.884 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-02-17 | 42 | 21.9627 | 10.864 | 32.8267 | 1.8745 | 0.76558 | 0.24404 | 2.8841 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-02-17 | 43 | 22.49 | 10.8314 | 33.3214 | 1.9314 | 0.76558 | 0.24772 | 2.9447 | 8.837% | 9.403% | 6.354% | 1.0969 | 1.1038 | 1.0679
2011-02-17 | 44 | 22.1393 | 10.6433 | 32.7826 | 1.8695 | 0.76558 | 0.24371 | 2.8788 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-02-17 | 45 | 21.0025 | 10.0652 | 31.0678 | 1.679 | 0.76558 | 0.23096 | 2.6756 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-02-17 | 46 | 19.5467 | 9.3502 | 28.8969 | 1.4526 | 0.76558 | 0.21482 | 2.433 | 8.419% | 8.958% | 6.054% | 1.0919 | 1.0984 | 1.0644
2011-02-17 | 47 | 17.5083 | 8.836 | 26.3443 | 1.2073 | 0.76558 | 0.19585 | 2.1687 | 8.232% | 8.759% | 5.919% | 1.0897 | 1.096 | 1.0629
2011-02-17 | 48 | 16.0666 | 8.9416 | 25.0083 | 1.0879 | 0.76558 | 0.18591 | 2.0394 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2011-02-18 | 1 | 14.2753 | 8.1882 | 22.4635 | 0.87779 | 0.76558 | 0.167 | 1.8104 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-18 | 2 | 13.3335 | 7.7803 | 21.1138 | 0.77547 | 0.76558 | 0.15696 | 1.698 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-18 | 3 | 12.3945 | 7.4059 | 19.8004 | 0.682 | 0.76558 | 0.1472 | 1.5948 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-18 | 4 | 11.8999 | 7.1528 | 19.0527 | 0.63147 | 0.76558 | 0.14164 | 1.5387 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-02-18 | 5 | 11.5859 | 6.9761 | 18.5621 | 0.59936 | 0.76558 | 0.13799 | 1.5029 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-18 | 6 | 11.3109 | 6.8631 | 18.174 | 0.57456 | 0.76558 | 0.13511 | 1.4752 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-02-18 | 7 | 11.2194 | 6.7568 | 17.9763 | 0.56213 | 0.76558 | 0.13364 | 1.4613 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-18 | 8 | 11.1765 | 6.7699 | 17.9464 | 0.56026 | 0.76558 | 0.13342 | 1.4593 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-18 | 9 | 11.3036 | 6.9327 | 18.2363 | 0.57851 | 0.76558 | 0.13557 | 1.4797 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-18 | 10 | 11.3792 | 7.0099 | 18.3891 | 0.58824 | 0.76558 | 0.13671 | 1.4905 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-18 | 11 | 11.5926 | 7.1892 | 18.7818 | 0.61363 | 0.76558 | 0.13963 | 1.5188 | 8.087% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-02-18 | 12 | 12.2615 | 7.3226 | 19.5841 | 0.66718 | 0.76558 | 0.14559 | 1.5783 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-18 | 13 | 13.7418 | 7.8384 | 21.5803 | 0.81012 | 0.76558 | 0.16043 | 1.7361 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-18 | 14 | 16.0173 | 8.5857 | 24.603 | 1.053 | 0.76558 | 0.1829 | 2.0014 | 8.135% | 8.656% | 5.849% | 1.0886 | 1.0948 | 1.0621
2011-02-18 | 15 | 19.2407 | 9.9604 | 29.2011 | 1.4833 | 0.76558 | 0.21708 | 2.466 | 8.445% | 8.985% | 6.072% | 1.0922 | 1.0987 | 1.0646
2011-02-18 | 16 | 21.5187 | 10.8887 | 32.4074 | 1.8269 | 0.76558 | 0.24092 | 2.8334 | 8.743% | 9.303% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-02-18 | 17 | 21.6381 | 10.8168 | 32.4549 | 1.8323 | 0.76558 | 0.24127 | 2.8391 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-02-18 | 18 | 23.1946 | 11.7569 | 34.9514 | 2.125 | 0.76558 | 0.25983 | 3.1504 | 9.014% | 9.591% | 6.481% | 1.0991 | 1.1061 | 1.0693
2011-02-18 | 19 | 24.3598 | 12.1562 | 36.516 | 2.3195 | 0.76558 | 0.27146 | 3.3566 | 9.192% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2011-02-18 | 20 | 24.4339 | 12.3609 | 36.7948 | 2.3551 | 0.76558 | 0.27354 | 3.3942 | 9.225% | 9.815% | 6.633% | 1.1016 | 1.1088 | 1.071
2011-02-18 | 21 | 24.0818 | 11.7773 | 35.8591 | 2.2368 | 0.76558 | 0.26658 | 3.269 | 9.116% | 9.7% | 6.555% | 1.1003 | 1.1074 | 1.0701
2011-02-18 | 22 | 23.5193 | 11.6909 | 35.2102 | 2.1566 | 0.76558 | 0.26176 | 3.1839 | 9.043% | 9.621% | 6.502% | 1.0994 | 1.1065 | 1.0695
2011-02-18 | 23 | 23.2386 | 11.2671 | 34.5056 | 2.0712 | 0.76558 | 0.25652 | 3.0933 | 8.965% | 9.538% | 6.445% | 1.0985 | 1.1054 | 1.0689
2011-02-18 | 24 | 22.4234 | 11.1352 | 33.5586 | 1.959 | 0.76558 | 0.24948 | 2.9741 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2011-02-18 | 25 | 21.9062 | 10.741 | 32.6471 | 1.8541 | 0.76558 | 0.2427 | 2.8623 | 8.768% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2011-02-18 | 26 | 21.4035 | 10.3418 | 31.7453 | 1.753 | 0.76558 | 0.236 | 2.7546 | 8.677% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-02-18 | 27 | 21.1714 | 10.2999 | 31.4713 | 1.7229 | 0.76558 | 0.23396 | 2.7225 | 8.651% | 9.204% | 6.22% | 1.0947 | 1.1014 | 1.0663
2011-02-18 | 28 | 20.9359 | 10.1149 | 31.0508 | 1.6772 | 0.76558 | 0.23084 | 2.6736 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-02-18 | 29 | 20.4438 | 9.6053 | 30.0491 | 1.5707 | 0.76558 | 0.22339 | 2.5597 | 8.518% | 9.064% | 6.125% | 1.0931 | 1.0997 | 1.0652
2011-02-18 | 30 | 20.0676 | 9.3938 | 29.4614 | 1.5099 | 0.76558 | 0.21902 | 2.4945 | 8.467% | 9.009% | 6.088% | 1.0925 | 1.099 | 1.0648
2011-02-18 | 31 | 20.1312 | 9.3936 | 29.5247 | 1.5164 | 0.76558 | 0.21949 | 2.5014 | 8.472% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-02-18 | 32 | 19.9988 | 9.3247 | 29.3236 | 1.4958 | 0.76558 | 0.21799 | 2.4794 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2011-02-18 | 33 | 20.7166 | 9.7104 | 30.427 | 1.6105 | 0.76558 | 0.2262 | 2.6022 | 8.552% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-02-18 | 34 | 21.2959 | 9.6898 | 30.9858 | 1.6702 | 0.76558 | 0.23035 | 2.6661 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-02-18 | 35 | 22.0747 | 10.0757 | 32.1504 | 1.7981 | 0.76558 | 0.23901 | 2.8027 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-02-18 | 36 | 23.2015 | 10.4224 | 33.6239 | 1.9667 | 0.76558 | 0.24996 | 2.9822 | 8.869% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-02-18 | 37 | 24.2116 | 10.4726 | 34.6843 | 2.0927 | 0.76558 | 0.25785 | 3.1161 | 8.984% | 9.559% | 6.46% | 1.0987 | 1.1057 | 1.0691
2011-02-18 | 38 | 25.0469 | 10.0834 | 35.1303 | 2.1468 | 0.76558 | 0.26116 | 3.1736 | 9.034% | 9.612% | 6.495% | 1.0993 | 1.1063 | 1.0695
2011-02-18 | 39 | 24.7861 | 9.727 | 34.513 | 2.0721 | 0.76558 | 0.25657 | 3.0942 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1055 | 1.0689
2011-02-18 | 40 | 24.6727 | 9.5817 | 34.2543 | 2.0411 | 0.76558 | 0.25465 | 3.0613 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2011-02-18 | 41 | 24.059 | 9.2912 | 33.3502 | 1.9348 | 0.76558 | 0.24793 | 2.9483 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-02-18 | 42 | 23.9475 | 9.2758 | 33.2233 | 1.9201 | 0.76558 | 0.24699 | 2.9327 | 8.827% | 9.392% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-02-18 | 43 | 23.7503 | 9.4386 | 33.1889 | 1.9161 | 0.76558 | 0.24673 | 2.9284 | 8.823% | 9.388% | 6.344% | 1.0968 | 1.1036 | 1.0677
2011-02-18 | 44 | 23.3212 | 9.1147 | 32.4359 | 1.8301 | 0.76558 | 0.24113 | 2.8369 | 8.746% | 9.306% | 6.288% | 1.0958 | 1.1026 | 1.0671
2011-02-18 | 45 | 22.1007 | 8.5794 | 30.6801 | 1.6374 | 0.76558 | 0.22808 | 2.631 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-02-18 | 46 | 20.2382 | 7.8828 | 28.121 | 1.3756 | 0.76558 | 0.20905 | 2.3502 | 8.358% | 8.893% | 6.009% | 1.0912 | 1.0976 | 1.0639
2011-02-18 | 47 | 18.604 | 7.4781 | 26.082 | 1.1834 | 0.76558 | 0.1939 | 2.1428 | 8.216% | 8.742% | 5.907% | 1.0895 | 1.0958 | 1.0628
2011-02-18 | 48 | 17.0303 | 7.3696 | 24.4 | 1.0357 | 0.76558 | 0.18139 | 1.9826 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-02-19 | 1 | 15.2214 | 6.5251 | 21.7466 | 0.82265 | 0.76558 | 0.16167 | 1.7499 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-19 | 2 | 14.1207 | 6.0347 | 20.1555 | 0.70668 | 0.76558 | 0.14984 | 1.6221 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-19 | 3 | 13.2647 | 5.7973 | 19.0619 | 0.63208 | 0.76558 | 0.14171 | 1.5394 | 8.076% | 8.592% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-02-19 | 4 | 12.8555 | 5.6025 | 18.4581 | 0.59266 | 0.76558 | 0.13722 | 1.4955 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-02-19 | 5 | 12.7351 | 5.505 | 18.2402 | 0.57875 | 0.76558 | 0.1356 | 1.4799 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-19 | 6 | 12.4164 | 5.3969 | 17.8133 | 0.55198 | 0.76558 | 0.13243 | 1.45 | 8.14% | 8.661% | 5.853% | 1.0886 | 1.0948 | 1.0622
2011-02-19 | 7 | 12.2011 | 5.4172 | 17.6183 | 0.53996 | 0.76558 | 0.13098 | 1.4365 | 8.154% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-19 | 8 | 11.8209 | 5.3766 | 17.1975 | 0.51448 | 0.76558 | 0.12785 | 1.4079 | 8.187% | 8.711% | 5.886% | 1.0892 | 1.0954 | 1.0625
2011-02-19 | 9 | 12.002 | 5.4585 | 17.4605 | 0.53033 | 0.76558 | 0.1298 | 1.4257 | 8.165% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2011-02-19 | 10 | 12.5322 | 5.6202 | 18.1524 | 0.57319 | 0.76558 | 0.13495 | 1.4737 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-02-19 | 11 | 12.8438 | 5.9958 | 18.8396 | 0.61741 | 0.76558 | 0.14006 | 1.523 | 8.084% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-02-19 | 12 | 13.6701 | 6.3437 | 20.0138 | 0.69678 | 0.76558 | 0.14879 | 1.6111 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-02-19 | 13 | 15.1639 | 6.9159 | 22.0798 | 0.84806 | 0.76558 | 0.16414 | 1.7778 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-02-19 | 14 | 17.3554 | 7.9335 | 25.2889 | 1.1125 | 0.76558 | 0.188 | 2.0661 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-02-19 | 15 | 20.9988 | 9.557 | 30.5558 | 1.6241 | 0.76558 | 0.22716 | 2.6169 | 8.564% | 9.112% | 6.158% | 1.0937 | 1.1003 | 1.0656
2011-02-19 | 16 | 24.0534 | 10.6811 | 34.7345 | 2.0987 | 0.76558 | 0.25822 | 3.1225 | 8.99% | 9.565% | 6.464% | 1.0988 | 1.1058 | 1.0691
2011-02-19 | 17 | 24.5297 | 10.8025 | 35.3322 | 2.1716 | 0.76558 | 0.26266 | 3.1998 | 9.056% | 9.636% | 6.512% | 1.0996 | 1.1066 | 1.0697
2011-02-19 | 18 | 25.9234 | 11.382 | 37.3055 | 2.4209 | 0.76558 | 0.27733 | 3.4638 | 9.285% | 9.879% | 6.676% | 1.1024 | 1.1096 | 1.0715
2011-02-19 | 19 | 25.3736 | 11.32 | 36.6935 | 2.3421 | 0.76558 | 0.27278 | 3.3805 | 9.213% | 9.802% | 6.624% | 1.1015 | 1.1087 | 1.0709
2011-02-19 | 20 | 24.283 | 10.9704 | 35.2534 | 2.1619 | 0.76558 | 0.26208 | 3.1896 | 9.048% | 9.627% | 6.505% | 1.0995 | 1.1065 | 1.0696
2011-02-19 | 21 | 23.6295 | 10.7301 | 34.3596 | 2.0537 | 0.76558 | 0.25543 | 3.0747 | 8.949% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-02-19 | 22 | 22.9651 | 10.681 | 33.646 | 1.9693 | 0.76558 | 0.25013 | 2.985 | 8.872% | 9.439% | 6.379% | 1.0974 | 1.1042 | 1.0681
2011-02-19 | 23 | 22.1274 | 10.1791 | 32.3064 | 1.8156 | 0.76558 | 0.24017 | 2.8213 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2011-02-19 | 24 | 21.2034 | 10.1625 | 31.3658 | 1.7114 | 0.76558 | 0.23318 | 2.7101 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2011-02-19 | 25 | 20.9828 | 10.1165 | 31.0993 | 1.6824 | 0.76558 | 0.2312 | 2.6792 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-02-19 | 26 | 20.6069 | 9.6203 | 30.2271 | 1.5894 | 0.76558 | 0.22471 | 2.5797 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-02-19 | 27 | 20.4773 | 9.9629 | 30.4402 | 1.6119 | 0.76558 | 0.2263 | 2.6037 | 8.554% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-02-19 | 28 | 20.4588 | 10.0087 | 30.4676 | 1.6148 | 0.76558 | 0.2265 | 2.6068 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2011-02-19 | 29 | 20.2008 | 9.7804 | 29.9812 | 1.5636 | 0.76558 | 0.22288 | 2.5521 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-02-19 | 30 | 19.9735 | 9.5585 | 29.5319 | 1.5171 | 0.76558 | 0.21954 | 2.5022 | 8.473% | 9.015% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-02-19 | 31 | 19.7844 | 9.4409 | 29.2252 | 1.4858 | 0.76558 | 0.21726 | 2.4686 | 8.447% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2011-02-19 | 32 | 19.6373 | 9.3233 | 28.9607 | 1.459 | 0.76558 | 0.2153 | 2.4399 | 8.425% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2011-02-19 | 33 | 20.3 | 9.5201 | 29.82 | 1.5469 | 0.76558 | 0.22169 | 2.5341 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-02-19 | 34 | 20.3789 | 9.5129 | 29.8919 | 1.5543 | 0.76558 | 0.22222 | 2.5421 | 8.504% | 9.049% | 6.115% | 1.0929 | 1.0995 | 1.0651
2011-02-19 | 35 | 20.6933 | 9.6651 | 30.3584 | 1.6032 | 0.76558 | 0.22569 | 2.5945 | 8.546% | 9.093% | 6.145% | 1.0934 | 1.1 | 1.0655
2011-02-19 | 36 | 20.9956 | 9.8197 | 30.8154 | 1.6518 | 0.76558 | 0.22909 | 2.6465 | 8.588% | 9.138% | 6.175% | 1.094 | 1.1006 | 1.0658
2011-02-19 | 37 | 21.6289 | 9.9658 | 31.5946 | 1.7364 | 0.76558 | 0.23488 | 2.7369 | 8.663% | 9.217% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-02-19 | 38 | 21.6846 | 9.6917 | 31.3763 | 1.7125 | 0.76558 | 0.23326 | 2.7114 | 8.641% | 9.194% | 6.213% | 1.0946 | 1.1013 | 1.0662
2011-02-19 | 39 | 21.5864 | 9.5695 | 31.1559 | 1.6886 | 0.76558 | 0.23162 | 2.6857 | 8.62% | 9.172% | 6.198% | 1.0943 | 1.101 | 1.0661
2011-02-19 | 40 | 21.4968 | 9.1688 | 30.6656 | 1.6358 | 0.76558 | 0.22797 | 2.6294 | 8.574% | 9.123% | 6.165% | 1.0938 | 1.1004 | 1.0657
2011-02-19 | 41 | 21.3429 | 8.83 | 30.173 | 1.5837 | 0.76558 | 0.22431 | 2.5736 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2011-02-19 | 42 | 21.3896 | 8.8138 | 30.2034 | 1.5869 | 0.76558 | 0.22454 | 2.577 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2011-02-19 | 43 | 21.8422 | 9.0377 | 30.8799 | 1.6588 | 0.76558 | 0.22956 | 2.6539 | 8.594% | 9.144% | 6.179% | 1.094 | 1.1006 | 1.0659
2011-02-19 | 44 | 21.7942 | 9.1421 | 30.9362 | 1.6648 | 0.76558 | 0.22998 | 2.6604 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2011-02-19 | 45 | 20.9071 | 8.7738 | 29.6808 | 1.5325 | 0.76558 | 0.22065 | 2.5187 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0993 | 1.065
2011-02-19 | 46 | 19.2513 | 8.3123 | 27.5636 | 1.3216 | 0.76558 | 0.20491 | 2.2921 | 8.316% | 8.848% | 5.979% | 1.0907 | 1.0971 | 1.0636
2011-02-19 | 47 | 17.8545 | 8.0529 | 25.9074 | 1.1676 | 0.76558 | 0.1926 | 2.1257 | 8.205% | 8.73% | 5.9% | 1.0894 | 1.0957 | 1.0627
2011-02-19 | 48 | 16.7241 | 8.1632 | 24.8873 | 1.0774 | 0.76558 | 0.18502 | 2.028 | 8.149% | 8.67% | 5.859% | 1.0887 | 1.0949 | 1.0622
2011-02-20 | 1 | 15.171 | 7.3882 | 22.5593 | 0.88529 | 0.76558 | 0.16771 | 1.8186 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-20 | 2 | 13.9293 | 6.7913 | 20.7206 | 0.74686 | 0.76558 | 0.15404 | 1.6665 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-20 | 3 | 13.3394 | 6.4387 | 19.7781 | 0.68046 | 0.76558 | 0.14703 | 1.5931 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-20 | 4 | 12.6111 | 6.2559 | 18.8671 | 0.61922 | 0.76558 | 0.14026 | 1.5251 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-02-20 | 5 | 11.9422 | 6.2909 | 18.2331 | 0.5783 | 0.76558 | 0.13555 | 1.4794 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-20 | 6 | 11.7702 | 6.2318 | 18.002 | 0.56374 | 0.76558 | 0.13383 | 1.4631 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-20 | 7 | 11.9263 | 6.1099 | 18.0362 | 0.56588 | 0.76558 | 0.13408 | 1.4655 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-02-20 | 8 | 11.8063 | 5.9034 | 17.7096 | 0.54557 | 0.76558 | 0.13166 | 1.4428 | 8.147% | 8.668% | 5.858% | 1.0887 | 1.0949 | 1.0622
2011-02-20 | 9 | 11.7778 | 5.9657 | 17.7436 | 0.54767 | 0.76558 | 0.13191 | 1.4452 | 8.145% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-02-20 | 10 | 11.9263 | 6.0191 | 17.9454 | 0.5602 | 0.76558 | 0.13341 | 1.4592 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-20 | 11 | 11.7987 | 6.1045 | 17.9032 | 0.55757 | 0.76558 | 0.13309 | 1.4562 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-02-20 | 12 | 12.1437 | 6.2021 | 18.3458 | 0.58547 | 0.76558 | 0.13638 | 1.4874 | 8.108% | 8.627% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-02-20 | 13 | 13.0256 | 6.5126 | 19.5382 | 0.66405 | 0.76558 | 0.14525 | 1.5749 | 8.061% | 8.576% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-20 | 14 | 14.2809 | 6.6557 | 20.9367 | 0.76252 | 0.76558 | 0.15565 | 1.6837 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-20 | 15 | 16.0093 | 6.8878 | 22.8971 | 0.912 | 0.76558 | 0.17022 | 1.8478 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-02-20 | 16 | 17.6219 | 7.6923 | 25.3142 | 1.1147 | 0.76558 | 0.18819 | 2.0685 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-02-20 | 17 | 19.4775 | 8.4579 | 27.9354 | 1.3575 | 0.76558 | 0.20768 | 2.3308 | 8.343% | 8.877% | 5.999% | 1.091 | 1.0974 | 1.0638
2011-02-20 | 18 | 20.7481 | 9.2151 | 29.9632 | 1.5618 | 0.76558 | 0.22275 | 2.5501 | 8.511% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2011-02-20 | 19 | 21.9009 | 9.7343 | 31.6351 | 1.7409 | 0.76558 | 0.23518 | 2.7417 | 8.666% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2011-02-20 | 20 | 22.3743 | 9.8952 | 32.2695 | 1.8114 | 0.76558 | 0.2399 | 2.8169 | 8.729% | 9.288% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-02-20 | 21 | 22.6263 | 10.0843 | 32.7106 | 1.8613 | 0.76558 | 0.24317 | 2.87 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-02-20 | 22 | 22.2588 | 10.0301 | 32.2889 | 1.8136 | 0.76558 | 0.24004 | 2.8192 | 8.731% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2011-02-20 | 23 | 21.8253 | 9.6695 | 31.4948 | 1.7255 | 0.76558 | 0.23414 | 2.7252 | 8.653% | 9.207% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-02-20 | 24 | 21.1831 | 9.709 | 30.8921 | 1.6601 | 0.76558 | 0.22966 | 2.6553 | 8.595% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-02-20 | 25 | 20.4713 | 9.7785 | 30.2498 | 1.5918 | 0.76558 | 0.22488 | 2.5822 | 8.536% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-02-20 | 26 | 19.9934 | 9.2564 | 29.2499 | 1.4883 | 0.76558 | 0.21745 | 2.4713 | 8.449% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2011-02-20 | 27 | 20.0339 | 9.1307 | 29.1646 | 1.4796 | 0.76558 | 0.21681 | 2.462 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2011-02-20 | 28 | 19.7423 | 9.2407 | 28.983 | 1.4612 | 0.76558 | 0.21546 | 2.4423 | 8.427% | 8.966% | 6.059% | 1.092 | 1.0985 | 1.0645
2011-02-20 | 29 | 19.4171 | 9.0555 | 28.4726 | 1.4102 | 0.76558 | 0.21167 | 2.3875 | 8.385% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2011-02-20 | 30 | 19.1337 | 8.9017 | 28.0354 | 1.3672 | 0.76558 | 0.20842 | 2.3412 | 8.351% | 8.886% | 6.004% | 1.0911 | 1.0975 | 1.0639
2011-02-20 | 31 | 18.9141 | 8.764 | 27.6782 | 1.3326 | 0.76558 | 0.20576 | 2.304 | 8.324% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2011-02-20 | 32 | 18.7922 | 8.6123 | 27.4045 | 1.3064 | 0.76558 | 0.20373 | 2.2757 | 8.304% | 8.836% | 5.971% | 1.0906 | 1.0969 | 1.0635
2011-02-20 | 33 | 19.284 | 8.788 | 28.072 | 1.3708 | 0.76558 | 0.20869 | 2.3451 | 8.354% | 8.888% | 6.006% | 1.0912 | 1.0976 | 1.0639
2011-02-20 | 34 | 19.464 | 8.8804 | 28.3444 | 1.3976 | 0.76558 | 0.21072 | 2.3738 | 8.375% | 8.911% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-02-20 | 35 | 19.7173 | 9.0973 | 28.8146 | 1.4443 | 0.76558 | 0.21421 | 2.4241 | 8.413% | 8.951% | 6.049% | 1.0919 | 1.0983 | 1.0644
2011-02-20 | 36 | 20.2805 | 9.2971 | 29.5775 | 1.5218 | 0.76558 | 0.21988 | 2.5073 | 8.477% | 9.019% | 6.095% | 1.0926 | 1.0991 | 1.0649
2011-02-20 | 37 | 20.6337 | 9.6094 | 30.243 | 1.5911 | 0.76558 | 0.22483 | 2.5815 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-02-20 | 38 | 20.707 | 9.5082 | 30.2152 | 1.5881 | 0.76558 | 0.22462 | 2.5783 | 8.533% | 9.079% | 6.135% | 1.0933 | 1.0999 | 1.0654
2011-02-20 | 39 | 20.8945 | 9.2899 | 30.1844 | 1.5849 | 0.76558 | 0.22439 | 2.5749 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2011-02-20 | 40 | 20.8639 | 9.2818 | 30.1458 | 1.5808 | 0.76558 | 0.22411 | 2.5705 | 8.527% | 9.073% | 6.131% | 1.0932 | 1.0998 | 1.0653
2011-02-20 | 41 | 20.6231 | 8.9627 | 29.5858 | 1.5227 | 0.76558 | 0.21994 | 2.5082 | 8.478% | 9.02% | 6.095% | 1.0926 | 1.0991 | 1.0649
2011-02-20 | 42 | 20.6393 | 8.7988 | 29.4382 | 1.5075 | 0.76558 | 0.21885 | 2.4919 | 8.465% | 9.007% | 6.086% | 1.0925 | 1.099 | 1.0648
2011-02-20 | 43 | 21.3749 | 9.1015 | 30.4764 | 1.6157 | 0.76558 | 0.22657 | 2.6078 | 8.557% | 9.105% | 6.152% | 1.0936 | 1.1002 | 1.0656
2011-02-20 | 44 | 21.024 | 8.9523 | 29.9764 | 1.5631 | 0.76558 | 0.22285 | 2.5515 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-02-20 | 45 | 20.023 | 8.6808 | 28.7038 | 1.4332 | 0.76558 | 0.21339 | 2.4122 | 8.404% | 8.942% | 6.042% | 1.0917 | 1.0982 | 1.0643
2011-02-20 | 46 | 18.6489 | 8.165 | 26.8139 | 1.2507 | 0.76558 | 0.19934 | 2.2156 | 8.263% | 8.792% | 5.941% | 1.0901 | 1.0964 | 1.0632
2011-02-20 | 47 | 17.5477 | 8.0985 | 25.6462 | 1.1441 | 0.76558 | 0.19066 | 2.1004 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2011-02-20 | 48 | 16.4757 | 8.2214 | 24.6971 | 1.061 | 0.76558 | 0.1836 | 2.0102 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-02-21 | 1 | 15.077 | 7.4881 | 22.5651 | 0.88574 | 0.76558 | 0.16775 | 1.8191 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-02-21 | 2 | 13.9486 | 6.9549 | 20.9035 | 0.7601 | 0.76558 | 0.1554 | 1.6811 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-21 | 3 | 13.1037 | 6.6491 | 19.7529 | 0.67873 | 0.76558 | 0.14685 | 1.5912 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-02-21 | 4 | 12.3435 | 6.281 | 18.6245 | 0.6034 | 0.76558 | 0.13846 | 1.5074 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-21 | 5 | 11.7745 | 6.1638 | 17.9382 | 0.55975 | 0.76558 | 0.13336 | 1.4587 | 8.132% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-02-21 | 6 | 11.5012 | 6.1196 | 17.6208 | 0.54012 | 0.76558 | 0.131 | 1.4367 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-21 | 7 | 11.5597 | 6.2222 | 17.7819 | 0.55004 | 0.76558 | 0.13219 | 1.4478 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-02-21 | 8 | 11.4946 | 5.9415 | 17.4361 | 0.52885 | 0.76558 | 0.12962 | 1.4241 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-02-21 | 9 | 11.5487 | 5.9921 | 17.5407 | 0.53522 | 0.76558 | 0.1304 | 1.4312 | 8.159% | 8.681% | 5.867% | 1.0888 | 1.0951 | 1.0623
2011-02-21 | 10 | 11.3583 | 6.099 | 17.4572 | 0.53013 | 0.76558 | 0.12978 | 1.4255 | 8.166% | 8.688% | 5.871% | 1.0889 | 1.0951 | 1.0624
2011-02-21 | 11 | 11.3647 | 6.0679 | 17.4326 | 0.52864 | 0.76558 | 0.1296 | 1.4238 | 8.168% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-02-21 | 12 | 11.6889 | 6.1288 | 17.8178 | 0.55226 | 0.76558 | 0.13246 | 1.4503 | 8.14% | 8.661% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-02-21 | 13 | 12.7349 | 6.1185 | 18.8534 | 0.61832 | 0.76558 | 0.14016 | 1.5241 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-02-21 | 14 | 13.5335 | 6.2905 | 19.824 | 0.68362 | 0.76558 | 0.14737 | 1.5966 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-02-21 | 15 | 14.6859 | 6.5177 | 21.2036 | 0.78209 | 0.76558 | 0.15763 | 1.7053 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-21 | 16 | 16.0904 | 7.1694 | 23.2597 | 0.94112 | 0.76558 | 0.17292 | 1.8796 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-02-21 | 17 | 17.3137 | 8.1376 | 25.4513 | 1.1268 | 0.76558 | 0.18921 | 2.0816 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2011-02-21 | 18 | 18.8822 | 8.7868 | 27.6691 | 1.3318 | 0.76558 | 0.2057 | 2.303 | 8.323% | 8.856% | 5.985% | 1.0908 | 1.0972 | 1.0637
2011-02-21 | 19 | 20.5657 | 9.4016 | 29.9673 | 1.5622 | 0.76558 | 0.22278 | 2.5505 | 8.511% | 9.056% | 6.119% | 1.093 | 1.0996 | 1.0652
2011-02-21 | 20 | 21.4223 | 9.7633 | 31.1856 | 1.6918 | 0.76558 | 0.23184 | 2.6892 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-02-21 | 21 | 21.9794 | 9.8478 | 31.8271 | 1.7621 | 0.76558 | 0.23661 | 2.7643 | 8.685% | 9.241% | 6.245% | 1.0951 | 1.1018 | 1.0666
2011-02-21 | 22 | 21.6666 | 10.0439 | 31.7105 | 1.7492 | 0.76558 | 0.23574 | 2.7505 | 8.674% | 9.229% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-21 | 23 | 20.9425 | 9.8617 | 30.8042 | 1.6506 | 0.76558 | 0.229 | 2.6452 | 8.587% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2011-02-21 | 24 | 20.1442 | 9.6995 | 29.8436 | 1.5493 | 0.76558 | 0.22186 | 2.5367 | 8.5% | 9.044% | 6.112% | 1.0929 | 1.0994 | 1.0651
2011-02-21 | 25 | 19.9089 | 9.8646 | 29.7735 | 1.542 | 0.76558 | 0.22134 | 2.529 | 8.494% | 9.038% | 6.107% | 1.0928 | 1.0994 | 1.065
2011-02-21 | 26 | 19.6632 | 9.6572 | 29.3204 | 1.4955 | 0.76558 | 0.21797 | 2.479 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0989 | 1.0647
2011-02-21 | 27 | 19.5253 | 9.7045 | 29.2298 | 1.4862 | 0.76558 | 0.2173 | 2.4691 | 8.447% | 8.988% | 6.074% | 1.0923 | 1.0988 | 1.0647
2011-02-21 | 28 | 19.2957 | 9.5979 | 28.8936 | 1.4522 | 0.76558 | 0.2148 | 2.4326 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2011-02-21 | 29 | 19.2325 | 9.1978 | 28.4302 | 1.406 | 0.76558 | 0.21135 | 2.383 | 8.382% | 8.918% | 6.027% | 1.0915 | 1.0979 | 1.0641
2011-02-21 | 30 | 18.555 | 9.0717 | 27.6267 | 1.3277 | 0.76558 | 0.20538 | 2.2986 | 8.32% | 8.853% | 5.982% | 1.0908 | 1.0971 | 1.0636
2011-02-21 | 31 | 18.4923 | 8.997 | 27.4894 | 1.3145 | 0.76558 | 0.20436 | 2.2844 | 8.31% | 8.842% | 5.975% | 1.0906 | 1.097 | 1.0635
2011-02-21 | 32 | 18.3451 | 9.1698 | 27.5148 | 1.3169 | 0.76558 | 0.20455 | 2.2871 | 8.312% | 8.844% | 5.976% | 1.0907 | 1.097 | 1.0636
2011-02-21 | 33 | 18.8716 | 9.5965 | 28.4681 | 1.4098 | 0.76558 | 0.21164 | 2.387 | 8.385% | 8.921% | 6.029% | 1.0915 | 1.098 | 1.0642
2011-02-21 | 34 | 19.2069 | 9.6819 | 28.8888 | 1.4518 | 0.76558 | 0.21476 | 2.4321 | 8.419% | 8.958% | 6.053% | 1.0919 | 1.0984 | 1.0644
2011-02-21 | 35 | 19.3334 | 9.9351 | 29.2685 | 1.4902 | 0.76558 | 0.21759 | 2.4733 | 8.45% | 8.991% | 6.076% | 1.0923 | 1.0988 | 1.0647
2011-02-21 | 36 | 20.1027 | 10.4466 | 30.5493 | 1.6234 | 0.76558 | 0.22711 | 2.6161 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2011-02-21 | 37 | 20.8823 | 10.7699 | 31.6522 | 1.7428 | 0.76558 | 0.23531 | 2.7437 | 8.668% | 9.223% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-02-21 | 38 | 21.124 | 10.8773 | 32.0013 | 1.7814 | 0.76558 | 0.2379 | 2.7849 | 8.703% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-02-21 | 39 | 20.935 | 10.6544 | 31.5894 | 1.7359 | 0.76558 | 0.23484 | 2.7363 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-02-21 | 40 | 20.988 | 10.5082 | 31.4963 | 1.7256 | 0.76558 | 0.23415 | 2.7254 | 8.653% | 9.207% | 6.222% | 1.0947 | 1.1014 | 1.0663
2011-02-21 | 41 | 20.8214 | 10.2128 | 31.0342 | 1.6754 | 0.76558 | 0.23071 | 2.6717 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-02-21 | 42 | 21.0871 | 9.9701 | 31.0571 | 1.6779 | 0.76558 | 0.23088 | 2.6743 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-02-21 | 43 | 21.5796 | 10.1261 | 31.7057 | 1.7487 | 0.76558 | 0.2357 | 2.75 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-02-21 | 44 | 21.3538 | 9.7425 | 31.0963 | 1.6821 | 0.76558 | 0.23117 | 2.6788 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-02-21 | 45 | 20.0957 | 9.0567 | 29.1524 | 1.4784 | 0.76558 | 0.21672 | 2.4607 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2011-02-21 | 46 | 18.3362 | 8.424 | 26.7601 | 1.2457 | 0.76558 | 0.19894 | 2.2102 | 8.259% | 8.788% | 5.938% | 1.09 | 1.0963 | 1.0631
2011-02-21 | 47 | 16.5513 | 7.9352 | 24.4865 | 1.043 | 0.76558 | 0.18204 | 1.9906 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-21 | 48 | 15.2313 | 7.8647 | 23.096 | 0.92791 | 0.76558 | 0.1717 | 1.8652 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-02-22 | 1 | 13.7673 | 7.0728 | 20.8401 | 0.7555 | 0.76558 | 0.15493 | 1.676 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-22 | 2 | 12.9279 | 6.6384 | 19.5663 | 0.66596 | 0.76558 | 0.14546 | 1.577 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-22 | 3 | 12.1736 | 6.3894 | 18.5631 | 0.59942 | 0.76558 | 0.138 | 1.503 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-22 | 4 | 11.7037 | 6.0865 | 17.7902 | 0.55055 | 0.76558 | 0.13225 | 1.4484 | 8.141% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-02-22 | 5 | 11.1401 | 6.2501 | 17.3903 | 0.52607 | 0.76558 | 0.12928 | 1.4209 | 8.171% | 8.694% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-02-22 | 6 | 11.0141 | 6.0612 | 17.0753 | 0.50719 | 0.76558 | 0.12694 | 1.3997 | 8.197% | 8.722% | 5.894% | 1.0893 | 1.0956 | 1.0626
2011-02-22 | 7 | 11.1625 | 5.9464 | 17.1088 | 0.50918 | 0.76558 | 0.12719 | 1.402 | 8.194% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2011-02-22 | 8 | 11.0444 | 5.8943 | 16.9387 | 0.49911 | 0.76558 | 0.12592 | 1.3906 | 8.21% | 8.735% | 5.903% | 1.0894 | 1.0957 | 1.0627
2011-02-22 | 9 | 11.0705 | 6.1097 | 17.1802 | 0.51344 | 0.76558 | 0.12772 | 1.4067 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2011-02-22 | 10 | 10.885 | 6.1672 | 17.0523 | 0.50582 | 0.76558 | 0.12677 | 1.3982 | 8.199% | 8.724% | 5.895% | 1.0893 | 1.0956 | 1.0626
2011-02-22 | 11 | 11.2257 | 6.2459 | 17.4716 | 0.53101 | 0.76558 | 0.12989 | 1.4265 | 8.165% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-02-22 | 12 | 11.6324 | 6.6214 | 18.2538 | 0.57962 | 0.76558 | 0.1357 | 1.4809 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-02-22 | 13 | 13.5242 | 7.1821 | 20.7063 | 0.74583 | 0.76558 | 0.15393 | 1.6653 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-22 | 14 | 15.1515 | 8.2656 | 23.4172 | 0.9539 | 0.76558 | 0.17409 | 1.8936 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-02-22 | 15 | 18.1779 | 9.4202 | 27.5981 | 1.3249 | 0.76558 | 0.20517 | 2.2957 | 8.318% | 8.851% | 5.981% | 1.0907 | 1.0971 | 1.0636
2011-02-22 | 16 | 20.7692 | 10.0903 | 30.8595 | 1.6566 | 0.76558 | 0.22941 | 2.6516 | 8.592% | 9.142% | 6.178% | 1.094 | 1.1006 | 1.0658
2011-02-22 | 17 | 22.1557 | 10.4526 | 32.6083 | 1.8497 | 0.76558 | 0.24241 | 2.8576 | 8.764% | 9.324% | 6.301% | 1.0961 | 1.1028 | 1.0672
2011-02-22 | 18 | 22.6792 | 10.5621 | 33.2413 | 1.9222 | 0.76558 | 0.24712 | 2.9349 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-02-22 | 19 | 22.6911 | 10.6696 | 33.3608 | 1.936 | 0.76558 | 0.24801 | 2.9496 | 8.841% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-02-22 | 20 | 22.4011 | 10.6599 | 33.061 | 1.9014 | 0.76558 | 0.24578 | 2.9127 | 8.81% | 9.374% | 6.335% | 1.0966 | 1.1034 | 1.0676
2011-02-22 | 21 | 22.0282 | 10.3554 | 32.3836 | 1.8243 | 0.76558 | 0.24074 | 2.8306 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2011-02-22 | 22 | 21.5832 | 10.5148 | 32.098 | 1.7922 | 0.76558 | 0.23862 | 2.7964 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-02-22 | 23 | 21.3705 | 10.4626 | 31.8331 | 1.7628 | 0.76558 | 0.23665 | 2.765 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2011-02-22 | 24 | 21.1765 | 10.5915 | 31.768 | 1.7556 | 0.76558 | 0.23617 | 2.7573 | 8.679% | 9.235% | 6.241% | 1.095 | 1.1017 | 1.0666
2011-02-22 | 25 | 20.5844 | 10.8422 | 31.4266 | 1.718 | 0.76558 | 0.23363 | 2.7172 | 8.646% | 9.2% | 6.217% | 1.0946 | 1.1013 | 1.0663
2011-02-22 | 26 | 20.3574 | 10.578 | 30.9354 | 1.6647 | 0.76558 | 0.22998 | 2.6603 | 8.6% | 9.15% | 6.183% | 1.0941 | 1.1007 | 1.0659
2011-02-22 | 27 | 20.7067 | 10.8962 | 31.603 | 1.7374 | 0.76558 | 0.23494 | 2.7379 | 8.663% | 9.218% | 6.229% | 1.0949 | 1.1015 | 1.0664
2011-02-22 | 28 | 20.684 | 11.1615 | 31.8455 | 1.7641 | 0.76558 | 0.23674 | 2.7665 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-02-22 | 29 | 20.3865 | 11.0623 | 31.4488 | 1.7205 | 0.76558 | 0.23379 | 2.7198 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-02-22 | 30 | 20.2546 | 11.1956 | 31.4503 | 1.7206 | 0.76558 | 0.23381 | 2.72 | 8.649% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-02-22 | 31 | 20.1627 | 11.0071 | 31.1698 | 1.6901 | 0.76558 | 0.23172 | 2.6874 | 8.622% | 9.173% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-02-22 | 32 | 19.9689 | 11.115 | 31.0839 | 1.6808 | 0.76558 | 0.23108 | 2.6774 | 8.614% | 9.165% | 6.193% | 1.0943 | 1.1009 | 1.066
2011-02-22 | 33 | 20.5272 | 11.5685 | 32.0956 | 1.792 | 0.76558 | 0.2386 | 2.7961 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-02-22 | 34 | 20.8883 | 10.8453 | 31.7336 | 1.7518 | 0.76558 | 0.23591 | 2.7532 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-02-22 | 35 | 20.7984 | 11.518 | 32.3164 | 1.8167 | 0.76558 | 0.24024 | 2.8225 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1025 | 1.067
2011-02-22 | 36 | 21.3521 | 12.019 | 33.3711 | 1.9372 | 0.76558 | 0.24808 | 2.9509 | 8.843% | 9.409% | 6.358% | 1.097 | 1.1039 | 1.0679
2011-02-22 | 37 | 22.1457 | 11.9973 | 34.1431 | 2.0279 | 0.76558 | 0.25382 | 3.0473 | 8.925% | 9.496% | 6.417% | 1.098 | 1.1049 | 1.0686
2011-02-22 | 38 | 22.4039 | 11.7905 | 34.1944 | 2.034 | 0.76558 | 0.25421 | 3.0538 | 8.931% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2011-02-22 | 39 | 21.9244 | 11.4695 | 33.3939 | 1.9399 | 0.76558 | 0.24825 | 2.9537 | 8.845% | 9.411% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-02-22 | 40 | 21.683 | 11.2369 | 32.9199 | 1.8852 | 0.76558 | 0.24473 | 2.8955 | 8.796% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-02-22 | 41 | 21.7207 | 11.0169 | 32.7377 | 1.8644 | 0.76558 | 0.24338 | 2.8733 | 8.777% | 9.339% | 6.311% | 1.0962 | 1.103 | 1.0674
2011-02-22 | 42 | 21.8535 | 11.248 | 33.1015 | 1.906 | 0.76558 | 0.24608 | 2.9177 | 8.814% | 9.378% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-02-22 | 43 | 22.1639 | 11.1395 | 33.3033 | 1.9293 | 0.76558 | 0.24758 | 2.9425 | 8.835% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-02-22 | 44 | 21.6622 | 10.7008 | 32.363 | 1.8219 | 0.76558 | 0.24059 | 2.8281 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2011-02-22 | 45 | 20.3562 | 9.9119 | 30.2681 | 1.5937 | 0.76558 | 0.22502 | 2.5843 | 8.538% | 9.084% | 6.139% | 1.0934 | 1.0999 | 1.0654
2011-02-22 | 46 | 18.5046 | 9.1153 | 27.6199 | 1.327 | 0.76558 | 0.20533 | 2.2979 | 8.32% | 8.852% | 5.982% | 1.0907 | 1.0971 | 1.0636
2011-02-22 | 47 | 16.5546 | 8.7666 | 25.3212 | 1.1153 | 0.76558 | 0.18824 | 2.0691 | 8.172% | 8.695% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-02-22 | 48 | 15.0703 | 8.7792 | 23.8495 | 0.98945 | 0.76558 | 0.1773 | 1.9323 | 8.102% | 8.621% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-02-23 | 1 | 13.4971 | 8.0132 | 21.5103 | 0.80488 | 0.76558 | 0.15991 | 1.7304 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-23 | 2 | 12.689 | 7.4275 | 20.1165 | 0.70394 | 0.76558 | 0.14955 | 1.6191 | 8.048% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-23 | 3 | 12.0612 | 7.1017 | 19.1629 | 0.63879 | 0.76558 | 0.14246 | 1.5468 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-02-23 | 4 | 11.5238 | 7.003 | 18.5268 | 0.59708 | 0.76558 | 0.13773 | 1.5004 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-23 | 5 | 11.4091 | 7.02 | 18.4291 | 0.5908 | 0.76558 | 0.137 | 1.4934 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2011-02-23 | 6 | 10.7057 | 6.9329 | 17.6386 | 0.54121 | 0.76558 | 0.13113 | 1.4379 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2011-02-23 | 7 | 10.6701 | 6.6762 | 17.3463 | 0.52342 | 0.76558 | 0.12895 | 1.4179 | 8.174% | 8.698% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-02-23 | 8 | 10.4959 | 6.686 | 17.1819 | 0.51354 | 0.76558 | 0.12773 | 1.4069 | 8.188% | 8.712% | 5.887% | 1.0892 | 1.0954 | 1.0626
2011-02-23 | 9 | 10.9244 | 6.7058 | 17.6302 | 0.54069 | 0.76558 | 0.13107 | 1.4373 | 8.153% | 8.674% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-23 | 10 | 11.0957 | 6.6257 | 17.7213 | 0.5463 | 0.76558 | 0.13174 | 1.4436 | 8.146% | 8.668% | 5.857% | 1.0887 | 1.0949 | 1.0622
2011-02-23 | 11 | 11.1658 | 6.6946 | 17.8604 | 0.5549 | 0.76558 | 0.13278 | 1.4533 | 8.137% | 8.658% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-02-23 | 12 | 11.5356 | 7.0457 | 18.5813 | 0.6006 | 0.76558 | 0.13814 | 1.5043 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-02-23 | 13 | 12.9794 | 7.6145 | 20.594 | 0.73776 | 0.76558 | 0.1531 | 1.6564 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-23 | 14 | 15.2874 | 8.7366 | 24.0241 | 1.004 | 0.76558 | 0.1786 | 1.9482 | 8.109% | 8.628% | 5.831% | 1.0882 | 1.0944 | 1.0619
2011-02-23 | 15 | 18.3528 | 10.1617 | 28.5145 | 1.4144 | 0.76558 | 0.21198 | 2.3919 | 8.389% | 8.925% | 6.031% | 1.0916 | 1.098 | 1.0642
2011-02-23 | 16 | 21.1535 | 10.8909 | 32.0443 | 1.7862 | 0.76558 | 0.23822 | 2.79 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2011-02-23 | 17 | 22.4006 | 11.1729 | 33.5735 | 1.9608 | 0.76558 | 0.24959 | 2.9759 | 8.864% | 9.431% | 6.373% | 1.0973 | 1.1041 | 1.0681
2011-02-23 | 18 | 22.3643 | 11.2778 | 33.6421 | 1.9688 | 0.76558 | 0.2501 | 2.9845 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2011-02-23 | 19 | 22.0968 | 11.0303 | 33.127 | 1.909 | 0.76558 | 0.24627 | 2.9208 | 8.817% | 9.381% | 6.339% | 1.0967 | 1.1035 | 1.0677
2011-02-23 | 20 | 21.4053 | 10.9254 | 32.3307 | 1.8183 | 0.76558 | 0.24035 | 2.8242 | 8.735% | 9.294% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-02-23 | 21 | 21.4449 | 10.839 | 32.2839 | 1.813 | 0.76558 | 0.24 | 2.8186 | 8.731% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2011-02-23 | 22 | 21.383 | 10.9855 | 32.3685 | 1.8226 | 0.76558 | 0.24063 | 2.8288 | 8.739% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.067
2011-02-23 | 23 | 20.8986 | 10.8252 | 31.7239 | 1.7507 | 0.76558 | 0.23584 | 2.7521 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-02-23 | 24 | 20.434 | 10.8089 | 31.2429 | 1.698 | 0.76558 | 0.23226 | 2.6958 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-02-23 | 25 | 20.4832 | 11.028 | 31.5112 | 1.7273 | 0.76558 | 0.23426 | 2.7271 | 8.654% | 9.208% | 6.223% | 1.0947 | 1.1014 | 1.0664
2011-02-23 | 26 | 19.7699 | 10.8021 | 30.572 | 1.6259 | 0.76558 | 0.22728 | 2.6187 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-02-23 | 27 | 19.6614 | 10.9618 | 30.6231 | 1.6313 | 0.76558 | 0.22766 | 2.6245 | 8.57% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2011-02-23 | 28 | 20.0931 | 11.1212 | 31.2143 | 1.6949 | 0.76558 | 0.23205 | 2.6925 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.1011 | 1.0661
2011-02-23 | 29 | 20.0141 | 11.196 | 31.2102 | 1.6944 | 0.76558 | 0.23202 | 2.692 | 8.626% | 9.178% | 6.202% | 1.0944 | 1.101 | 1.0661
2011-02-23 | 30 | 19.6829 | 11.329 | 31.012 | 1.673 | 0.76558 | 0.23055 | 2.6691 | 8.607% | 9.158% | 6.188% | 1.0942 | 1.1008 | 1.066
2011-02-23 | 31 | 19.8132 | 11.5832 | 31.3964 | 1.7147 | 0.76558 | 0.2334 | 2.7137 | 8.643% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-02-23 | 32 | 19.893 | 11.747 | 31.64 | 1.7414 | 0.76558 | 0.23522 | 2.7422 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-02-23 | 33 | 20.2223 | 12.1085 | 32.3308 | 1.8183 | 0.76558 | 0.24035 | 2.8242 | 8.735% | 9.295% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-02-23 | 34 | 20.2111 | 11.8506 | 32.0617 | 1.7882 | 0.76558 | 0.23835 | 2.7921 | 8.709% | 9.266% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-02-23 | 35 | 20.7486 | 12.1242 | 32.8727 | 1.8798 | 0.76558 | 0.24438 | 2.8897 | 8.791% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-02-23 | 36 | 21.0612 | 12.3957 | 33.4569 | 1.9472 | 0.76558 | 0.24872 | 2.9615 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-02-23 | 37 | 21.483 | 12.5547 | 34.0377 | 2.0154 | 0.76558 | 0.25304 | 3.034 | 8.914% | 9.484% | 6.409% | 1.0979 | 1.1048 | 1.0685
2011-02-23 | 38 | 21.8445 | 12.2976 | 34.1421 | 2.0278 | 0.76558 | 0.25382 | 3.0472 | 8.925% | 9.496% | 6.417% | 1.098 | 1.1049 | 1.0686
2011-02-23 | 39 | 21.8319 | 11.7751 | 33.607 | 1.9647 | 0.76558 | 0.24984 | 2.9801 | 8.868% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2011-02-23 | 40 | 21.772 | 11.3701 | 33.1421 | 1.9107 | 0.76558 | 0.24638 | 2.9227 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2011-02-23 | 41 | 21.1733 | 11.0458 | 32.2191 | 1.8058 | 0.76558 | 0.23952 | 2.8109 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-02-23 | 42 | 21.1849 | 11.0538 | 32.2387 | 1.808 | 0.76558 | 0.23967 | 2.8132 | 8.726% | 9.285% | 6.274% | 1.0956 | 1.1023 | 1.0669
2011-02-23 | 43 | 21.6785 | 11.3521 | 33.0306 | 1.8979 | 0.76558 | 0.24555 | 2.909 | 8.807% | 9.371% | 6.332% | 1.0966 | 1.1034 | 1.0676
2011-02-23 | 44 | 21.5467 | 10.9707 | 32.5174 | 1.8394 | 0.76558 | 0.24174 | 2.8467 | 8.754% | 9.315% | 6.294% | 1.0959 | 1.1027 | 1.0672
2011-02-23 | 45 | 20.5526 | 10.3652 | 30.9178 | 1.6628 | 0.76558 | 0.22985 | 2.6583 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-02-23 | 46 | 18.7395 | 9.5585 | 28.298 | 1.393 | 0.76558 | 0.21037 | 2.3689 | 8.371% | 8.907% | 6.019% | 1.0914 | 1.0978 | 1.064
2011-02-23 | 47 | 17.0061 | 9.1923 | 26.1985 | 1.194 | 0.76558 | 0.19476 | 2.1543 | 8.223% | 8.749% | 5.912% | 1.0896 | 1.0959 | 1.0628
2011-02-23 | 48 | 15.5241 | 8.945 | 24.4691 | 1.0415 | 0.76558 | 0.18191 | 1.989 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-24 | 1 | 14.2699 | 7.9165 | 22.1864 | 0.85627 | 0.76558 | 0.16494 | 1.7868 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-02-24 | 2 | 12.7248 | 7.4012 | 20.126 | 0.70461 | 0.76558 | 0.14962 | 1.6198 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-24 | 3 | 12.1103 | 7.1589 | 19.2691 | 0.64589 | 0.76558 | 0.14325 | 1.5547 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-02-24 | 4 | 11.6466 | 6.9223 | 18.569 | 0.59981 | 0.76558 | 0.13804 | 1.5034 | 8.096% | 8.615% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-02-24 | 5 | 11.6171 | 7.0387 | 18.6558 | 0.60543 | 0.76558 | 0.13869 | 1.5097 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-02-24 | 6 | 11.2977 | 6.9306 | 18.2282 | 0.57799 | 0.76558 | 0.13551 | 1.4791 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-24 | 7 | 11.0002 | 6.7682 | 17.7685 | 0.5492 | 0.76558 | 0.13209 | 1.4469 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2011-02-24 | 8 | 10.7564 | 6.673 | 17.4293 | 0.52844 | 0.76558 | 0.12957 | 1.4236 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2011-02-24 | 9 | 10.6124 | 6.7376 | 17.35 | 0.52364 | 0.76558 | 0.12898 | 1.4182 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-02-24 | 10 | 10.8621 | 6.7624 | 17.6244 | 0.54034 | 0.76558 | 0.13102 | 1.4369 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-24 | 11 | 11.3366 | 6.9232 | 18.2598 | 0.58 | 0.76558 | 0.13575 | 1.4813 | 8.112% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-02-24 | 12 | 11.8778 | 7.0961 | 18.9739 | 0.62625 | 0.76558 | 0.14105 | 1.5329 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-24 | 13 | 13.3403 | 7.7727 | 21.113 | 0.77542 | 0.76558 | 0.15696 | 1.698 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-24 | 14 | 15.3065 | 8.8634 | 24.1699 | 1.0162 | 0.76558 | 0.17968 | 1.9615 | 8.115% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-24 | 15 | 18.1651 | 10.2079 | 28.373 | 1.4004 | 0.76558 | 0.21093 | 2.3769 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2011-02-24 | 16 | 20.8711 | 11.3228 | 32.1939 | 1.8029 | 0.76558 | 0.23933 | 2.8079 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2011-02-24 | 17 | 22.1489 | 11.7743 | 33.9232 | 2.0018 | 0.76558 | 0.25219 | 3.0196 | 8.901% | 9.471% | 6.4% | 1.0977 | 1.1046 | 1.0684
2011-02-24 | 18 | 22.2304 | 11.7674 | 33.9978 | 2.0106 | 0.76558 | 0.25274 | 3.029 | 8.909% | 9.48% | 6.406% | 1.0978 | 1.1047 | 1.0684
2011-02-24 | 19 | 22.2008 | 11.7878 | 33.9885 | 2.0096 | 0.76558 | 0.25267 | 3.0278 | 8.908% | 9.478% | 6.405% | 1.0978 | 1.1047 | 1.0684
2011-02-24 | 20 | 21.7985 | 11.6434 | 33.4419 | 1.9454 | 0.76558 | 0.24861 | 2.9596 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.104 | 1.068
2011-02-24 | 21 | 21.5001 | 11.5286 | 33.0287 | 1.8977 | 0.76558 | 0.24554 | 2.9088 | 8.807% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2011-02-24 | 22 | 20.898 | 11.4639 | 32.362 | 1.8218 | 0.76558 | 0.24058 | 2.828 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2011-02-24 | 23 | 20.3597 | 11.0918 | 31.4515 | 1.7207 | 0.76558 | 0.23381 | 2.7201 | 8.649% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-02-24 | 24 | 20.2349 | 11.1568 | 31.3917 | 1.7142 | 0.76558 | 0.23337 | 2.7132 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-02-24 | 25 | 20.4267 | 11.3343 | 31.761 | 1.7548 | 0.76558 | 0.23612 | 2.7565 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-02-24 | 26 | 19.995 | 11.1525 | 31.1474 | 1.6876 | 0.76558 | 0.23155 | 2.6848 | 8.62% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-02-24 | 27 | 19.9676 | 11.3263 | 31.2939 | 1.7035 | 0.76558 | 0.23264 | 2.7018 | 8.634% | 9.186% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-02-24 | 28 | 20.2556 | 11.4053 | 31.661 | 1.7437 | 0.76558 | 0.23537 | 2.7447 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2011-02-24 | 29 | 19.7683 | 11.2139 | 30.9822 | 1.6698 | 0.76558 | 0.23033 | 2.6657 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-02-24 | 30 | 19.5571 | 11.0383 | 30.5954 | 1.6283 | 0.76558 | 0.22745 | 2.6214 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-02-24 | 31 | 19.9192 | 10.9733 | 30.8924 | 1.6601 | 0.76558 | 0.22966 | 2.6554 | 8.595% | 9.146% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-02-24 | 32 | 19.7206 | 10.89 | 30.6106 | 1.63 | 0.76558 | 0.22756 | 2.6231 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2011-02-24 | 33 | 19.9581 | 11.1399 | 31.0981 | 1.6823 | 0.76558 | 0.23119 | 2.6791 | 8.615% | 9.166% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-02-24 | 34 | 20.4486 | 11.0153 | 31.4639 | 1.7221 | 0.76558 | 0.23391 | 2.7216 | 8.65% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-02-24 | 35 | 21.1765 | 11.1711 | 32.3476 | 1.8202 | 0.76558 | 0.24048 | 2.8263 | 8.737% | 9.296% | 6.282% | 1.0957 | 1.1025 | 1.067
2011-02-24 | 36 | 22.0597 | 11.4096 | 33.4694 | 1.9486 | 0.76558 | 0.24882 | 2.963 | 8.853% | 9.42% | 6.365% | 1.0971 | 1.104 | 1.068
2011-02-24 | 37 | 22.3739 | 11.5081 | 33.8821 | 1.997 | 0.76558 | 0.25188 | 3.0144 | 8.897% | 9.466% | 6.397% | 1.0977 | 1.1046 | 1.0683
2011-02-24 | 38 | 22.6489 | 11.38 | 34.0289 | 2.0143 | 0.76558 | 0.25297 | 3.0329 | 8.913% | 9.483% | 6.408% | 1.0978 | 1.1048 | 1.0685
2011-02-24 | 39 | 22.524 | 11.0715 | 33.5955 | 1.9633 | 0.76558 | 0.24975 | 2.9787 | 8.866% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2011-02-24 | 40 | 22.0515 | 10.7282 | 32.7798 | 1.8692 | 0.76558 | 0.24369 | 2.8784 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-02-24 | 41 | 21.7961 | 10.4643 | 32.2604 | 1.8104 | 0.76558 | 0.23983 | 2.8158 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-02-24 | 42 | 22.1968 | 10.6091 | 32.8058 | 1.8721 | 0.76558 | 0.24388 | 2.8816 | 8.784% | 9.346% | 6.316% | 1.0963 | 1.1031 | 1.0674
2011-02-24 | 43 | 22.3337 | 10.9385 | 33.2721 | 1.9257 | 0.76558 | 0.24735 | 2.9387 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-02-24 | 44 | 21.5925 | 10.4777 | 32.0702 | 1.7891 | 0.76558 | 0.23841 | 2.7931 | 8.709% | 9.267% | 6.262% | 1.0954 | 1.1021 | 1.0668
2011-02-24 | 45 | 20.0619 | 9.9237 | 29.9856 | 1.5641 | 0.76558 | 0.22292 | 2.5526 | 8.513% | 9.057% | 6.121% | 1.093 | 1.0996 | 1.0652
2011-02-24 | 46 | 18.5902 | 9.0882 | 27.6785 | 1.3327 | 0.76558 | 0.20577 | 2.304 | 8.324% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2011-02-24 | 47 | 16.6946 | 8.8094 | 25.504 | 1.1315 | 0.76558 | 0.1896 | 2.0867 | 8.182% | 8.705% | 5.883% | 1.0891 | 1.0954 | 1.0625
2011-02-24 | 48 | 15.1838 | 8.814 | 23.9978 | 1.0018 | 0.76558 | 0.1784 | 1.9458 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-02-25 | 1 | 13.6079 | 8.151 | 21.7589 | 0.82358 | 0.76558 | 0.16176 | 1.7509 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-25 | 2 | 12.9502 | 7.7409 | 20.6911 | 0.74473 | 0.76558 | 0.15382 | 1.6641 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-25 | 3 | 12.2185 | 7.4459 | 19.6644 | 0.67266 | 0.76558 | 0.14619 | 1.5844 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-02-25 | 4 | 11.821 | 7.3231 | 19.1441 | 0.63754 | 0.76558 | 0.14232 | 1.5454 | 8.073% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-02-25 | 5 | 11.1567 | 7.3777 | 18.5344 | 0.59757 | 0.76558 | 0.13779 | 1.5009 | 8.098% | 8.616% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-02-25 | 6 | 10.9287 | 7.3054 | 18.2342 | 0.57837 | 0.76558 | 0.13555 | 1.4795 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-25 | 7 | 10.6901 | 7.3039 | 17.994 | 0.56324 | 0.76558 | 0.13377 | 1.4626 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-25 | 8 | 10.8754 | 7.233 | 18.1084 | 0.57042 | 0.76558 | 0.13462 | 1.4706 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-25 | 9 | 11.1263 | 7.4288 | 18.5551 | 0.59891 | 0.76558 | 0.13794 | 1.5024 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-02-25 | 10 | 11.3127 | 7.3946 | 18.7073 | 0.60878 | 0.76558 | 0.13907 | 1.5134 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-25 | 11 | 11.2343 | 7.5151 | 18.7494 | 0.61152 | 0.76558 | 0.13939 | 1.5165 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-02-25 | 12 | 11.5048 | 7.8388 | 19.3436 | 0.65089 | 0.76558 | 0.1438 | 1.5603 | 8.066% | 8.582% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-02-25 | 13 | 12.9818 | 8.1672 | 21.149 | 0.77806 | 0.76558 | 0.15722 | 1.7009 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-25 | 14 | 15.4472 | 8.9979 | 24.4452 | 1.0395 | 0.76558 | 0.18173 | 1.9868 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-25 | 15 | 18.8346 | 10.3887 | 29.2233 | 1.4856 | 0.76558 | 0.21725 | 2.4684 | 8.447% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2011-02-25 | 16 | 21.4178 | 11.267 | 32.6847 | 1.8583 | 0.76558 | 0.24298 | 2.8669 | 8.771% | 9.333% | 6.307% | 1.0961 | 1.1029 | 1.0673
2011-02-25 | 17 | 22.2917 | 11.6744 | 33.9661 | 2.0069 | 0.76558 | 0.25251 | 3.025 | 8.906% | 9.476% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-02-25 | 18 | 22.2556 | 11.8608 | 34.1164 | 2.0247 | 0.76558 | 0.25363 | 3.0439 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2011-02-25 | 19 | 21.7891 | 11.9827 | 33.7718 | 1.984 | 0.76558 | 0.25106 | 3.0006 | 8.885% | 9.454% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-02-25 | 20 | 21.6117 | 11.788 | 33.3997 | 1.9405 | 0.76558 | 0.2483 | 2.9544 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-02-25 | 21 | 21.6489 | 11.3046 | 32.9535 | 1.889 | 0.76558 | 0.24498 | 2.8996 | 8.799% | 9.362% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-02-25 | 22 | 21.3199 | 11.4673 | 32.7873 | 1.87 | 0.76558 | 0.24374 | 2.8793 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-02-25 | 23 | 20.9148 | 11.5424 | 32.4571 | 1.8325 | 0.76558 | 0.24129 | 2.8394 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-02-25 | 24 | 20.7257 | 11.5278 | 32.2535 | 1.8096 | 0.76558 | 0.23978 | 2.815 | 8.728% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2011-02-25 | 25 | 20.2677 | 11.4605 | 31.7282 | 1.7512 | 0.76558 | 0.23587 | 2.7526 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-02-25 | 26 | 19.76 | 11.2216 | 30.9815 | 1.6697 | 0.76558 | 0.23032 | 2.6656 | 8.604% | 9.155% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-02-25 | 27 | 19.6763 | 11.3015 | 30.9779 | 1.6693 | 0.76558 | 0.23029 | 2.6652 | 8.604% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-02-25 | 28 | 19.8047 | 11.3645 | 31.1691 | 1.69 | 0.76558 | 0.23172 | 2.6873 | 8.622% | 9.173% | 6.199% | 1.0944 | 1.101 | 1.0661
2011-02-25 | 29 | 19.6607 | 11.1662 | 30.8269 | 1.6531 | 0.76558 | 0.22917 | 2.6478 | 8.589% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-02-25 | 30 | 19.4991 | 10.8781 | 30.3772 | 1.6052 | 0.76558 | 0.22583 | 2.5966 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2011-02-25 | 31 | 19.3496 | 10.5872 | 29.9368 | 1.559 | 0.76558 | 0.22255 | 2.5471 | 8.508% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2011-02-25 | 32 | 19.4572 | 10.4249 | 29.8822 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-02-25 | 33 | 19.5194 | 10.8422 | 30.3616 | 1.6036 | 0.76558 | 0.22571 | 2.5948 | 8.546% | 9.093% | 6.145% | 1.0935 | 1.1 | 1.0655
2011-02-25 | 34 | 19.9079 | 10.7687 | 30.6767 | 1.637 | 0.76558 | 0.22805 | 2.6306 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-02-25 | 35 | 20.5526 | 10.9897 | 31.5423 | 1.7307 | 0.76558 | 0.23449 | 2.7308 | 8.657% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2011-02-25 | 36 | 21.1105 | 11.1963 | 32.3068 | 1.8156 | 0.76558 | 0.24017 | 2.8214 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2011-02-25 | 37 | 21.5854 | 11.5222 | 33.1076 | 1.9067 | 0.76558 | 0.24613 | 2.9184 | 8.815% | 9.379% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-02-25 | 38 | 22.1605 | 11.5944 | 33.7549 | 1.982 | 0.76558 | 0.25094 | 2.9985 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-02-25 | 39 | 22.1281 | 11.34 | 33.4682 | 1.9485 | 0.76558 | 0.24881 | 2.9629 | 8.853% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2011-02-25 | 40 | 21.918 | 10.9976 | 32.9156 | 1.8847 | 0.76558 | 0.2447 | 2.895 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-02-25 | 41 | 21.3399 | 10.8574 | 32.1973 | 1.8033 | 0.76558 | 0.23936 | 2.8083 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2011-02-25 | 42 | 21.7104 | 10.9028 | 32.6133 | 1.8502 | 0.76558 | 0.24245 | 2.8582 | 8.764% | 9.325% | 6.301% | 1.0961 | 1.1028 | 1.0673
2011-02-25 | 43 | 22.3532 | 10.898 | 33.2512 | 1.9233 | 0.76558 | 0.24719 | 2.9361 | 8.83% | 9.395% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-02-25 | 44 | 21.7133 | 10.3896 | 32.1029 | 1.7928 | 0.76558 | 0.23866 | 2.797 | 8.713% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-02-25 | 45 | 20.2815 | 9.7958 | 30.0773 | 1.5737 | 0.76558 | 0.2236 | 2.5628 | 8.521% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2011-02-25 | 46 | 18.4944 | 9.0903 | 27.5847 | 1.3236 | 0.76558 | 0.20507 | 2.2943 | 8.317% | 8.85% | 5.98% | 1.0907 | 1.0971 | 1.0636
2011-02-25 | 47 | 16.7213 | 8.6405 | 25.3618 | 1.1189 | 0.76558 | 0.18854 | 2.073 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-02-25 | 48 | 15.5495 | 8.682 | 24.2315 | 1.0214 | 0.76558 | 0.18014 | 1.9671 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-02-26 | 1 | 13.6415 | 7.9261 | 21.5675 | 0.80916 | 0.76558 | 0.16034 | 1.7351 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-26 | 2 | 12.6518 | 7.5384 | 20.1901 | 0.70911 | 0.76558 | 0.1501 | 1.6248 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-26 | 3 | 12.3292 | 7.216 | 19.5452 | 0.66453 | 0.76558 | 0.1453 | 1.5754 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-26 | 4 | 11.9829 | 6.9962 | 18.9791 | 0.62659 | 0.76558 | 0.14109 | 1.5333 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-26 | 5 | 11.725 | 6.9034 | 18.6284 | 0.60365 | 0.76558 | 0.13849 | 1.5077 | 8.094% | 8.612% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-26 | 6 | 11.3122 | 6.8024 | 18.1146 | 0.57081 | 0.76558 | 0.13467 | 1.4711 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-02-26 | 7 | 10.9962 | 6.7551 | 17.7513 | 0.54814 | 0.76558 | 0.13197 | 1.4457 | 8.144% | 8.665% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-02-26 | 8 | 10.8691 | 6.7582 | 17.6274 | 0.54052 | 0.76558 | 0.13104 | 1.4371 | 8.153% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-26 | 9 | 11.236 | 6.77 | 18.0059 | 0.56398 | 0.76558 | 0.13386 | 1.4634 | 8.127% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-02-26 | 10 | 11.4015 | 6.8344 | 18.2359 | 0.57848 | 0.76558 | 0.13557 | 1.4796 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-02-26 | 11 | 11.6779 | 7.0783 | 18.7562 | 0.61196 | 0.76558 | 0.13944 | 1.517 | 8.088% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-02-26 | 12 | 11.9833 | 7.4217 | 19.4049 | 0.65503 | 0.76558 | 0.14426 | 1.5649 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-02-26 | 13 | 13.3871 | 7.8982 | 21.2854 | 0.78813 | 0.76558 | 0.15824 | 1.7119 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-26 | 14 | 15.5089 | 8.9873 | 24.4962 | 1.0438 | 0.76558 | 0.18211 | 1.9915 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-26 | 15 | 19.1652 | 10.2928 | 29.458 | 1.5095 | 0.76558 | 0.21899 | 2.4941 | 8.467% | 9.008% | 6.088% | 1.0925 | 1.099 | 1.0648
2011-02-26 | 16 | 22.3816 | 11.317 | 33.6986 | 1.9754 | 0.76558 | 0.25052 | 2.9915 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-02-26 | 17 | 23.4629 | 11.6141 | 35.077 | 2.1403 | 0.76558 | 0.26077 | 3.1667 | 9.028% | 9.606% | 6.491% | 1.0992 | 1.1063 | 1.0694
2011-02-26 | 18 | 23.54 | 11.7206 | 35.2606 | 2.1628 | 0.76558 | 0.26213 | 3.1905 | 9.048% | 9.627% | 6.506% | 1.0995 | 1.1065 | 1.0696
2011-02-26 | 19 | 22.994 | 11.7885 | 34.7825 | 2.1045 | 0.76558 | 0.25858 | 3.1287 | 8.995% | 9.571% | 6.467% | 1.0988 | 1.1058 | 1.0691
2011-02-26 | 20 | 22.2936 | 11.5463 | 33.84 | 1.992 | 0.76558 | 0.25157 | 3.0092 | 8.892% | 9.461% | 6.394% | 1.0976 | 1.1045 | 1.0683
2011-02-26 | 21 | 21.703 | 11.1693 | 32.8724 | 1.8797 | 0.76558 | 0.24438 | 2.8897 | 8.791% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-02-26 | 22 | 21.1962 | 11.2872 | 32.4833 | 1.8355 | 0.76558 | 0.24149 | 2.8426 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-02-26 | 23 | 20.7746 | 11.2028 | 31.9774 | 1.7788 | 0.76558 | 0.23772 | 2.7821 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-02-26 | 24 | 20.3895 | 11.0266 | 31.4161 | 1.7169 | 0.76558 | 0.23355 | 2.716 | 8.645% | 9.199% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-02-26 | 25 | 20.1204 | 11.2276 | 31.348 | 1.7094 | 0.76558 | 0.23305 | 2.7081 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-02-26 | 26 | 19.6966 | 11.0936 | 30.7902 | 1.6491 | 0.76558 | 0.2289 | 2.6436 | 8.586% | 9.135% | 6.173% | 1.0939 | 1.1005 | 1.0658
2011-02-26 | 27 | 19.2855 | 11.1753 | 30.4608 | 1.6141 | 0.76558 | 0.22645 | 2.6061 | 8.556% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2011-02-26 | 28 | 19.3338 | 11.2862 | 30.62 | 1.631 | 0.76558 | 0.22763 | 2.6242 | 8.57% | 9.119% | 6.162% | 1.0937 | 1.1003 | 1.0657
2011-02-26 | 29 | 19.6114 | 11.0746 | 30.6861 | 1.638 | 0.76558 | 0.22812 | 2.6317 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-02-26 | 30 | 19.2556 | 10.9383 | 30.1939 | 1.5859 | 0.76558 | 0.22447 | 2.5759 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-02-26 | 31 | 19.3948 | 10.8732 | 30.268 | 1.5937 | 0.76558 | 0.22502 | 2.5843 | 8.538% | 9.084% | 6.139% | 1.0934 | 1.0999 | 1.0654
2011-02-26 | 32 | 19.1488 | 11.0341 | 30.1829 | 1.5847 | 0.76558 | 0.22438 | 2.5747 | 8.53% | 9.076% | 6.133% | 1.0933 | 1.0998 | 1.0653
2011-02-26 | 33 | 19.6317 | 11.5971 | 31.2288 | 1.6965 | 0.76558 | 0.23216 | 2.6942 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-02-26 | 34 | 19.7983 | 11.79 | 31.5883 | 1.7358 | 0.76558 | 0.23483 | 2.7362 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-02-26 | 35 | 19.6198 | 11.9664 | 31.5862 | 1.7355 | 0.76558 | 0.23482 | 2.7359 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-02-26 | 36 | 19.6178 | 12.0414 | 31.6592 | 1.7435 | 0.76558 | 0.23536 | 2.7445 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2011-02-26 | 37 | 20.1338 | 12.2236 | 32.3574 | 1.8213 | 0.76558 | 0.24055 | 2.8274 | 8.738% | 9.297% | 6.283% | 1.0957 | 1.1025 | 1.067
2011-02-26 | 38 | 20.625 | 12.1277 | 32.7527 | 1.8661 | 0.76558 | 0.24349 | 2.8751 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2011-02-26 | 39 | 20.4972 | 11.9834 | 32.4807 | 1.8352 | 0.76558 | 0.24147 | 2.8422 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-02-26 | 40 | 20.3889 | 11.7595 | 32.1484 | 1.7978 | 0.76558 | 0.23899 | 2.8024 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-02-26 | 41 | 19.847 | 11.504 | 31.3509 | 1.7098 | 0.76558 | 0.23307 | 2.7084 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-02-26 | 42 | 20.4137 | 11.5083 | 31.922 | 1.7726 | 0.76558 | 0.23731 | 2.7755 | 8.695% | 9.251% | 6.251% | 1.0952 | 1.1019 | 1.0667
2011-02-26 | 43 | 21.0045 | 11.7469 | 32.7513 | 1.8659 | 0.76558 | 0.24348 | 2.875 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2011-02-26 | 44 | 20.3695 | 11.1749 | 31.5444 | 1.7309 | 0.76558 | 0.2345 | 2.731 | 8.658% | 9.212% | 6.225% | 1.0948 | 1.1015 | 1.0664
2011-02-26 | 45 | 19.265 | 10.502 | 29.7669 | 1.5414 | 0.76558 | 0.22129 | 2.5282 | 8.493% | 9.037% | 6.107% | 1.0928 | 1.0993 | 1.065
2011-02-26 | 46 | 18.1928 | 9.9619 | 28.1547 | 1.3789 | 0.76558 | 0.20931 | 2.3538 | 8.36% | 8.895% | 6.011% | 1.0912 | 1.0976 | 1.064
2011-02-26 | 47 | 16.8501 | 9.8231 | 26.6731 | 1.2376 | 0.76558 | 0.19829 | 2.2015 | 8.254% | 8.782% | 5.934% | 1.09 | 1.0963 | 1.0631
2011-02-26 | 48 | 15.7164 | 9.8725 | 25.5889 | 1.139 | 0.76558 | 0.19023 | 2.0948 | 8.187% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2011-02-27 | 1 | 14.2792 | 8.9139 | 23.1931 | 0.93573 | 0.76558 | 0.17242 | 1.8737 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-02-27 | 2 | 13.1676 | 8.3996 | 21.5672 | 0.80914 | 0.76558 | 0.16033 | 1.7351 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-27 | 3 | 12.2214 | 8.0025 | 20.2239 | 0.71149 | 0.76558 | 0.15035 | 1.6274 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-02-27 | 4 | 11.6697 | 7.7443 | 19.414 | 0.65564 | 0.76558 | 0.14433 | 1.5655 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-02-27 | 5 | 11.3663 | 7.7224 | 19.0886 | 0.63385 | 0.76558 | 0.14191 | 1.5413 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-02-27 | 6 | 11.6084 | 7.4486 | 19.057 | 0.63175 | 0.76558 | 0.14167 | 1.539 | 8.076% | 8.593% | 5.806% | 1.0879 | 1.094 | 1.0616
2011-02-27 | 7 | 11.3023 | 7.3419 | 18.6442 | 0.60468 | 0.76558 | 0.1386 | 1.5089 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-02-27 | 8 | 11.1878 | 7.2007 | 18.3885 | 0.5882 | 0.76558 | 0.1367 | 1.4905 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-27 | 9 | 10.9444 | 7.2698 | 18.2142 | 0.5771 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-27 | 10 | 10.7385 | 7.2203 | 17.9588 | 0.56103 | 0.76558 | 0.13351 | 1.4601 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-02-27 | 11 | 11.1376 | 7.2551 | 18.3927 | 0.58847 | 0.76558 | 0.13673 | 1.4908 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-02-27 | 12 | 11.6817 | 7.265 | 18.9467 | 0.62445 | 0.76558 | 0.14085 | 1.5309 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-02-27 | 13 | 12.7647 | 7.3757 | 20.1404 | 0.70562 | 0.76558 | 0.14973 | 1.6209 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-02-27 | 14 | 13.5574 | 7.8932 | 21.4506 | 0.80041 | 0.76558 | 0.15947 | 1.7255 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-02-27 | 15 | 15.0057 | 8.4744 | 23.4801 | 0.95904 | 0.76558 | 0.17455 | 1.8992 | 8.088% | 8.606% | 5.816% | 1.088 | 1.0942 | 1.0617
2011-02-27 | 16 | 16.4557 | 9.2682 | 25.724 | 1.1511 | 0.76558 | 0.19124 | 2.1079 | 8.194% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2011-02-27 | 17 | 18.3236 | 10.1339 | 28.4575 | 1.4087 | 0.76558 | 0.21156 | 2.3859 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2011-02-27 | 18 | 20.26 | 10.6628 | 30.9227 | 1.6634 | 0.76558 | 0.22988 | 2.6588 | 8.598% | 9.149% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-02-27 | 19 | 21.579 | 11.1865 | 32.7655 | 1.8675 | 0.76558 | 0.24358 | 2.8767 | 8.78% | 9.342% | 6.313% | 1.0962 | 1.103 | 1.0674
2011-02-27 | 20 | 22.2322 | 11.4067 | 33.6388 | 1.9684 | 0.76558 | 0.25008 | 2.9841 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2011-02-27 | 21 | 22.0948 | 11.484 | 33.5789 | 1.9614 | 0.76558 | 0.24963 | 2.9766 | 8.865% | 9.432% | 6.374% | 1.0973 | 1.1041 | 1.0681
2011-02-27 | 22 | 21.6522 | 11.767 | 33.4192 | 1.9428 | 0.76558 | 0.24844 | 2.9568 | 8.848% | 9.414% | 6.361% | 1.0971 | 1.1039 | 1.0679
2011-02-27 | 23 | 20.6576 | 11.2157 | 31.8733 | 1.7672 | 0.76558 | 0.23695 | 2.7697 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-02-27 | 24 | 20.2494 | 11.1601 | 31.4095 | 1.7162 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-02-27 | 25 | 20.0102 | 11.0483 | 31.0586 | 1.678 | 0.76558 | 0.23089 | 2.6745 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-02-27 | 26 | 19.6421 | 10.6491 | 30.2912 | 1.5961 | 0.76558 | 0.22519 | 2.5869 | 8.54% | 9.087% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-02-27 | 27 | 19.5124 | 10.5828 | 30.0952 | 1.5755 | 0.76558 | 0.22373 | 2.5648 | 8.522% | 9.068% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-02-27 | 28 | 19.4294 | 10.3818 | 29.8111 | 1.5459 | 0.76558 | 0.22162 | 2.5331 | 8.497% | 9.041% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-02-27 | 29 | 18.8764 | 10.1198 | 28.9962 | 1.4626 | 0.76558 | 0.21556 | 2.4437 | 8.428% | 8.967% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-02-27 | 30 | 18.4672 | 10.2054 | 28.6727 | 1.4301 | 0.76558 | 0.21316 | 2.4088 | 8.401% | 8.939% | 6.04% | 1.0917 | 1.0982 | 1.0643
2011-02-27 | 31 | 18.7261 | 10.0236 | 28.7497 | 1.4378 | 0.76558 | 0.21373 | 2.4171 | 8.407% | 8.946% | 6.045% | 1.0918 | 1.0982 | 1.0643
2011-02-27 | 32 | 18.7321 | 9.8438 | 28.5759 | 1.4205 | 0.76558 | 0.21244 | 2.3985 | 8.393% | 8.931% | 6.035% | 1.0916 | 1.0981 | 1.0642
2011-02-27 | 33 | 18.7897 | 10.1595 | 28.9491 | 1.4578 | 0.76558 | 0.21521 | 2.4386 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2011-02-27 | 34 | 19.0661 | 10.1923 | 29.2584 | 1.4891 | 0.76558 | 0.21751 | 2.4722 | 8.45% | 8.99% | 6.075% | 1.0923 | 1.0988 | 1.0647
2011-02-27 | 35 | 19.3911 | 10.486 | 29.8771 | 1.5528 | 0.76558 | 0.22211 | 2.5405 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-02-27 | 36 | 19.7502 | 10.7166 | 30.4668 | 1.6147 | 0.76558 | 0.22649 | 2.6068 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2011-02-27 | 37 | 20.2155 | 10.7818 | 30.9974 | 1.6714 | 0.76558 | 0.23044 | 2.6674 | 8.605% | 9.156% | 6.187% | 1.0942 | 1.1008 | 1.066
2011-02-27 | 38 | 19.9909 | 10.7497 | 30.7406 | 1.6438 | 0.76558 | 0.22853 | 2.6379 | 8.581% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-02-27 | 39 | 20.1631 | 10.6102 | 30.7733 | 1.6473 | 0.76558 | 0.22877 | 2.6417 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-02-27 | 40 | 20.0766 | 10.2978 | 30.3744 | 1.6049 | 0.76558 | 0.22581 | 2.5963 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2011-02-27 | 41 | 19.897 | 10.2119 | 30.1089 | 1.577 | 0.76558 | 0.22383 | 2.5664 | 8.524% | 9.069% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-02-27 | 42 | 20.3877 | 10.1828 | 30.5705 | 1.6257 | 0.76558 | 0.22726 | 2.6185 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-02-27 | 43 | 20.9276 | 10.0976 | 31.0252 | 1.6744 | 0.76558 | 0.23065 | 2.6706 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-02-27 | 44 | 20.2726 | 9.7545 | 30.0271 | 1.5684 | 0.76558 | 0.22323 | 2.5572 | 8.516% | 9.061% | 6.123% | 1.0931 | 1.0996 | 1.0652
2011-02-27 | 45 | 19.2117 | 9.3912 | 28.603 | 1.4232 | 0.76558 | 0.21264 | 2.4014 | 8.396% | 8.933% | 6.036% | 1.0917 | 1.0981 | 1.0642
2011-02-27 | 46 | 17.7063 | 8.687 | 26.3933 | 1.2118 | 0.76558 | 0.19621 | 2.1736 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2011-02-27 | 47 | 16.5009 | 8.4795 | 24.9804 | 1.0855 | 0.76558 | 0.18571 | 2.0368 | 8.154% | 8.675% | 5.862% | 1.0888 | 1.095 | 1.0623
2011-02-27 | 48 | 15.5675 | 8.5541 | 24.1216 | 1.0122 | 0.76558 | 0.17932 | 1.9571 | 8.113% | 8.633% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-02-28 | 1 | 14.2687 | 7.8089 | 22.0776 | 0.84789 | 0.76558 | 0.16413 | 1.7776 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-02-28 | 2 | 13.407 | 7.1993 | 20.6063 | 0.73864 | 0.76558 | 0.15319 | 1.6574 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-02-28 | 3 | 12.6345 | 6.948 | 19.5826 | 0.66707 | 0.76558 | 0.14558 | 1.5782 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-02-28 | 4 | 12.1193 | 6.7273 | 18.8466 | 0.61787 | 0.76558 | 0.14011 | 1.5236 | 8.084% | 8.601% | 5.812% | 1.088 | 1.0941 | 1.0617
2011-02-28 | 5 | 11.5422 | 6.6729 | 18.2151 | 0.57716 | 0.76558 | 0.13541 | 1.4782 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-02-28 | 6 | 11.2361 | 6.5453 | 17.7815 | 0.55001 | 0.76558 | 0.13219 | 1.4478 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-02-28 | 7 | 11.2262 | 6.647 | 17.8732 | 0.5557 | 0.76558 | 0.13287 | 1.4541 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-02-28 | 8 | 11.1769 | 6.6374 | 17.8143 | 0.55204 | 0.76558 | 0.13243 | 1.4501 | 8.14% | 8.661% | 5.853% | 1.0886 | 1.0948 | 1.0622
2011-02-28 | 9 | 11.3352 | 6.6352 | 17.9703 | 0.56176 | 0.76558 | 0.13359 | 1.4609 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-02-28 | 10 | 11.0621 | 6.6858 | 17.7478 | 0.54793 | 0.76558 | 0.13194 | 1.4454 | 8.144% | 8.666% | 5.856% | 1.0887 | 1.0949 | 1.0622
2011-02-28 | 11 | 10.9573 | 6.8095 | 17.7668 | 0.5491 | 0.76558 | 0.13208 | 1.4468 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2011-02-28 | 12 | 11.1546 | 6.697 | 17.8516 | 0.55436 | 0.76558 | 0.13271 | 1.4526 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-02-28 | 13 | 12.0039 | 6.6969 | 18.7008 | 0.60835 | 0.76558 | 0.13902 | 1.513 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-02-28 | 14 | 12.9222 | 6.981 | 19.9032 | 0.6891 | 0.76558 | 0.14796 | 1.6026 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-02-28 | 15 | 13.9867 | 7.1874 | 21.1741 | 0.77991 | 0.76558 | 0.15741 | 1.7029 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-02-28 | 16 | 15.2806 | 7.7627 | 23.0434 | 0.92369 | 0.76558 | 0.17131 | 1.8606 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-02-28 | 17 | 16.7737 | 8.5157 | 25.2894 | 1.1125 | 0.76558 | 0.188 | 2.0661 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-02-28 | 18 | 18.3293 | 9.088 | 27.4173 | 1.3076 | 0.76558 | 0.20382 | 2.277 | 8.305% | 8.837% | 5.971% | 1.0906 | 1.0969 | 1.0635
2011-02-28 | 19 | 20.1195 | 9.6785 | 29.798 | 1.5446 | 0.76558 | 0.22152 | 2.5317 | 8.496% | 9.04% | 6.109% | 1.0928 | 1.0994 | 1.0651
2011-02-28 | 20 | 21.1669 | 10.1016 | 31.2685 | 1.7008 | 0.76558 | 0.23245 | 2.6988 | 8.631% | 9.183% | 6.206% | 1.0945 | 1.1011 | 1.0662
2011-02-28 | 21 | 21.4508 | 10.2831 | 31.7338 | 1.7518 | 0.76558 | 0.23591 | 2.7533 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-02-28 | 22 | 21.2478 | 10.4281 | 31.6758 | 1.7454 | 0.76558 | 0.23548 | 2.7464 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-02-28 | 23 | 20.8962 | 10.4892 | 31.3854 | 1.7135 | 0.76558 | 0.23332 | 2.7124 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-02-28 | 24 | 20.1269 | 10.1474 | 30.2743 | 1.5943 | 0.76558 | 0.22506 | 2.585 | 8.539% | 9.085% | 6.139% | 1.0934 | 1.0999 | 1.0654
2011-02-28 | 25 | 19.6544 | 10.0948 | 29.7492 | 1.5395 | 0.76558 | 0.22116 | 2.5263 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-02-28 | 26 | 19.7221 | 10.1343 | 29.8565 | 1.5506 | 0.76558 | 0.22196 | 2.5382 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2011-02-28 | 27 | 19.6353 | 10.156 | 29.7912 | 1.5439 | 0.76558 | 0.22147 | 2.5309 | 8.496% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2011-02-28 | 28 | 19.6368 | 9.8167 | 29.4535 | 1.5091 | 0.76558 | 0.21896 | 2.4936 | 8.466% | 9.008% | 6.087% | 1.0925 | 1.099 | 1.0648
2011-02-28 | 29 | 19.3514 | 9.6526 | 29.004 | 1.4634 | 0.76558 | 0.21562 | 2.4446 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-02-28 | 30 | 19.0883 | 9.3715 | 28.4598 | 1.409 | 0.76558 | 0.21157 | 2.3861 | 8.384% | 8.921% | 6.028% | 1.0915 | 1.0979 | 1.0641
2011-02-28 | 31 | 18.6869 | 9.346 | 28.033 | 1.367 | 0.76558 | 0.2084 | 2.341 | 8.351% | 8.885% | 6.004% | 1.0911 | 1.0975 | 1.0639
2011-02-28 | 32 | 18.5744 | 9.2116 | 27.786 | 1.343 | 0.76558 | 0.20656 | 2.3152 | 8.332% | 8.865% | 5.991% | 1.0909 | 1.0973 | 1.0637
2011-02-28 | 33 | 19.1023 | 9.3495 | 28.4517 | 1.4082 | 0.76558 | 0.21151 | 2.3853 | 8.384% | 8.92% | 6.028% | 1.0915 | 1.0979 | 1.0641
2011-02-28 | 34 | 19.4466 | 9.5477 | 28.9943 | 1.4624 | 0.76558 | 0.21555 | 2.4435 | 8.428% | 8.967% | 6.059% | 1.092 | 1.0985 | 1.0645
2011-02-28 | 35 | 20.1071 | 10.1143 | 30.2214 | 1.5888 | 0.76558 | 0.22467 | 2.579 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-02-28 | 36 | 20.7963 | 10.7298 | 31.5261 | 1.7289 | 0.76558 | 0.23437 | 2.7289 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2011-02-28 | 37 | 21.4073 | 11.0151 | 32.4224 | 1.8286 | 0.76558 | 0.24103 | 2.8352 | 8.745% | 9.304% | 6.287% | 1.0958 | 1.1026 | 1.0671
2011-02-28 | 38 | 21.7815 | 11.0166 | 32.7981 | 1.8712 | 0.76558 | 0.24382 | 2.8807 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2011-02-28 | 39 | 21.4354 | 10.7224 | 32.1578 | 1.7989 | 0.76558 | 0.23906 | 2.8035 | 8.718% | 9.276% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-02-28 | 40 | 20.8601 | 10.4485 | 31.3086 | 1.7051 | 0.76558 | 0.23275 | 2.7035 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-02-28 | 41 | 21.1123 | 10.38 | 31.4923 | 1.7252 | 0.76558 | 0.23412 | 2.7249 | 8.653% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-02-28 | 42 | 21.6393 | 10.3562 | 31.9955 | 1.7808 | 0.76558 | 0.23786 | 2.7842 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-02-28 | 43 | 21.2272 | 10.1009 | 31.3282 | 1.7073 | 0.76558 | 0.2329 | 2.7058 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2011-02-28 | 44 | 20.6924 | 9.7734 | 30.4658 | 1.6146 | 0.76558 | 0.22649 | 2.6067 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0655
2011-02-28 | 45 | 19.215 | 9.0507 | 28.2657 | 1.3898 | 0.76558 | 0.21013 | 2.3655 | 8.369% | 8.904% | 6.017% | 1.0913 | 1.0977 | 1.064
2011-02-28 | 46 | 17.6447 | 8.4102 | 26.0549 | 1.1809 | 0.76558 | 0.1937 | 2.1402 | 8.214% | 8.74% | 5.906% | 1.0895 | 1.0958 | 1.0628
2011-02-28 | 47 | 16.0266 | 8.1782 | 24.2048 | 1.0192 | 0.76558 | 0.17994 | 1.9647 | 8.117% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-02-28 | 48 | 14.5277 | 8.3199 | 22.8476 | 0.90806 | 0.76558 | 0.16985 | 1.8435 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-03-01 | 1 | 13.0791 | 7.6502 | 20.7294 | 0.74749 | 0.76558 | 0.1541 | 1.6672 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-01 | 2 | 12.4902 | 7.1303 | 19.6205 | 0.66966 | 0.76558 | 0.14586 | 1.5811 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-01 | 3 | 11.9286 | 6.82 | 18.7486 | 0.61147 | 0.76558 | 0.13938 | 1.5164 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-03-01 | 4 | 11.4707 | 6.5482 | 18.0189 | 0.5648 | 0.76558 | 0.13395 | 1.4643 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2011-03-01 | 5 | 10.9886 | 6.5272 | 17.5157 | 0.53369 | 0.76558 | 0.13021 | 1.4295 | 8.161% | 8.683% | 5.868% | 1.0889 | 1.0951 | 1.0623
2011-03-01 | 6 | 10.7561 | 6.4095 | 17.1656 | 0.51257 | 0.76558 | 0.12761 | 1.4058 | 8.189% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2011-03-01 | 7 | 10.6261 | 6.3401 | 16.9661 | 0.50073 | 0.76558 | 0.12613 | 1.3924 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2011-03-01 | 8 | 10.8511 | 6.4532 | 17.3043 | 0.52088 | 0.76558 | 0.12864 | 1.4151 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2011-03-01 | 9 | 10.868 | 6.614 | 17.4821 | 0.53164 | 0.76558 | 0.12996 | 1.4272 | 8.164% | 8.686% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-03-01 | 10 | 11.023 | 6.546 | 17.569 | 0.53694 | 0.76558 | 0.13061 | 1.4331 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2011-03-01 | 11 | 11.1421 | 6.691 | 17.8331 | 0.55321 | 0.76558 | 0.13257 | 1.4514 | 8.139% | 8.659% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-03-01 | 12 | 11.5877 | 6.9054 | 18.4931 | 0.59491 | 0.76558 | 0.13748 | 1.498 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-01 | 13 | 12.7899 | 7.5643 | 20.3542 | 0.72068 | 0.76558 | 0.15132 | 1.6376 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-01 | 14 | 14.8943 | 8.5569 | 23.4512 | 0.95668 | 0.76558 | 0.17434 | 1.8966 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-03-01 | 15 | 18.264 | 9.9387 | 28.2026 | 1.3836 | 0.76558 | 0.20966 | 2.3589 | 8.364% | 8.899% | 6.014% | 1.0913 | 1.0977 | 1.064
2011-03-01 | 16 | 21.054 | 10.7798 | 31.8337 | 1.7628 | 0.76558 | 0.23666 | 2.7651 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2011-03-01 | 17 | 22.2404 | 10.9902 | 33.2307 | 1.9209 | 0.76558 | 0.24704 | 2.9336 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-03-01 | 18 | 22.5174 | 11.0304 | 33.5477 | 1.9578 | 0.76558 | 0.2494 | 2.9727 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-03-01 | 19 | 22.3168 | 11.229 | 33.5458 | 1.9575 | 0.76558 | 0.24938 | 2.9725 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-03-01 | 20 | 22.039 | 11.1336 | 33.1726 | 1.9142 | 0.76558 | 0.24661 | 2.9264 | 8.822% | 9.386% | 6.343% | 1.0968 | 1.1036 | 1.0677
2011-03-01 | 21 | 22.1063 | 10.9885 | 33.0948 | 1.9053 | 0.76558 | 0.24603 | 2.9169 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2011-03-01 | 22 | 21.7396 | 11.0862 | 32.8259 | 1.8744 | 0.76558 | 0.24403 | 2.884 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-03-01 | 23 | 21.5457 | 10.7704 | 32.316 | 1.8166 | 0.76558 | 0.24024 | 2.8225 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2011-03-01 | 24 | 21.3878 | 10.817 | 32.2048 | 1.8042 | 0.76558 | 0.23941 | 2.8092 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-03-01 | 25 | 21.3158 | 10.8663 | 32.1821 | 1.8016 | 0.76558 | 0.23925 | 2.8064 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-03-01 | 26 | 21.4118 | 10.5984 | 32.0103 | 1.7824 | 0.76558 | 0.23797 | 2.786 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-01 | 27 | 21.585 | 10.788 | 32.373 | 1.8231 | 0.76558 | 0.24066 | 2.8293 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-03-01 | 28 | 22.0806 | 10.8387 | 32.9194 | 1.8851 | 0.76558 | 0.24473 | 2.8954 | 8.795% | 9.358% | 6.324% | 1.0964 | 1.1032 | 1.0675
2011-03-01 | 29 | 21.8007 | 10.6748 | 32.4755 | 1.8346 | 0.76558 | 0.24143 | 2.8416 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-03-01 | 30 | 21.9049 | 10.3316 | 32.2365 | 1.8077 | 0.76558 | 0.23965 | 2.8129 | 8.726% | 9.284% | 6.274% | 1.0956 | 1.1023 | 1.0669
2011-03-01 | 31 | 22.1981 | 10.2319 | 32.43 | 1.8295 | 0.76558 | 0.24109 | 2.8361 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2011-03-01 | 32 | 22.2412 | 10.1486 | 32.3898 | 1.825 | 0.76558 | 0.24079 | 2.8313 | 8.741% | 9.301% | 6.285% | 1.0958 | 1.1025 | 1.0671
2011-03-01 | 33 | 22.4053 | 10.387 | 32.7923 | 1.8706 | 0.76558 | 0.24378 | 2.8799 | 8.782% | 9.344% | 6.315% | 1.0963 | 1.1031 | 1.0674
2011-03-01 | 34 | 22.4417 | 10.4546 | 32.8963 | 1.8825 | 0.76558 | 0.24456 | 2.8926 | 8.793% | 9.356% | 6.322% | 1.0964 | 1.1032 | 1.0675
2011-03-01 | 35 | 22.4486 | 10.7547 | 33.2033 | 1.9178 | 0.76558 | 0.24684 | 2.9302 | 8.825% | 9.39% | 6.345% | 1.0968 | 1.1036 | 1.0678
2011-03-01 | 36 | 22.7534 | 11.0274 | 33.7808 | 1.9851 | 0.76558 | 0.25113 | 3.0018 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2011-03-01 | 37 | 23.2623 | 11.138 | 34.4003 | 2.0585 | 0.76558 | 0.25574 | 3.0799 | 8.953% | 9.526% | 6.437% | 1.0983 | 1.1053 | 1.0688
2011-03-01 | 38 | 22.7805 | 11.1118 | 33.8922 | 1.9982 | 0.76558 | 0.25196 | 3.0157 | 8.898% | 9.467% | 6.398% | 1.0977 | 1.1046 | 1.0683
2011-03-01 | 39 | 22.2316 | 10.7237 | 32.9553 | 1.8892 | 0.76558 | 0.24499 | 2.8998 | 8.799% | 9.362% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-03-01 | 40 | 22.3391 | 10.6025 | 32.9416 | 1.8877 | 0.76558 | 0.24489 | 2.8981 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-03-01 | 41 | 22.1989 | 10.3699 | 32.5688 | 1.8452 | 0.76558 | 0.24212 | 2.8529 | 8.76% | 9.32% | 6.298% | 1.096 | 1.1028 | 1.0672
2011-03-01 | 42 | 23.0753 | 10.5478 | 33.6231 | 1.9666 | 0.76558 | 0.24996 | 2.9821 | 8.869% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-03-01 | 43 | 23.1013 | 10.4654 | 33.5667 | 1.96 | 0.76558 | 0.24954 | 2.9751 | 8.863% | 9.43% | 6.373% | 1.0973 | 1.1041 | 1.0681
2011-03-01 | 44 | 22.7289 | 9.9324 | 32.6614 | 1.8557 | 0.76558 | 0.24281 | 2.8641 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-03-01 | 45 | 21.2535 | 9.2592 | 30.5127 | 1.6196 | 0.76558 | 0.22684 | 2.612 | 8.56% | 9.108% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-03-01 | 46 | 19.1647 | 8.5228 | 27.6875 | 1.3335 | 0.76558 | 0.20583 | 2.3049 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2011-03-01 | 47 | 17.2932 | 8.0588 | 25.3521 | 1.118 | 0.76558 | 0.18847 | 2.0721 | 8.173% | 8.696% | 5.877% | 1.089 | 1.0952 | 1.0624
2011-03-01 | 48 | 16.2173 | 8.1045 | 24.3218 | 1.029 | 0.76558 | 0.18081 | 1.9754 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-02 | 1 | 14.7592 | 7.4448 | 22.204 | 0.85762 | 0.76558 | 0.16507 | 1.7883 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-02 | 2 | 13.6016 | 6.8664 | 20.468 | 0.72876 | 0.76558 | 0.15216 | 1.6465 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-02 | 3 | 12.7535 | 6.5548 | 19.3083 | 0.64852 | 0.76558 | 0.14354 | 1.5576 | 8.067% | 8.583% | 5.8% | 1.0878 | 1.0939 | 1.0616
2011-03-02 | 4 | 12.1454 | 6.4473 | 18.5927 | 0.60134 | 0.76558 | 0.13822 | 1.5051 | 8.095% | 8.613% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-02 | 5 | 11.6713 | 6.5427 | 18.214 | 0.57709 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-02 | 6 | 11.5671 | 6.5329 | 18.1 | 0.56989 | 0.76558 | 0.13456 | 1.47 | 8.122% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-02 | 7 | 11.6008 | 6.4423 | 18.0431 | 0.56631 | 0.76558 | 0.13413 | 1.466 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-02 | 8 | 11.7046 | 6.3329 | 18.0375 | 0.56596 | 0.76558 | 0.13409 | 1.4656 | 8.125% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-02 | 9 | 12.0021 | 6.4051 | 18.4072 | 0.5894 | 0.76558 | 0.13684 | 1.4918 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-03-02 | 10 | 11.8955 | 6.4478 | 18.3433 | 0.58531 | 0.76558 | 0.13637 | 1.4873 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-03-02 | 11 | 12.1674 | 6.62 | 18.7874 | 0.614 | 0.76558 | 0.13967 | 1.5192 | 8.087% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-03-02 | 12 | 12.7934 | 6.8202 | 19.6136 | 0.66919 | 0.76558 | 0.14581 | 1.5806 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-02 | 13 | 14.4055 | 7.4642 | 21.8696 | 0.83199 | 0.76558 | 0.16258 | 1.7601 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-02 | 14 | 16.7988 | 8.5213 | 25.3201 | 1.1152 | 0.76558 | 0.18823 | 2.069 | 8.172% | 8.695% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-03-02 | 15 | 20.2853 | 10.0779 | 30.3632 | 1.6037 | 0.76558 | 0.22572 | 2.595 | 8.547% | 9.094% | 6.145% | 1.0935 | 1.1 | 1.0655
2011-03-02 | 16 | 23.6151 | 10.9744 | 34.5896 | 2.0813 | 0.76558 | 0.25714 | 3.104 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2011-03-02 | 17 | 24.5129 | 11.4593 | 35.9721 | 2.251 | 0.76558 | 0.26742 | 3.284 | 9.129% | 9.713% | 6.564% | 1.1005 | 1.1076 | 1.0702
2011-03-02 | 18 | 24.3931 | 11.3452 | 35.7382 | 2.2218 | 0.76558 | 0.26568 | 3.253 | 9.102% | 9.685% | 6.545% | 1.1001 | 1.1072 | 1.07
2011-03-02 | 19 | 24.0012 | 11.3761 | 35.3773 | 2.1771 | 0.76558 | 0.263 | 3.2057 | 9.061% | 9.641% | 6.515% | 1.0996 | 1.1067 | 1.0697
2011-03-02 | 20 | 22.977 | 11.0125 | 33.9895 | 2.0097 | 0.76558 | 0.25268 | 3.0279 | 8.908% | 9.479% | 6.405% | 1.0978 | 1.1047 | 1.0684
2011-03-02 | 21 | 22.429 | 10.7093 | 33.1383 | 1.9103 | 0.76558 | 0.24635 | 2.9222 | 8.818% | 9.383% | 6.34% | 1.0967 | 1.1035 | 1.0677
2011-03-02 | 22 | 21.8867 | 10.9617 | 32.8484 | 1.877 | 0.76558 | 0.2442 | 2.8868 | 8.788% | 9.351% | 6.319% | 1.0963 | 1.1032 | 1.0674
2011-03-02 | 23 | 21.6472 | 10.6615 | 32.3087 | 1.8158 | 0.76558 | 0.24019 | 2.8216 | 8.733% | 9.292% | 6.279% | 1.0957 | 1.1024 | 1.067
2011-03-02 | 24 | 20.8128 | 10.5486 | 31.3614 | 1.7109 | 0.76558 | 0.23314 | 2.7096 | 8.64% | 9.193% | 6.212% | 1.0946 | 1.1012 | 1.0662
2011-03-02 | 25 | 20.5799 | 10.4285 | 31.0084 | 1.6726 | 0.76558 | 0.23052 | 2.6687 | 8.606% | 9.157% | 6.188% | 1.0942 | 1.1008 | 1.066
2011-03-02 | 26 | 20.2427 | 10.2795 | 30.5222 | 1.6206 | 0.76558 | 0.22691 | 2.6131 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-03-02 | 27 | 20.2357 | 10.529 | 30.7647 | 1.6464 | 0.76558 | 0.22871 | 2.6407 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-03-02 | 28 | 20.0395 | 10.3914 | 30.4309 | 1.6109 | 0.76558 | 0.22623 | 2.6027 | 8.553% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-03-02 | 29 | 19.6972 | 10.136 | 29.8332 | 1.5482 | 0.76558 | 0.22178 | 2.5356 | 8.499% | 9.043% | 6.111% | 1.0929 | 1.0994 | 1.0651
2011-03-02 | 30 | 19.1682 | 9.9206 | 29.0889 | 1.4719 | 0.76558 | 0.21625 | 2.4538 | 8.435% | 8.975% | 6.065% | 1.0921 | 1.0986 | 1.0646
2011-03-02 | 31 | 18.9849 | 9.9442 | 28.9291 | 1.4558 | 0.76558 | 0.21506 | 2.4364 | 8.422% | 8.961% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-03-02 | 32 | 19.0945 | 10.2181 | 29.3126 | 1.4947 | 0.76558 | 0.21791 | 2.4782 | 8.454% | 8.995% | 6.079% | 1.0923 | 1.0988 | 1.0647
2011-03-02 | 33 | 19.7575 | 10.5892 | 30.3467 | 1.602 | 0.76558 | 0.2256 | 2.5932 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-03-02 | 34 | 19.8243 | 10.7269 | 30.5512 | 1.6236 | 0.76558 | 0.22712 | 2.6163 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2011-03-02 | 35 | 20.3627 | 11.1043 | 31.467 | 1.7224 | 0.76558 | 0.23393 | 2.722 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-02 | 36 | 20.9809 | 11.6575 | 32.6384 | 1.8531 | 0.76558 | 0.24264 | 2.8613 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-03-02 | 37 | 21.4884 | 11.7371 | 33.2256 | 1.9203 | 0.76558 | 0.247 | 2.9329 | 8.827% | 9.392% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-03-02 | 38 | 21.7627 | 11.5134 | 33.2762 | 1.9262 | 0.76558 | 0.24738 | 2.9392 | 8.833% | 9.398% | 6.351% | 1.0969 | 1.1037 | 1.0678
2011-03-02 | 39 | 22.1704 | 11.5175 | 33.6879 | 1.9742 | 0.76558 | 0.25044 | 2.9902 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2011-03-02 | 40 | 22.4985 | 11.2463 | 33.7448 | 1.9808 | 0.76558 | 0.25086 | 2.9973 | 8.882% | 9.451% | 6.386% | 1.0975 | 1.1044 | 1.0682
2011-03-02 | 41 | 23.2235 | 11.1366 | 34.3601 | 2.0537 | 0.76558 | 0.25544 | 3.0747 | 8.949% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-02 | 42 | 24.1957 | 11.2322 | 35.4279 | 2.1834 | 0.76558 | 0.26338 | 3.2123 | 9.067% | 9.647% | 6.519% | 1.0997 | 1.1068 | 1.0697
2011-03-02 | 43 | 23.6617 | 11.0294 | 34.6911 | 2.0935 | 0.76558 | 0.2579 | 3.117 | 8.985% | 9.56% | 6.46% | 1.0987 | 1.1057 | 1.0691
2011-03-02 | 44 | 22.3345 | 10.6369 | 32.9714 | 1.8911 | 0.76558 | 0.24511 | 2.9018 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-03-02 | 45 | 20.6367 | 9.8112 | 30.4479 | 1.6127 | 0.76558 | 0.22635 | 2.6046 | 8.554% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2011-03-02 | 46 | 18.823 | 9.2337 | 28.0568 | 1.3693 | 0.76558 | 0.20858 | 2.3435 | 8.353% | 8.887% | 6.006% | 1.0911 | 1.0975 | 1.0639
2011-03-02 | 47 | 17.2333 | 8.8537 | 26.087 | 1.1838 | 0.76558 | 0.19393 | 2.1433 | 8.216% | 8.742% | 5.907% | 1.0895 | 1.0958 | 1.0628
2011-03-02 | 48 | 15.8978 | 8.7686 | 24.6664 | 1.0584 | 0.76558 | 0.18337 | 2.0073 | 8.138% | 8.659% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-03-03 | 1 | 14.4013 | 7.9952 | 22.3965 | 0.87256 | 0.76558 | 0.1665 | 1.8046 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-03 | 2 | 13.4713 | 7.5645 | 21.0358 | 0.76975 | 0.76558 | 0.15638 | 1.6917 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-03 | 3 | 12.2617 | 7.1772 | 19.4389 | 0.65732 | 0.76558 | 0.14451 | 1.5674 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-03-03 | 4 | 11.9112 | 6.9115 | 18.8227 | 0.61631 | 0.76558 | 0.13993 | 1.5218 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-03-03 | 5 | 12.0375 | 6.9132 | 18.9506 | 0.62472 | 0.76558 | 0.14088 | 1.5312 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-03-03 | 6 | 11.7823 | 6.8783 | 18.6606 | 0.60574 | 0.76558 | 0.13872 | 1.51 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-03 | 7 | 11.5613 | 6.8429 | 18.4041 | 0.5892 | 0.76558 | 0.13682 | 1.4916 | 8.105% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-03-03 | 8 | 11.4103 | 6.8287 | 18.239 | 0.57868 | 0.76558 | 0.13559 | 1.4798 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-03 | 9 | 11.3488 | 6.9284 | 18.2772 | 0.5811 | 0.76558 | 0.13587 | 1.4826 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-03 | 10 | 11.3779 | 6.8964 | 18.2742 | 0.58092 | 0.76558 | 0.13585 | 1.4823 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-03 | 11 | 11.9712 | 7.0689 | 19.0401 | 0.63063 | 0.76558 | 0.14155 | 1.5378 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-03-03 | 12 | 12.6649 | 7.2415 | 19.9064 | 0.68932 | 0.76558 | 0.14799 | 1.6029 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0615
2011-03-03 | 13 | 14.2379 | 7.9136 | 22.1515 | 0.85357 | 0.76558 | 0.16468 | 1.7838 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-03 | 14 | 16.2967 | 9.0238 | 25.3206 | 1.1153 | 0.76558 | 0.18824 | 2.0691 | 8.172% | 8.695% | 5.875% | 1.089 | 1.0952 | 1.0624
2011-03-03 | 15 | 19.6998 | 10.5344 | 30.2342 | 1.5901 | 0.76558 | 0.22476 | 2.5805 | 8.535% | 9.081% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-03-03 | 16 | 22.3743 | 11.3865 | 33.7608 | 1.9827 | 0.76558 | 0.25098 | 2.9993 | 8.884% | 9.452% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-03-03 | 17 | 22.8399 | 11.3739 | 34.2138 | 2.0363 | 0.76558 | 0.25435 | 3.0562 | 8.933% | 9.504% | 6.423% | 1.0981 | 1.105 | 1.0686
2011-03-03 | 18 | 23.8599 | 11.7922 | 35.6522 | 2.2111 | 0.76558 | 0.26504 | 3.2417 | 9.093% | 9.675% | 6.538% | 1.1 | 1.1071 | 1.0699
2011-03-03 | 19 | 23.4543 | 11.7997 | 35.2539 | 2.162 | 0.76558 | 0.26208 | 3.1896 | 9.048% | 9.627% | 6.505% | 1.0995 | 1.1065 | 1.0696
2011-03-03 | 20 | 22.7371 | 11.4733 | 34.2104 | 2.0359 | 0.76558 | 0.25432 | 3.0558 | 8.932% | 9.504% | 6.422% | 1.0981 | 1.105 | 1.0686
2011-03-03 | 21 | 22.3477 | 11.2686 | 33.6163 | 1.9658 | 0.76558 | 0.24991 | 2.9813 | 8.869% | 9.436% | 6.376% | 1.0973 | 1.1042 | 1.0681
2011-03-03 | 22 | 21.4749 | 10.9854 | 32.4603 | 1.8329 | 0.76558 | 0.24131 | 2.8398 | 8.749% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-03-03 | 23 | 20.8406 | 10.7356 | 31.5762 | 1.7344 | 0.76558 | 0.23474 | 2.7347 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-03 | 24 | 20.4188 | 10.6291 | 31.0479 | 1.6769 | 0.76558 | 0.23081 | 2.6733 | 8.61% | 9.161% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-03-03 | 25 | 20.4126 | 10.8279 | 31.2405 | 1.6977 | 0.76558 | 0.23225 | 2.6956 | 8.628% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-03-03 | 26 | 20.0305 | 10.4886 | 30.5191 | 1.6202 | 0.76558 | 0.22688 | 2.6127 | 8.561% | 9.109% | 6.155% | 1.0936 | 1.1002 | 1.0656
2011-03-03 | 27 | 20.0545 | 10.6935 | 30.748 | 1.6446 | 0.76558 | 0.22858 | 2.6388 | 8.582% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-03-03 | 28 | 19.9602 | 10.6786 | 30.6388 | 1.633 | 0.76558 | 0.22777 | 2.6263 | 8.572% | 9.12% | 6.163% | 1.0938 | 1.1004 | 1.0657
2011-03-03 | 29 | 19.7212 | 10.3871 | 30.1083 | 1.5769 | 0.76558 | 0.22383 | 2.5663 | 8.524% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-03-03 | 30 | 19.551 | 10.1099 | 29.6609 | 1.5304 | 0.76558 | 0.2205 | 2.5165 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-03-03 | 31 | 19.4073 | 10.1346 | 29.5419 | 1.5181 | 0.76558 | 0.21962 | 2.5033 | 8.474% | 9.016% | 6.093% | 1.0926 | 1.0991 | 1.0649
2011-03-03 | 32 | 19.4143 | 10.2785 | 29.6927 | 1.5337 | 0.76558 | 0.22074 | 2.52 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2011-03-03 | 33 | 19.5713 | 10.6214 | 30.1927 | 1.5858 | 0.76558 | 0.22446 | 2.5758 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-03-03 | 34 | 19.9188 | 10.4618 | 30.3806 | 1.6056 | 0.76558 | 0.22585 | 2.597 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1001 | 1.0655
2011-03-03 | 35 | 19.9102 | 10.8969 | 30.8071 | 1.651 | 0.76558 | 0.22902 | 2.6456 | 8.588% | 9.137% | 6.174% | 1.0939 | 1.1006 | 1.0658
2011-03-03 | 36 | 20.8201 | 11.2291 | 32.0492 | 1.7868 | 0.76558 | 0.23826 | 2.7906 | 8.707% | 9.265% | 6.261% | 1.0954 | 1.1021 | 1.0668
2011-03-03 | 37 | 21.7596 | 11.4955 | 33.2552 | 1.9238 | 0.76558 | 0.24722 | 2.9366 | 8.83% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-03-03 | 38 | 22.0467 | 11.3805 | 33.4273 | 1.9437 | 0.76558 | 0.2485 | 2.9578 | 8.849% | 9.415% | 6.362% | 1.0971 | 1.1039 | 1.0679
2011-03-03 | 39 | 22.1174 | 11.2867 | 33.404 | 1.941 | 0.76558 | 0.24833 | 2.9549 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-03-03 | 40 | 21.9337 | 11.2089 | 33.1426 | 1.9108 | 0.76558 | 0.24639 | 2.9227 | 8.819% | 9.383% | 6.341% | 1.0967 | 1.1035 | 1.0677
2011-03-03 | 41 | 21.8899 | 10.9718 | 32.8617 | 1.8785 | 0.76558 | 0.2443 | 2.8884 | 8.79% | 9.352% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-03-03 | 42 | 22.4895 | 11.3389 | 33.8284 | 1.9907 | 0.76558 | 0.25148 | 3.0077 | 8.891% | 9.46% | 6.393% | 1.0976 | 1.1045 | 1.0683
2011-03-03 | 43 | 22.8958 | 11.2967 | 34.1925 | 2.0337 | 0.76558 | 0.25419 | 3.0535 | 8.93% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2011-03-03 | 44 | 21.9857 | 10.7448 | 32.7305 | 1.8635 | 0.76558 | 0.24332 | 2.8724 | 8.776% | 9.338% | 6.31% | 1.0962 | 1.103 | 1.0673
2011-03-03 | 45 | 20.7706 | 10.0672 | 30.8378 | 1.6543 | 0.76558 | 0.22925 | 2.6491 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-03-03 | 46 | 18.9497 | 9.123 | 28.0726 | 1.3709 | 0.76558 | 0.2087 | 2.3452 | 8.354% | 8.889% | 6.006% | 1.0912 | 1.0976 | 1.0639
2011-03-03 | 47 | 17.0076 | 8.7194 | 25.727 | 1.1514 | 0.76558 | 0.19126 | 2.1082 | 8.195% | 8.719% | 5.892% | 1.0893 | 1.0955 | 1.0626
2011-03-03 | 48 | 15.6811 | 8.8481 | 24.5292 | 1.0466 | 0.76558 | 0.18235 | 1.9946 | 8.131% | 8.652% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-03-04 | 1 | 13.8934 | 8.0736 | 21.967 | 0.83941 | 0.76558 | 0.16331 | 1.7683 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-03-04 | 2 | 13.0863 | 7.6147 | 20.701 | 0.74545 | 0.76558 | 0.15389 | 1.6649 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-04 | 3 | 12.552 | 7.4521 | 20.0041 | 0.6961 | 0.76558 | 0.14871 | 1.6104 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-03-04 | 4 | 12.1793 | 7.188 | 19.3673 | 0.65249 | 0.76558 | 0.14398 | 1.562 | 8.065% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-03-04 | 5 | 11.8042 | 7.2173 | 19.0215 | 0.6294 | 0.76558 | 0.14141 | 1.5364 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2011-03-04 | 6 | 11.5294 | 7.1531 | 18.6824 | 0.60716 | 0.76558 | 0.13889 | 1.5116 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-04 | 7 | 11.0376 | 7.1115 | 18.1491 | 0.57299 | 0.76558 | 0.13492 | 1.4735 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0946 | 1.062
2011-03-04 | 8 | 10.9239 | 7.0766 | 18.0005 | 0.56364 | 0.76558 | 0.13382 | 1.463 | 8.128% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-03-04 | 9 | 10.9913 | 7.1076 | 18.0989 | 0.56982 | 0.76558 | 0.13455 | 1.4699 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-04 | 10 | 11.3807 | 7.0052 | 18.3859 | 0.58804 | 0.76558 | 0.13668 | 1.4903 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-04 | 11 | 11.8637 | 7.0814 | 18.945 | 0.62435 | 0.76558 | 0.14084 | 1.5308 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-03-04 | 12 | 12.3626 | 7.4063 | 19.7689 | 0.67983 | 0.76558 | 0.14696 | 1.5924 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-04 | 13 | 13.8816 | 8.0433 | 21.9249 | 0.8362 | 0.76558 | 0.16299 | 1.7648 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-04 | 14 | 15.782 | 9.1667 | 24.9487 | 1.0828 | 0.76558 | 0.18547 | 2.0338 | 8.152% | 8.674% | 5.861% | 1.0888 | 1.095 | 1.0623
2011-03-04 | 15 | 19.1359 | 10.8765 | 30.0124 | 1.5669 | 0.76558 | 0.22312 | 2.5556 | 8.515% | 9.06% | 6.122% | 1.0931 | 1.0996 | 1.0652
2011-03-04 | 16 | 22.2837 | 11.8309 | 34.1146 | 2.0245 | 0.76558 | 0.25361 | 3.0437 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2011-03-04 | 17 | 23.6013 | 12.0285 | 35.6298 | 2.2083 | 0.76558 | 0.26488 | 3.2388 | 9.09% | 9.672% | 6.536% | 1.1 | 1.1071 | 1.0699
2011-03-04 | 18 | 23.3111 | 12.0739 | 35.3851 | 2.1781 | 0.76558 | 0.26306 | 3.2067 | 9.062% | 9.642% | 6.516% | 1.0997 | 1.1067 | 1.0697
2011-03-04 | 19 | 22.9063 | 11.8576 | 34.7639 | 2.1023 | 0.76558 | 0.25844 | 3.1263 | 8.993% | 9.569% | 6.466% | 1.0988 | 1.1058 | 1.0691
2011-03-04 | 20 | 22.3 | 11.7873 | 34.0873 | 2.0212 | 0.76558 | 0.25341 | 3.0402 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1048 | 1.0685
2011-03-04 | 21 | 21.6909 | 11.6598 | 33.3507 | 1.9348 | 0.76558 | 0.24793 | 2.9483 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-03-04 | 22 | 21.1797 | 11.6491 | 32.8289 | 1.8748 | 0.76558 | 0.24405 | 2.8844 | 8.786% | 9.348% | 6.317% | 1.0963 | 1.1031 | 1.0674
2011-03-04 | 23 | 20.6587 | 11.6008 | 32.2595 | 1.8103 | 0.76558 | 0.23982 | 2.8157 | 8.728% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-03-04 | 24 | 20.8205 | 11.6201 | 32.4406 | 1.8307 | 0.76558 | 0.24117 | 2.8374 | 8.747% | 9.306% | 6.289% | 1.0958 | 1.1026 | 1.0671
2011-03-04 | 25 | 20.3081 | 11.5695 | 31.8776 | 1.7677 | 0.76558 | 0.23698 | 2.7702 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-03-04 | 26 | 20.0343 | 11.1747 | 31.209 | 1.6943 | 0.76558 | 0.23201 | 2.6919 | 8.625% | 9.177% | 6.202% | 1.0944 | 1.101 | 1.0661
2011-03-04 | 27 | 19.7942 | 11.3536 | 31.1478 | 1.6877 | 0.76558 | 0.23156 | 2.6848 | 8.62% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-03-04 | 28 | 19.5639 | 11.2859 | 30.8498 | 1.6555 | 0.76558 | 0.22934 | 2.6505 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-03-04 | 29 | 19.5352 | 11.0733 | 30.6085 | 1.6297 | 0.76558 | 0.22755 | 2.6229 | 8.569% | 9.118% | 6.161% | 1.0937 | 1.1003 | 1.0657
2011-03-04 | 30 | 19.4351 | 10.8109 | 30.246 | 1.5914 | 0.76558 | 0.22485 | 2.5818 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-03-04 | 31 | 19.9176 | 10.613 | 30.5307 | 1.6215 | 0.76558 | 0.22697 | 2.614 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-03-04 | 32 | 19.6365 | 10.5658 | 30.2023 | 1.5868 | 0.76558 | 0.22453 | 2.5769 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2011-03-04 | 33 | 19.9283 | 11.0325 | 30.9608 | 1.6675 | 0.76558 | 0.23017 | 2.6632 | 8.602% | 9.152% | 6.185% | 1.0941 | 1.1007 | 1.0659
2011-03-04 | 34 | 19.9612 | 11.1092 | 31.0704 | 1.6793 | 0.76558 | 0.23098 | 2.6759 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-03-04 | 35 | 19.8721 | 11.2911 | 31.1632 | 1.6893 | 0.76558 | 0.23167 | 2.6866 | 8.621% | 9.173% | 6.199% | 1.0943 | 1.101 | 1.0661
2011-03-04 | 36 | 20.5279 | 11.6915 | 32.2194 | 1.8058 | 0.76558 | 0.23952 | 2.8109 | 8.724% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-03-04 | 37 | 21.3983 | 11.9079 | 33.3062 | 1.9297 | 0.76558 | 0.2476 | 2.9429 | 8.836% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-03-04 | 38 | 22.0119 | 11.751 | 33.7628 | 1.983 | 0.76558 | 0.251 | 2.9995 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-03-04 | 39 | 21.8393 | 11.6976 | 33.5369 | 1.9565 | 0.76558 | 0.24932 | 2.9714 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-03-04 | 40 | 21.8256 | 11.7206 | 33.5462 | 1.9576 | 0.76558 | 0.24939 | 2.9726 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-03-04 | 41 | 21.8461 | 11.7954 | 33.6416 | 1.9687 | 0.76558 | 0.2501 | 2.9844 | 8.871% | 9.439% | 6.378% | 1.0973 | 1.1042 | 1.0681
2011-03-04 | 42 | 22.3319 | 12.1491 | 34.481 | 2.0682 | 0.76558 | 0.25634 | 3.0901 | 8.962% | 9.535% | 6.444% | 1.0984 | 1.1054 | 1.0689
2011-03-04 | 43 | 22.2087 | 12.3529 | 34.5616 | 2.0779 | 0.76558 | 0.25694 | 3.1004 | 8.971% | 9.545% | 6.45% | 1.0985 | 1.1055 | 1.0689
2011-03-04 | 44 | 21.5052 | 11.8024 | 33.3076 | 1.9298 | 0.76558 | 0.24761 | 2.943 | 8.836% | 9.401% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-03-04 | 45 | 20.1068 | 11.2298 | 31.3366 | 1.7082 | 0.76558 | 0.23296 | 2.7067 | 8.638% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2011-03-04 | 46 | 18.3456 | 10.0117 | 28.3573 | 1.3988 | 0.76558 | 0.21081 | 2.3752 | 8.376% | 8.912% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-03-04 | 47 | 16.5406 | 9.3962 | 25.9367 | 1.1702 | 0.76558 | 0.19282 | 2.1286 | 8.207% | 8.732% | 5.901% | 1.0894 | 1.0957 | 1.0627
2011-03-04 | 48 | 15.2226 | 9.4275 | 24.65 | 1.057 | 0.76558 | 0.18325 | 2.0058 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-03-05 | 1 | 14.0076 | 8.7402 | 22.7478 | 0.90015 | 0.76558 | 0.16911 | 1.8348 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-03-05 | 2 | 12.9148 | 8.2102 | 21.1251 | 0.7763 | 0.76558 | 0.15705 | 1.6989 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-05 | 3 | 12.2838 | 7.9101 | 20.1939 | 0.70938 | 0.76558 | 0.15012 | 1.6251 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-05 | 4 | 12.0654 | 7.8894 | 19.9548 | 0.69267 | 0.76558 | 0.14835 | 1.6066 | 8.051% | 8.566% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-05 | 5 | 11.7932 | 7.8982 | 19.6914 | 0.67451 | 0.76558 | 0.14639 | 1.5865 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-05 | 6 | 11.5574 | 7.6336 | 19.191 | 0.64066 | 0.76558 | 0.14267 | 1.5489 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-05 | 7 | 11.1977 | 7.5486 | 18.7463 | 0.61132 | 0.76558 | 0.13936 | 1.5163 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-03-05 | 8 | 10.9189 | 7.3643 | 18.2832 | 0.58149 | 0.76558 | 0.13592 | 1.483 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-05 | 9 | 11.0657 | 7.462 | 18.5277 | 0.59714 | 0.76558 | 0.13774 | 1.5005 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-03-05 | 10 | 11.082 | 7.4806 | 18.5626 | 0.59939 | 0.76558 | 0.138 | 1.503 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-05 | 11 | 11.678 | 7.6945 | 19.3725 | 0.65284 | 0.76558 | 0.14402 | 1.5624 | 8.065% | 8.581% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-03-05 | 12 | 12.0918 | 7.8479 | 19.9397 | 0.69163 | 0.76558 | 0.14823 | 1.6054 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-05 | 13 | 13.6679 | 8.6601 | 22.328 | 0.86723 | 0.76558 | 0.16599 | 1.7988 | 8.056% | 8.572% | 5.792% | 1.0876 | 1.0938 | 1.0615
2011-03-05 | 14 | 15.5092 | 9.5614 | 25.0706 | 1.0934 | 0.76558 | 0.18638 | 2.0453 | 8.158% | 8.68% | 5.866% | 1.0888 | 1.0951 | 1.0623
2011-03-05 | 15 | 19.0856 | 10.961 | 30.0466 | 1.5705 | 0.76558 | 0.22337 | 2.5594 | 8.518% | 9.063% | 6.125% | 1.0931 | 1.0997 | 1.0652
2011-03-05 | 16 | 22.2178 | 11.908 | 34.1258 | 2.0258 | 0.76558 | 0.2537 | 3.0451 | 8.923% | 9.494% | 6.416% | 1.098 | 1.1049 | 1.0686
2011-03-05 | 17 | 23.5377 | 12.5241 | 36.0618 | 2.2622 | 0.76558 | 0.26809 | 3.2959 | 9.139% | 9.724% | 6.571% | 1.1006 | 1.1077 | 1.0703
2011-03-05 | 18 | 23.9354 | 12.6059 | 36.5412 | 2.3227 | 0.76558 | 0.27165 | 3.36 | 9.195% | 9.783% | 6.611% | 1.1013 | 1.1084 | 1.0708
2011-03-05 | 19 | 23.7929 | 12.4816 | 36.2745 | 2.289 | 0.76558 | 0.26967 | 3.3242 | 9.164% | 9.751% | 6.589% | 1.1009 | 1.108 | 1.0705
2011-03-05 | 20 | 23.2907 | 12.4302 | 35.7209 | 2.2196 | 0.76558 | 0.26555 | 3.2508 | 9.1% | 9.683% | 6.543% | 1.1001 | 1.1072 | 1.07
2011-03-05 | 21 | 22.8492 | 12.3847 | 35.2339 | 2.1595 | 0.76558 | 0.26193 | 3.187 | 9.045% | 9.624% | 6.504% | 1.0994 | 1.1065 | 1.0696
2011-03-05 | 22 | 22.4213 | 12.4187 | 34.84 | 2.1115 | 0.76558 | 0.259 | 3.1361 | 9.001% | 9.577% | 6.472% | 1.0989 | 1.1059 | 1.0692
2011-03-05 | 23 | 22.6613 | 12.2821 | 34.9434 | 2.1241 | 0.76558 | 0.25977 | 3.1494 | 9.013% | 9.59% | 6.48% | 1.0991 | 1.1061 | 1.0693
2011-03-05 | 24 | 22.931 | 11.9287 | 34.8596 | 2.1139 | 0.76558 | 0.25915 | 3.1386 | 9.004% | 9.58% | 6.474% | 1.0989 | 1.1059 | 1.0692
2011-03-05 | 25 | 22.6897 | 11.7364 | 34.4261 | 2.0616 | 0.76558 | 0.25593 | 3.0831 | 8.956% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2011-03-05 | 26 | 21.7413 | 11.4981 | 33.2394 | 1.9219 | 0.76558 | 0.24711 | 2.9346 | 8.829% | 9.394% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-03-05 | 27 | 21.0472 | 11.5454 | 32.5926 | 1.8479 | 0.76558 | 0.2423 | 2.8557 | 8.762% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-03-05 | 28 | 20.4486 | 11.3463 | 31.7948 | 1.7585 | 0.76558 | 0.23637 | 2.7605 | 8.682% | 9.238% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-03-05 | 29 | 20.3125 | 11.1022 | 31.4147 | 1.7167 | 0.76558 | 0.23354 | 2.7158 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-03-05 | 30 | 20.1757 | 10.9516 | 31.1273 | 1.6855 | 0.76558 | 0.2314 | 2.6824 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.1009 | 1.0661
2011-03-05 | 31 | 20.1249 | 10.6854 | 30.8103 | 1.6513 | 0.76558 | 0.22905 | 2.6459 | 8.588% | 9.137% | 6.175% | 1.0939 | 1.1006 | 1.0658
2011-03-05 | 32 | 19.9255 | 10.665 | 30.5904 | 1.6278 | 0.76558 | 0.22741 | 2.6208 | 8.567% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-03-05 | 33 | 19.8773 | 11.0683 | 30.9456 | 1.6658 | 0.76558 | 0.23005 | 2.6615 | 8.6% | 9.151% | 6.184% | 1.0941 | 1.1007 | 1.0659
2011-03-05 | 34 | 19.9573 | 10.8155 | 30.7728 | 1.6473 | 0.76558 | 0.22877 | 2.6416 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-03-05 | 35 | 19.9287 | 10.9034 | 30.8321 | 1.6536 | 0.76558 | 0.22921 | 2.6484 | 8.59% | 9.14% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-03-05 | 36 | 20.3271 | 10.9833 | 31.3104 | 1.7053 | 0.76558 | 0.23277 | 2.7037 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-03-05 | 37 | 21.08 | 11.0757 | 32.1557 | 1.7987 | 0.76558 | 0.23905 | 2.8033 | 8.718% | 9.276% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-03-05 | 38 | 21.2833 | 10.935 | 32.2182 | 1.8057 | 0.76558 | 0.23951 | 2.8108 | 8.724% | 9.282% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-03-05 | 39 | 21.2727 | 10.5833 | 31.856 | 1.7653 | 0.76558 | 0.23682 | 2.7677 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2011-03-05 | 40 | 20.9315 | 10.464 | 31.3956 | 1.7146 | 0.76558 | 0.2334 | 2.7136 | 8.643% | 9.196% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-05 | 41 | 21.0549 | 10.5968 | 31.6517 | 1.7427 | 0.76558 | 0.2353 | 2.7436 | 8.668% | 9.223% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-03-05 | 42 | 21.6675 | 10.9714 | 32.6389 | 1.8531 | 0.76558 | 0.24264 | 2.8613 | 8.767% | 9.328% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-03-05 | 43 | 21.8562 | 10.7904 | 32.6466 | 1.854 | 0.76558 | 0.2427 | 2.8623 | 8.767% | 9.329% | 6.304% | 1.0961 | 1.1029 | 1.0673
2011-03-05 | 44 | 21.1704 | 10.4147 | 31.5851 | 1.7354 | 0.76558 | 0.23481 | 2.7358 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-03-05 | 45 | 19.9965 | 9.6013 | 29.5978 | 1.5239 | 0.76558 | 0.22003 | 2.5095 | 8.479% | 9.021% | 6.096% | 1.0926 | 1.0992 | 1.0649
2011-03-05 | 46 | 18.7407 | 9.2915 | 28.0322 | 1.3669 | 0.76558 | 0.20839 | 2.3409 | 8.351% | 8.885% | 6.004% | 1.0911 | 1.0975 | 1.0639
2011-03-05 | 47 | 17.3847 | 9.2352 | 26.6199 | 1.2327 | 0.76558 | 0.1979 | 2.1961 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2011-03-05 | 48 | 15.8254 | 9.1831 | 25.0084 | 1.0879 | 0.76558 | 0.18592 | 2.0394 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2011-03-06 | 1 | 14.4781 | 8.2901 | 22.7682 | 0.90176 | 0.76558 | 0.16926 | 1.8366 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-03-06 | 2 | 13.6715 | 7.8035 | 21.475 | 0.80224 | 0.76558 | 0.15965 | 1.7275 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-06 | 3 | 12.9042 | 7.5219 | 20.4261 | 0.72578 | 0.76558 | 0.15185 | 1.6432 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-06 | 4 | 12.2319 | 7.2596 | 19.4915 | 0.66089 | 0.76558 | 0.1449 | 1.5714 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-06 | 5 | 11.9553 | 7.2472 | 19.2025 | 0.64143 | 0.76558 | 0.14275 | 1.5498 | 8.071% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-06 | 6 | 11.4845 | 7.1834 | 18.668 | 0.60622 | 0.76558 | 0.13878 | 1.5106 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-06 | 7 | 11.259 | 7.1519 | 18.411 | 0.58964 | 0.76558 | 0.13687 | 1.4921 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-03-06 | 8 | 11.1836 | 6.9768 | 18.1604 | 0.5737 | 0.76558 | 0.13501 | 1.4743 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-03-06 | 9 | 11.5417 | 6.9522 | 18.4939 | 0.59497 | 0.76558 | 0.13749 | 1.498 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-06 | 10 | 11.7473 | 7.0699 | 18.8171 | 0.61594 | 0.76558 | 0.13989 | 1.5214 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-03-06 | 11 | 11.6902 | 7.2303 | 18.9205 | 0.62273 | 0.76558 | 0.14066 | 1.529 | 8.081% | 8.598% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-03-06 | 12 | 11.8093 | 7.3688 | 19.1781 | 0.6398 | 0.76558 | 0.14257 | 1.548 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-06 | 13 | 12.7492 | 7.4364 | 20.1856 | 0.70879 | 0.76558 | 0.15006 | 1.6244 | 8.047% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-06 | 14 | 13.9317 | 7.6008 | 21.5325 | 0.80654 | 0.76558 | 0.16008 | 1.7322 | 8.045% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-06 | 15 | 15.696 | 8.2538 | 23.9498 | 0.99779 | 0.76558 | 0.17805 | 1.9414 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-06 | 16 | 17.365 | 8.867 | 26.232 | 1.197 | 0.76558 | 0.19501 | 2.1576 | 8.225% | 8.751% | 5.914% | 1.0896 | 1.0959 | 1.0629
2011-03-06 | 17 | 19.4089 | 9.7459 | 29.1549 | 1.4786 | 0.76558 | 0.21674 | 2.4609 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2011-03-06 | 18 | 20.9131 | 10.5341 | 31.4471 | 1.7203 | 0.76558 | 0.23378 | 2.7196 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-03-06 | 19 | 21.8042 | 11.0579 | 32.8621 | 1.8786 | 0.76558 | 0.2443 | 2.8884 | 8.79% | 9.352% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-03-06 | 20 | 22.2147 | 11.2291 | 33.4438 | 1.9457 | 0.76558 | 0.24863 | 2.9599 | 8.85% | 9.417% | 6.363% | 1.0971 | 1.104 | 1.068
2011-03-06 | 21 | 22.315 | 11.2306 | 33.5457 | 1.9575 | 0.76558 | 0.24938 | 2.9725 | 8.861% | 9.428% | 6.371% | 1.0972 | 1.1041 | 1.068
2011-03-06 | 22 | 21.962 | 11.3055 | 33.2675 | 1.9252 | 0.76558 | 0.24731 | 2.9381 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-03-06 | 23 | 21.3568 | 10.9825 | 32.3393 | 1.8193 | 0.76558 | 0.24041 | 2.8253 | 8.736% | 9.295% | 6.281% | 1.0957 | 1.1025 | 1.067
2011-03-06 | 24 | 20.9528 | 10.835 | 31.7878 | 1.7577 | 0.76558 | 0.23631 | 2.7596 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-03-06 | 25 | 20.0114 | 10.708 | 30.7194 | 1.6416 | 0.76558 | 0.22837 | 2.6355 | 8.579% | 9.128% | 6.169% | 1.0938 | 1.1005 | 1.0657
2011-03-06 | 26 | 19.6543 | 10.3524 | 30.0067 | 1.5663 | 0.76558 | 0.22307 | 2.5549 | 8.515% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2011-03-06 | 27 | 19.608 | 10.3358 | 29.9438 | 1.5597 | 0.76558 | 0.22261 | 2.5479 | 8.509% | 9.054% | 6.118% | 1.093 | 1.0995 | 1.0652
2011-03-06 | 28 | 19.513 | 10.5475 | 30.0605 | 1.5719 | 0.76558 | 0.22347 | 2.561 | 8.519% | 9.065% | 6.125% | 1.0931 | 1.0997 | 1.0653
2011-03-06 | 29 | 19.3206 | 10.296 | 29.6165 | 1.5258 | 0.76558 | 0.22017 | 2.5116 | 8.48% | 9.023% | 6.097% | 1.0927 | 1.0992 | 1.0649
2011-03-06 | 30 | 18.7981 | 10.0752 | 28.8734 | 1.4502 | 0.76558 | 0.21465 | 2.4304 | 8.418% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2011-03-06 | 31 | 18.6224 | 9.7667 | 28.389 | 1.402 | 0.76558 | 0.21105 | 2.3786 | 8.379% | 8.915% | 6.024% | 1.0914 | 1.0979 | 1.0641
2011-03-06 | 32 | 18.484 | 9.764 | 28.248 | 1.3881 | 0.76558 | 0.21 | 2.3636 | 8.367% | 8.903% | 6.016% | 1.0913 | 1.0977 | 1.064
2011-03-06 | 33 | 18.8173 | 10.0424 | 28.8597 | 1.4488 | 0.76558 | 0.21455 | 2.429 | 8.416% | 8.955% | 6.051% | 1.0919 | 1.0984 | 1.0644
2011-03-06 | 34 | 19.2131 | 9.9003 | 29.1134 | 1.4744 | 0.76558 | 0.21643 | 2.4564 | 8.437% | 8.977% | 6.067% | 1.0921 | 1.0986 | 1.0646
2011-03-06 | 35 | 19.8404 | 10.303 | 30.1434 | 1.5806 | 0.76558 | 0.22409 | 2.5703 | 8.527% | 9.072% | 6.131% | 1.0932 | 1.0998 | 1.0653
2011-03-06 | 36 | 19.931 | 10.7053 | 30.6363 | 1.6327 | 0.76558 | 0.22775 | 2.626 | 8.572% | 9.12% | 6.163% | 1.0938 | 1.1004 | 1.0657
2011-03-06 | 37 | 20.6086 | 10.6928 | 31.3014 | 1.7044 | 0.76558 | 0.2327 | 2.7026 | 8.634% | 9.187% | 6.208% | 1.0945 | 1.1012 | 1.0662
2011-03-06 | 38 | 20.676 | 10.7229 | 31.399 | 1.715 | 0.76558 | 0.23342 | 2.714 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-06 | 39 | 20.7637 | 10.4657 | 31.2293 | 1.6965 | 0.76558 | 0.23216 | 2.6943 | 8.627% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-03-06 | 40 | 20.3928 | 10.0405 | 30.4333 | 1.6111 | 0.76558 | 0.22625 | 2.603 | 8.553% | 9.1% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-03-06 | 41 | 20.5139 | 9.8818 | 30.3957 | 1.6072 | 0.76558 | 0.22597 | 2.5987 | 8.55% | 9.097% | 6.147% | 1.0935 | 1.1001 | 1.0655
2011-03-06 | 42 | 21.7917 | 10.2162 | 32.0079 | 1.7822 | 0.76558 | 0.23795 | 2.7857 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-06 | 43 | 21.4028 | 10.419 | 31.8218 | 1.7615 | 0.76558 | 0.23657 | 2.7636 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-03-06 | 44 | 20.5328 | 10.2383 | 30.7711 | 1.6471 | 0.76558 | 0.22876 | 2.6414 | 8.584% | 9.134% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-03-06 | 45 | 19.586 | 9.7877 | 29.3737 | 1.5009 | 0.76558 | 0.21837 | 2.4848 | 8.459% | 9.001% | 6.082% | 1.0924 | 1.0989 | 1.0648
2011-03-06 | 46 | 17.976 | 9.2904 | 27.2664 | 1.2933 | 0.76558 | 0.2027 | 2.2616 | 8.294% | 8.825% | 5.964% | 1.0904 | 1.0968 | 1.0634
2011-03-06 | 47 | 16.6881 | 9.0119 | 25.7 | 1.149 | 0.76558 | 0.19106 | 2.1056 | 8.193% | 8.717% | 5.891% | 1.0892 | 1.0955 | 1.0626
2011-03-06 | 48 | 15.6589 | 9.0298 | 24.6886 | 1.0603 | 0.76558 | 0.18354 | 2.0094 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-03-07 | 1 | 14.5367 | 8.2378 | 22.7745 | 0.90226 | 0.76558 | 0.16931 | 1.8371 | 8.067% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-03-07 | 2 | 13.4641 | 7.7933 | 21.2574 | 0.78606 | 0.76558 | 0.15803 | 1.7097 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-07 | 3 | 12.7192 | 7.4979 | 20.2171 | 0.711 | 0.76558 | 0.1503 | 1.6269 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-07 | 4 | 11.8811 | 7.2951 | 19.1763 | 0.63968 | 0.76558 | 0.14256 | 1.5478 | 8.072% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-07 | 5 | 11.5668 | 7.2567 | 18.8235 | 0.61636 | 0.76558 | 0.13994 | 1.5219 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-03-07 | 6 | 11.2313 | 7.0543 | 18.2856 | 0.58164 | 0.76558 | 0.13594 | 1.4832 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-07 | 7 | 11.4081 | 7.0908 | 18.4989 | 0.59529 | 0.76558 | 0.13752 | 1.4984 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-07 | 8 | 11.4224 | 7.2172 | 18.6396 | 0.60437 | 0.76558 | 0.13857 | 1.5085 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-03-07 | 9 | 11.4583 | 7.0432 | 18.5015 | 0.59546 | 0.76558 | 0.13754 | 1.4986 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-07 | 10 | 11.2639 | 6.9244 | 18.1883 | 0.57546 | 0.76558 | 0.13521 | 1.4763 | 8.117% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-03-07 | 11 | 11.4916 | 7.0535 | 18.5451 | 0.59827 | 0.76558 | 0.13787 | 1.5017 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-07 | 12 | 11.6779 | 7.0264 | 18.7043 | 0.60858 | 0.76558 | 0.13905 | 1.5132 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-03-07 | 13 | 12.7421 | 6.9567 | 19.6988 | 0.67501 | 0.76558 | 0.14644 | 1.587 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-07 | 14 | 13.6446 | 7.0255 | 20.6701 | 0.74323 | 0.76558 | 0.15366 | 1.6625 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-07 | 15 | 14.9862 | 7.3891 | 22.3753 | 0.87091 | 0.76558 | 0.16634 | 1.8028 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-07 | 16 | 16.3249 | 7.8302 | 24.1551 | 1.015 | 0.76558 | 0.17957 | 1.9601 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-07 | 17 | 17.9824 | 8.8258 | 26.8082 | 1.2502 | 0.76558 | 0.1993 | 2.215 | 8.263% | 8.791% | 5.941% | 1.0901 | 1.0964 | 1.0632
2011-03-07 | 18 | 19.406 | 9.5932 | 28.9992 | 1.4629 | 0.76558 | 0.21558 | 2.444 | 8.428% | 8.967% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-03-07 | 19 | 21.0652 | 10.4262 | 31.4915 | 1.7251 | 0.76558 | 0.23411 | 2.7248 | 8.653% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-03-07 | 20 | 21.6469 | 10.7838 | 32.4307 | 1.8296 | 0.76558 | 0.24109 | 2.8362 | 8.746% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2011-03-07 | 21 | 22.1724 | 10.8542 | 33.0266 | 1.8974 | 0.76558 | 0.24552 | 2.9085 | 8.807% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2011-03-07 | 22 | 21.9508 | 10.8226 | 32.7734 | 1.8684 | 0.76558 | 0.24364 | 2.8777 | 8.78% | 9.342% | 6.313% | 1.0963 | 1.1031 | 1.0674
2011-03-07 | 23 | 21.1767 | 10.5742 | 31.7509 | 1.7537 | 0.76558 | 0.23604 | 2.7553 | 8.678% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-03-07 | 24 | 20.2286 | 10.584 | 30.8126 | 1.6515 | 0.76558 | 0.22906 | 2.6462 | 8.588% | 9.138% | 6.175% | 1.0939 | 1.1006 | 1.0658
2011-03-07 | 25 | 19.9465 | 10.5141 | 30.4606 | 1.614 | 0.76558 | 0.22645 | 2.6061 | 8.556% | 9.103% | 6.151% | 1.0936 | 1.1001 | 1.0655
2011-03-07 | 26 | 19.6297 | 10.2523 | 29.882 | 1.5533 | 0.76558 | 0.22215 | 2.541 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-03-07 | 27 | 19.3454 | 10.3146 | 29.66 | 1.5303 | 0.76558 | 0.2205 | 2.5164 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-03-07 | 28 | 19.1347 | 10.249 | 29.3837 | 1.5019 | 0.76558 | 0.21844 | 2.4859 | 8.46% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-03-07 | 29 | 18.6017 | 10.0211 | 28.6228 | 1.4251 | 0.76558 | 0.21279 | 2.4035 | 8.397% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2011-03-07 | 30 | 18.0885 | 9.6823 | 27.7709 | 1.3416 | 0.76558 | 0.20645 | 2.3136 | 8.331% | 8.864% | 5.99% | 1.0909 | 1.0973 | 1.0637
2011-03-07 | 31 | 18.2628 | 9.5987 | 27.8616 | 1.3503 | 0.76558 | 0.20713 | 2.3231 | 8.338% | 8.871% | 5.995% | 1.091 | 1.0974 | 1.0638
2011-03-07 | 32 | 18.3797 | 9.5293 | 27.9091 | 1.355 | 0.76558 | 0.20748 | 2.328 | 8.341% | 8.875% | 5.997% | 1.091 | 1.0974 | 1.0638
2011-03-07 | 33 | 18.6747 | 9.7935 | 28.4682 | 1.4098 | 0.76558 | 0.21164 | 2.387 | 8.385% | 8.921% | 6.029% | 1.0915 | 1.098 | 1.0642
2011-03-07 | 34 | 18.9117 | 10.1483 | 29.06 | 1.469 | 0.76558 | 0.21604 | 2.4506 | 8.433% | 8.973% | 6.063% | 1.0921 | 1.0986 | 1.0645
2011-03-07 | 35 | 19.3272 | 10.6215 | 29.9488 | 1.5602 | 0.76558 | 0.22264 | 2.5485 | 8.509% | 9.054% | 6.118% | 1.093 | 1.0996 | 1.0652
2011-03-07 | 36 | 19.8465 | 11.2052 | 31.0518 | 1.6773 | 0.76558 | 0.23084 | 2.6737 | 8.61% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-03-07 | 37 | 20.3754 | 11.415 | 31.7903 | 1.758 | 0.76558 | 0.23633 | 2.7599 | 8.682% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-03-07 | 38 | 21.0705 | 11.4021 | 32.4725 | 1.8343 | 0.76558 | 0.2414 | 2.8413 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-03-07 | 39 | 21.2048 | 11.1976 | 32.4025 | 1.8264 | 0.76558 | 0.24088 | 2.8328 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-03-07 | 40 | 20.9468 | 10.9537 | 31.9005 | 1.7702 | 0.76558 | 0.23715 | 2.773 | 8.693% | 9.249% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-03-07 | 41 | 21.0041 | 10.9952 | 31.9992 | 1.7812 | 0.76558 | 0.23789 | 2.7847 | 8.702% | 9.259% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-03-07 | 42 | 21.7691 | 11.3947 | 33.1638 | 1.9132 | 0.76558 | 0.24654 | 2.9253 | 8.821% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2011-03-07 | 43 | 21.7293 | 11.1059 | 32.8353 | 1.8755 | 0.76558 | 0.2441 | 2.8852 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-03-07 | 44 | 20.6054 | 10.6467 | 31.2521 | 1.699 | 0.76558 | 0.23233 | 2.6969 | 8.63% | 9.182% | 6.205% | 1.0944 | 1.1011 | 1.0662
2011-03-07 | 45 | 19.1964 | 9.9536 | 29.15 | 1.4781 | 0.76558 | 0.2167 | 2.4604 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2011-03-07 | 46 | 17.6739 | 8.9529 | 26.6267 | 1.2333 | 0.76558 | 0.19795 | 2.1968 | 8.25% | 8.778% | 5.932% | 1.0899 | 1.0962 | 1.0631
2011-03-07 | 47 | 16.1091 | 8.8249 | 24.9339 | 1.0815 | 0.76558 | 0.18536 | 2.0324 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2011-03-07 | 48 | 14.8987 | 8.8102 | 23.7089 | 0.97782 | 0.76558 | 0.17626 | 1.9197 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-08 | 1 | 13.6245 | 8.1254 | 21.7499 | 0.82291 | 0.76558 | 0.16169 | 1.7502 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-08 | 2 | 12.5365 | 7.5223 | 20.0587 | 0.69991 | 0.76558 | 0.14912 | 1.6146 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-03-08 | 3 | 11.8015 | 7.1559 | 18.9574 | 0.62516 | 0.76558 | 0.14093 | 1.5317 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-03-08 | 4 | 11.3483 | 7.1183 | 18.4666 | 0.59321 | 0.76558 | 0.13728 | 1.4961 | 8.101% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-03-08 | 5 | 11.2019 | 7.1243 | 18.3262 | 0.58422 | 0.76558 | 0.13624 | 1.486 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-03-08 | 6 | 11.0664 | 7.1668 | 18.2332 | 0.57831 | 0.76558 | 0.13555 | 1.4794 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-08 | 7 | 11.0044 | 7.2105 | 18.2149 | 0.57715 | 0.76558 | 0.13541 | 1.4781 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-08 | 8 | 10.8751 | 7.1441 | 18.0192 | 0.56482 | 0.76558 | 0.13396 | 1.4644 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2011-03-08 | 9 | 10.6722 | 7.1618 | 17.834 | 0.55326 | 0.76558 | 0.13258 | 1.4514 | 8.139% | 8.659% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-03-08 | 10 | 10.9727 | 7.1361 | 18.1088 | 0.57044 | 0.76558 | 0.13462 | 1.4706 | 8.121% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-08 | 11 | 11.3489 | 7.1928 | 18.5417 | 0.59805 | 0.76558 | 0.13784 | 1.5015 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-08 | 12 | 12.1068 | 7.4556 | 19.5624 | 0.6657 | 0.76558 | 0.14543 | 1.5767 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-08 | 13 | 13.3953 | 8.0552 | 21.4505 | 0.80041 | 0.76558 | 0.15947 | 1.7254 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-08 | 14 | 15.0949 | 9.0601 | 24.1551 | 1.015 | 0.76558 | 0.17957 | 1.9601 | 8.115% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-08 | 15 | 18.1988 | 10.731 | 28.9298 | 1.4559 | 0.76558 | 0.21507 | 2.4365 | 8.422% | 8.961% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-03-08 | 16 | 20.3455 | 11.6301 | 31.9756 | 1.7786 | 0.76558 | 0.23771 | 2.7819 | 8.7% | 9.257% | 6.255% | 1.0953 | 1.102 | 1.0667
2011-03-08 | 17 | 22.3419 | 12.0121 | 34.354 | 2.053 | 0.76558 | 0.25539 | 3.074 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-08 | 18 | 22.3771 | 12.0457 | 34.4228 | 2.0612 | 0.76558 | 0.2559 | 3.0827 | 8.955% | 9.529% | 6.439% | 1.0984 | 1.1053 | 1.0688
2011-03-08 | 19 | 22.2458 | 11.8781 | 34.1239 | 2.0256 | 0.76558 | 0.25368 | 3.0449 | 8.923% | 9.494% | 6.416% | 1.098 | 1.1049 | 1.0686
2011-03-08 | 20 | 21.8979 | 11.8155 | 33.7134 | 1.9771 | 0.76558 | 0.25063 | 2.9934 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-03-08 | 21 | 21.4317 | 11.528 | 32.9597 | 1.8897 | 0.76558 | 0.24503 | 2.9003 | 8.8% | 9.363% | 6.327% | 1.0965 | 1.1033 | 1.0675
2011-03-08 | 22 | 20.746 | 11.7797 | 32.5257 | 1.8403 | 0.76558 | 0.2418 | 2.8477 | 8.755% | 9.315% | 6.295% | 1.096 | 1.1027 | 1.0672
2011-03-08 | 23 | 20.3504 | 11.5052 | 31.8556 | 1.7653 | 0.76558 | 0.23682 | 2.7676 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2011-03-08 | 24 | 20.415 | 11.4623 | 31.8773 | 1.7677 | 0.76558 | 0.23698 | 2.7702 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-03-08 | 25 | 20.3613 | 11.6502 | 32.0115 | 1.7826 | 0.76558 | 0.23798 | 2.7861 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-08 | 26 | 20.041 | 11.4258 | 31.4668 | 1.7224 | 0.76558 | 0.23393 | 2.7219 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-08 | 27 | 20.1728 | 11.7518 | 31.9246 | 1.7729 | 0.76558 | 0.23733 | 2.7758 | 8.695% | 9.251% | 6.252% | 1.0952 | 1.1019 | 1.0667
2011-03-08 | 28 | 19.9448 | 11.9581 | 31.903 | 1.7705 | 0.76558 | 0.23717 | 2.7733 | 8.693% | 9.249% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-03-08 | 29 | 19.9206 | 11.9512 | 31.8718 | 1.767 | 0.76558 | 0.23694 | 2.7696 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-03-08 | 30 | 20.1428 | 11.4981 | 31.6409 | 1.7415 | 0.76558 | 0.23522 | 2.7423 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-03-08 | 31 | 20.2308 | 11.3901 | 31.6209 | 1.7393 | 0.76558 | 0.23507 | 2.74 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-03-08 | 32 | 20.2137 | 11.5747 | 31.7884 | 1.7578 | 0.76558 | 0.23632 | 2.7597 | 8.681% | 9.237% | 6.242% | 1.0951 | 1.1018 | 1.0666
2011-03-08 | 33 | 20.4161 | 11.9409 | 32.357 | 1.8213 | 0.76558 | 0.24055 | 2.8274 | 8.738% | 9.297% | 6.283% | 1.0957 | 1.1025 | 1.067
2011-03-08 | 34 | 20.478 | 11.7875 | 32.2655 | 1.811 | 0.76558 | 0.23987 | 2.8164 | 8.729% | 9.288% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-03-08 | 35 | 20.4846 | 11.92 | 32.4045 | 1.8266 | 0.76558 | 0.2409 | 2.8331 | 8.743% | 9.302% | 6.286% | 1.0958 | 1.1026 | 1.0671
2011-03-08 | 36 | 21.2046 | 12.2051 | 33.4097 | 1.9417 | 0.76558 | 0.24837 | 2.9556 | 8.847% | 9.413% | 6.361% | 1.0971 | 1.1039 | 1.0679
2011-03-08 | 37 | 21.9713 | 12.4185 | 34.3898 | 2.0573 | 0.76558 | 0.25566 | 3.0785 | 8.952% | 9.525% | 6.436% | 1.0983 | 1.1053 | 1.0688
2011-03-08 | 38 | 22.2357 | 12.0067 | 34.2424 | 2.0397 | 0.76558 | 0.25456 | 3.0598 | 8.936% | 9.508% | 6.425% | 1.0981 | 1.1051 | 1.0687
2011-03-08 | 39 | 22.0915 | 11.9465 | 34.038 | 2.0154 | 0.76558 | 0.25304 | 3.034 | 8.914% | 9.484% | 6.409% | 1.0979 | 1.1048 | 1.0685
2011-03-08 | 40 | 22.2502 | 11.286 | 33.5362 | 1.9564 | 0.76558 | 0.24931 | 2.9713 | 8.86% | 9.427% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-03-08 | 41 | 22.1812 | 11.1708 | 33.3521 | 1.935 | 0.76558 | 0.24794 | 2.9485 | 8.841% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-03-08 | 42 | 22.6405 | 11.3189 | 33.9594 | 2.0061 | 0.76558 | 0.25246 | 3.0241 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-03-08 | 43 | 22.4093 | 11.1677 | 33.577 | 1.9612 | 0.76558 | 0.24962 | 2.9764 | 8.864% | 9.432% | 6.373% | 1.0973 | 1.1041 | 1.0681
2011-03-08 | 44 | 21.7122 | 10.6511 | 32.3632 | 1.822 | 0.76558 | 0.24059 | 2.8281 | 8.739% | 9.298% | 6.283% | 1.0958 | 1.1025 | 1.067
2011-03-08 | 45 | 20.3683 | 9.8948 | 30.2631 | 1.5932 | 0.76558 | 0.22498 | 2.5837 | 8.538% | 9.084% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-03-08 | 46 | 18.5024 | 8.925 | 27.4275 | 1.3086 | 0.76558 | 0.2039 | 2.2781 | 8.306% | 8.837% | 5.972% | 1.0906 | 1.0969 | 1.0635
2011-03-08 | 47 | 16.6809 | 8.5541 | 25.235 | 1.1077 | 0.76558 | 0.1876 | 2.0609 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-03-08 | 48 | 15.3038 | 8.6753 | 23.9791 | 1.0002 | 0.76558 | 0.17826 | 1.9441 | 8.107% | 8.626% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-03-09 | 1 | 13.8334 | 8.0195 | 21.8529 | 0.83072 | 0.76558 | 0.16246 | 1.7588 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-09 | 2 | 12.8057 | 7.6945 | 20.5002 | 0.73105 | 0.76558 | 0.1524 | 1.649 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-09 | 3 | 12.3334 | 7.4047 | 19.7381 | 0.67771 | 0.76558 | 0.14674 | 1.59 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-03-09 | 4 | 11.915 | 7.2158 | 19.1308 | 0.63665 | 0.76558 | 0.14222 | 1.5444 | 8.073% | 8.59% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-03-09 | 5 | 11.7975 | 7.2353 | 19.0327 | 0.63014 | 0.76558 | 0.14149 | 1.5372 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2011-03-09 | 6 | 11.481 | 7.2308 | 18.7118 | 0.60907 | 0.76558 | 0.13911 | 1.5138 | 8.09% | 8.608% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-03-09 | 7 | 11.2232 | 7.2117 | 18.4349 | 0.59117 | 0.76558 | 0.13705 | 1.4938 | 8.103% | 8.622% | 5.826% | 1.0882 | 1.0944 | 1.0619
2011-03-09 | 8 | 10.9349 | 7.1561 | 18.091 | 0.56933 | 0.76558 | 0.13449 | 1.4694 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-09 | 9 | 10.7965 | 7.057 | 17.8535 | 0.55448 | 0.76558 | 0.13273 | 1.4528 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-03-09 | 10 | 11.2133 | 7.1571 | 18.3704 | 0.58704 | 0.76558 | 0.13657 | 1.4892 | 8.106% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-03-09 | 11 | 11.5375 | 7.4088 | 18.9463 | 0.62443 | 0.76558 | 0.14085 | 1.5309 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-03-09 | 12 | 12.1191 | 7.6985 | 19.8176 | 0.68318 | 0.76558 | 0.14733 | 1.5961 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-09 | 13 | 13.5079 | 8.1946 | 21.7026 | 0.81933 | 0.76558 | 0.16134 | 1.7462 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-09 | 14 | 15.3213 | 9.2528 | 24.5741 | 1.0505 | 0.76558 | 0.18269 | 1.9988 | 8.134% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-03-09 | 15 | 18.5196 | 11.0166 | 29.5362 | 1.5175 | 0.76558 | 0.21958 | 2.5027 | 8.473% | 9.016% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-03-09 | 16 | 21.2081 | 11.7757 | 32.9839 | 1.8925 | 0.76558 | 0.24521 | 2.9033 | 8.802% | 9.365% | 6.329% | 1.0965 | 1.1033 | 1.0676
2011-03-09 | 17 | 22.267 | 12.0078 | 34.2748 | 2.0435 | 0.76558 | 0.2548 | 3.0639 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2011-03-09 | 18 | 22.1082 | 11.8713 | 33.9795 | 2.0085 | 0.76558 | 0.25261 | 3.0267 | 8.907% | 9.477% | 6.404% | 1.0978 | 1.1047 | 1.0684
2011-03-09 | 19 | 22.0826 | 11.7597 | 33.8423 | 1.9923 | 0.76558 | 0.25159 | 3.0095 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2011-03-09 | 20 | 21.6174 | 11.5367 | 33.1541 | 1.9121 | 0.76558 | 0.24647 | 2.9241 | 8.82% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2011-03-09 | 21 | 21.1639 | 11.3778 | 32.5417 | 1.8421 | 0.76558 | 0.24192 | 2.8496 | 8.757% | 9.317% | 6.296% | 1.096 | 1.1027 | 1.0672
2011-03-09 | 22 | 20.8656 | 11.5905 | 32.4561 | 1.8324 | 0.76558 | 0.24128 | 2.8393 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-03-09 | 23 | 20.9758 | 11.028 | 32.0038 | 1.7817 | 0.76558 | 0.23792 | 2.7852 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0667
2011-03-09 | 24 | 20.7268 | 10.8448 | 31.5716 | 1.7339 | 0.76558 | 0.23471 | 2.7342 | 8.66% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-09 | 25 | 20.6564 | 11.0229 | 31.6793 | 1.7458 | 0.76558 | 0.23551 | 2.7468 | 8.671% | 9.226% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-03-09 | 26 | 20.373 | 10.9373 | 31.3103 | 1.7053 | 0.76558 | 0.23276 | 2.7037 | 8.635% | 9.188% | 6.209% | 1.0945 | 1.1012 | 1.0662
2011-03-09 | 27 | 20.2432 | 11.4031 | 31.6463 | 1.7421 | 0.76558 | 0.23526 | 2.743 | 8.668% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-03-09 | 28 | 20.0024 | 11.5341 | 31.5365 | 1.7301 | 0.76558 | 0.23445 | 2.7301 | 8.657% | 9.211% | 6.224% | 1.0948 | 1.1015 | 1.0664
2011-03-09 | 29 | 20.0319 | 11.3012 | 31.3331 | 1.7078 | 0.76558 | 0.23293 | 2.7063 | 8.637% | 9.19% | 6.21% | 1.0945 | 1.1012 | 1.0662
2011-03-09 | 30 | 19.8284 | 11.2823 | 31.1107 | 1.6837 | 0.76558 | 0.23128 | 2.6805 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-03-09 | 31 | 20.1636 | 11.3296 | 31.4932 | 1.7253 | 0.76558 | 0.23412 | 2.725 | 8.653% | 9.206% | 6.221% | 1.0947 | 1.1014 | 1.0663
2011-03-09 | 32 | 20.2475 | 11.3859 | 31.6334 | 1.7407 | 0.76558 | 0.23517 | 2.7415 | 8.666% | 9.221% | 6.231% | 1.0949 | 1.1016 | 1.0665
2011-03-09 | 33 | 20.4026 | 11.6028 | 32.0054 | 1.7819 | 0.76558 | 0.23793 | 2.7854 | 8.703% | 9.26% | 6.257% | 1.0953 | 1.102 | 1.0668
2011-03-09 | 34 | 20.7428 | 11.9447 | 32.6875 | 1.8586 | 0.76558 | 0.243 | 2.8672 | 8.772% | 9.333% | 6.307% | 1.0962 | 1.1029 | 1.0673
2011-03-09 | 35 | 21.0019 | 12.4531 | 33.455 | 1.947 | 0.76558 | 0.24871 | 2.9612 | 8.851% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-03-09 | 36 | 21.4125 | 12.7594 | 34.1719 | 2.0313 | 0.76558 | 0.25404 | 3.0509 | 8.928% | 9.5% | 6.419% | 1.098 | 1.105 | 1.0686
2011-03-09 | 37 | 21.7385 | 13.0579 | 34.7964 | 2.1062 | 0.76558 | 0.25868 | 3.1305 | 8.997% | 9.572% | 6.469% | 1.0989 | 1.1059 | 1.0692
2011-03-09 | 38 | 22.0411 | 12.9262 | 34.9674 | 2.127 | 0.76558 | 0.25995 | 3.1525 | 9.016% | 9.593% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-03-09 | 39 | 21.8304 | 12.4478 | 34.2782 | 2.044 | 0.76558 | 0.25483 | 3.0644 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2011-03-09 | 40 | 21.7072 | 12.0038 | 33.711 | 1.9769 | 0.76558 | 0.25061 | 2.9931 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-03-09 | 41 | 21.6516 | 11.8071 | 33.4587 | 1.9474 | 0.76558 | 0.24874 | 2.9617 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-03-09 | 42 | 22.251 | 12.1029 | 34.3539 | 2.053 | 0.76558 | 0.25539 | 3.074 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-09 | 43 | 22.0232 | 12.1622 | 34.1854 | 2.0329 | 0.76558 | 0.25414 | 3.0526 | 8.93% | 9.501% | 6.42% | 1.0981 | 1.105 | 1.0686
2011-03-09 | 44 | 21.5555 | 11.72 | 33.2756 | 1.9261 | 0.76558 | 0.24737 | 2.9391 | 8.833% | 9.398% | 6.351% | 1.0969 | 1.1037 | 1.0678
2011-03-09 | 45 | 20.0141 | 11.0186 | 31.0327 | 1.6752 | 0.76558 | 0.2307 | 2.6715 | 8.609% | 9.16% | 6.19% | 1.0942 | 1.1008 | 1.066
2011-03-09 | 46 | 18.2704 | 10.1136 | 28.384 | 1.4015 | 0.76558 | 0.21101 | 2.3781 | 8.378% | 8.914% | 6.024% | 1.0914 | 1.0979 | 1.0641
2011-03-09 | 47 | 16.6526 | 9.4451 | 26.0977 | 1.1848 | 0.76558 | 0.19401 | 2.1444 | 8.217% | 8.743% | 5.908% | 1.0895 | 1.0958 | 1.0628
2011-03-09 | 48 | 15.2325 | 9.5017 | 24.7342 | 1.0642 | 0.76558 | 0.18388 | 2.0137 | 8.141% | 8.662% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-03-10 | 1 | 13.5379 | 8.7 | 22.238 | 0.86025 | 0.76558 | 0.16532 | 1.7911 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-10 | 2 | 12.2404 | 8.1598 | 20.4002 | 0.72394 | 0.76558 | 0.15166 | 1.6412 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-10 | 3 | 11.9068 | 7.8572 | 19.764 | 0.67949 | 0.76558 | 0.14693 | 1.592 | 8.055% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-03-10 | 4 | 11.6416 | 7.626 | 19.2676 | 0.64579 | 0.76558 | 0.14324 | 1.5546 | 8.068% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-03-10 | 5 | 11.498 | 7.7156 | 19.2136 | 0.64217 | 0.76558 | 0.14284 | 1.5506 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-10 | 6 | 11.0813 | 7.7878 | 18.8691 | 0.61935 | 0.76558 | 0.14028 | 1.5252 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-03-10 | 7 | 10.8264 | 7.6724 | 18.4988 | 0.59528 | 0.76558 | 0.13752 | 1.4984 | 8.1% | 8.618% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-10 | 8 | 10.5777 | 7.4906 | 18.0684 | 0.5679 | 0.76558 | 0.13432 | 1.4678 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-03-10 | 9 | 10.5312 | 7.5217 | 18.0528 | 0.56693 | 0.76558 | 0.13421 | 1.4667 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-10 | 10 | 11.0238 | 7.6909 | 18.7147 | 0.60926 | 0.76558 | 0.13913 | 1.514 | 8.09% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2011-03-10 | 11 | 11.4163 | 7.8745 | 19.2907 | 0.64734 | 0.76558 | 0.14341 | 1.5563 | 8.068% | 8.584% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-03-10 | 12 | 11.9157 | 8.0265 | 19.9422 | 0.6918 | 0.76558 | 0.14825 | 1.6056 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-10 | 13 | 13.2683 | 8.6463 | 21.9145 | 0.83541 | 0.76558 | 0.16292 | 1.7639 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-10 | 14 | 15.0567 | 9.4921 | 24.5488 | 1.0483 | 0.76558 | 0.1825 | 1.9964 | 8.132% | 8.653% | 5.847% | 1.0885 | 1.0947 | 1.0621
2011-03-10 | 15 | 18.1988 | 11.192 | 29.3908 | 1.5026 | 0.76558 | 0.21849 | 2.4867 | 8.461% | 9.002% | 6.083% | 1.0924 | 1.0989 | 1.0648
2011-03-10 | 16 | 21.1408 | 12.0942 | 33.235 | 1.9214 | 0.76558 | 0.24707 | 2.9341 | 8.828% | 9.393% | 6.348% | 1.0968 | 1.1037 | 1.0678
2011-03-10 | 17 | 22.2908 | 12.2415 | 34.5323 | 2.0744 | 0.76558 | 0.25672 | 3.0967 | 8.967% | 9.541% | 6.448% | 1.0985 | 1.1055 | 1.0689
2011-03-10 | 18 | 22.1137 | 11.8418 | 33.9555 | 2.0056 | 0.76558 | 0.25243 | 3.0237 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-03-10 | 19 | 21.6664 | 11.5276 | 33.194 | 1.9167 | 0.76558 | 0.24677 | 2.929 | 8.824% | 9.389% | 6.344% | 1.0968 | 1.1036 | 1.0677
2011-03-10 | 20 | 21.1457 | 11.3552 | 32.5009 | 1.8375 | 0.76558 | 0.24162 | 2.8447 | 8.753% | 9.313% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-03-10 | 21 | 21.1066 | 11.1108 | 32.2174 | 1.8056 | 0.76558 | 0.23951 | 2.8107 | 8.724% | 9.282% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-03-10 | 22 | 20.8796 | 11.3573 | 32.2369 | 1.8078 | 0.76558 | 0.23965 | 2.813 | 8.726% | 9.284% | 6.274% | 1.0956 | 1.1023 | 1.0669
2011-03-10 | 23 | 20.5596 | 11.2165 | 31.7761 | 1.7564 | 0.76558 | 0.23623 | 2.7583 | 8.68% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2011-03-10 | 24 | 20.1912 | 11.2181 | 31.4093 | 1.7161 | 0.76558 | 0.2335 | 2.7152 | 8.645% | 9.198% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-10 | 25 | 20.1589 | 11.4076 | 31.5665 | 1.7334 | 0.76558 | 0.23467 | 2.7336 | 8.66% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-03-10 | 26 | 20.0846 | 11.1532 | 31.2377 | 1.6974 | 0.76558 | 0.23223 | 2.6952 | 8.628% | 9.18% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-03-10 | 27 | 20.0931 | 11.6475 | 31.7406 | 1.7525 | 0.76558 | 0.23596 | 2.7541 | 8.677% | 9.232% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-03-10 | 28 | 20.0675 | 11.5521 | 31.6196 | 1.7392 | 0.76558 | 0.23506 | 2.7398 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-03-10 | 29 | 19.8273 | 11.3992 | 31.2265 | 1.6962 | 0.76558 | 0.23214 | 2.6939 | 8.627% | 9.179% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-03-10 | 30 | 19.1492 | 11.3559 | 30.5051 | 1.6187 | 0.76558 | 0.22678 | 2.6111 | 8.56% | 9.107% | 6.154% | 1.0936 | 1.1002 | 1.0656
2011-03-10 | 31 | 19.2546 | 11.2396 | 30.4942 | 1.6176 | 0.76558 | 0.2267 | 2.6099 | 8.559% | 9.106% | 6.154% | 1.0936 | 1.1002 | 1.0656
2011-03-10 | 32 | 19.5453 | 11.5111 | 31.0564 | 1.6778 | 0.76558 | 0.23088 | 2.6742 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-03-10 | 33 | 19.9872 | 11.9755 | 31.9627 | 1.7771 | 0.76558 | 0.23761 | 2.7803 | 8.699% | 9.255% | 6.254% | 1.0953 | 1.102 | 1.0667
2011-03-10 | 34 | 20.3715 | 12.0829 | 32.4543 | 1.8322 | 0.76558 | 0.24127 | 2.8391 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-03-10 | 35 | 20.7768 | 12.1955 | 32.9722 | 1.8912 | 0.76558 | 0.24512 | 2.9019 | 8.801% | 9.364% | 6.328% | 1.0965 | 1.1033 | 1.0676
2011-03-10 | 36 | 21.0388 | 12.447 | 33.4858 | 1.9505 | 0.76558 | 0.24894 | 2.9651 | 8.855% | 9.421% | 6.367% | 1.0971 | 1.104 | 1.068
2011-03-10 | 37 | 21.8725 | 12.7986 | 34.671 | 2.0911 | 0.76558 | 0.25775 | 3.1144 | 8.983% | 9.558% | 6.459% | 1.0987 | 1.1057 | 1.069
2011-03-10 | 38 | 22.1254 | 12.7805 | 34.9059 | 2.1195 | 0.76558 | 0.25949 | 3.1446 | 9.009% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2011-03-10 | 39 | 22.1422 | 12.4483 | 34.5905 | 2.0814 | 0.76558 | 0.25715 | 3.1041 | 8.974% | 9.548% | 6.452% | 1.0986 | 1.1056 | 1.069
2011-03-10 | 40 | 21.7628 | 11.792 | 33.5548 | 1.9586 | 0.76558 | 0.24945 | 2.9736 | 8.862% | 9.429% | 6.372% | 1.0972 | 1.1041 | 1.0681
2011-03-10 | 41 | 21.9701 | 11.2981 | 33.2682 | 1.9253 | 0.76558 | 0.24732 | 2.9382 | 8.832% | 9.397% | 6.35% | 1.0969 | 1.1037 | 1.0678
2011-03-10 | 42 | 22.708 | 11.5068 | 34.2148 | 2.0364 | 0.76558 | 0.25436 | 3.0563 | 8.933% | 9.504% | 6.423% | 1.0981 | 1.105 | 1.0686
2011-03-10 | 43 | 22.1394 | 11.2127 | 33.3521 | 1.935 | 0.76558 | 0.24794 | 2.9485 | 8.841% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-03-10 | 44 | 20.9446 | 10.801 | 31.7455 | 1.7531 | 0.76558 | 0.236 | 2.7546 | 8.677% | 9.233% | 6.239% | 1.095 | 1.1017 | 1.0665
2011-03-10 | 45 | 19.4386 | 10.3316 | 29.7702 | 1.5417 | 0.76558 | 0.22132 | 2.5286 | 8.494% | 9.037% | 6.107% | 1.0928 | 1.0994 | 1.065
2011-03-10 | 46 | 17.8908 | 9.604 | 27.4948 | 1.315 | 0.76558 | 0.2044 | 2.285 | 8.311% | 8.843% | 5.975% | 1.0906 | 1.097 | 1.0636
2011-03-10 | 47 | 16.3217 | 9.3323 | 25.6541 | 1.1448 | 0.76558 | 0.19072 | 2.1011 | 8.19% | 8.714% | 5.889% | 1.0892 | 1.0955 | 1.0626
2011-03-10 | 48 | 15.0061 | 9.4742 | 24.4802 | 1.0425 | 0.76558 | 0.18199 | 1.99 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-11 | 1 | 13.4914 | 8.8471 | 22.3385 | 0.86805 | 0.76558 | 0.16607 | 1.7997 | 8.056% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-11 | 2 | 12.5323 | 8.1581 | 20.6904 | 0.74468 | 0.76558 | 0.15381 | 1.6641 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-11 | 3 | 11.7831 | 7.8375 | 19.6206 | 0.66967 | 0.76558 | 0.14586 | 1.5811 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-11 | 4 | 11.3937 | 7.6223 | 19.016 | 0.62903 | 0.76558 | 0.14137 | 1.536 | 8.077% | 8.594% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-03-11 | 5 | 11.321 | 7.5628 | 18.8838 | 0.62032 | 0.76558 | 0.14038 | 1.5263 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-03-11 | 6 | 11.0574 | 7.4896 | 18.5469 | 0.59838 | 0.76558 | 0.13788 | 1.5018 | 8.098% | 8.616% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-11 | 7 | 10.8835 | 7.411 | 18.2946 | 0.58221 | 0.76558 | 0.136 | 1.4838 | 8.111% | 8.63% | 5.831% | 1.0883 | 1.0944 | 1.0619
2011-03-11 | 8 | 10.7756 | 7.347 | 18.1226 | 0.57131 | 0.76558 | 0.13473 | 1.4716 | 8.12% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-11 | 9 | 10.569 | 7.4979 | 18.0668 | 0.5678 | 0.76558 | 0.13431 | 1.4677 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-03-11 | 10 | 10.795 | 7.6699 | 18.4649 | 0.5931 | 0.76558 | 0.13727 | 1.496 | 8.102% | 8.62% | 5.825% | 1.0882 | 1.0943 | 1.0619
2011-03-11 | 11 | 11.2851 | 7.8794 | 19.1646 | 0.6389 | 0.76558 | 0.14247 | 1.547 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-03-11 | 12 | 11.7992 | 7.9689 | 19.7681 | 0.67978 | 0.76558 | 0.14696 | 1.5923 | 8.055% | 8.57% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-03-11 | 13 | 13.4196 | 8.5019 | 21.9214 | 0.83594 | 0.76558 | 0.16297 | 1.7645 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-11 | 14 | 15.5236 | 9.5353 | 25.0589 | 1.0923 | 0.76558 | 0.18629 | 2.0442 | 8.158% | 8.68% | 5.865% | 1.0888 | 1.095 | 1.0623
2011-03-11 | 15 | 18.8555 | 11.2586 | 30.1141 | 1.5775 | 0.76558 | 0.22387 | 2.567 | 8.524% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-03-11 | 16 | 21.296 | 12.1408 | 33.4368 | 1.9448 | 0.76558 | 0.24857 | 2.959 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2011-03-11 | 17 | 22.3402 | 12.3617 | 34.7019 | 2.0948 | 0.76558 | 0.25798 | 3.1183 | 8.986% | 9.561% | 6.461% | 1.0987 | 1.1057 | 1.0691
2011-03-11 | 18 | 22.8861 | 12.0802 | 34.9663 | 2.1268 | 0.76558 | 0.25994 | 3.1524 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-03-11 | 19 | 22.6094 | 11.8878 | 34.4972 | 2.0702 | 0.76558 | 0.25646 | 3.0922 | 8.964% | 9.537% | 6.445% | 1.0985 | 1.1054 | 1.0689
2011-03-11 | 20 | 21.8953 | 11.8538 | 33.7492 | 1.9813 | 0.76558 | 0.2509 | 2.9978 | 8.883% | 9.451% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-03-11 | 21 | 22.0894 | 12.2209 | 34.3103 | 2.0478 | 0.76558 | 0.25507 | 3.0684 | 8.943% | 9.516% | 6.43% | 1.0982 | 1.1052 | 1.0687
2011-03-11 | 22 | 21.5643 | 12.3496 | 33.9139 | 2.0007 | 0.76558 | 0.25212 | 3.0184 | 8.9% | 9.47% | 6.399% | 1.0977 | 1.1046 | 1.0684
2011-03-11 | 23 | 21.2629 | 12.046 | 33.3089 | 1.93 | 0.76558 | 0.24762 | 2.9432 | 8.836% | 9.402% | 6.353% | 1.0969 | 1.1038 | 1.0678
2011-03-11 | 24 | 21.302 | 11.481 | 32.783 | 1.8695 | 0.76558 | 0.24371 | 2.8788 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-03-11 | 25 | 21.3835 | 11.4502 | 32.8337 | 1.8753 | 0.76558 | 0.24409 | 2.885 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-03-11 | 26 | 21.1977 | 10.8959 | 32.0936 | 1.7917 | 0.76558 | 0.23859 | 2.7959 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-03-11 | 27 | 21.1499 | 11.0555 | 32.2054 | 1.8042 | 0.76558 | 0.23942 | 2.8092 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-03-11 | 28 | 20.6177 | 10.7826 | 31.4003 | 1.7152 | 0.76558 | 0.23343 | 2.7142 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-11 | 29 | 20.3245 | 10.4195 | 30.744 | 1.6442 | 0.76558 | 0.22855 | 2.6383 | 8.582% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-03-11 | 30 | 20.0479 | 10.1521 | 30.2 | 1.5865 | 0.76558 | 0.22451 | 2.5766 | 8.532% | 9.078% | 6.134% | 1.0933 | 1.0998 | 1.0654
2011-03-11 | 31 | 20.2538 | 10.1208 | 30.3745 | 1.6049 | 0.76558 | 0.22581 | 2.5963 | 8.548% | 9.095% | 6.146% | 1.0935 | 1.1 | 1.0655
2011-03-11 | 32 | 20.2576 | 10.3062 | 30.5638 | 1.625 | 0.76558 | 0.22721 | 2.6178 | 8.565% | 9.113% | 6.158% | 1.0937 | 1.1003 | 1.0656
2011-03-11 | 33 | 20.3923 | 10.7553 | 31.1476 | 1.6877 | 0.76558 | 0.23155 | 2.6848 | 8.62% | 9.171% | 6.197% | 1.0943 | 1.101 | 1.0661
2011-03-11 | 34 | 20.5361 | 10.922 | 31.4582 | 1.7215 | 0.76558 | 0.23386 | 2.7209 | 8.649% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-11 | 35 | 20.4855 | 10.9704 | 31.4559 | 1.7212 | 0.76558 | 0.23385 | 2.7207 | 8.649% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-11 | 36 | 21.2556 | 11.2715 | 32.5271 | 1.8405 | 0.76558 | 0.24181 | 2.8478 | 8.755% | 9.316% | 6.295% | 1.096 | 1.1027 | 1.0672
2011-03-11 | 37 | 22.2375 | 11.3217 | 33.5593 | 1.9591 | 0.76558 | 0.24948 | 2.9742 | 8.862% | 9.43% | 6.372% | 1.0972 | 1.1041 | 1.0681
2011-03-11 | 38 | 22.7923 | 11.2463 | 34.0386 | 2.0155 | 0.76558 | 0.25305 | 3.0341 | 8.914% | 9.484% | 6.409% | 1.0979 | 1.1048 | 1.0685
2011-03-11 | 39 | 23.0178 | 11.1044 | 34.1222 | 2.0254 | 0.76558 | 0.25367 | 3.0446 | 8.923% | 9.494% | 6.415% | 1.098 | 1.1049 | 1.0686
2011-03-11 | 40 | 23.2188 | 11.0446 | 34.2634 | 2.0422 | 0.76558 | 0.25472 | 3.0625 | 8.938% | 9.51% | 6.426% | 1.0982 | 1.1051 | 1.0687
2011-03-11 | 41 | 23.3962 | 11.1372 | 34.5334 | 2.0745 | 0.76558 | 0.25673 | 3.0968 | 8.968% | 9.541% | 6.448% | 1.0985 | 1.1055 | 1.0689
2011-03-11 | 42 | 24.2444 | 11.502 | 35.7463 | 2.2228 | 0.76558 | 0.26574 | 3.2541 | 9.103% | 9.686% | 6.545% | 1.1002 | 1.1072 | 1.07
2011-03-11 | 43 | 24.1016 | 11.3813 | 35.483 | 2.1902 | 0.76558 | 0.26378 | 3.2195 | 9.073% | 9.654% | 6.524% | 1.0998 | 1.1069 | 1.0698
2011-03-11 | 44 | 23.1531 | 10.9199 | 34.0729 | 2.0195 | 0.76558 | 0.2533 | 3.0384 | 8.917% | 9.488% | 6.412% | 1.0979 | 1.1048 | 1.0685
2011-03-11 | 45 | 21.6311 | 10.2258 | 31.857 | 1.7654 | 0.76558 | 0.23683 | 2.7678 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2011-03-11 | 46 | 19.7371 | 8.9227 | 28.6599 | 1.4288 | 0.76558 | 0.21306 | 2.4075 | 8.4% | 8.938% | 6.04% | 1.0917 | 1.0982 | 1.0643
2011-03-11 | 47 | 17.9767 | 8.3543 | 26.331 | 1.2061 | 0.76558 | 0.19575 | 2.1674 | 8.231% | 8.758% | 5.918% | 1.0897 | 1.096 | 1.0629
2011-03-11 | 48 | 16.6093 | 8.4197 | 25.029 | 1.0897 | 0.76558 | 0.18607 | 2.0414 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-03-12 | 1 | 14.8506 | 7.7131 | 22.5638 | 0.88564 | 0.76558 | 0.16774 | 1.819 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-12 | 2 | 14.0091 | 7.1622 | 21.1713 | 0.7797 | 0.76558 | 0.15739 | 1.7027 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-12 | 3 | 13.4115 | 6.857 | 20.2685 | 0.71462 | 0.76558 | 0.15068 | 1.6309 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-12 | 4 | 12.9152 | 6.6189 | 19.5341 | 0.66378 | 0.76558 | 0.14522 | 1.5746 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-12 | 5 | 12.6372 | 6.5236 | 19.1608 | 0.63865 | 0.76558 | 0.14244 | 1.5467 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-03-12 | 6 | 12.0704 | 6.4875 | 18.5579 | 0.59909 | 0.76558 | 0.13796 | 1.5026 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-12 | 7 | 11.9657 | 6.5649 | 18.5306 | 0.59733 | 0.76558 | 0.13776 | 1.5007 | 8.098% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-03-12 | 8 | 11.8397 | 6.545 | 18.3848 | 0.58796 | 0.76558 | 0.13667 | 1.4902 | 8.106% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-12 | 9 | 12.1537 | 6.5732 | 18.7269 | 0.61005 | 0.76558 | 0.13922 | 1.5148 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2011-03-12 | 10 | 12.4728 | 6.516 | 18.9887 | 0.62723 | 0.76558 | 0.14116 | 1.534 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-03-12 | 11 | 12.8178 | 6.8056 | 19.6234 | 0.66986 | 0.76558 | 0.14588 | 1.5813 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-12 | 12 | 13.071 | 6.9831 | 20.0541 | 0.69959 | 0.76558 | 0.14908 | 1.6143 | 8.049% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-03-12 | 13 | 14.6608 | 7.7054 | 22.3662 | 0.8702 | 0.76558 | 0.16627 | 1.802 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-12 | 14 | 16.9288 | 8.9269 | 25.8557 | 1.1629 | 0.76558 | 0.19221 | 2.1207 | 8.202% | 8.727% | 5.897% | 1.0893 | 1.0956 | 1.0627
2011-03-12 | 15 | 20.7969 | 10.8667 | 31.6636 | 1.744 | 0.76558 | 0.23539 | 2.745 | 8.669% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2011-03-12 | 16 | 22.5758 | 11.7428 | 34.3186 | 2.0488 | 0.76558 | 0.25513 | 3.0695 | 8.944% | 9.516% | 6.431% | 1.0982 | 1.1052 | 1.0687
2011-03-12 | 17 | 24.2156 | 12.4792 | 36.6948 | 2.3423 | 0.76558 | 0.27279 | 3.3807 | 9.213% | 9.803% | 6.624% | 1.1015 | 1.1087 | 1.0709
2011-03-12 | 18 | 27.7407 | 13.4792 | 41.2199 | 2.9556 | 0.76558 | 0.30643 | 4.0276 | 9.771% | 10.4% | 7.025% | 1.1083 | 1.116 | 1.0756
2011-03-12 | 19 | 26.7115 | 13.0435 | 39.755 | 2.7493 | 0.76558 | 0.29554 | 3.8104 | 9.585% | 10.2% | 6.891% | 1.106 | 1.1136 | 1.074
2011-03-12 | 20 | 26.9488 | 12.9261 | 39.8749 | 2.7659 | 0.76558 | 0.29644 | 3.8279 | 9.6% | 10.21% | 6.902% | 1.1062 | 1.1138 | 1.0741
2011-03-12 | 21 | 26.2167 | 12.0149 | 38.2316 | 2.5426 | 0.76558 | 0.28422 | 3.5924 | 9.396% | 9.998% | 6.756% | 1.1037 | 1.1111 | 1.0725
2011-03-12 | 22 | 25.3434 | 11.7183 | 37.0617 | 2.3894 | 0.76558 | 0.27552 | 3.4305 | 9.256% | 9.849% | 6.655% | 1.102 | 1.1092 | 1.0713
2011-03-12 | 23 | 24.8955 | 11.3897 | 36.2852 | 2.2903 | 0.76558 | 0.26975 | 3.3256 | 9.165% | 9.752% | 6.59% | 1.1009 | 1.1081 | 1.0705
2011-03-12 | 24 | 24.0378 | 11.4114 | 35.4491 | 2.186 | 0.76558 | 0.26353 | 3.2151 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2011-03-12 | 25 | 23.0615 | 11.2886 | 34.3501 | 2.0525 | 0.76558 | 0.25536 | 3.0735 | 8.947% | 9.52% | 6.433% | 1.0983 | 1.1052 | 1.0688
2011-03-12 | 26 | 22.1193 | 10.719 | 32.8383 | 1.8758 | 0.76558 | 0.24412 | 2.8855 | 8.787% | 9.35% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-03-12 | 27 | 22.1009 | 10.6667 | 32.7676 | 1.8678 | 0.76558 | 0.2436 | 2.877 | 8.78% | 9.342% | 6.313% | 1.0962 | 1.103 | 1.0674
2011-03-12 | 28 | 22.1886 | 10.528 | 32.7166 | 1.862 | 0.76558 | 0.24322 | 2.8708 | 8.775% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-03-12 | 29 | 22.1622 | 10.1033 | 32.2655 | 1.811 | 0.76558 | 0.23987 | 2.8164 | 8.729% | 9.288% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-03-12 | 30 | 21.5965 | 9.7842 | 31.3807 | 1.713 | 0.76558 | 0.23329 | 2.7119 | 8.642% | 9.195% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-03-12 | 31 | 21.4897 | 9.6717 | 31.1614 | 1.6891 | 0.76558 | 0.23166 | 2.6864 | 8.621% | 9.173% | 6.198% | 1.0943 | 1.101 | 1.0661
2011-03-12 | 32 | 21.3171 | 9.7027 | 31.0198 | 1.6738 | 0.76558 | 0.23061 | 2.67 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-03-12 | 33 | 21.6314 | 9.9535 | 31.5849 | 1.7354 | 0.76558 | 0.23481 | 2.7358 | 8.662% | 9.216% | 6.228% | 1.0948 | 1.1015 | 1.0664
2011-03-12 | 34 | 21.8755 | 9.9658 | 31.8413 | 1.7637 | 0.76558 | 0.23671 | 2.766 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-03-12 | 35 | 22.0397 | 10.3358 | 32.3755 | 1.8233 | 0.76558 | 0.24068 | 2.8296 | 8.74% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.0671
2011-03-12 | 36 | 22.5684 | 10.7976 | 33.366 | 1.9366 | 0.76558 | 0.24805 | 2.9502 | 8.842% | 9.408% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-03-12 | 37 | 23.3973 | 10.8594 | 34.2567 | 2.0414 | 0.76558 | 0.25467 | 3.0616 | 8.937% | 9.509% | 6.426% | 1.0981 | 1.1051 | 1.0687
2011-03-12 | 38 | 24.1536 | 10.904 | 35.0577 | 2.138 | 0.76558 | 0.26062 | 3.1642 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2011-03-12 | 39 | 24.1951 | 10.8507 | 35.0457 | 2.1365 | 0.76558 | 0.26053 | 3.1626 | 9.024% | 9.602% | 6.488% | 1.0992 | 1.1062 | 1.0694
2011-03-12 | 40 | 24.4586 | 10.4742 | 34.9329 | 2.1228 | 0.76558 | 0.2597 | 3.148 | 9.012% | 9.588% | 6.479% | 1.099 | 1.1061 | 1.0693
2011-03-12 | 41 | 25.3621 | 10.6071 | 35.9692 | 2.2506 | 0.76558 | 0.2674 | 3.2836 | 9.129% | 9.713% | 6.564% | 1.1005 | 1.1076 | 1.0702
2011-03-12 | 42 | 26.4015 | 10.796 | 37.1976 | 2.4069 | 0.76558 | 0.27653 | 3.449 | 9.272% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2011-03-12 | 43 | 25.8135 | 10.334 | 36.1475 | 2.273 | 0.76558 | 0.26872 | 3.3073 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2011-03-12 | 44 | 24.9087 | 9.7874 | 34.6961 | 2.0941 | 0.76558 | 0.25794 | 3.1176 | 8.985% | 9.561% | 6.461% | 1.0987 | 1.1057 | 1.0691
2011-03-12 | 45 | 23.3529 | 9.0577 | 32.4106 | 1.8273 | 0.76558 | 0.24094 | 2.8338 | 8.743% | 9.303% | 6.287% | 1.0958 | 1.1026 | 1.0671
2011-03-12 | 46 | 21.3299 | 8.4261 | 29.756 | 1.5402 | 0.76558 | 0.22121 | 2.527 | 8.492% | 9.036% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-03-12 | 47 | 19.6889 | 7.7794 | 27.4683 | 1.3125 | 0.76558 | 0.2042 | 2.2823 | 8.309% | 8.841% | 5.974% | 1.0906 | 1.097 | 1.0635
2011-03-12 | 48 | 18.8807 | 8.0934 | 26.974 | 1.2657 | 0.76558 | 0.20053 | 2.2318 | 8.274% | 8.803% | 5.949% | 1.0902 | 1.0965 | 1.0633
2011-03-13 | 1 | 17.3565 | 7.5061 | 24.8627 | 1.0753 | 0.76558 | 0.18483 | 2.0257 | 8.148% | 8.669% | 5.858% | 1.0887 | 1.0949 | 1.0622
2011-03-13 | 2 | 16.0493 | 6.9035 | 22.9529 | 0.91645 | 0.76558 | 0.17063 | 1.8527 | 8.072% | 8.588% | 5.803% | 1.0878 | 1.094 | 1.0616
2011-03-13 | 3 | 15.0979 | 6.462 | 21.5599 | 0.80859 | 0.76558 | 0.16028 | 1.7344 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-13 | 4 | 14.3389 | 6.2086 | 20.5475 | 0.73443 | 0.76558 | 0.15275 | 1.6528 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-13 | 5 | 13.8171 | 6.1693 | 19.9863 | 0.69487 | 0.76558 | 0.14858 | 1.609 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-03-13 | 6 | 13.4573 | 6.1548 | 19.6121 | 0.66909 | 0.76558 | 0.1458 | 1.5805 | 8.059% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-13 | 7 | 13.65 | 6.0833 | 19.7333 | 0.67739 | 0.76558 | 0.1467 | 1.5897 | 8.056% | 8.571% | 5.792% | 1.0876 | 1.0937 | 1.0615
2011-03-13 | 8 | 13.6191 | 5.9378 | 19.5569 | 0.66532 | 0.76558 | 0.14539 | 1.5763 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-13 | 9 | 13.6391 | 5.8666 | 19.5057 | 0.66185 | 0.76558 | 0.14501 | 1.5724 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-13 | 10 | 13.5879 | 5.9449 | 19.5328 | 0.66369 | 0.76558 | 0.14521 | 1.5745 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-13 | 11 | 13.6358 | 6.0466 | 19.6824 | 0.67389 | 0.76558 | 0.14632 | 1.5858 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-13 | 12 | 13.9147 | 6.2078 | 20.1225 | 0.70437 | 0.76558 | 0.14959 | 1.6195 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-13 | 13 | 15.4397 | 6.6268 | 22.0665 | 0.84704 | 0.76558 | 0.16405 | 1.7767 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-13 | 14 | 16.9927 | 6.9498 | 23.9426 | 0.99719 | 0.76558 | 0.17799 | 1.9408 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-13 | 15 | 18.9891 | 7.6812 | 26.6703 | 1.2373 | 0.76558 | 0.19827 | 2.2012 | 8.253% | 8.782% | 5.934% | 1.09 | 1.0963 | 1.0631
2011-03-13 | 16 | 20.5942 | 8.4452 | 29.0393 | 1.4669 | 0.76558 | 0.21588 | 2.4484 | 8.431% | 8.971% | 6.062% | 1.0921 | 1.0985 | 1.0645
2011-03-13 | 17 | 22.3978 | 9.5346 | 31.9324 | 1.7738 | 0.76558 | 0.23739 | 2.7767 | 8.696% | 9.252% | 6.252% | 1.0952 | 1.102 | 1.0667
2011-03-13 | 18 | 24.0131 | 10.3487 | 34.3619 | 2.0539 | 0.76558 | 0.25545 | 3.075 | 8.949% | 9.522% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-13 | 19 | 25.6949 | 11.183 | 36.8779 | 2.3657 | 0.76558 | 0.27415 | 3.4055 | 9.234% | 9.825% | 6.64% | 1.1017 | 1.109 | 1.0711
2011-03-13 | 20 | 25.8651 | 11.4994 | 37.3645 | 2.4286 | 0.76558 | 0.27777 | 3.4719 | 9.292% | 9.887% | 6.681% | 1.1024 | 1.1097 | 1.0716
2011-03-13 | 21 | 26.1774 | 11.5244 | 37.7018 | 2.4726 | 0.76558 | 0.28028 | 3.5185 | 9.332% | 9.93% | 6.71% | 1.1029 | 1.1102 | 1.0719
2011-03-13 | 22 | 25.6287 | 11.5701 | 37.1988 | 2.4071 | 0.76558 | 0.27654 | 3.4492 | 9.272% | 9.866% | 6.667% | 1.1022 | 1.1095 | 1.0714
2011-03-13 | 23 | 24.5058 | 11.0093 | 35.5151 | 2.1941 | 0.76558 | 0.26402 | 3.2237 | 9.077% | 9.658% | 6.526% | 1.0998 | 1.1069 | 1.0698
2011-03-13 | 24 | 23.674 | 10.722 | 34.396 | 2.058 | 0.76558 | 0.2557 | 3.0793 | 8.953% | 9.525% | 6.437% | 1.0983 | 1.1053 | 1.0688
2011-03-13 | 25 | 23.3365 | 10.4908 | 33.8273 | 1.9905 | 0.76558 | 0.25148 | 3.0076 | 8.891% | 9.46% | 6.393% | 1.0976 | 1.1045 | 1.0683
2011-03-13 | 26 | 22.8889 | 9.8633 | 32.7522 | 1.866 | 0.76558 | 0.24348 | 2.8751 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2011-03-13 | 27 | 22.3747 | 9.8108 | 32.1855 | 1.802 | 0.76558 | 0.23927 | 2.8069 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-03-13 | 28 | 22.0921 | 9.614 | 31.7061 | 1.7487 | 0.76558 | 0.23571 | 2.75 | 8.673% | 9.229% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-03-13 | 29 | 21.0169 | 9.2315 | 30.2484 | 1.5916 | 0.76558 | 0.22487 | 2.5821 | 8.536% | 9.083% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-03-13 | 30 | 20.5017 | 8.8655 | 29.3672 | 1.5002 | 0.76558 | 0.21832 | 2.4841 | 8.459% | 9% | 6.082% | 1.0924 | 1.0989 | 1.0648
2011-03-13 | 31 | 20.55 | 8.8223 | 29.3723 | 1.5008 | 0.76558 | 0.21836 | 2.4847 | 8.459% | 9.001% | 6.082% | 1.0924 | 1.0989 | 1.0648
2011-03-13 | 32 | 20.5737 | 8.6256 | 29.1993 | 1.4831 | 0.76558 | 0.21707 | 2.4658 | 8.445% | 8.985% | 6.072% | 1.0922 | 1.0987 | 1.0646
2011-03-13 | 33 | 21.0175 | 9.119 | 30.1365 | 1.5799 | 0.76558 | 0.22404 | 2.5695 | 8.526% | 9.072% | 6.13% | 1.0932 | 1.0998 | 1.0653
2011-03-13 | 34 | 21.4311 | 9.1199 | 30.551 | 1.6236 | 0.76558 | 0.22712 | 2.6163 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2011-03-13 | 35 | 21.8349 | 9.5166 | 31.3515 | 1.7098 | 0.76558 | 0.23307 | 2.7085 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-03-13 | 36 | 22.9706 | 10.089 | 33.0596 | 1.9012 | 0.76558 | 0.24577 | 2.9126 | 8.81% | 9.374% | 6.334% | 1.0966 | 1.1034 | 1.0676
2011-03-13 | 37 | 23.5833 | 10.433 | 34.0162 | 2.0128 | 0.76558 | 0.25288 | 3.0313 | 8.911% | 9.482% | 6.407% | 1.0978 | 1.1047 | 1.0685
2011-03-13 | 38 | 24.6086 | 10.2941 | 34.9027 | 2.1191 | 0.76558 | 0.25947 | 3.1442 | 9.008% | 9.585% | 6.477% | 1.099 | 1.106 | 1.0693
2011-03-13 | 39 | 24.4732 | 10.1028 | 34.576 | 2.0796 | 0.76558 | 0.25704 | 3.1022 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2011-03-13 | 40 | 24.5269 | 9.9885 | 34.5154 | 2.0723 | 0.76558 | 0.25659 | 3.0945 | 8.966% | 9.539% | 6.446% | 1.0985 | 1.1055 | 1.0689
2011-03-13 | 41 | 24.5878 | 9.9616 | 34.5494 | 2.0764 | 0.76558 | 0.25684 | 3.0988 | 8.969% | 9.543% | 6.449% | 1.0985 | 1.1055 | 1.0689
2011-03-13 | 42 | 24.4151 | 10.0622 | 34.4773 | 2.0678 | 0.76558 | 0.25631 | 3.0897 | 8.961% | 9.535% | 6.443% | 1.0984 | 1.1054 | 1.0689
2011-03-13 | 43 | 23.472 | 9.4697 | 32.9418 | 1.8877 | 0.76558 | 0.24489 | 2.8982 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-03-13 | 44 | 22.5957 | 8.9832 | 31.5789 | 1.7347 | 0.76558 | 0.23476 | 2.7351 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-13 | 45 | 21.3765 | 8.4808 | 29.8573 | 1.5507 | 0.76558 | 0.22196 | 2.5383 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2011-03-13 | 46 | 19.781 | 7.9272 | 27.7082 | 1.3355 | 0.76558 | 0.20599 | 2.3071 | 8.326% | 8.859% | 5.987% | 1.0908 | 1.0972 | 1.0637
2011-03-13 | 47 | 18.4417 | 7.7357 | 26.1774 | 1.192 | 0.76558 | 0.19461 | 2.1522 | 8.222% | 8.748% | 5.911% | 1.0896 | 1.0959 | 1.0628
2011-03-13 | 48 | 17.4565 | 7.869 | 25.3256 | 1.1157 | 0.76558 | 0.18827 | 2.0696 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-03-14 | 1 | 15.8497 | 7.1009 | 22.9506 | 0.91627 | 0.76558 | 0.17062 | 1.8525 | 8.072% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-14 | 2 | 14.5038 | 6.6288 | 21.1326 | 0.77685 | 0.76558 | 0.1571 | 1.6995 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-14 | 3 | 13.6658 | 6.36 | 20.0258 | 0.69761 | 0.76558 | 0.14887 | 1.6121 | 8.05% | 8.565% | 5.788% | 1.0875 | 1.0937 | 1.0614
2011-03-14 | 4 | 13.1628 | 6.1861 | 19.3489 | 0.65125 | 0.76558 | 0.14384 | 1.5607 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-03-14 | 5 | 12.9716 | 6.0743 | 19.046 | 0.63102 | 0.76558 | 0.14159 | 1.5382 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-03-14 | 6 | 12.6486 | 5.9897 | 18.6383 | 0.60429 | 0.76558 | 0.13856 | 1.5084 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-03-14 | 7 | 12.1623 | 6.031 | 18.1933 | 0.57578 | 0.76558 | 0.13525 | 1.4766 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-03-14 | 8 | 11.8024 | 5.986 | 17.7884 | 0.55044 | 0.76558 | 0.13224 | 1.4483 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-03-14 | 9 | 11.8544 | 5.9138 | 17.7682 | 0.54919 | 0.76558 | 0.13209 | 1.4469 | 8.143% | 8.664% | 5.855% | 1.0886 | 1.0949 | 1.0622
2011-03-14 | 10 | 11.972 | 5.8868 | 17.8588 | 0.55481 | 0.76558 | 0.13276 | 1.4531 | 8.137% | 8.658% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-03-14 | 11 | 12.3046 | 5.9251 | 18.2297 | 0.57809 | 0.76558 | 0.13552 | 1.4792 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-14 | 12 | 12.5883 | 5.8033 | 18.3916 | 0.5884 | 0.76558 | 0.13673 | 1.4907 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-14 | 13 | 13.3484 | 6.0099 | 19.3582 | 0.65188 | 0.76558 | 0.14391 | 1.5614 | 8.066% | 8.582% | 5.799% | 1.0877 | 1.0939 | 1.0616
2011-03-14 | 14 | 13.8887 | 6.1813 | 20.07 | 0.70069 | 0.76558 | 0.1492 | 1.6155 | 8.049% | 8.564% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-14 | 15 | 15.098 | 6.5758 | 21.6739 | 0.81716 | 0.76558 | 0.16113 | 1.7439 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-14 | 16 | 16.6039 | 7.0131 | 23.6169 | 0.97024 | 0.76558 | 0.17557 | 1.9114 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-03-14 | 17 | 18.9585 | 7.9166 | 26.8752 | 1.2564 | 0.76558 | 0.19979 | 2.2218 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2011-03-14 | 18 | 20.7661 | 8.9321 | 29.6982 | 1.5342 | 0.76558 | 0.22078 | 2.5206 | 8.487% | 9.031% | 6.102% | 1.0927 | 1.0993 | 1.065
2011-03-14 | 19 | 22.3849 | 9.7658 | 32.1507 | 1.7981 | 0.76558 | 0.23901 | 2.8027 | 8.717% | 9.275% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-03-14 | 20 | 22.9058 | 10.1117 | 33.0175 | 1.8964 | 0.76558 | 0.24546 | 2.9074 | 8.806% | 9.369% | 6.331% | 1.0966 | 1.1034 | 1.0676
2011-03-14 | 21 | 23.1979 | 10.3041 | 33.5019 | 1.9524 | 0.76558 | 0.24906 | 2.9671 | 8.856% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2011-03-14 | 22 | 22.8816 | 10.2785 | 33.1601 | 1.9128 | 0.76558 | 0.24652 | 2.9249 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2011-03-14 | 23 | 22.5365 | 10.179 | 32.7154 | 1.8618 | 0.76558 | 0.24321 | 2.8706 | 8.775% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-03-14 | 24 | 22.1253 | 10.0813 | 32.2066 | 1.8044 | 0.76558 | 0.23943 | 2.8094 | 8.723% | 9.281% | 6.272% | 1.0956 | 1.1023 | 1.0669
2011-03-14 | 25 | 21.5011 | 10.1396 | 31.6408 | 1.7415 | 0.76558 | 0.23522 | 2.7423 | 8.667% | 9.222% | 6.232% | 1.0949 | 1.1016 | 1.0665
2011-03-14 | 26 | 21.0119 | 9.8047 | 30.8165 | 1.652 | 0.76558 | 0.22909 | 2.6466 | 8.588% | 9.138% | 6.175% | 1.094 | 1.1006 | 1.0658
2011-03-14 | 27 | 20.4288 | 9.8573 | 30.2861 | 1.5956 | 0.76558 | 0.22515 | 2.5863 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-03-14 | 28 | 20.1463 | 9.6942 | 29.8405 | 1.549 | 0.76558 | 0.22184 | 2.5364 | 8.5% | 9.044% | 6.111% | 1.0929 | 1.0994 | 1.0651
2011-03-14 | 29 | 19.8002 | 9.4194 | 29.2197 | 1.4852 | 0.76558 | 0.21722 | 2.468 | 8.446% | 8.987% | 6.073% | 1.0923 | 1.0987 | 1.0647
2011-03-14 | 30 | 19.5091 | 9.2484 | 28.7575 | 1.4386 | 0.76558 | 0.21379 | 2.418 | 8.408% | 8.946% | 6.045% | 1.0918 | 1.0983 | 1.0643
2011-03-14 | 31 | 19.5336 | 9.0685 | 28.6021 | 1.4231 | 0.76558 | 0.21263 | 2.4013 | 8.396% | 8.933% | 6.036% | 1.0916 | 1.0981 | 1.0642
2011-03-14 | 32 | 19.3075 | 9.1268 | 28.4343 | 1.4064 | 0.76558 | 0.21138 | 2.3834 | 8.382% | 8.919% | 6.027% | 1.0915 | 1.0979 | 1.0641
2011-03-14 | 33 | 19.3356 | 9.3858 | 28.7215 | 1.435 | 0.76558 | 0.21352 | 2.4141 | 8.405% | 8.943% | 6.043% | 1.0918 | 1.0982 | 1.0643
2011-03-14 | 34 | 19.4004 | 9.5727 | 28.9732 | 1.4602 | 0.76558 | 0.21539 | 2.4412 | 8.426% | 8.965% | 6.058% | 1.092 | 1.0985 | 1.0645
2011-03-14 | 35 | 19.8364 | 10.1515 | 29.9879 | 1.5643 | 0.76558 | 0.22293 | 2.5528 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2011-03-14 | 36 | 20.5701 | 10.5588 | 31.1289 | 1.6856 | 0.76558 | 0.23142 | 2.6826 | 8.618% | 9.169% | 6.196% | 1.0943 | 1.1009 | 1.0661
2011-03-14 | 37 | 21.4745 | 10.8007 | 32.2752 | 1.8121 | 0.76558 | 0.23994 | 2.8176 | 8.73% | 9.289% | 6.277% | 1.0956 | 1.1024 | 1.067
2011-03-14 | 38 | 22.0351 | 10.7441 | 32.7792 | 1.8691 | 0.76558 | 0.24368 | 2.8784 | 8.781% | 9.343% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-03-14 | 39 | 22.067 | 10.6851 | 32.752 | 1.866 | 0.76558 | 0.24348 | 2.8751 | 8.778% | 9.34% | 6.312% | 1.0962 | 1.103 | 1.0674
2011-03-14 | 40 | 21.9101 | 10.4762 | 32.3863 | 1.8246 | 0.76558 | 0.24076 | 2.8309 | 8.741% | 9.3% | 6.285% | 1.0958 | 1.1025 | 1.0671
2011-03-14 | 41 | 22.086 | 10.8504 | 32.9363 | 1.8871 | 0.76558 | 0.24485 | 2.8975 | 8.797% | 9.36% | 6.325% | 1.0965 | 1.1033 | 1.0675
2011-03-14 | 42 | 22.809 | 11.0899 | 33.8989 | 1.999 | 0.76558 | 0.25201 | 3.0166 | 8.899% | 9.468% | 6.398% | 1.0977 | 1.1046 | 1.0684
2011-03-14 | 43 | 22.6023 | 10.7266 | 33.3289 | 1.9323 | 0.76558 | 0.24777 | 2.9457 | 8.838% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2011-03-14 | 44 | 21.4109 | 9.9912 | 31.4021 | 1.7153 | 0.76558 | 0.23345 | 2.7144 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-14 | 45 | 20.1334 | 9.1826 | 29.316 | 1.495 | 0.76558 | 0.21794 | 2.4785 | 8.455% | 8.996% | 6.079% | 1.0924 | 1.0988 | 1.0647
2011-03-14 | 46 | 18.1271 | 8.4752 | 26.6023 | 1.231 | 0.76558 | 0.19776 | 2.1944 | 8.249% | 8.777% | 5.931% | 1.0899 | 1.0962 | 1.063
2011-03-14 | 47 | 16.6736 | 7.9737 | 24.6473 | 1.0567 | 0.76558 | 0.18323 | 2.0056 | 8.137% | 8.658% | 5.851% | 1.0886 | 1.0948 | 1.0621
2011-03-14 | 48 | 15.5374 | 8.1063 | 23.6437 | 0.97245 | 0.76558 | 0.17577 | 1.9138 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-03-15 | 1 | 14.1108 | 7.2947 | 21.4054 | 0.79704 | 0.76558 | 0.15913 | 1.7218 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-15 | 2 | 13.183 | 6.665 | 19.848 | 0.68528 | 0.76558 | 0.14755 | 1.5984 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-15 | 3 | 12.8109 | 6.2409 | 19.0518 | 0.6314 | 0.76558 | 0.14163 | 1.5386 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-03-15 | 4 | 12.3882 | 6.1332 | 18.5215 | 0.59674 | 0.76558 | 0.13769 | 1.5 | 8.099% | 8.617% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-03-15 | 5 | 11.9755 | 6.0307 | 18.0062 | 0.564 | 0.76558 | 0.13386 | 1.4634 | 8.127% | 8.648% | 5.844% | 1.0885 | 1.0947 | 1.0621
2011-03-15 | 6 | 11.5307 | 6.0567 | 17.5874 | 0.53807 | 0.76558 | 0.13075 | 1.4344 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-03-15 | 7 | 11.3297 | 6.0234 | 17.3531 | 0.52383 | 0.76558 | 0.12901 | 1.4184 | 8.174% | 8.697% | 5.877% | 1.089 | 1.0953 | 1.0624
2011-03-15 | 8 | 11.2303 | 6.0027 | 17.233 | 0.5166 | 0.76558 | 0.12811 | 1.4103 | 8.184% | 8.707% | 5.884% | 1.0891 | 1.0954 | 1.0625
2011-03-15 | 9 | 11.4853 | 5.9283 | 17.4136 | 0.52748 | 0.76558 | 0.12945 | 1.4225 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-03-15 | 10 | 11.9257 | 5.9416 | 17.8673 | 0.55533 | 0.76558 | 0.13283 | 1.4537 | 8.136% | 8.657% | 5.85% | 1.0886 | 1.0948 | 1.0621
2011-03-15 | 11 | 12.2569 | 5.9977 | 18.2546 | 0.57967 | 0.76558 | 0.13571 | 1.481 | 8.113% | 8.632% | 5.833% | 1.0883 | 1.0945 | 1.0619
2011-03-15 | 12 | 12.8477 | 6.4096 | 19.2574 | 0.6451 | 0.76558 | 0.14316 | 1.5538 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-03-15 | 13 | 14.0186 | 6.9996 | 21.0183 | 0.76847 | 0.76558 | 0.15625 | 1.6903 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-15 | 14 | 16.0347 | 8.1291 | 24.1638 | 1.0157 | 0.76558 | 0.17964 | 1.9609 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-15 | 15 | 20.0814 | 10.0644 | 30.1458 | 1.5808 | 0.76558 | 0.22411 | 2.5705 | 8.527% | 9.073% | 6.131% | 1.0932 | 1.0998 | 1.0653
2011-03-15 | 16 | 23.171 | 11.2448 | 34.4158 | 2.0604 | 0.76558 | 0.25585 | 3.0818 | 8.955% | 9.528% | 6.438% | 1.0984 | 1.1053 | 1.0688
2011-03-15 | 17 | 24.372 | 11.5594 | 35.9314 | 2.2459 | 0.76558 | 0.26712 | 3.2786 | 9.124% | 9.708% | 6.561% | 1.1004 | 1.1075 | 1.0702
2011-03-15 | 18 | 24.2711 | 11.4036 | 35.6746 | 2.2139 | 0.76558 | 0.26521 | 3.2447 | 9.095% | 9.677% | 6.539% | 1.1001 | 1.1071 | 1.07
2011-03-15 | 19 | 23.9817 | 11.0286 | 35.0103 | 2.1322 | 0.76558 | 0.26027 | 3.158 | 9.02% | 9.598% | 6.486% | 1.0991 | 1.1062 | 1.0694
2011-03-15 | 20 | 22.893 | 10.888 | 33.781 | 1.9851 | 0.76558 | 0.25113 | 3.0018 | 8.886% | 9.455% | 6.389% | 1.0975 | 1.1044 | 1.0683
2011-03-15 | 21 | 22.5463 | 10.6139 | 33.1602 | 1.9128 | 0.76558 | 0.24652 | 2.9249 | 8.82% | 9.385% | 6.342% | 1.0967 | 1.1036 | 1.0677
2011-03-15 | 22 | 22.2416 | 10.6259 | 32.8674 | 1.8792 | 0.76558 | 0.24434 | 2.8891 | 8.79% | 9.353% | 6.32% | 1.0964 | 1.1032 | 1.0675
2011-03-15 | 23 | 21.5381 | 10.4711 | 32.0092 | 1.7823 | 0.76558 | 0.23796 | 2.7859 | 8.703% | 9.26% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-15 | 24 | 21.025 | 10.5433 | 31.5683 | 1.7336 | 0.76558 | 0.23468 | 2.7338 | 8.66% | 9.214% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-15 | 25 | 20.7689 | 10.6207 | 31.3897 | 1.714 | 0.76558 | 0.23335 | 2.7129 | 8.643% | 9.196% | 6.214% | 1.0946 | 1.1013 | 1.0663
2011-03-15 | 26 | 20.3435 | 10.1937 | 30.5373 | 1.6222 | 0.76558 | 0.22702 | 2.6148 | 8.563% | 9.111% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-03-15 | 27 | 19.7418 | 10.3615 | 30.1033 | 1.5764 | 0.76558 | 0.22379 | 2.5658 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-03-15 | 28 | 20.1177 | 10.464 | 30.5817 | 1.6269 | 0.76558 | 0.22735 | 2.6198 | 8.567% | 9.115% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-03-15 | 29 | 20.1447 | 10.3624 | 30.5071 | 1.619 | 0.76558 | 0.22679 | 2.6113 | 8.56% | 9.108% | 6.154% | 1.0936 | 1.1002 | 1.0656
2011-03-15 | 30 | 19.8371 | 10.1012 | 29.9384 | 1.5592 | 0.76558 | 0.22257 | 2.5473 | 8.508% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2011-03-15 | 31 | 19.9112 | 9.9671 | 29.8783 | 1.5529 | 0.76558 | 0.22212 | 2.5406 | 8.503% | 9.047% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-03-15 | 32 | 19.7651 | 10.0525 | 29.8177 | 1.5466 | 0.76558 | 0.22167 | 2.5339 | 8.498% | 9.042% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-03-15 | 33 | 19.9361 | 10.1517 | 30.0878 | 1.5748 | 0.76558 | 0.22368 | 2.564 | 8.522% | 9.067% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-03-15 | 34 | 20.0047 | 10.2431 | 30.2478 | 1.5916 | 0.76558 | 0.22487 | 2.582 | 8.536% | 9.082% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-03-15 | 35 | 20.6243 | 10.6183 | 31.2427 | 1.698 | 0.76558 | 0.23226 | 2.6958 | 8.629% | 9.181% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-03-15 | 36 | 21.2144 | 11.1551 | 32.3695 | 1.8227 | 0.76558 | 0.24064 | 2.8289 | 8.739% | 9.299% | 6.284% | 1.0958 | 1.1025 | 1.067
2011-03-15 | 37 | 21.7005 | 11.6613 | 33.3618 | 1.9361 | 0.76558 | 0.24802 | 2.9497 | 8.842% | 9.407% | 6.357% | 1.097 | 1.1038 | 1.0679
2011-03-15 | 38 | 22.4192 | 11.4281 | 33.8473 | 1.9929 | 0.76558 | 0.25163 | 3.0101 | 8.893% | 9.462% | 6.394% | 1.0976 | 1.1045 | 1.0683
2011-03-15 | 39 | 22.7098 | 11.2332 | 33.943 | 2.0042 | 0.76558 | 0.25234 | 3.0221 | 8.903% | 9.473% | 6.402% | 1.0977 | 1.1046 | 1.0684
2011-03-15 | 40 | 22.6038 | 10.7481 | 33.352 | 1.935 | 0.76558 | 0.24794 | 2.9485 | 8.841% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-03-15 | 41 | 22.8538 | 11.0188 | 33.8726 | 1.9959 | 0.76558 | 0.25181 | 3.0133 | 8.896% | 9.465% | 6.396% | 1.0976 | 1.1045 | 1.0683
2011-03-15 | 42 | 23.8629 | 11.0996 | 34.9625 | 2.1264 | 0.76558 | 0.25992 | 3.1519 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-03-15 | 43 | 23.0871 | 10.6771 | 33.7642 | 1.9831 | 0.76558 | 0.25101 | 2.9997 | 8.884% | 9.453% | 6.388% | 1.0975 | 1.1044 | 1.0682
2011-03-15 | 44 | 22.1458 | 10.1192 | 32.2651 | 1.8109 | 0.76558 | 0.23986 | 2.8164 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-03-15 | 45 | 20.5443 | 9.4394 | 29.9837 | 1.5639 | 0.76558 | 0.2229 | 2.5524 | 8.513% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-03-15 | 46 | 18.7545 | 8.758 | 27.5125 | 1.3167 | 0.76558 | 0.20453 | 2.2868 | 8.312% | 8.844% | 5.976% | 1.0907 | 1.097 | 1.0636
2011-03-15 | 47 | 16.7155 | 8.5469 | 25.2624 | 1.1102 | 0.76558 | 0.1878 | 2.0635 | 8.168% | 8.691% | 5.873% | 1.0889 | 1.0952 | 1.0624
2011-03-15 | 48 | 15.5876 | 8.6864 | 24.274 | 1.025 | 0.76558 | 0.18046 | 1.971 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-03-16 | 1 | 14.2037 | 7.8566 | 22.0603 | 0.84656 | 0.76558 | 0.164 | 1.7761 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-16 | 2 | 13.3907 | 7.4997 | 20.8903 | 0.75915 | 0.76558 | 0.1553 | 1.68 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-16 | 3 | 12.7494 | 7.1836 | 19.9329 | 0.69116 | 0.76558 | 0.14818 | 1.6049 | 8.052% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-16 | 4 | 12.3332 | 6.8794 | 19.2127 | 0.64211 | 0.76558 | 0.14283 | 1.5505 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-16 | 5 | 12.0713 | 6.6831 | 18.7544 | 0.61185 | 0.76558 | 0.13942 | 1.5168 | 8.088% | 8.606% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-03-16 | 6 | 11.707 | 6.6673 | 18.3743 | 0.5873 | 0.76558 | 0.1366 | 1.4895 | 8.106% | 8.625% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-16 | 7 | 11.3828 | 6.6001 | 17.9829 | 0.56254 | 0.76558 | 0.13369 | 1.4618 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-16 | 8 | 10.9097 | 6.3433 | 17.253 | 0.5178 | 0.76558 | 0.12826 | 1.4116 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2011-03-16 | 9 | 11.3483 | 6.4823 | 17.8306 | 0.55305 | 0.76558 | 0.13255 | 1.4512 | 8.139% | 8.66% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-03-16 | 10 | 11.65 | 6.5775 | 18.2274 | 0.57794 | 0.76558 | 0.1355 | 1.479 | 8.114% | 8.634% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-16 | 11 | 11.7864 | 6.7777 | 18.564 | 0.59949 | 0.76558 | 0.13801 | 1.5031 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-16 | 12 | 12.472 | 7.0852 | 19.5573 | 0.66535 | 0.76558 | 0.14539 | 1.5763 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-16 | 13 | 13.7744 | 7.8534 | 21.6277 | 0.81369 | 0.76558 | 0.16078 | 1.74 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-16 | 14 | 15.9278 | 8.9714 | 24.8992 | 1.0785 | 0.76558 | 0.1851 | 2.0291 | 8.149% | 8.671% | 5.859% | 1.0887 | 1.0949 | 1.0622
2011-03-16 | 15 | 19.5946 | 10.8156 | 30.4101 | 1.6087 | 0.76558 | 0.22607 | 2.6003 | 8.551% | 9.098% | 6.148% | 1.0935 | 1.1001 | 1.0655
2011-03-16 | 16 | 22.5699 | 11.8651 | 34.435 | 2.0627 | 0.76558 | 0.25599 | 3.0843 | 8.957% | 9.53% | 6.44% | 1.0984 | 1.1053 | 1.0688
2011-03-16 | 17 | 23.6907 | 12.0228 | 35.7135 | 2.2187 | 0.76558 | 0.2655 | 3.2498 | 9.1% | 9.682% | 6.543% | 1.1001 | 1.1072 | 1.07
2011-03-16 | 18 | 24 | 11.7559 | 35.7559 | 2.224 | 0.76558 | 0.26581 | 3.2554 | 9.104% | 9.687% | 6.546% | 1.1002 | 1.1073 | 1.07
2011-03-16 | 19 | 25 | 11.4152 | 36.4152 | 2.3068 | 0.76558 | 0.27072 | 3.343 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2011-03-16 | 20 | 27 | 11.1769 | 38.1769 | 2.5353 | 0.76558 | 0.28381 | 3.5847 | 9.39% | 9.991% | 6.751% | 1.1036 | 1.111 | 1.0724
2011-03-16 | 21 | 28.332 | 10.9253 | 39.2573 | 2.6809 | 0.76558 | 0.29184 | 3.7383 | 9.523% | 10.13% | 6.847% | 1.1052 | 1.1127 | 1.0735
2011-03-16 | 22 | 23.9135 | 11.1274 | 35.0409 | 2.1359 | 0.76558 | 0.2605 | 3.162 | 9.024% | 9.601% | 6.488% | 1.0992 | 1.1062 | 1.0694
2011-03-16 | 23 | 22.7676 | 10.6866 | 33.4542 | 1.9469 | 0.76558 | 0.2487 | 2.9611 | 8.851% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-03-16 | 24 | 21.9832 | 10.4902 | 32.4734 | 1.8344 | 0.76558 | 0.24141 | 2.8414 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-03-16 | 25 | 21.4526 | 10.6489 | 32.1015 | 1.7926 | 0.76558 | 0.23865 | 2.7968 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-03-16 | 26 | 20.9996 | 10.5275 | 31.5271 | 1.729 | 0.76558 | 0.23438 | 2.729 | 8.656% | 9.21% | 6.224% | 1.0948 | 1.1014 | 1.0664
2011-03-16 | 27 | 20.6923 | 10.754 | 31.4463 | 1.7202 | 0.76558 | 0.23378 | 2.7195 | 8.648% | 9.202% | 6.218% | 1.0947 | 1.1013 | 1.0663
2011-03-16 | 28 | 20.7314 | 10.8254 | 31.5568 | 1.7323 | 0.76558 | 0.2346 | 2.7325 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-03-16 | 29 | 20.7858 | 10.4171 | 31.2029 | 1.6937 | 0.76558 | 0.23197 | 2.6912 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-03-16 | 30 | 20.529 | 10.2996 | 30.8286 | 1.6533 | 0.76558 | 0.22918 | 2.648 | 8.59% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-03-16 | 31 | 20.6264 | 10.2215 | 30.848 | 1.6553 | 0.76558 | 0.22933 | 2.6502 | 8.591% | 9.141% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-03-16 | 32 | 20.5878 | 10.1208 | 30.7086 | 1.6404 | 0.76558 | 0.22829 | 2.6343 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-03-16 | 33 | 20.3835 | 10.4455 | 30.8289 | 1.6533 | 0.76558 | 0.22919 | 2.6481 | 8.59% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-03-16 | 34 | 20.9335 | 10.4964 | 31.4299 | 1.7184 | 0.76558 | 0.23365 | 2.7176 | 8.647% | 9.2% | 6.217% | 1.0946 | 1.1013 | 1.0663
2011-03-16 | 35 | 21.1542 | 11.0678 | 32.222 | 1.8061 | 0.76558 | 0.23954 | 2.8112 | 8.725% | 9.283% | 6.273% | 1.0956 | 1.1023 | 1.0669
2011-03-16 | 36 | 21.9023 | 11.4243 | 33.3266 | 1.932 | 0.76558 | 0.24775 | 2.9454 | 8.838% | 9.404% | 6.354% | 1.0969 | 1.1038 | 1.0679
2011-03-16 | 37 | 22.7177 | 11.6034 | 34.3211 | 2.0491 | 0.76558 | 0.25515 | 3.0698 | 8.944% | 9.517% | 6.431% | 1.0982 | 1.1052 | 1.0687
2011-03-16 | 38 | 23.0046 | 11.5043 | 34.509 | 2.0716 | 0.76558 | 0.25654 | 3.0937 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2011-03-16 | 39 | 23.2473 | 11.3726 | 34.6199 | 2.0849 | 0.76558 | 0.25737 | 3.1078 | 8.977% | 9.552% | 6.455% | 1.0986 | 1.1056 | 1.069
2011-03-16 | 40 | 23.0403 | 11.4231 | 34.4635 | 2.0661 | 0.76558 | 0.25621 | 3.0879 | 8.96% | 9.533% | 6.442% | 1.0984 | 1.1054 | 1.0689
2011-03-16 | 41 | 23.7346 | 11.7169 | 35.4516 | 2.1863 | 0.76558 | 0.26355 | 3.2154 | 9.07% | 9.65% | 6.521% | 1.0997 | 1.1068 | 1.0698
2011-03-16 | 42 | 24.8196 | 11.4985 | 36.3181 | 2.2945 | 0.76558 | 0.26999 | 3.33 | 9.169% | 9.756% | 6.593% | 1.1009 | 1.1081 | 1.0706
2011-03-16 | 43 | 24.1685 | 10.9445 | 35.113 | 2.1447 | 0.76558 | 0.26103 | 3.1713 | 9.032% | 9.61% | 6.494% | 1.0993 | 1.1063 | 1.0694
2011-03-16 | 44 | 23.2946 | 10.1544 | 33.4489 | 1.9463 | 0.76558 | 0.24866 | 2.9605 | 8.851% | 9.417% | 6.364% | 1.0971 | 1.104 | 1.068
2011-03-16 | 45 | 21.7695 | 9.2845 | 31.054 | 1.6775 | 0.76558 | 0.23086 | 2.674 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-03-16 | 46 | 20.1739 | 8.4539 | 28.6278 | 1.4256 | 0.76558 | 0.21282 | 2.404 | 8.398% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2011-03-16 | 47 | 18.2282 | 8.0234 | 26.2517 | 1.1988 | 0.76558 | 0.19516 | 2.1595 | 8.226% | 8.753% | 5.915% | 1.0896 | 1.0959 | 1.0629
2011-03-16 | 48 | 16.8248 | 8.183 | 25.0078 | 1.0879 | 0.76558 | 0.18591 | 2.0394 | 8.155% | 8.677% | 5.863% | 1.0888 | 1.095 | 1.0623
2011-03-17 | 1 | 15.1884 | 7.4904 | 22.6787 | 0.89469 | 0.76558 | 0.1686 | 1.8289 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-03-17 | 2 | 14.336 | 6.978 | 21.314 | 0.79025 | 0.76558 | 0.15845 | 1.7143 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-17 | 3 | 13.5384 | 6.7763 | 20.3147 | 0.71789 | 0.76558 | 0.15102 | 1.6345 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-17 | 4 | 13.194 | 6.6306 | 19.8245 | 0.68366 | 0.76558 | 0.14738 | 1.5966 | 8.054% | 8.569% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-17 | 5 | 12.4474 | 6.5632 | 19.0106 | 0.62868 | 0.76558 | 0.14133 | 1.5356 | 8.077% | 8.594% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-03-17 | 6 | 12.1262 | 6.3583 | 18.4845 | 0.59436 | 0.76558 | 0.13742 | 1.4974 | 8.101% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-17 | 7 | 12.2025 | 6.3879 | 18.5904 | 0.60119 | 0.76558 | 0.1382 | 1.505 | 8.095% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-17 | 8 | 12.3674 | 6.301 | 18.6684 | 0.60625 | 0.76558 | 0.13878 | 1.5106 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-17 | 9 | 12.6018 | 6.2491 | 18.8509 | 0.61815 | 0.76558 | 0.14014 | 1.5239 | 8.084% | 8.601% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-03-17 | 10 | 13.0409 | 6.4137 | 19.4545 | 0.65838 | 0.76558 | 0.14463 | 1.5686 | 8.063% | 8.579% | 5.797% | 1.0877 | 1.0938 | 1.0615
2011-03-17 | 11 | 13.0637 | 6.4768 | 19.5406 | 0.66422 | 0.76558 | 0.14527 | 1.5751 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-17 | 12 | 13.6082 | 6.9315 | 20.5396 | 0.73387 | 0.76558 | 0.15269 | 1.6521 | 8.044% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-17 | 13 | 15.2902 | 7.6185 | 22.9087 | 0.91292 | 0.76558 | 0.17031 | 1.8488 | 8.07% | 8.587% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-17 | 14 | 17.9512 | 8.9211 | 26.8723 | 1.2562 | 0.76558 | 0.19977 | 2.2215 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2011-03-17 | 15 | 21.9337 | 10.8635 | 32.7972 | 1.8711 | 0.76558 | 0.24382 | 2.8805 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2011-03-17 | 16 | 23.2616 | 11.1594 | 34.421 | 2.061 | 0.76558 | 0.25589 | 3.0825 | 8.955% | 9.528% | 6.439% | 1.0984 | 1.1053 | 1.0688
2011-03-17 | 17 | 22.9387 | 10.7612 | 33.6999 | 1.9756 | 0.76558 | 0.25053 | 2.9917 | 8.877% | 9.446% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-03-17 | 18 | 27.1645 | 13.0265 | 40.1911 | 2.8099 | 0.76558 | 0.29879 | 3.8743 | 9.64% | 10.26% | 6.931% | 1.1067 | 1.1143 | 1.0745
2011-03-17 | 19 | 28.0814 | 13.3286 | 41.41 | 2.9829 | 0.76558 | 0.30785 | 4.0564 | 9.796% | 10.42% | 7.043% | 1.1086 | 1.1164 | 1.0758
2011-03-17 | 20 | 26.2714 | 12.1992 | 38.4705 | 2.5745 | 0.76558 | 0.28599 | 3.6261 | 9.426% | 10.03% | 6.777% | 1.1041 | 1.1115 | 1.0727
2011-03-17 | 21 | 24.652 | 11.1662 | 35.8182 | 2.2317 | 0.76558 | 0.26628 | 3.2636 | 9.112% | 9.695% | 6.551% | 1.1002 | 1.1074 | 1.0701
2011-03-17 | 22 | 25.1146 | 11.7989 | 36.9134 | 2.3703 | 0.76558 | 0.27442 | 3.4103 | 9.239% | 9.83% | 6.643% | 1.1018 | 1.109 | 1.0712
2011-03-17 | 23 | 23.5375 | 11.1163 | 34.6538 | 2.089 | 0.76558 | 0.25762 | 3.1122 | 8.981% | 9.556% | 6.457% | 1.0987 | 1.1057 | 1.069
2011-03-17 | 24 | 22.8995 | 11.0702 | 33.9697 | 2.0073 | 0.76558 | 0.25253 | 3.0254 | 8.906% | 9.476% | 6.404% | 1.0978 | 1.1047 | 1.0684
2011-03-17 | 25 | 22.3886 | 10.9603 | 33.3489 | 1.9346 | 0.76558 | 0.24792 | 2.9481 | 8.84% | 9.406% | 6.356% | 1.097 | 1.1038 | 1.0679
2011-03-17 | 26 | 21.5194 | 10.4225 | 31.9419 | 1.7748 | 0.76558 | 0.23746 | 2.7779 | 8.697% | 9.253% | 6.253% | 1.0952 | 1.102 | 1.0667
2011-03-17 | 27 | 21.1796 | 10.4933 | 31.6729 | 1.7451 | 0.76558 | 0.23546 | 2.7461 | 8.67% | 9.225% | 6.234% | 1.0949 | 1.1016 | 1.0665
2011-03-17 | 28 | 21.1071 | 10.4713 | 31.5784 | 1.7347 | 0.76558 | 0.23476 | 2.735 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-17 | 29 | 20.8021 | 10.3076 | 31.1097 | 1.6835 | 0.76558 | 0.23127 | 2.6804 | 8.616% | 9.167% | 6.195% | 1.0943 | 1.1009 | 1.066
2011-03-17 | 30 | 20.4411 | 10.0918 | 30.5329 | 1.6217 | 0.76558 | 0.22699 | 2.6143 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-03-17 | 31 | 20.2945 | 9.9498 | 30.2443 | 1.5912 | 0.76558 | 0.22484 | 2.5816 | 8.536% | 9.082% | 6.137% | 1.0933 | 1.0999 | 1.0654
2011-03-17 | 32 | 20.1977 | 9.9718 | 30.1694 | 1.5833 | 0.76558 | 0.22428 | 2.5732 | 8.529% | 9.075% | 6.132% | 1.0932 | 1.0998 | 1.0653
2011-03-17 | 33 | 20.3086 | 10.1625 | 30.4711 | 1.6151 | 0.76558 | 0.22653 | 2.6072 | 8.556% | 9.104% | 6.152% | 1.0936 | 1.1002 | 1.0656
2011-03-17 | 34 | 20.6395 | 10.1298 | 30.7693 | 1.6469 | 0.76558 | 0.22874 | 2.6412 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-03-17 | 35 | 20.6012 | 10.4173 | 31.0185 | 1.6737 | 0.76558 | 0.2306 | 2.6699 | 8.607% | 9.158% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-03-17 | 36 | 21.1942 | 10.9884 | 32.1827 | 1.8017 | 0.76558 | 0.23925 | 2.8065 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-03-17 | 37 | 22.4442 | 11.2359 | 33.6801 | 1.9732 | 0.76558 | 0.25038 | 2.9892 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-03-17 | 38 | 23.4002 | 11.1608 | 34.561 | 2.0778 | 0.76558 | 0.25693 | 3.1003 | 8.971% | 9.545% | 6.45% | 1.0985 | 1.1055 | 1.0689
2011-03-17 | 39 | 23.8613 | 10.8862 | 34.7475 | 2.1003 | 0.76558 | 0.25832 | 3.1242 | 8.991% | 9.567% | 6.465% | 1.0988 | 1.1058 | 1.0691
2011-03-17 | 40 | 24.1122 | 10.9728 | 35.085 | 2.1413 | 0.76558 | 0.26083 | 3.1677 | 9.029% | 9.606% | 6.492% | 1.0992 | 1.1063 | 1.0694
2011-03-17 | 41 | 25.1915 | 11.4979 | 36.6894 | 2.3416 | 0.76558 | 0.27275 | 3.38 | 9.212% | 9.802% | 6.624% | 1.1015 | 1.1087 | 1.0709
2011-03-17 | 42 | 25.7897 | 11.7845 | 37.5742 | 2.4559 | 0.76558 | 0.27933 | 3.5008 | 9.317% | 9.913% | 6.699% | 1.1027 | 1.11 | 1.0718
2011-03-17 | 43 | 25.1235 | 11.272 | 36.3955 | 2.3043 | 0.76558 | 0.27057 | 3.3404 | 9.178% | 9.765% | 6.599% | 1.1011 | 1.1082 | 1.0707
2011-03-17 | 44 | 24.6341 | 10.7134 | 35.3475 | 2.1735 | 0.76558 | 0.26278 | 3.2018 | 9.058% | 9.638% | 6.513% | 1.0996 | 1.1067 | 1.0697
2011-03-17 | 45 | 22.9084 | 9.8035 | 32.7119 | 1.8614 | 0.76558 | 0.24318 | 2.8702 | 8.774% | 9.336% | 6.309% | 1.0962 | 1.103 | 1.0673
2011-03-17 | 46 | 21.0422 | 8.8957 | 29.9379 | 1.5591 | 0.76558 | 0.22256 | 2.5473 | 8.508% | 9.053% | 6.118% | 1.093 | 1.0995 | 1.0652
2011-03-17 | 47 | 19.2301 | 8.4572 | 27.6873 | 1.3335 | 0.76558 | 0.20583 | 2.3049 | 8.325% | 8.858% | 5.986% | 1.0908 | 1.0972 | 1.0637
2011-03-17 | 48 | 17.8403 | 8.5509 | 26.3912 | 1.2116 | 0.76558 | 0.1962 | 2.1734 | 8.235% | 8.762% | 5.921% | 1.0897 | 1.096 | 1.0629
2011-03-18 | 1 | 16.2829 | 7.7802 | 24.063 | 1.0072 | 0.76558 | 0.17889 | 1.9517 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-18 | 2 | 15.185 | 7.2968 | 22.4818 | 0.87922 | 0.76558 | 0.16713 | 1.8119 | 8.06% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-18 | 3 | 14.7309 | 6.8902 | 21.6211 | 0.81318 | 0.76558 | 0.16073 | 1.7395 | 8.045% | 8.56% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 4 | 14.2971 | 6.7654 | 21.0625 | 0.77171 | 0.76558 | 0.15658 | 1.6939 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 5 | 13.8413 | 6.7278 | 20.5691 | 0.73598 | 0.76558 | 0.15291 | 1.6545 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 6 | 13.2455 | 6.7363 | 19.9817 | 0.69455 | 0.76558 | 0.14855 | 1.6087 | 8.051% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-03-18 | 7 | 13.1974 | 6.6829 | 19.8803 | 0.68751 | 0.76558 | 0.14779 | 1.6009 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-18 | 8 | 13.0334 | 6.6327 | 19.6662 | 0.67278 | 0.76558 | 0.1462 | 1.5846 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-18 | 9 | 13.523 | 6.6027 | 20.1257 | 0.70459 | 0.76558 | 0.14962 | 1.6198 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-18 | 10 | 13.7577 | 6.7223 | 20.48 | 0.72961 | 0.76558 | 0.15225 | 1.6474 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 11 | 14.0678 | 6.9282 | 20.996 | 0.76685 | 0.76558 | 0.15609 | 1.6885 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 12 | 14.3456 | 7.246 | 21.5916 | 0.81097 | 0.76558 | 0.16051 | 1.7371 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-18 | 13 | 15.7676 | 8.0338 | 23.8014 | 0.98546 | 0.76558 | 0.17694 | 1.928 | 8.1% | 8.619% | 5.824% | 1.0881 | 1.0943 | 1.0618
2011-03-18 | 14 | 18.215 | 9.1497 | 27.3647 | 1.3026 | 0.76558 | 0.20343 | 2.2716 | 8.301% | 8.833% | 5.969% | 1.0905 | 1.0969 | 1.0635
2011-03-18 | 15 | 22.3039 | 11.16 | 33.4639 | 1.948 | 0.76558 | 0.24877 | 2.9624 | 8.852% | 9.419% | 6.365% | 1.0971 | 1.104 | 1.068
2011-03-18 | 16 | 23.3352 | 11.5442 | 34.8795 | 2.1163 | 0.76558 | 0.2593 | 3.1412 | 9.006% | 9.582% | 6.475% | 1.099 | 1.106 | 1.0692
2011-03-18 | 17 | 24.4964 | 11.9199 | 36.4163 | 2.3069 | 0.76558 | 0.27072 | 3.3432 | 9.18% | 9.768% | 6.601% | 1.1011 | 1.1083 | 1.0707
2011-03-18 | 18 | 26.8863 | 12.6519 | 39.5382 | 2.7194 | 0.76558 | 0.29393 | 3.7789 | 9.558% | 10.17% | 6.872% | 1.1057 | 1.1132 | 1.0738
2011-03-18 | 19 | 26.1867 | 12.9837 | 39.1704 | 2.669 | 0.76558 | 0.2912 | 3.7258 | 9.512% | 10.12% | 6.839% | 1.1051 | 1.1126 | 1.0734
2011-03-18 | 20 | 27.1696 | 13.204 | 40.3736 | 2.8355 | 0.76558 | 0.30014 | 3.9012 | 9.663% | 10.28% | 6.948% | 1.107 | 1.1146 | 1.0747
2011-03-18 | 21 | 25.9926 | 12.4317 | 38.4243 | 2.5683 | 0.76558 | 0.28565 | 3.6195 | 9.42% | 10.02% | 6.773% | 1.104 | 1.1114 | 1.0726
2011-03-18 | 22 | 26.1385 | 12.8315 | 38.97 | 2.6418 | 0.76558 | 0.28971 | 3.6971 | 9.487% | 10.09% | 6.821% | 1.1048 | 1.1123 | 1.0732
2011-03-18 | 23 | 27.0945 | 12.8317 | 39.9262 | 2.773 | 0.76558 | 0.29682 | 3.8354 | 9.606% | 10.22% | 6.907% | 1.1063 | 1.1138 | 1.0742
2011-03-18 | 24 | 24.6985 | 11.9486 | 36.647 | 2.3362 | 0.76558 | 0.27244 | 3.3742 | 9.207% | 9.797% | 6.62% | 1.1014 | 1.1086 | 1.0709
2011-03-18 | 25 | 24.822 | 12.2342 | 37.0563 | 2.3887 | 0.76558 | 0.27548 | 3.4297 | 9.255% | 9.848% | 6.655% | 1.102 | 1.1092 | 1.0713
2011-03-18 | 26 | 23.9797 | 11.4038 | 35.3835 | 2.1779 | 0.76558 | 0.26305 | 3.2065 | 9.062% | 9.642% | 6.516% | 1.0997 | 1.1067 | 1.0697
2011-03-18 | 27 | 22.8876 | 11.2231 | 34.1107 | 2.024 | 0.76558 | 0.25358 | 3.0432 | 8.922% | 9.492% | 6.415% | 1.098 | 1.1049 | 1.0685
2011-03-18 | 28 | 22.6994 | 10.5286 | 33.228 | 1.9206 | 0.76558 | 0.24702 | 2.9332 | 8.828% | 9.393% | 6.347% | 1.0968 | 1.1037 | 1.0678
2011-03-18 | 29 | 21.9785 | 10.1439 | 32.1224 | 1.7949 | 0.76558 | 0.2388 | 2.7993 | 8.715% | 9.272% | 6.266% | 1.0955 | 1.1022 | 1.0668
2011-03-18 | 30 | 21.5463 | 10.0314 | 31.5777 | 1.7346 | 0.76558 | 0.23475 | 2.7349 | 8.661% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-18 | 31 | 21.4587 | 9.835 | 31.2937 | 1.7035 | 0.76558 | 0.23264 | 2.7017 | 8.634% | 9.186% | 6.207% | 1.0945 | 1.1012 | 1.0662
2011-03-18 | 32 | 21.0747 | 9.9923 | 31.067 | 1.6789 | 0.76558 | 0.23096 | 2.6755 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-03-18 | 33 | 21.4478 | 10.3995 | 31.8473 | 1.7643 | 0.76558 | 0.23676 | 2.7667 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-03-18 | 34 | 21.9755 | 10.7913 | 32.7668 | 1.8677 | 0.76558 | 0.24359 | 2.8769 | 8.78% | 9.342% | 6.313% | 1.0962 | 1.103 | 1.0674
2011-03-18 | 35 | 22.0713 | 10.9984 | 33.0697 | 1.9024 | 0.76558 | 0.24584 | 2.9138 | 8.811% | 9.375% | 6.335% | 1.0966 | 1.1034 | 1.0676
2011-03-18 | 36 | 22.595 | 11.2675 | 33.8625 | 1.9947 | 0.76558 | 0.25174 | 3.012 | 8.895% | 9.464% | 6.395% | 1.0976 | 1.1045 | 1.0683
2011-03-18 | 37 | 23.2997 | 11.5423 | 34.842 | 2.1117 | 0.76558 | 0.25902 | 3.1363 | 9.002% | 9.578% | 6.472% | 1.0989 | 1.1059 | 1.0692
2011-03-18 | 38 | 23.5901 | 11.4084 | 34.9985 | 2.1308 | 0.76558 | 0.26018 | 3.1565 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1061 | 1.0693
2011-03-18 | 39 | 23.7467 | 11.4169 | 35.1636 | 2.1509 | 0.76558 | 0.26141 | 3.1779 | 9.037% | 9.616% | 6.498% | 1.0994 | 1.1064 | 1.0695
2011-03-18 | 40 | 24.0653 | 11.18 | 35.2453 | 2.1609 | 0.76558 | 0.26202 | 3.1885 | 9.047% | 9.626% | 6.505% | 1.0995 | 1.1065 | 1.0696
2011-03-18 | 41 | 25.0012 | 11.7523 | 36.7535 | 2.3498 | 0.76558 | 0.27323 | 3.3886 | 9.22% | 9.81% | 6.629% | 1.1016 | 1.1088 | 1.071
2011-03-18 | 42 | 25.5089 | 12.2593 | 37.7682 | 2.4813 | 0.76558 | 0.28077 | 3.5277 | 9.34% | 9.938% | 6.716% | 1.103 | 1.1103 | 1.072
2011-03-18 | 43 | 24.682 | 11.7701 | 36.4521 | 2.3114 | 0.76558 | 0.27099 | 3.348 | 9.185% | 9.772% | 6.604% | 1.1011 | 1.1083 | 1.0707
2011-03-18 | 44 | 23.5848 | 11.0814 | 34.6662 | 2.0905 | 0.76558 | 0.25771 | 3.1138 | 8.982% | 9.557% | 6.458% | 1.0987 | 1.1057 | 1.069
2011-03-18 | 45 | 22.0131 | 10.1011 | 32.1142 | 1.794 | 0.76558 | 0.23874 | 2.7983 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2011-03-18 | 46 | 19.9708 | 9.2285 | 29.1993 | 1.4831 | 0.76558 | 0.21707 | 2.4658 | 8.445% | 8.985% | 6.072% | 1.0922 | 1.0987 | 1.0646
2011-03-18 | 47 | 18.2166 | 8.6625 | 26.879 | 1.2568 | 0.76558 | 0.19982 | 2.2222 | 8.267% | 8.796% | 5.944% | 1.0901 | 1.0964 | 1.0632
2011-03-18 | 48 | 17.1758 | 8.5028 | 25.6786 | 1.147 | 0.76558 | 0.1909 | 2.1035 | 8.192% | 8.716% | 5.89% | 1.0892 | 1.0955 | 1.0626
2011-03-19 | 1 | 15.6953 | 7.678 | 23.3733 | 0.95033 | 0.76558 | 0.17376 | 1.8897 | 8.085% | 8.602% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-03-19 | 2 | 14.5509 | 7.0359 | 21.5868 | 0.81061 | 0.76558 | 0.16048 | 1.7367 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-19 | 3 | 13.9236 | 6.5683 | 20.4919 | 0.73046 | 0.76558 | 0.15234 | 1.6484 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-19 | 4 | 13.293 | 6.2621 | 19.5551 | 0.66521 | 0.76558 | 0.14538 | 1.5762 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-19 | 5 | 12.9582 | 6.2739 | 19.2321 | 0.64341 | 0.76558 | 0.14297 | 1.552 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-03-19 | 6 | 12.8861 | 6.2949 | 19.181 | 0.64 | 0.76558 | 0.14259 | 1.5482 | 8.071% | 8.588% | 5.803% | 1.0878 | 1.0939 | 1.0616
2011-03-19 | 7 | 12.6303 | 6.269 | 18.8993 | 0.62133 | 0.76558 | 0.1405 | 1.5274 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-03-19 | 8 | 12.3987 | 6.421 | 18.8198 | 0.61612 | 0.76558 | 0.13991 | 1.5216 | 8.085% | 8.603% | 5.813% | 1.088 | 1.0941 | 1.0617
2011-03-19 | 9 | 12.5534 | 6.4126 | 18.9659 | 0.62572 | 0.76558 | 0.14099 | 1.5323 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-03-19 | 10 | 12.6387 | 6.3221 | 18.9608 | 0.62538 | 0.76558 | 0.14096 | 1.5319 | 8.079% | 8.596% | 5.809% | 1.0879 | 1.094 | 1.0617
2011-03-19 | 11 | 13.3421 | 6.5171 | 19.8591 | 0.68605 | 0.76558 | 0.14764 | 1.5993 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-19 | 12 | 14.0995 | 7.035 | 21.1345 | 0.77699 | 0.76558 | 0.15712 | 1.6997 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-19 | 13 | 15.6461 | 7.6793 | 23.3254 | 0.94644 | 0.76558 | 0.1734 | 1.8854 | 8.083% | 8.6% | 5.812% | 1.0879 | 1.0941 | 1.0617
2011-03-19 | 14 | 17.8713 | 8.9277 | 26.799 | 1.2493 | 0.76558 | 0.19923 | 2.2141 | 8.262% | 8.791% | 5.94% | 1.0901 | 1.0964 | 1.0632
2011-03-19 | 15 | 21.3154 | 10.9381 | 32.2535 | 1.8096 | 0.76558 | 0.23978 | 2.815 | 8.728% | 9.286% | 6.275% | 1.0956 | 1.1024 | 1.067
2011-03-19 | 16 | 24.6946 | 12.3467 | 37.0413 | 2.3867 | 0.76558 | 0.27537 | 3.4277 | 9.254% | 9.846% | 6.653% | 1.102 | 1.1092 | 1.0713
2011-03-19 | 17 | 26.1389 | 12.6695 | 38.8083 | 2.6199 | 0.76558 | 0.28851 | 3.674 | 9.467% | 10.07% | 6.807% | 1.1046 | 1.112 | 1.073
2011-03-19 | 18 | 26.4814 | 12.5578 | 39.0392 | 2.6512 | 0.76558 | 0.29022 | 3.707 | 9.495% | 10.1% | 6.827% | 1.1049 | 1.1124 | 1.0733
2011-03-19 | 19 | 25.456 | 12.3115 | 37.7675 | 2.4813 | 0.76558 | 0.28077 | 3.5276 | 9.34% | 9.938% | 6.716% | 1.103 | 1.1103 | 1.072
2011-03-19 | 20 | 24.5303 | 12.0329 | 36.5632 | 2.3255 | 0.76558 | 0.27182 | 3.3629 | 9.198% | 9.786% | 6.613% | 1.1013 | 1.1085 | 1.0708
2011-03-19 | 21 | 24.049 | 11.6179 | 35.667 | 2.2129 | 0.76558 | 0.26515 | 3.2437 | 9.094% | 9.676% | 6.539% | 1.1 | 1.1071 | 1.07
2011-03-19 | 22 | 23.2351 | 11.3821 | 34.6172 | 2.0846 | 0.76558 | 0.25735 | 3.1075 | 8.977% | 9.551% | 6.454% | 1.0986 | 1.1056 | 1.069
2011-03-19 | 23 | 22.0351 | 11.1773 | 33.2123 | 1.9188 | 0.76558 | 0.2469 | 2.9313 | 8.826% | 9.391% | 6.346% | 1.0968 | 1.1036 | 1.0678
2011-03-19 | 24 | 21.4293 | 10.727 | 32.1563 | 1.7987 | 0.76558 | 0.23905 | 2.8034 | 8.718% | 9.276% | 6.268% | 1.0955 | 1.1022 | 1.0669
2011-03-19 | 25 | 21.4443 | 10.4539 | 31.8982 | 1.77 | 0.76558 | 0.23714 | 2.7727 | 8.692% | 9.249% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-03-19 | 26 | 20.8771 | 9.8283 | 30.7055 | 1.6401 | 0.76558 | 0.22827 | 2.6339 | 8.578% | 9.127% | 6.168% | 1.0938 | 1.1004 | 1.0657
2011-03-19 | 27 | 20.4837 | 10.2049 | 30.6886 | 1.6383 | 0.76558 | 0.22814 | 2.632 | 8.576% | 9.125% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-03-19 | 28 | 20.288 | 10.2638 | 30.5518 | 1.6237 | 0.76558 | 0.22713 | 2.6164 | 8.564% | 9.112% | 6.157% | 1.0937 | 1.1003 | 1.0656
2011-03-19 | 29 | 20.0445 | 9.9554 | 30 | 1.5656 | 0.76558 | 0.22302 | 2.5542 | 8.514% | 9.059% | 6.122% | 1.0931 | 1.0996 | 1.0652
2011-03-19 | 30 | 19.6588 | 9.7651 | 29.4239 | 1.506 | 0.76558 | 0.21874 | 2.4904 | 8.464% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2011-03-19 | 31 | 20.1325 | 9.7361 | 29.8687 | 1.5519 | 0.76558 | 0.22205 | 2.5395 | 8.502% | 9.046% | 6.113% | 1.0929 | 1.0995 | 1.0651
2011-03-19 | 32 | 20.1403 | 10.1205 | 30.2608 | 1.5929 | 0.76558 | 0.22496 | 2.5835 | 8.537% | 9.084% | 6.138% | 1.0933 | 1.0999 | 1.0654
2011-03-19 | 33 | 20.2335 | 10.3034 | 30.537 | 1.6221 | 0.76558 | 0.22702 | 2.6147 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-03-19 | 34 | 20.1667 | 10.4037 | 30.5704 | 1.6257 | 0.76558 | 0.22726 | 2.6185 | 8.566% | 9.114% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-03-19 | 35 | 20.45 | 10.6204 | 31.0704 | 1.6793 | 0.76558 | 0.23098 | 2.6759 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-03-19 | 36 | 20.7943 | 10.8717 | 31.666 | 1.7443 | 0.76558 | 0.23541 | 2.7453 | 8.67% | 9.224% | 6.233% | 1.0949 | 1.1016 | 1.0665
2011-03-19 | 37 | 21.3431 | 10.9208 | 32.2639 | 1.8108 | 0.76558 | 0.23985 | 2.8162 | 8.729% | 9.287% | 6.276% | 1.0956 | 1.1024 | 1.067
2011-03-19 | 38 | 21.4897 | 10.9861 | 32.4759 | 1.8347 | 0.76558 | 0.24143 | 2.8417 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-03-19 | 39 | 21.9172 | 10.9658 | 32.883 | 1.881 | 0.76558 | 0.24446 | 2.891 | 8.792% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-03-19 | 40 | 21.9832 | 10.6154 | 32.5986 | 1.8486 | 0.76558 | 0.24234 | 2.8565 | 8.763% | 9.323% | 6.3% | 1.096 | 1.1028 | 1.0672
2011-03-19 | 41 | 23.0718 | 11.1107 | 34.1825 | 2.0326 | 0.76558 | 0.25412 | 3.0523 | 8.929% | 9.501% | 6.42% | 1.098 | 1.105 | 1.0686
2011-03-19 | 42 | 23.3659 | 11.2059 | 34.5718 | 2.0791 | 0.76558 | 0.25701 | 3.1017 | 8.972% | 9.546% | 6.451% | 1.0986 | 1.1055 | 1.069
2011-03-19 | 43 | 22.6927 | 10.7248 | 33.4175 | 1.9426 | 0.76558 | 0.24843 | 2.9566 | 8.847% | 9.414% | 6.361% | 1.0971 | 1.1039 | 1.0679
2011-03-19 | 44 | 21.7828 | 10.0146 | 31.7973 | 1.7588 | 0.76558 | 0.23639 | 2.7608 | 8.682% | 9.238% | 6.243% | 1.0951 | 1.1018 | 1.0666
2011-03-19 | 45 | 20.5941 | 9.2876 | 29.8818 | 1.5533 | 0.76558 | 0.22214 | 2.541 | 8.503% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-03-19 | 46 | 19.1755 | 8.6177 | 27.7933 | 1.3437 | 0.76558 | 0.20662 | 2.3159 | 8.333% | 8.866% | 5.991% | 1.0909 | 1.0973 | 1.0637
2011-03-19 | 47 | 17.6698 | 8.2744 | 25.9442 | 1.1709 | 0.76558 | 0.19287 | 2.1293 | 8.207% | 8.733% | 5.901% | 1.0894 | 1.0957 | 1.0627
2011-03-19 | 48 | 16.8748 | 8.4012 | 25.276 | 1.1114 | 0.76558 | 0.18791 | 2.0648 | 8.169% | 8.692% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-03-20 | 1 | 15.3646 | 7.4348 | 22.7993 | 0.90423 | 0.76558 | 0.16949 | 1.8393 | 8.067% | 8.584% | 5.8% | 1.0878 | 1.0939 | 1.0616
2011-03-20 | 2 | 14.1647 | 6.8726 | 21.0373 | 0.76987 | 0.76558 | 0.15639 | 1.6918 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-20 | 3 | 13.1726 | 6.6018 | 19.7744 | 0.68021 | 0.76558 | 0.14701 | 1.5928 | 8.055% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-20 | 4 | 12.4626 | 6.4887 | 18.9513 | 0.62476 | 0.76558 | 0.14089 | 1.5312 | 8.08% | 8.597% | 5.809% | 1.0879 | 1.0941 | 1.0617
2011-03-20 | 5 | 12.4052 | 6.3243 | 18.7295 | 0.61022 | 0.76558 | 0.13924 | 1.515 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2011-03-20 | 6 | 12.0722 | 6.1285 | 18.2007 | 0.57625 | 0.76558 | 0.13531 | 1.4771 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-20 | 7 | 11.841 | 6.1202 | 17.9612 | 0.56119 | 0.76558 | 0.13353 | 1.4603 | 8.13% | 8.651% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-03-20 | 8 | 11.751 | 6.2691 | 18.0201 | 0.56487 | 0.76558 | 0.13396 | 1.4644 | 8.127% | 8.647% | 5.843% | 1.0885 | 1.0947 | 1.0621
2011-03-20 | 9 | 11.5669 | 6.2279 | 17.7949 | 0.55084 | 0.76558 | 0.13229 | 1.4487 | 8.141% | 8.662% | 5.853% | 1.0886 | 1.0948 | 1.0622
2011-03-20 | 10 | 11.8159 | 6.4226 | 18.2385 | 0.57865 | 0.76558 | 0.13559 | 1.4798 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-20 | 11 | 12.0903 | 6.4863 | 18.5767 | 0.6003 | 0.76558 | 0.1381 | 1.504 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-20 | 12 | 12.4619 | 6.6987 | 19.1605 | 0.63863 | 0.76558 | 0.14244 | 1.5467 | 8.072% | 8.589% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-03-20 | 13 | 13.4136 | 7.0833 | 20.4969 | 0.73082 | 0.76558 | 0.15238 | 1.6488 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-20 | 14 | 14.2115 | 7.5623 | 21.7738 | 0.82472 | 0.76558 | 0.16187 | 1.7522 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-20 | 15 | 15.4644 | 8.1792 | 23.6436 | 0.97244 | 0.76558 | 0.17577 | 1.9138 | 8.094% | 8.612% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-03-20 | 16 | 16.803 | 8.6898 | 25.4928 | 1.1305 | 0.76558 | 0.18952 | 2.0856 | 8.181% | 8.705% | 5.882% | 1.0891 | 1.0953 | 1.0625
2011-03-20 | 17 | 18.947 | 9.3643 | 28.3113 | 1.3943 | 0.76558 | 0.21047 | 2.3703 | 8.372% | 8.908% | 6.02% | 1.0914 | 1.0978 | 1.0641
2011-03-20 | 18 | 21.2737 | 10.2074 | 31.4811 | 1.724 | 0.76558 | 0.23403 | 2.7236 | 8.652% | 9.205% | 6.22% | 1.0947 | 1.1014 | 1.0663
2011-03-20 | 19 | 22.7632 | 10.8436 | 33.6068 | 1.9647 | 0.76558 | 0.24984 | 2.9801 | 8.867% | 9.435% | 6.376% | 1.0973 | 1.1042 | 1.0681
2011-03-20 | 20 | 23.2866 | 11.2212 | 34.5079 | 2.0714 | 0.76558 | 0.25654 | 3.0935 | 8.965% | 9.539% | 6.446% | 1.0985 | 1.1054 | 1.0689
2011-03-20 | 21 | 23.6043 | 11.2318 | 34.8362 | 2.111 | 0.76558 | 0.25898 | 3.1356 | 9.001% | 9.577% | 6.472% | 1.0989 | 1.1059 | 1.0692
2011-03-20 | 22 | 23.1602 | 11.2005 | 34.3607 | 2.0538 | 0.76558 | 0.25544 | 3.0748 | 8.949% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-20 | 23 | 22.637 | 10.9905 | 33.6274 | 1.9671 | 0.76558 | 0.24999 | 2.9826 | 8.87% | 9.437% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-03-20 | 24 | 21.7115 | 10.981 | 32.6925 | 1.8592 | 0.76558 | 0.24304 | 2.8678 | 8.772% | 9.334% | 6.307% | 1.0962 | 1.1029 | 1.0673
2011-03-20 | 25 | 21.1425 | 10.9527 | 32.0951 | 1.7919 | 0.76558 | 0.2386 | 2.7961 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-03-20 | 26 | 20.9276 | 10.5047 | 31.4323 | 1.7187 | 0.76558 | 0.23367 | 2.7179 | 8.647% | 9.2% | 6.217% | 1.0947 | 1.1013 | 1.0663
2011-03-20 | 27 | 20.6413 | 10.413 | 31.0544 | 1.6776 | 0.76558 | 0.23086 | 2.674 | 8.611% | 9.162% | 6.191% | 1.0942 | 1.1009 | 1.066
2011-03-20 | 28 | 20.351 | 10.0737 | 30.4246 | 1.6102 | 0.76558 | 0.22618 | 2.602 | 8.552% | 9.1% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-03-20 | 29 | 19.6197 | 9.7332 | 29.3529 | 1.4988 | 0.76558 | 0.21821 | 2.4826 | 8.458% | 8.999% | 6.081% | 1.0924 | 1.0989 | 1.0647
2011-03-20 | 30 | 19.42 | 9.5277 | 28.9477 | 1.4577 | 0.76558 | 0.2152 | 2.4385 | 8.424% | 8.963% | 6.057% | 1.092 | 1.0985 | 1.0645
2011-03-20 | 31 | 19.1932 | 9.4726 | 28.6658 | 1.4294 | 0.76558 | 0.21311 | 2.4081 | 8.401% | 8.938% | 6.04% | 1.0917 | 1.0982 | 1.0643
2011-03-20 | 32 | 19.1898 | 9.4838 | 28.6736 | 1.4302 | 0.76558 | 0.21316 | 2.409 | 8.401% | 8.939% | 6.041% | 1.0917 | 1.0982 | 1.0643
2011-03-20 | 33 | 19.5785 | 9.732 | 29.3105 | 1.4945 | 0.76558 | 0.2179 | 2.4779 | 8.454% | 8.995% | 6.078% | 1.0923 | 1.0988 | 1.0647
2011-03-20 | 34 | 19.9252 | 9.8077 | 29.733 | 1.5378 | 0.76558 | 0.22104 | 2.5245 | 8.49% | 9.034% | 6.105% | 1.0928 | 1.0993 | 1.065
2011-03-20 | 35 | 20.3515 | 10.2566 | 30.6082 | 1.6297 | 0.76558 | 0.22754 | 2.6228 | 8.569% | 9.117% | 6.161% | 1.0937 | 1.1003 | 1.0657
2011-03-20 | 36 | 21.1858 | 10.8294 | 32.0152 | 1.783 | 0.76558 | 0.238 | 2.7866 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-20 | 37 | 21.7037 | 11.0612 | 32.7649 | 1.8675 | 0.76558 | 0.24358 | 2.8766 | 8.78% | 9.341% | 6.313% | 1.0962 | 1.103 | 1.0674
2011-03-20 | 38 | 21.6548 | 10.8273 | 32.4821 | 1.8354 | 0.76558 | 0.24148 | 2.8424 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-03-20 | 39 | 21.2935 | 10.5859 | 31.8794 | 1.7679 | 0.76558 | 0.237 | 2.7705 | 8.69% | 9.247% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-03-20 | 40 | 21.9388 | 10.3749 | 32.3137 | 1.8164 | 0.76558 | 0.24022 | 2.8222 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1024 | 1.067
2011-03-20 | 41 | 22.7942 | 10.5349 | 33.3291 | 1.9323 | 0.76558 | 0.24777 | 2.9457 | 8.838% | 9.404% | 6.355% | 1.097 | 1.1038 | 1.0679
2011-03-20 | 42 | 23.0718 | 10.328 | 33.3997 | 1.9405 | 0.76558 | 0.2483 | 2.9544 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-03-20 | 43 | 22.393 | 9.9047 | 32.2977 | 1.8146 | 0.76558 | 0.2401 | 2.8203 | 8.732% | 9.291% | 6.278% | 1.0957 | 1.1024 | 1.067
2011-03-20 | 44 | 21.5602 | 9.6443 | 31.2045 | 1.6938 | 0.76558 | 0.23198 | 2.6914 | 8.625% | 9.177% | 6.201% | 1.0944 | 1.101 | 1.0661
2011-03-20 | 45 | 20.1148 | 8.8127 | 28.9274 | 1.4556 | 0.76558 | 0.21505 | 2.4363 | 8.422% | 8.961% | 6.055% | 1.092 | 1.0984 | 1.0645
2011-03-20 | 46 | 18.2688 | 8.192 | 26.4607 | 1.218 | 0.76558 | 0.19671 | 2.1803 | 8.24% | 8.767% | 5.924% | 1.0898 | 1.0961 | 1.063
2011-03-20 | 47 | 17.0295 | 8.0015 | 25.031 | 1.0899 | 0.76558 | 0.18608 | 2.0416 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-03-20 | 48 | 16.1463 | 8.0643 | 24.2106 | 1.0196 | 0.76558 | 0.17998 | 1.9652 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-03-21 | 1 | 14.7634 | 7.3935 | 22.1569 | 0.85399 | 0.76558 | 0.16472 | 1.7843 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-21 | 2 | 13.5991 | 6.9343 | 20.5333 | 0.73342 | 0.76558 | 0.15265 | 1.6516 | 8.044% | 8.559% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-21 | 3 | 12.9338 | 6.6151 | 19.5489 | 0.66478 | 0.76558 | 0.14533 | 1.5757 | 8.06% | 8.576% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-21 | 4 | 12.1935 | 6.3886 | 18.5822 | 0.60066 | 0.76558 | 0.13814 | 1.5044 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-21 | 5 | 11.8248 | 6.2496 | 18.0744 | 0.56828 | 0.76558 | 0.13437 | 1.4682 | 8.123% | 8.643% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-03-21 | 6 | 11.5459 | 6.2304 | 17.7763 | 0.54969 | 0.76558 | 0.13215 | 1.4474 | 8.142% | 8.664% | 5.854% | 1.0886 | 1.0949 | 1.0622
2011-03-21 | 7 | 11.5378 | 6.2431 | 17.781 | 0.54998 | 0.76558 | 0.13219 | 1.4477 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-03-21 | 8 | 11.4605 | 6.2528 | 17.7133 | 0.5458 | 0.76558 | 0.13168 | 1.4431 | 8.147% | 8.668% | 5.858% | 1.0887 | 1.0949 | 1.0622
2011-03-21 | 9 | 11.4986 | 6.1575 | 17.6562 | 0.54228 | 0.76558 | 0.13126 | 1.4391 | 8.151% | 8.672% | 5.86% | 1.0887 | 1.095 | 1.0623
2011-03-21 | 10 | 11.6785 | 6.3706 | 18.049 | 0.56669 | 0.76558 | 0.13418 | 1.4664 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-21 | 11 | 11.5649 | 6.3822 | 17.947 | 0.5603 | 0.76558 | 0.13342 | 1.4593 | 8.131% | 8.652% | 5.846% | 1.0885 | 1.0947 | 1.0621
2011-03-21 | 12 | 11.6836 | 6.4895 | 18.1731 | 0.5745 | 0.76558 | 0.1351 | 1.4752 | 8.117% | 8.637% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-03-21 | 13 | 12.7203 | 6.6806 | 19.4009 | 0.65476 | 0.76558 | 0.14423 | 1.5646 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0616
2011-03-21 | 14 | 13.589 | 6.9237 | 20.5127 | 0.73195 | 0.76558 | 0.15249 | 1.65 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-21 | 15 | 15.1982 | 7.1688 | 22.367 | 0.87026 | 0.76558 | 0.16628 | 1.8021 | 8.057% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-21 | 16 | 16.3474 | 7.7918 | 24.1393 | 1.0136 | 0.76558 | 0.17945 | 1.9587 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-21 | 17 | 17.7683 | 8.7505 | 26.5188 | 1.2233 | 0.76558 | 0.19714 | 2.1861 | 8.243% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-03-21 | 18 | 19.058 | 9.1312 | 28.1892 | 1.3823 | 0.76558 | 0.20956 | 2.3574 | 8.363% | 8.898% | 6.013% | 1.0913 | 1.0977 | 1.064
2011-03-21 | 19 | 20.4644 | 9.514 | 29.9784 | 1.5633 | 0.76558 | 0.22286 | 2.5518 | 8.512% | 9.057% | 6.12% | 1.093 | 1.0996 | 1.0652
2011-03-21 | 20 | 21.6124 | 9.7354 | 31.3479 | 1.7094 | 0.76558 | 0.23304 | 2.708 | 8.639% | 9.192% | 6.211% | 1.0946 | 1.1012 | 1.0662
2011-03-21 | 21 | 22.3843 | 9.8056 | 32.1899 | 1.8025 | 0.76558 | 0.2393 | 2.8074 | 8.721% | 9.279% | 6.271% | 1.0955 | 1.1023 | 1.0669
2011-03-21 | 22 | 21.9871 | 10.1061 | 32.0933 | 1.7917 | 0.76558 | 0.23859 | 2.7959 | 8.712% | 9.269% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-03-21 | 23 | 21.3955 | 9.8391 | 31.2345 | 1.6971 | 0.76558 | 0.2322 | 2.6949 | 8.628% | 9.18% | 6.203% | 1.0944 | 1.1011 | 1.0661
2011-03-21 | 24 | 20.7618 | 9.6572 | 30.419 | 1.6096 | 0.76558 | 0.22614 | 2.6013 | 8.552% | 9.099% | 6.149% | 1.0935 | 1.1001 | 1.0655
2011-03-21 | 25 | 20.4789 | 9.7159 | 30.1948 | 1.586 | 0.76558 | 0.22447 | 2.576 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-03-21 | 26 | 20.2462 | 9.399 | 29.6452 | 1.5288 | 0.76558 | 0.22039 | 2.5147 | 8.483% | 9.026% | 6.099% | 1.0927 | 1.0992 | 1.065
2011-03-21 | 27 | 20.3511 | 9.7418 | 30.0929 | 1.5753 | 0.76558 | 0.22371 | 2.5646 | 8.522% | 9.068% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-03-21 | 28 | 20.1321 | 9.7161 | 29.8483 | 1.5498 | 0.76558 | 0.2219 | 2.5373 | 8.501% | 9.045% | 6.112% | 1.0929 | 1.0994 | 1.0651
2011-03-21 | 29 | 19.6259 | 9.319 | 28.9448 | 1.4574 | 0.76558 | 0.21518 | 2.4382 | 8.423% | 8.963% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-03-21 | 30 | 19.1 | 8.9122 | 28.0122 | 1.365 | 0.76558 | 0.20825 | 2.3388 | 8.349% | 8.884% | 6.003% | 1.0911 | 1.0975 | 1.0639
2011-03-21 | 31 | 18.833 | 8.8145 | 27.6475 | 1.3297 | 0.76558 | 0.20554 | 2.3008 | 8.322% | 8.854% | 5.983% | 1.0908 | 1.0971 | 1.0636
2011-03-21 | 32 | 18.8942 | 8.9055 | 27.7997 | 1.3444 | 0.76558 | 0.20667 | 2.3166 | 8.333% | 8.867% | 5.992% | 1.0909 | 1.0973 | 1.0637
2011-03-21 | 33 | 19.1443 | 9.0975 | 28.2418 | 1.3875 | 0.76558 | 0.20995 | 2.363 | 8.367% | 8.902% | 6.016% | 1.0913 | 1.0977 | 1.064
2011-03-21 | 34 | 19.4887 | 8.9913 | 28.48 | 1.411 | 0.76558 | 0.21172 | 2.3883 | 8.386% | 8.922% | 6.029% | 1.0915 | 1.098 | 1.0642
2011-03-21 | 35 | 19.6379 | 9.5281 | 29.166 | 1.4797 | 0.76558 | 0.21682 | 2.4621 | 8.442% | 8.982% | 6.07% | 1.0922 | 1.0987 | 1.0646
2011-03-21 | 36 | 20.6869 | 9.9542 | 30.6411 | 1.6332 | 0.76558 | 0.22779 | 2.6266 | 8.572% | 9.121% | 6.163% | 1.0938 | 1.1004 | 1.0657
2011-03-21 | 37 | 20.7615 | 10.3028 | 31.0643 | 1.6786 | 0.76558 | 0.23094 | 2.6752 | 8.612% | 9.163% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-03-21 | 38 | 21.1921 | 10.3421 | 31.5341 | 1.7298 | 0.76558 | 0.23443 | 2.7298 | 8.657% | 9.211% | 6.224% | 1.0948 | 1.1015 | 1.0664
2011-03-21 | 39 | 21.5792 | 10.1206 | 31.6998 | 1.748 | 0.76558 | 0.23566 | 2.7493 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-03-21 | 40 | 21.7757 | 10.0612 | 31.8369 | 1.7632 | 0.76558 | 0.23668 | 2.7654 | 8.686% | 9.242% | 6.245% | 1.0951 | 1.1018 | 1.0666
2011-03-21 | 41 | 22.9091 | 10.5738 | 33.4828 | 1.9502 | 0.76558 | 0.24892 | 2.9647 | 8.854% | 9.421% | 6.366% | 1.0971 | 1.104 | 1.068
2011-03-21 | 42 | 22.8424 | 10.4127 | 33.2551 | 1.9238 | 0.76558 | 0.24722 | 2.9366 | 8.83% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-03-21 | 43 | 21.9183 | 9.9199 | 31.8381 | 1.7633 | 0.76558 | 0.23669 | 2.7656 | 8.686% | 9.242% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-03-21 | 44 | 20.6806 | 9.4915 | 30.1721 | 1.5836 | 0.76558 | 0.2243 | 2.5735 | 8.529% | 9.075% | 6.133% | 1.0932 | 1.0998 | 1.0653
2011-03-21 | 45 | 18.8974 | 8.9783 | 27.8757 | 1.3517 | 0.76558 | 0.20723 | 2.3245 | 8.339% | 8.873% | 5.996% | 1.091 | 1.0974 | 1.0638
2011-03-21 | 46 | 17.4542 | 8.4554 | 25.9096 | 1.1678 | 0.76558 | 0.19261 | 2.126 | 8.205% | 8.73% | 5.9% | 1.0894 | 1.0957 | 1.0627
2011-03-21 | 47 | 16.5113 | 8.0935 | 24.6048 | 1.0531 | 0.76558 | 0.18292 | 2.0016 | 8.135% | 8.656% | 5.849% | 1.0886 | 1.0948 | 1.0621
2011-03-21 | 48 | 15.557 | 8.1341 | 23.6911 | 0.97635 | 0.76558 | 0.17612 | 1.918 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-22 | 1 | 14.3197 | 7.5166 | 21.8362 | 0.82945 | 0.76558 | 0.16233 | 1.7574 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-22 | 2 | 13.1602 | 7.1312 | 20.2914 | 0.71624 | 0.76558 | 0.15085 | 1.6327 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-22 | 3 | 12.3428 | 6.8269 | 19.1697 | 0.63924 | 0.76558 | 0.14251 | 1.5473 | 8.072% | 8.588% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-03-22 | 4 | 11.6654 | 6.5275 | 18.1929 | 0.57575 | 0.76558 | 0.13525 | 1.4766 | 8.116% | 8.636% | 5.836% | 1.0883 | 1.0945 | 1.062
2011-03-22 | 5 | 11.6391 | 6.338 | 17.9771 | 0.56218 | 0.76558 | 0.13364 | 1.4614 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-22 | 6 | 11.6468 | 6.2517 | 17.8984 | 0.55727 | 0.76558 | 0.13306 | 1.4559 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0947 | 1.0621
2011-03-22 | 7 | 11.4961 | 6.2336 | 17.7297 | 0.54681 | 0.76558 | 0.1318 | 1.4442 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2011-03-22 | 8 | 11.1199 | 6.3146 | 17.4346 | 0.52876 | 0.76558 | 0.12961 | 1.4239 | 8.167% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-03-22 | 9 | 10.9234 | 6.2963 | 17.2197 | 0.51581 | 0.76558 | 0.12801 | 1.4094 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2011-03-22 | 10 | 11.0041 | 6.2356 | 17.2398 | 0.51701 | 0.76558 | 0.12816 | 1.4107 | 8.183% | 8.707% | 5.884% | 1.0891 | 1.0954 | 1.0625
2011-03-22 | 11 | 11.4644 | 6.1319 | 17.5963 | 0.53861 | 0.76558 | 0.13081 | 1.435 | 8.155% | 8.677% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-03-22 | 12 | 11.9654 | 6.3086 | 18.274 | 0.5809 | 0.76558 | 0.13585 | 1.4823 | 8.112% | 8.631% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-22 | 13 | 13.1439 | 6.6609 | 19.8048 | 0.6823 | 0.76558 | 0.14723 | 1.5951 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-22 | 14 | 14.206 | 6.959 | 21.165 | 0.77924 | 0.76558 | 0.15734 | 1.7022 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-22 | 15 | 15.902 | 7.3959 | 23.2979 | 0.94421 | 0.76558 | 0.1732 | 1.883 | 8.082% | 8.599% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-03-22 | 16 | 17.816 | 8.0876 | 25.9036 | 1.1672 | 0.76558 | 0.19257 | 2.1254 | 8.205% | 8.73% | 5.899% | 1.0894 | 1.0957 | 1.0627
2011-03-22 | 17 | 19.636 | 8.6899 | 28.3259 | 1.3957 | 0.76558 | 0.21058 | 2.3719 | 8.374% | 8.909% | 6.021% | 1.0914 | 1.0978 | 1.0641
2011-03-22 | 18 | 21.762 | 9.3394 | 31.1014 | 1.6827 | 0.76558 | 0.23121 | 2.6794 | 8.615% | 9.167% | 6.194% | 1.0943 | 1.1009 | 1.066
2011-03-22 | 19 | 22.204 | 9.6193 | 31.8233 | 1.7617 | 0.76558 | 0.23658 | 2.7638 | 8.685% | 9.241% | 6.244% | 1.0951 | 1.1018 | 1.0666
2011-03-22 | 20 | 22.03 | 10.1436 | 32.1736 | 1.8007 | 0.76558 | 0.23918 | 2.8054 | 8.72% | 9.278% | 6.269% | 1.0955 | 1.1023 | 1.0669
2011-03-22 | 21 | 22.326 | 10.2469 | 32.5729 | 1.8456 | 0.76558 | 0.24215 | 2.8534 | 8.76% | 9.321% | 6.298% | 1.096 | 1.1028 | 1.0672
2011-03-22 | 22 | 21.892 | 10.5989 | 32.4909 | 1.8364 | 0.76558 | 0.24154 | 2.8435 | 8.752% | 9.312% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-03-22 | 23 | 21.036 | 10.4312 | 31.4672 | 1.7225 | 0.76558 | 0.23393 | 2.722 | 8.65% | 9.204% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-22 | 24 | 20.68 | 10.3449 | 31.0249 | 1.6744 | 0.76558 | 0.23064 | 2.6706 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-03-22 | 25 | 20.572 | 10.179 | 30.751 | 1.6449 | 0.76558 | 0.22861 | 2.6391 | 8.582% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-03-22 | 26 | 20.336 | 9.7368 | 30.0728 | 1.5732 | 0.76558 | 0.22357 | 2.5623 | 8.52% | 9.066% | 6.126% | 1.0931 | 1.0997 | 1.0653
2011-03-22 | 27 | 20.046 | 9.7649 | 29.8109 | 1.5459 | 0.76558 | 0.22162 | 2.5331 | 8.497% | 9.041% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-03-22 | 28 | 19.632 | 9.6124 | 29.2444 | 1.4877 | 0.76558 | 0.21741 | 2.4707 | 8.448% | 8.989% | 6.074% | 1.0923 | 1.0988 | 1.0647
2011-03-22 | 29 | 19.12 | 9.2322 | 28.3522 | 1.3983 | 0.76558 | 0.21077 | 2.3747 | 8.376% | 8.912% | 6.022% | 1.0914 | 1.0978 | 1.0641
2011-03-22 | 30 | 18.702 | 8.9604 | 27.6624 | 1.3311 | 0.76558 | 0.20565 | 2.3023 | 8.323% | 8.856% | 5.984% | 1.0908 | 1.0972 | 1.0637
2011-03-22 | 31 | 19.194 | 8.919 | 28.113 | 1.3748 | 0.76558 | 0.209 | 2.3494 | 8.357% | 8.892% | 6.009% | 1.0912 | 1.0976 | 1.0639
2011-03-22 | 32 | 19.508 | 8.8883 | 28.3963 | 1.4027 | 0.76558 | 0.2111 | 2.3794 | 8.379% | 8.915% | 6.025% | 1.0915 | 1.0979 | 1.0641
2011-03-22 | 33 | 19.728 | 8.8945 | 28.6225 | 1.4251 | 0.76558 | 0.21278 | 2.4035 | 8.397% | 8.935% | 6.038% | 1.0917 | 1.0981 | 1.0643
2011-03-22 | 34 | 19.862 | 9.0097 | 28.8717 | 1.45 | 0.76558 | 0.21464 | 2.4303 | 8.417% | 8.956% | 6.052% | 1.0919 | 1.0984 | 1.0644
2011-03-22 | 35 | 20.208 | 9.4514 | 29.6594 | 1.5302 | 0.76558 | 0.22049 | 2.5163 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-03-22 | 36 | 20.864 | 9.8735 | 30.7375 | 1.6435 | 0.76558 | 0.22851 | 2.6376 | 8.581% | 9.13% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-03-22 | 37 | 21.8741 | 10.2514 | 32.1255 | 1.7953 | 0.76558 | 0.23883 | 2.7997 | 8.715% | 9.273% | 6.266% | 1.0955 | 1.1022 | 1.0668
2011-03-22 | 38 | 22.3176 | 10.1625 | 32.4802 | 1.8351 | 0.76558 | 0.24146 | 2.8422 | 8.751% | 9.311% | 6.292% | 1.0959 | 1.1027 | 1.0671
2011-03-22 | 39 | 22.6467 | 9.9555 | 32.6021 | 1.849 | 0.76558 | 0.24237 | 2.8569 | 8.763% | 9.324% | 6.301% | 1.096 | 1.1028 | 1.0672
2011-03-22 | 40 | 22.7339 | 10.0743 | 32.8082 | 1.8724 | 0.76558 | 0.2439 | 2.8819 | 8.784% | 9.346% | 6.316% | 1.0963 | 1.1031 | 1.0674
2011-03-22 | 41 | 23.5651 | 10.3881 | 33.9531 | 2.0054 | 0.76558 | 0.25241 | 3.0234 | 8.905% | 9.474% | 6.402% | 1.0977 | 1.1047 | 1.0684
2011-03-22 | 42 | 23.5291 | 10.1184 | 33.6475 | 1.9694 | 0.76558 | 0.25014 | 2.9851 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2011-03-22 | 43 | 22.3405 | 9.5728 | 31.9133 | 1.7716 | 0.76558 | 0.23725 | 2.7745 | 8.694% | 9.25% | 6.251% | 1.0952 | 1.1019 | 1.0667
2011-03-22 | 44 | 21.898 | 8.9855 | 30.8835 | 1.6592 | 0.76558 | 0.22959 | 2.6543 | 8.595% | 9.145% | 6.18% | 1.094 | 1.1007 | 1.0659
2011-03-22 | 45 | 20.0562 | 8.3179 | 28.3741 | 1.4005 | 0.76558 | 0.21094 | 2.377 | 8.377% | 8.914% | 6.023% | 1.0914 | 1.0979 | 1.0641
2011-03-22 | 46 | 18.2138 | 7.5558 | 25.7696 | 1.1552 | 0.76558 | 0.19157 | 2.1123 | 8.197% | 8.722% | 5.894% | 1.0893 | 1.0955 | 1.0626
2011-03-22 | 47 | 16.8426 | 7.4171 | 24.2597 | 1.0238 | 0.76558 | 0.18035 | 1.9697 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-03-22 | 48 | 15.5085 | 7.658 | 23.1665 | 0.93359 | 0.76558 | 0.17222 | 1.8714 | 8.078% | 8.595% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-03-23 | 1 | 14.0079 | 6.9634 | 20.9714 | 0.76505 | 0.76558 | 0.1559 | 1.6865 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-23 | 2 | 13.1209 | 6.5148 | 19.6358 | 0.6707 | 0.76558 | 0.14597 | 1.5823 | 8.058% | 8.574% | 5.794% | 1.0876 | 1.0938 | 1.0615
2011-03-23 | 3 | 12.8326 | 6.1132 | 18.9458 | 0.6244 | 0.76558 | 0.14085 | 1.5308 | 8.08% | 8.597% | 5.81% | 1.0879 | 1.0941 | 1.0617
2011-03-23 | 4 | 12.5536 | 5.9579 | 18.5114 | 0.59609 | 0.76558 | 0.13762 | 1.4993 | 8.099% | 8.618% | 5.823% | 1.0881 | 1.0943 | 1.0618
2011-03-23 | 5 | 12.1023 | 5.9896 | 18.0919 | 0.56938 | 0.76558 | 0.1345 | 1.4695 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-23 | 6 | 11.5092 | 5.9087 | 17.418 | 0.52775 | 0.76558 | 0.12949 | 1.4228 | 8.169% | 8.691% | 5.873% | 1.089 | 1.0952 | 1.0624
2011-03-23 | 7 | 11.4074 | 5.7921 | 17.1995 | 0.5146 | 0.76558 | 0.12786 | 1.408 | 8.187% | 8.71% | 5.886% | 1.0892 | 1.0954 | 1.0625
2011-03-23 | 8 | 11.3749 | 5.7151 | 17.09 | 0.50807 | 0.76558 | 0.12705 | 1.4007 | 8.196% | 8.721% | 5.893% | 1.0893 | 1.0955 | 1.0626
2011-03-23 | 9 | 11.7019 | 5.5882 | 17.2901 | 0.52003 | 0.76558 | 0.12854 | 1.4141 | 8.179% | 8.702% | 5.881% | 1.0891 | 1.0953 | 1.0625
2011-03-23 | 10 | 11.929 | 5.5995 | 17.5286 | 0.53447 | 0.76558 | 0.13031 | 1.4304 | 8.16% | 8.682% | 5.867% | 1.0889 | 1.0951 | 1.0623
2011-03-23 | 11 | 12.2866 | 5.7813 | 18.0679 | 0.56787 | 0.76558 | 0.13432 | 1.4678 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-03-23 | 12 | 12.5478 | 6.1661 | 18.714 | 0.60921 | 0.76558 | 0.13912 | 1.5139 | 8.09% | 8.607% | 5.817% | 1.088 | 1.0942 | 1.0618
2011-03-23 | 13 | 14.0206 | 6.9628 | 20.9834 | 0.76592 | 0.76558 | 0.15599 | 1.6875 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-23 | 14 | 16.0797 | 8.1597 | 24.2394 | 1.0221 | 0.76558 | 0.1802 | 1.9678 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-03-23 | 15 | 20.202 | 10.0868 | 30.2888 | 1.5959 | 0.76558 | 0.22517 | 2.5866 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-03-23 | 16 | 23.7287 | 11.2909 | 35.0196 | 2.1333 | 0.76558 | 0.26034 | 3.1592 | 9.021% | 9.599% | 6.486% | 1.0992 | 1.1062 | 1.0694
2011-03-23 | 17 | 25.4791 | 11.8194 | 37.2985 | 2.42 | 0.76558 | 0.27728 | 3.4629 | 9.284% | 9.878% | 6.675% | 1.1023 | 1.1096 | 1.0715
2011-03-23 | 18 | 25.3972 | 11.6796 | 37.0768 | 2.3913 | 0.76558 | 0.27563 | 3.4325 | 9.258% | 9.85% | 6.656% | 1.102 | 1.1093 | 1.0713
2011-03-23 | 19 | 24.74 | 11.2731 | 36.013 | 2.2561 | 0.76558 | 0.26773 | 3.2894 | 9.134% | 9.718% | 6.567% | 1.1005 | 1.1076 | 1.0703
2011-03-23 | 20 | 23.9627 | 10.637 | 34.5998 | 2.0825 | 0.76558 | 0.25722 | 3.1053 | 8.975% | 9.549% | 6.453% | 1.0986 | 1.1056 | 1.069
2011-03-23 | 21 | 23.6626 | 10.4134 | 34.076 | 2.0199 | 0.76558 | 0.25332 | 3.0388 | 8.918% | 9.488% | 6.412% | 1.0979 | 1.1048 | 1.0685
2011-03-23 | 22 | 23.1946 | 10.3052 | 33.4998 | 1.9522 | 0.76558 | 0.24904 | 2.9668 | 8.856% | 9.423% | 6.368% | 1.0972 | 1.104 | 1.068
2011-03-23 | 23 | 22.5646 | 10.0925 | 32.6571 | 1.8552 | 0.76558 | 0.24278 | 2.8636 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-03-23 | 24 | 22.0549 | 9.965 | 32.0198 | 1.7835 | 0.76558 | 0.23804 | 2.7871 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-23 | 25 | 21.3691 | 10.1971 | 31.5663 | 1.7333 | 0.76558 | 0.23467 | 2.7336 | 8.66% | 9.214% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-03-23 | 26 | 20.5494 | 9.7993 | 30.3487 | 1.6022 | 0.76558 | 0.22562 | 2.5934 | 8.545% | 9.092% | 6.144% | 1.0934 | 1.1 | 1.0655
2011-03-23 | 27 | 20.467 | 9.9848 | 30.4518 | 1.6131 | 0.76558 | 0.22638 | 2.6051 | 8.555% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2011-03-23 | 28 | 20.698 | 10.0355 | 30.7335 | 1.6431 | 0.76558 | 0.22848 | 2.6371 | 8.581% | 9.13% | 6.169% | 1.0939 | 1.1005 | 1.0658
2011-03-23 | 29 | 20.5016 | 9.604 | 30.1056 | 1.5766 | 0.76558 | 0.22381 | 2.566 | 8.523% | 9.069% | 6.128% | 1.0932 | 1.0997 | 1.0653
2011-03-23 | 30 | 20.2457 | 9.4537 | 29.6994 | 1.5344 | 0.76558 | 0.22079 | 2.5207 | 8.488% | 9.031% | 6.103% | 1.0927 | 1.0993 | 1.065
2011-03-23 | 31 | 20.3157 | 9.3647 | 29.6804 | 1.5324 | 0.76558 | 0.22065 | 2.5186 | 8.486% | 9.029% | 6.101% | 1.0927 | 1.0993 | 1.065
2011-03-23 | 32 | 20.1713 | 9.4858 | 29.6571 | 1.53 | 0.76558 | 0.22047 | 2.5161 | 8.484% | 9.027% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-03-23 | 33 | 20.3124 | 9.5937 | 29.9061 | 1.5558 | 0.76558 | 0.22233 | 2.5437 | 8.506% | 9.05% | 6.116% | 1.093 | 1.0995 | 1.0651
2011-03-23 | 34 | 20.9292 | 9.653 | 30.5822 | 1.6269 | 0.76558 | 0.22735 | 2.6199 | 8.567% | 9.115% | 6.159% | 1.0937 | 1.1003 | 1.0656
2011-03-23 | 35 | 21.6511 | 10.2846 | 31.9357 | 1.7741 | 0.76558 | 0.23741 | 2.7771 | 8.696% | 9.253% | 6.252% | 1.0952 | 1.102 | 1.0667
2011-03-23 | 36 | 22.8241 | 10.8498 | 33.6739 | 1.9725 | 0.76558 | 0.25034 | 2.9884 | 8.875% | 9.443% | 6.381% | 1.0974 | 1.1043 | 1.0682
2011-03-23 | 37 | 23.841 | 10.9205 | 34.7615 | 2.102 | 0.76558 | 0.25842 | 3.126 | 8.993% | 9.568% | 6.466% | 1.0988 | 1.1058 | 1.0691
2011-03-23 | 38 | 24.3534 | 10.9093 | 35.2628 | 2.1631 | 0.76558 | 0.26215 | 3.1908 | 9.049% | 9.628% | 6.506% | 1.0995 | 1.1065 | 1.0696
2011-03-23 | 39 | 24.3497 | 10.9745 | 35.3242 | 2.1706 | 0.76558 | 0.2626 | 3.1988 | 9.055% | 9.635% | 6.511% | 1.0996 | 1.1066 | 1.0696
2011-03-23 | 40 | 24.812 | 10.9186 | 35.7306 | 2.2208 | 0.76558 | 0.26563 | 3.252 | 9.102% | 9.684% | 6.544% | 1.1001 | 1.1072 | 1.07
2011-03-23 | 41 | 25.5472 | 10.9622 | 36.5094 | 2.3187 | 0.76558 | 0.27142 | 3.3557 | 9.191% | 9.78% | 6.609% | 1.1012 | 1.1084 | 1.0708
2011-03-23 | 42 | 25.3482 | 10.6888 | 36.037 | 2.2591 | 0.76558 | 0.2679 | 3.2926 | 9.137% | 9.721% | 6.569% | 1.1006 | 1.1077 | 1.0703
2011-03-23 | 43 | 24.1199 | 10.2389 | 34.3588 | 2.0536 | 0.76558 | 0.25543 | 3.0746 | 8.948% | 9.521% | 6.434% | 1.0983 | 1.1052 | 1.0688
2011-03-23 | 44 | 23.3016 | 9.577 | 32.8785 | 1.8804 | 0.76558 | 0.24442 | 2.8904 | 8.791% | 9.354% | 6.321% | 1.0964 | 1.1032 | 1.0675
2011-03-23 | 45 | 20.9382 | 8.7733 | 29.7115 | 1.5356 | 0.76558 | 0.22088 | 2.5221 | 8.489% | 9.032% | 6.103% | 1.0928 | 1.0993 | 1.065
2011-03-23 | 46 | 19.041 | 7.9098 | 26.9508 | 1.2635 | 0.76558 | 0.20036 | 2.2294 | 8.272% | 8.802% | 5.948% | 1.0902 | 1.0965 | 1.0632
2011-03-23 | 47 | 17.3274 | 7.4497 | 24.7771 | 1.0679 | 0.76558 | 0.1842 | 2.0177 | 8.143% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2011-03-23 | 48 | 16.7919 | 7.6119 | 24.4038 | 1.036 | 0.76558 | 0.18142 | 1.983 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-24 | 1 | 15.3405 | 6.8901 | 22.2306 | 0.85968 | 0.76558 | 0.16527 | 1.7905 | 8.054% | 8.57% | 5.791% | 1.0876 | 1.0937 | 1.0615
2011-03-24 | 2 | 14.1769 | 6.4374 | 20.6143 | 0.73922 | 0.76558 | 0.15325 | 1.658 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-24 | 3 | 13.392 | 6.298 | 19.69 | 0.67441 | 0.76558 | 0.14638 | 1.5864 | 8.057% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-24 | 4 | 12.682 | 5.9951 | 18.6771 | 0.60681 | 0.76558 | 0.13885 | 1.5112 | 8.091% | 8.609% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-24 | 5 | 12.326 | 6.0122 | 18.3382 | 0.58499 | 0.76558 | 0.13633 | 1.4869 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-03-24 | 6 | 12.122 | 6.0078 | 18.1298 | 0.57177 | 0.76558 | 0.13478 | 1.4721 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-03-24 | 7 | 12.234 | 5.9233 | 18.1573 | 0.5735 | 0.76558 | 0.13498 | 1.4741 | 8.118% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-03-24 | 8 | 12.194 | 5.7239 | 17.9179 | 0.55848 | 0.76558 | 0.1332 | 1.4573 | 8.133% | 8.654% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-03-24 | 9 | 12.196 | 5.779 | 17.975 | 0.56205 | 0.76558 | 0.13363 | 1.4613 | 8.129% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-24 | 10 | 12.226 | 5.8748 | 18.1008 | 0.56994 | 0.76558 | 0.13456 | 1.4701 | 8.122% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-24 | 11 | 12.478 | 6.1588 | 18.6368 | 0.60419 | 0.76558 | 0.13855 | 1.5083 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-03-24 | 12 | 13.168 | 6.481 | 19.649 | 0.67161 | 0.76558 | 0.14607 | 1.5833 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-24 | 13 | 14.886 | 7.2958 | 22.1818 | 0.85591 | 0.76558 | 0.1649 | 1.7864 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-24 | 14 | 17.266 | 8.3805 | 25.6465 | 1.1442 | 0.76558 | 0.19066 | 2.1004 | 8.19% | 8.714% | 5.888% | 1.0892 | 1.0955 | 1.0626
2011-03-24 | 15 | 21.282 | 10.1298 | 31.4118 | 1.7164 | 0.76558 | 0.23352 | 2.7155 | 8.645% | 9.198% | 6.216% | 1.0946 | 1.1013 | 1.0663
2011-03-24 | 16 | 24.486 | 11.4489 | 35.9349 | 2.2463 | 0.76558 | 0.26714 | 3.279 | 9.125% | 9.709% | 6.561% | 1.1004 | 1.1075 | 1.0702
2011-03-24 | 17 | 26.4429 | 11.9301 | 38.3731 | 2.5615 | 0.76558 | 0.28527 | 3.6123 | 9.414% | 10.02% | 6.768% | 1.1039 | 1.1113 | 1.0726
2011-03-24 | 18 | 26.0984 | 11.6219 | 37.7203 | 2.4751 | 0.76558 | 0.28042 | 3.5211 | 9.335% | 9.932% | 6.712% | 1.103 | 1.1103 | 1.0719
2011-03-24 | 19 | 25.5331 | 10.6862 | 36.2192 | 2.282 | 0.76558 | 0.26926 | 3.3168 | 9.158% | 9.744% | 6.584% | 1.1008 | 1.108 | 1.0705
2011-03-24 | 20 | 24.6271 | 10.3985 | 35.0255 | 2.134 | 0.76558 | 0.26038 | 3.16 | 9.022% | 9.599% | 6.487% | 1.0992 | 1.1062 | 1.0694
2011-03-24 | 21 | 24.2544 | 9.8597 | 34.1141 | 2.0244 | 0.76558 | 0.25361 | 3.0436 | 8.922% | 9.493% | 6.415% | 1.098 | 1.1049 | 1.0685
2011-03-24 | 22 | 23.9843 | 9.9721 | 33.9564 | 2.0058 | 0.76558 | 0.25244 | 3.0238 | 8.905% | 9.475% | 6.403% | 1.0978 | 1.1047 | 1.0684
2011-03-24 | 23 | 23.3442 | 9.8067 | 33.1509 | 1.9117 | 0.76558 | 0.24645 | 2.9238 | 8.82% | 9.384% | 6.341% | 1.0967 | 1.1036 | 1.0677
2011-03-24 | 24 | 22.8981 | 9.9035 | 32.8016 | 1.8716 | 0.76558 | 0.24385 | 2.8811 | 8.783% | 9.345% | 6.315% | 1.0963 | 1.1031 | 1.0674
2011-03-24 | 25 | 23.0221 | 9.6762 | 32.6983 | 1.8599 | 0.76558 | 0.24308 | 2.8685 | 8.773% | 9.334% | 6.308% | 1.0962 | 1.103 | 1.0673
2011-03-24 | 26 | 22.7341 | 9.3104 | 32.0445 | 1.7862 | 0.76558 | 0.23822 | 2.79 | 8.707% | 9.264% | 6.26% | 1.0954 | 1.1021 | 1.0668
2011-03-24 | 27 | 22.758 | 9.4872 | 32.2452 | 1.8087 | 0.76558 | 0.23971 | 2.814 | 8.727% | 9.285% | 6.275% | 1.0956 | 1.1024 | 1.0669
2011-03-24 | 28 | 22.7263 | 9.4373 | 32.1635 | 1.7995 | 0.76558 | 0.23911 | 2.8042 | 8.719% | 9.277% | 6.269% | 1.0955 | 1.1023 | 1.0669
2011-03-24 | 29 | 22.146 | 9.1065 | 31.2525 | 1.699 | 0.76558 | 0.23234 | 2.697 | 8.63% | 9.182% | 6.205% | 1.0944 | 1.1011 | 1.0662
2011-03-24 | 30 | 21.542 | 8.8935 | 30.4355 | 1.6114 | 0.76558 | 0.22626 | 2.6032 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-03-24 | 31 | 21.638 | 8.899 | 30.537 | 1.6221 | 0.76558 | 0.22702 | 2.6147 | 8.562% | 9.11% | 6.156% | 1.0936 | 1.1002 | 1.0656
2011-03-24 | 32 | 21.892 | 8.9467 | 30.8387 | 1.6543 | 0.76558 | 0.22926 | 2.6492 | 8.59% | 9.14% | 6.177% | 1.094 | 1.1006 | 1.0658
2011-03-24 | 33 | 22.406 | 9.2477 | 31.6537 | 1.7429 | 0.76558 | 0.23532 | 2.7438 | 8.668% | 9.223% | 6.233% | 1.0949 | 1.1016 | 1.0665
2011-03-24 | 34 | 22.4739 | 9.5402 | 32.0142 | 1.7829 | 0.76558 | 0.238 | 2.7864 | 8.704% | 9.261% | 6.258% | 1.0953 | 1.1021 | 1.0668
2011-03-24 | 35 | 22.908 | 10.1193 | 33.0274 | 1.8975 | 0.76558 | 0.24553 | 2.9086 | 8.807% | 9.37% | 6.332% | 1.0966 | 1.1034 | 1.0676
2011-03-24 | 36 | 23.772 | 10.5121 | 34.2841 | 2.0447 | 0.76558 | 0.25487 | 3.0651 | 8.94% | 9.512% | 6.428% | 1.0982 | 1.1051 | 1.0687
2011-03-24 | 37 | 24.484 | 10.6992 | 35.1831 | 2.1533 | 0.76558 | 0.26156 | 3.1804 | 9.04% | 9.618% | 6.5% | 1.0994 | 1.1064 | 1.0695
2011-03-24 | 38 | 25.242 | 10.762 | 36.004 | 2.2549 | 0.76558 | 0.26766 | 3.2882 | 9.133% | 9.717% | 6.566% | 1.1005 | 1.1076 | 1.0703
2011-03-24 | 39 | 25.908 | 10.7904 | 36.6984 | 2.3428 | 0.76558 | 0.27282 | 3.3812 | 9.213% | 9.803% | 6.624% | 1.1015 | 1.1087 | 1.0709
2011-03-24 | 40 | 26.5799 | 10.7804 | 37.3602 | 2.428 | 0.76558 | 0.27774 | 3.4713 | 9.292% | 9.886% | 6.681% | 1.1024 | 1.1097 | 1.0716
2011-03-24 | 41 | 27.4798 | 10.975 | 38.4547 | 2.5724 | 0.76558 | 0.28588 | 3.6238 | 9.424% | 10.03% | 6.776% | 1.104 | 1.1114 | 1.0727
2011-03-24 | 42 | 27.4096 | 10.8135 | 38.2231 | 2.5415 | 0.76558 | 0.28416 | 3.5912 | 9.395% | 9.997% | 6.755% | 1.1037 | 1.1111 | 1.0724
2011-03-24 | 43 | 26.2125 | 10.5232 | 36.7357 | 2.3475 | 0.76558 | 0.2731 | 3.3862 | 9.218% | 9.808% | 6.628% | 1.1015 | 1.1087 | 1.071
2011-03-24 | 44 | 25.0488 | 9.9494 | 34.9981 | 2.1307 | 0.76558 | 0.26018 | 3.1565 | 9.019% | 9.596% | 6.485% | 1.0991 | 1.1061 | 1.0693
2011-03-24 | 45 | 23.0708 | 8.8289 | 31.8997 | 1.7701 | 0.76558 | 0.23715 | 2.7729 | 8.692% | 9.249% | 6.25% | 1.0952 | 1.1019 | 1.0667
2011-03-24 | 46 | 20.9849 | 7.9712 | 28.9561 | 1.4585 | 0.76558 | 0.21526 | 2.4394 | 8.424% | 8.964% | 6.057% | 1.092 | 1.0985 | 1.0645
2011-03-24 | 47 | 19.1798 | 7.585 | 26.7648 | 1.2461 | 0.76558 | 0.19897 | 2.2107 | 8.26% | 8.788% | 5.939% | 1.09 | 1.0964 | 1.0631
2011-03-24 | 48 | 18.326 | 7.6719 | 25.998 | 1.1757 | 0.76558 | 0.19327 | 2.1346 | 8.211% | 8.736% | 5.903% | 1.0895 | 1.0957 | 1.0627
2011-03-25 | 1 | 16.7597 | 6.9189 | 23.6786 | 0.97532 | 0.76558 | 0.17603 | 1.9169 | 8.096% | 8.614% | 5.821% | 1.0881 | 1.0943 | 1.0618
2011-03-25 | 2 | 15.306 | 6.5075 | 21.8135 | 0.82773 | 0.76558 | 0.16216 | 1.7555 | 8.048% | 8.563% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-25 | 3 | 14.2034 | 6.0902 | 20.2936 | 0.7164 | 0.76558 | 0.15087 | 1.6328 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-25 | 4 | 13.6403 | 5.884 | 19.5243 | 0.66311 | 0.76558 | 0.14515 | 1.5738 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-25 | 5 | 13.4494 | 5.8004 | 19.2498 | 0.64459 | 0.76558 | 0.14311 | 1.5533 | 8.069% | 8.585% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-03-25 | 6 | 13.2262 | 5.9105 | 19.1367 | 0.63705 | 0.76558 | 0.14226 | 1.5449 | 8.073% | 8.59% | 5.804% | 1.0878 | 1.094 | 1.0616
2011-03-25 | 7 | 13.2079 | 5.8813 | 19.0892 | 0.63388 | 0.76558 | 0.14191 | 1.5414 | 8.075% | 8.591% | 5.806% | 1.0878 | 1.094 | 1.0616
2011-03-25 | 8 | 13.0405 | 5.8447 | 18.8852 | 0.62041 | 0.76558 | 0.14039 | 1.5264 | 8.082% | 8.6% | 5.811% | 1.0879 | 1.0941 | 1.0617
2011-03-25 | 9 | 12.915 | 5.8833 | 18.7983 | 0.61471 | 0.76558 | 0.13975 | 1.52 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-03-25 | 10 | 12.932 | 5.8622 | 18.7942 | 0.61444 | 0.76558 | 0.13972 | 1.5197 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-03-25 | 11 | 13.4964 | 6.0348 | 19.5312 | 0.66358 | 0.76558 | 0.1452 | 1.5744 | 8.061% | 8.577% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-25 | 12 | 14.0579 | 6.3369 | 20.3948 | 0.72356 | 0.76558 | 0.15162 | 1.6408 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-25 | 13 | 15.5744 | 7.0044 | 22.5788 | 0.88682 | 0.76558 | 0.16785 | 1.8203 | 8.062% | 8.578% | 5.796% | 1.0877 | 1.0938 | 1.0615
2011-03-25 | 14 | 18.3296 | 8.3521 | 26.6817 | 1.2384 | 0.76558 | 0.19835 | 2.2023 | 8.254% | 8.782% | 5.935% | 1.09 | 1.0963 | 1.0631
2011-03-25 | 15 | 22.6608 | 10.3198 | 32.9806 | 1.8921 | 0.76558 | 0.24518 | 2.9029 | 8.802% | 9.365% | 6.329% | 1.0965 | 1.1033 | 1.0676
2011-03-25 | 16 | 24.6064 | 11.0378 | 35.6442 | 2.2101 | 0.76558 | 0.26498 | 3.2407 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2011-03-25 | 17 | 25.9107 | 11.3881 | 37.2988 | 2.4201 | 0.76558 | 0.27728 | 3.4629 | 9.284% | 9.878% | 6.675% | 1.1023 | 1.1096 | 1.0715
2011-03-25 | 18 | 26.8143 | 11.9501 | 38.7644 | 2.614 | 0.76558 | 0.28818 | 3.6677 | 9.462% | 10.07% | 6.803% | 1.1045 | 1.1119 | 1.073
2011-03-25 | 19 | 25.8985 | 10.7145 | 36.6129 | 2.3319 | 0.76558 | 0.27218 | 3.3696 | 9.203% | 9.792% | 6.617% | 1.1014 | 1.1086 | 1.0709
2011-03-25 | 20 | 27.794 | 11.5717 | 39.3658 | 2.6957 | 0.76558 | 0.29265 | 3.7539 | 9.536% | 10.15% | 6.856% | 1.1054 | 1.1129 | 1.0736
2011-03-25 | 21 | 26.6948 | 10.9244 | 37.6192 | 2.4618 | 0.76558 | 0.27967 | 3.5071 | 9.323% | 9.919% | 6.703% | 1.1028 | 1.1101 | 1.0718
2011-03-25 | 22 | 25.6257 | 10.7998 | 36.4255 | 2.3081 | 0.76558 | 0.27079 | 3.3444 | 9.182% | 9.769% | 6.602% | 1.1011 | 1.1083 | 1.0707
2011-03-25 | 23 | 24.037 | 10.3385 | 34.3756 | 2.0556 | 0.76558 | 0.25555 | 3.0767 | 8.95% | 9.523% | 6.435% | 1.0983 | 1.1053 | 1.0688
2011-03-25 | 24 | 22.7247 | 10.0647 | 32.7894 | 1.8703 | 0.76558 | 0.24376 | 2.8796 | 8.782% | 9.344% | 6.314% | 1.0963 | 1.1031 | 1.0674
2011-03-25 | 25 | 22.3179 | 10.0034 | 32.3213 | 1.8172 | 0.76558 | 0.24028 | 2.8231 | 8.734% | 9.293% | 6.28% | 1.0957 | 1.1025 | 1.067
2011-03-25 | 26 | 21.8714 | 9.6677 | 31.5391 | 1.7303 | 0.76558 | 0.23447 | 2.7304 | 8.657% | 9.211% | 6.224% | 1.0948 | 1.1015 | 1.0664
2011-03-25 | 27 | 21.4779 | 9.7038 | 31.1817 | 1.6914 | 0.76558 | 0.23181 | 2.6887 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-03-25 | 28 | 21.2819 | 9.7419 | 31.0238 | 1.6743 | 0.76558 | 0.23063 | 2.6705 | 8.608% | 9.159% | 6.189% | 1.0942 | 1.1008 | 1.066
2011-03-25 | 29 | 21.0284 | 9.4234 | 30.4518 | 1.6131 | 0.76558 | 0.22638 | 2.6051 | 8.555% | 9.102% | 6.151% | 1.0935 | 1.1001 | 1.0655
2011-03-25 | 30 | 20.3488 | 9.1664 | 29.5152 | 1.5154 | 0.76558 | 0.21942 | 2.5004 | 8.472% | 9.014% | 6.091% | 1.0926 | 1.0991 | 1.0649
2011-03-25 | 31 | 20.4935 | 9.043 | 29.5365 | 1.5176 | 0.76558 | 0.21958 | 2.5027 | 8.473% | 9.016% | 6.092% | 1.0926 | 1.0991 | 1.0649
2011-03-25 | 32 | 20.5117 | 9.2148 | 29.7265 | 1.5372 | 0.76558 | 0.22099 | 2.5237 | 8.49% | 9.033% | 6.104% | 1.0928 | 1.0993 | 1.065
2011-03-25 | 33 | 20.8536 | 9.4617 | 30.3153 | 1.5987 | 0.76558 | 0.22537 | 2.5896 | 8.542% | 9.089% | 6.142% | 1.0934 | 1.1 | 1.0654
2011-03-25 | 34 | 20.7678 | 9.4541 | 30.2219 | 1.5888 | 0.76558 | 0.22467 | 2.5791 | 8.534% | 9.08% | 6.136% | 1.0933 | 1.0999 | 1.0654
2011-03-25 | 35 | 20.8694 | 9.8827 | 30.752 | 1.6451 | 0.76558 | 0.22861 | 2.6393 | 8.582% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-03-25 | 36 | 21.5448 | 10.179 | 31.7238 | 1.7507 | 0.76558 | 0.23584 | 2.7521 | 8.675% | 9.23% | 6.237% | 1.095 | 1.1017 | 1.0665
2011-03-25 | 37 | 22.3023 | 10.3291 | 32.6314 | 1.8523 | 0.76558 | 0.24259 | 2.8604 | 8.766% | 9.327% | 6.303% | 1.0961 | 1.1029 | 1.0673
2011-03-25 | 38 | 22.9343 | 10.3175 | 33.2519 | 1.9234 | 0.76558 | 0.2472 | 2.9362 | 8.83% | 9.395% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-03-25 | 39 | 23.471 | 10.2848 | 33.7557 | 1.9821 | 0.76558 | 0.25094 | 2.9986 | 8.883% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-03-25 | 40 | 24.2869 | 10.355 | 34.6419 | 2.0876 | 0.76558 | 0.25753 | 3.1107 | 8.979% | 9.554% | 6.456% | 1.0987 | 1.1056 | 1.069
2011-03-25 | 41 | 25.4475 | 10.5311 | 35.9786 | 2.2518 | 0.76558 | 0.26747 | 3.2848 | 9.13% | 9.714% | 6.564% | 1.1005 | 1.1076 | 1.0703
2011-03-25 | 42 | 25.4532 | 10.3866 | 35.8398 | 2.2344 | 0.76558 | 0.26644 | 3.2664 | 9.114% | 9.697% | 6.553% | 1.1003 | 1.1074 | 1.0701
2011-03-25 | 43 | 24.2953 | 9.9001 | 34.1954 | 2.0341 | 0.76558 | 0.25421 | 3.0539 | 8.931% | 9.502% | 6.421% | 1.0981 | 1.105 | 1.0686
2011-03-25 | 44 | 23.0815 | 9.3432 | 32.4247 | 1.8289 | 0.76558 | 0.24105 | 2.8355 | 8.745% | 9.305% | 6.288% | 1.0958 | 1.1026 | 1.0671
2011-03-25 | 45 | 21.0789 | 8.5742 | 29.6532 | 1.5296 | 0.76558 | 0.22045 | 2.5156 | 8.483% | 9.026% | 6.1% | 1.0927 | 1.0992 | 1.065
2011-03-25 | 46 | 19.6076 | 7.9319 | 27.5395 | 1.3193 | 0.76558 | 0.20473 | 2.2896 | 8.314% | 8.846% | 5.978% | 1.0907 | 1.097 | 1.0636
2011-03-25 | 47 | 17.8638 | 7.4719 | 25.3357 | 1.1166 | 0.76558 | 0.18835 | 2.0705 | 8.172% | 8.695% | 5.876% | 1.089 | 1.0952 | 1.0624
2011-03-25 | 48 | 17.0469 | 7.5441 | 24.591 | 1.0519 | 0.76558 | 0.18281 | 2.0003 | 8.134% | 8.655% | 5.849% | 1.0885 | 1.0948 | 1.0621
2011-03-26 | 1 | 15.2171 | 6.7902 | 22.0073 | 0.8425 | 0.76558 | 0.1636 | 1.7717 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-03-26 | 2 | 13.7967 | 6.336 | 20.1327 | 0.70508 | 0.76558 | 0.14967 | 1.6203 | 8.048% | 8.563% | 5.787% | 1.0875 | 1.0937 | 1.0614
2011-03-26 | 3 | 13.0187 | 6.0357 | 19.0544 | 0.63158 | 0.76558 | 0.14165 | 1.5388 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-03-26 | 4 | 12.6245 | 5.7895 | 18.414 | 0.58983 | 0.76558 | 0.13689 | 1.4923 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-03-26 | 5 | 12.6079 | 5.7874 | 18.3953 | 0.58864 | 0.76558 | 0.13675 | 1.491 | 8.105% | 8.624% | 5.828% | 1.0882 | 1.0944 | 1.0619
2011-03-26 | 6 | 12.3219 | 5.7571 | 18.079 | 0.56857 | 0.76558 | 0.1344 | 1.4685 | 8.123% | 8.643% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-26 | 7 | 12.1113 | 5.674 | 17.7854 | 0.55025 | 0.76558 | 0.13222 | 1.448 | 8.142% | 8.663% | 5.854% | 1.0886 | 1.0948 | 1.0622
2011-03-26 | 8 | 11.69 | 5.6253 | 17.3153 | 0.52155 | 0.76558 | 0.12872 | 1.4158 | 8.177% | 8.7% | 5.879% | 1.0891 | 1.0953 | 1.0625
2011-03-26 | 9 | 11.8213 | 5.6492 | 17.4706 | 0.53094 | 0.76558 | 0.12988 | 1.4264 | 8.165% | 8.687% | 5.87% | 1.0889 | 1.0951 | 1.0624
2011-03-26 | 10 | 12.1102 | 5.7057 | 17.816 | 0.55215 | 0.76558 | 0.13245 | 1.4502 | 8.14% | 8.661% | 5.852% | 1.0886 | 1.0948 | 1.0622
2011-03-26 | 11 | 12.5913 | 6.0055 | 18.5968 | 0.6016 | 0.76558 | 0.13825 | 1.5054 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0943 | 1.0618
2011-03-26 | 12 | 13.1471 | 6.2664 | 19.4135 | 0.65561 | 0.76558 | 0.14432 | 1.5655 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-03-26 | 13 | 14.3774 | 6.8886 | 21.2659 | 0.78669 | 0.76558 | 0.15809 | 1.7104 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-26 | 14 | 16.137 | 7.9907 | 24.1277 | 1.0127 | 0.76558 | 0.17937 | 1.9576 | 8.114% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.062
2011-03-26 | 15 | 19.9648 | 9.8113 | 29.7761 | 1.5423 | 0.76558 | 0.22136 | 2.5292 | 8.494% | 9.038% | 6.107% | 1.0928 | 1.0994 | 1.065
2011-03-26 | 16 | 22.9962 | 11.1048 | 34.101 | 2.0229 | 0.76558 | 0.25351 | 3.042 | 8.92% | 9.491% | 6.414% | 1.0979 | 1.1049 | 1.0685
2011-03-26 | 17 | 24.1599 | 11.4575 | 35.6174 | 2.2068 | 0.76558 | 0.26478 | 3.2371 | 9.089% | 9.67% | 6.535% | 1.1 | 1.1071 | 1.0699
2011-03-26 | 18 | 24.2976 | 11.0859 | 35.3835 | 2.1779 | 0.76558 | 0.26305 | 3.2065 | 9.062% | 9.642% | 6.516% | 1.0997 | 1.1067 | 1.0697
2011-03-26 | 19 | 23.7405 | 10.9996 | 34.7402 | 2.0994 | 0.76558 | 0.25826 | 3.1233 | 8.99% | 9.566% | 6.464% | 1.0988 | 1.1058 | 1.0691
2011-03-26 | 20 | 23.1046 | 10.6528 | 33.7574 | 1.9823 | 0.76558 | 0.25096 | 2.9988 | 8.884% | 9.452% | 6.387% | 1.0975 | 1.1044 | 1.0682
2011-03-26 | 21 | 22.8648 | 10.3868 | 33.2515 | 1.9233 | 0.76558 | 0.2472 | 2.9361 | 8.83% | 9.395% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-03-26 | 22 | 22.4648 | 10.5695 | 33.0342 | 1.8983 | 0.76558 | 0.24558 | 2.9094 | 8.807% | 9.371% | 6.333% | 1.0966 | 1.1034 | 1.0676
2011-03-26 | 23 | 22.2021 | 10.2603 | 32.4625 | 1.8332 | 0.76558 | 0.24133 | 2.8401 | 8.749% | 9.309% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-03-26 | 24 | 21.7792 | 10.067 | 31.8462 | 1.7642 | 0.76558 | 0.23675 | 2.7665 | 8.687% | 9.243% | 6.246% | 1.0951 | 1.1018 | 1.0666
2011-03-26 | 25 | 21.2208 | 10.1783 | 31.3991 | 1.715 | 0.76558 | 0.23342 | 2.714 | 8.644% | 9.197% | 6.215% | 1.0946 | 1.1013 | 1.0663
2011-03-26 | 26 | 20.8744 | 9.878 | 30.7524 | 1.6451 | 0.76558 | 0.22862 | 2.6393 | 8.582% | 9.132% | 6.171% | 1.0939 | 1.1005 | 1.0658
2011-03-26 | 27 | 20.4152 | 10.0227 | 30.4379 | 1.6116 | 0.76558 | 0.22628 | 2.6035 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-03-26 | 28 | 20.2687 | 9.936 | 30.2046 | 1.587 | 0.76558 | 0.22454 | 2.5771 | 8.532% | 9.078% | 6.135% | 1.0933 | 1.0998 | 1.0654
2011-03-26 | 29 | 20.1883 | 9.6994 | 29.8877 | 1.5539 | 0.76558 | 0.22219 | 2.5417 | 8.504% | 9.048% | 6.114% | 1.0929 | 1.0995 | 1.0651
2011-03-26 | 30 | 19.9668 | 9.4374 | 29.4042 | 1.504 | 0.76558 | 0.21859 | 2.4882 | 8.462% | 9.004% | 6.084% | 1.0924 | 1.0989 | 1.0648
2011-03-26 | 31 | 19.9238 | 9.2089 | 29.1327 | 1.4764 | 0.76558 | 0.21658 | 2.4585 | 8.439% | 8.979% | 6.068% | 1.0922 | 1.0986 | 1.0646
2011-03-26 | 32 | 20.1025 | 9.1901 | 29.2925 | 1.4926 | 0.76558 | 0.21776 | 2.476 | 8.453% | 8.993% | 6.077% | 1.0923 | 1.0988 | 1.0647
2011-03-26 | 33 | 20.3043 | 9.4721 | 29.7764 | 1.5423 | 0.76558 | 0.22136 | 2.5293 | 8.494% | 9.038% | 6.107% | 1.0928 | 1.0994 | 1.065
2011-03-26 | 34 | 20.4517 | 9.5074 | 29.9591 | 1.5613 | 0.76558 | 0.22272 | 2.5496 | 8.51% | 9.055% | 6.119% | 1.093 | 1.0996 | 1.0652
2011-03-26 | 35 | 20.4302 | 9.7598 | 30.19 | 1.5855 | 0.76558 | 0.22444 | 2.5755 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-03-26 | 36 | 20.7844 | 10.0248 | 30.8093 | 1.6512 | 0.76558 | 0.22904 | 2.6458 | 8.588% | 9.137% | 6.175% | 1.0939 | 1.1006 | 1.0658
2011-03-26 | 37 | 21.4515 | 10.1767 | 31.6282 | 1.7401 | 0.76558 | 0.23513 | 2.7408 | 8.666% | 9.22% | 6.231% | 1.0949 | 1.1016 | 1.0664
2011-03-26 | 38 | 21.6958 | 10.0381 | 31.7339 | 1.7518 | 0.76558 | 0.23591 | 2.7533 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-03-26 | 39 | 21.842 | 10.0138 | 31.8559 | 1.7653 | 0.76558 | 0.23682 | 2.7677 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2011-03-26 | 40 | 21.9901 | 9.9347 | 31.9248 | 1.7729 | 0.76558 | 0.23733 | 2.7758 | 8.695% | 9.251% | 6.252% | 1.0952 | 1.1019 | 1.0667
2011-03-26 | 41 | 23.2862 | 10.2433 | 33.5296 | 1.9556 | 0.76558 | 0.24926 | 2.9705 | 8.859% | 9.426% | 6.37% | 1.0972 | 1.1041 | 1.068
2011-03-26 | 42 | 23.2273 | 9.8868 | 33.1141 | 1.9075 | 0.76558 | 0.24617 | 2.9192 | 8.816% | 9.38% | 6.338% | 1.0967 | 1.1035 | 1.0677
2011-03-26 | 43 | 22.2298 | 9.5016 | 31.7313 | 1.7515 | 0.76558 | 0.23589 | 2.753 | 8.676% | 9.231% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-03-26 | 44 | 21.2131 | 9.0743 | 30.2874 | 1.5957 | 0.76558 | 0.22516 | 2.5865 | 8.54% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-03-26 | 45 | 19.599 | 8.3477 | 27.9466 | 1.3586 | 0.76558 | 0.20776 | 2.3319 | 8.344% | 8.878% | 6% | 1.091 | 1.0974 | 1.0638
2011-03-26 | 46 | 18.1882 | 8.015 | 26.2032 | 1.1944 | 0.76558 | 0.1948 | 2.1548 | 8.223% | 8.75% | 5.913% | 1.0896 | 1.0959 | 1.0628
2011-03-26 | 47 | 17.3459 | 7.8695 | 25.2154 | 1.106 | 0.76558 | 0.18745 | 2.0591 | 8.166% | 8.689% | 5.871% | 1.0889 | 1.0952 | 1.0624
2011-03-26 | 48 | 16.394 | 8.0125 | 24.4065 | 1.0362 | 0.76558 | 0.18144 | 1.9832 | 8.126% | 8.646% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-27 | 1 | 15.0266 | 7.1192 | 22.1458 | 0.85313 | 0.76558 | 0.16463 | 1.7833 | 8.053% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-27 | 2 | 13.7604 | 6.6438 | 20.4042 | 0.72422 | 0.76558 | 0.15169 | 1.6415 | 8.045% | 8.56% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-27 | 3 | 12.7561 | 6.2738 | 19.0299 | 0.62995 | 0.76558 | 0.14147 | 1.537 | 8.077% | 8.594% | 5.807% | 1.0879 | 1.094 | 1.0617
2011-03-27 | 4 | 12.1879 | 6.0177 | 18.2056 | 0.57656 | 0.76558 | 0.13534 | 1.4775 | 8.116% | 8.635% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-27 | 5 | 11.8449 | 5.9113 | 17.7561 | 0.54844 | 0.76558 | 0.132 | 1.446 | 8.144% | 8.665% | 5.855% | 1.0887 | 1.0949 | 1.0622
2011-03-27 | 6 | 11.3765 | 5.876 | 17.2525 | 0.51777 | 0.76558 | 0.12826 | 1.4116 | 8.182% | 8.706% | 5.883% | 1.0891 | 1.0954 | 1.0625
2011-03-27 | 7 | 11.2777 | 5.8152 | 17.0929 | 0.50824 | 0.76558 | 0.12707 | 1.4009 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2011-03-27 | 8 | 11.0244 | 5.5707 | 16.5951 | 0.47907 | 0.76558 | 0.12337 | 1.368 | 8.243% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-03-27 | 9 | 10.9883 | 5.6094 | 16.5977 | 0.47922 | 0.76558 | 0.12339 | 1.3682 | 8.243% | 8.771% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-03-27 | 10 | 11.1233 | 5.8044 | 16.9277 | 0.49846 | 0.76558 | 0.12584 | 1.3899 | 8.211% | 8.736% | 5.903% | 1.0895 | 1.0957 | 1.0627
2011-03-27 | 11 | 11.546 | 5.9645 | 17.5105 | 0.53338 | 0.76558 | 0.13018 | 1.4291 | 8.162% | 8.684% | 5.868% | 1.0889 | 1.0951 | 1.0623
2011-03-27 | 12 | 12.0263 | 6.0186 | 18.0449 | 0.56643 | 0.76558 | 0.13415 | 1.4662 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-27 | 13 | 12.7723 | 5.9973 | 18.7696 | 0.61284 | 0.76558 | 0.13954 | 1.518 | 8.087% | 8.605% | 5.815% | 1.088 | 1.0942 | 1.0617
2011-03-27 | 14 | 13.42 | 6.1647 | 19.5848 | 0.66722 | 0.76558 | 0.1456 | 1.5784 | 8.059% | 8.575% | 5.795% | 1.0877 | 1.0938 | 1.0615
2011-03-27 | 15 | 14.9385 | 6.7861 | 21.7246 | 0.82099 | 0.76558 | 0.1615 | 1.7481 | 8.047% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-27 | 16 | 16.5804 | 7.6638 | 24.2441 | 1.0225 | 0.76558 | 0.18023 | 1.9683 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0945 | 1.062
2011-03-27 | 17 | 18.7968 | 8.885 | 27.6818 | 1.333 | 0.76558 | 0.20579 | 2.3043 | 8.324% | 8.857% | 5.985% | 1.0908 | 1.0972 | 1.0637
2011-03-27 | 18 | 20.6332 | 9.6748 | 30.308 | 1.5979 | 0.76558 | 0.22531 | 2.5888 | 8.542% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2011-03-27 | 19 | 21.9944 | 10.2907 | 32.2851 | 1.8132 | 0.76558 | 0.24001 | 2.8188 | 8.731% | 9.29% | 6.277% | 1.0957 | 1.1024 | 1.067
2011-03-27 | 20 | 22.4515 | 10.4902 | 32.9417 | 1.8877 | 0.76558 | 0.24489 | 2.8981 | 8.798% | 9.361% | 6.326% | 1.0965 | 1.1033 | 1.0675
2011-03-27 | 21 | 22.4877 | 10.6008 | 33.0886 | 1.9045 | 0.76558 | 0.24598 | 2.9161 | 8.813% | 9.377% | 6.337% | 1.0966 | 1.1035 | 1.0677
2011-03-27 | 22 | 22.1288 | 10.7077 | 32.8365 | 1.8756 | 0.76558 | 0.24411 | 2.8853 | 8.787% | 9.349% | 6.318% | 1.0963 | 1.1031 | 1.0674
2011-03-27 | 23 | 21.666 | 10.6257 | 32.2917 | 1.8139 | 0.76558 | 0.24006 | 2.8195 | 8.732% | 9.29% | 6.278% | 1.0957 | 1.1024 | 1.067
2011-03-27 | 24 | 21.5636 | 10.6221 | 32.1857 | 1.802 | 0.76558 | 0.23927 | 2.8069 | 8.721% | 9.279% | 6.27% | 1.0955 | 1.1023 | 1.0669
2011-03-27 | 25 | 20.8531 | 10.3827 | 31.2358 | 1.6972 | 0.76558 | 0.23221 | 2.695 | 8.628% | 9.18% | 6.204% | 1.0944 | 1.1011 | 1.0661
2011-03-27 | 26 | 20.4963 | 9.8959 | 30.3923 | 1.6068 | 0.76558 | 0.22594 | 2.5983 | 8.549% | 9.096% | 6.147% | 1.0935 | 1.1001 | 1.0655
2011-03-27 | 27 | 20.1208 | 9.6661 | 29.787 | 1.5434 | 0.76558 | 0.22144 | 2.5305 | 8.495% | 9.039% | 6.108% | 1.0928 | 1.0994 | 1.0651
2011-03-27 | 28 | 20.2046 | 9.3407 | 29.5453 | 1.5185 | 0.76558 | 0.21964 | 2.5037 | 8.474% | 9.016% | 6.093% | 1.0926 | 1.0991 | 1.0649
2011-03-27 | 29 | 20.054 | 8.8592 | 28.9132 | 1.4542 | 0.76558 | 0.21494 | 2.4347 | 8.421% | 8.96% | 6.055% | 1.092 | 1.0984 | 1.0644
2011-03-27 | 30 | 19.3729 | 8.5809 | 27.9538 | 1.3593 | 0.76558 | 0.20781 | 2.3327 | 8.345% | 8.879% | 6% | 1.091 | 1.0974 | 1.0638
2011-03-27 | 31 | 19.1999 | 8.6212 | 27.8211 | 1.3464 | 0.76558 | 0.20683 | 2.3188 | 8.335% | 8.868% | 5.993% | 1.0909 | 1.0973 | 1.0637
2011-03-27 | 32 | 18.9526 | 8.7021 | 27.6546 | 1.3304 | 0.76558 | 0.20559 | 2.3015 | 8.322% | 8.855% | 5.984% | 1.0908 | 1.0972 | 1.0636
2011-03-27 | 33 | 19.2044 | 8.9747 | 28.1791 | 1.3813 | 0.76558 | 0.20949 | 2.3564 | 8.362% | 8.897% | 6.012% | 1.0913 | 1.0977 | 1.064
2011-03-27 | 34 | 19.3797 | 8.9884 | 28.3681 | 1.3999 | 0.76558 | 0.21089 | 2.3764 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0979 | 1.0641
2011-03-27 | 35 | 20.1133 | 9.2286 | 29.3419 | 1.4977 | 0.76558 | 0.21813 | 2.4814 | 8.457% | 8.998% | 6.08% | 1.0924 | 1.0989 | 1.0647
2011-03-27 | 36 | 20.9485 | 9.7087 | 30.6572 | 1.6349 | 0.76558 | 0.22791 | 2.6284 | 8.574% | 9.122% | 6.164% | 1.0938 | 1.1004 | 1.0657
2011-03-27 | 37 | 21.4455 | 9.878 | 31.3235 | 1.7068 | 0.76558 | 0.23286 | 2.7052 | 8.636% | 9.189% | 6.21% | 1.0945 | 1.1012 | 1.0662
2011-03-27 | 38 | 21.6115 | 10.1257 | 31.7373 | 1.7522 | 0.76558 | 0.23594 | 2.7537 | 8.676% | 9.232% | 6.238% | 1.095 | 1.1017 | 1.0665
2011-03-27 | 39 | 22.0776 | 10.0218 | 32.0994 | 1.7924 | 0.76558 | 0.23863 | 2.7966 | 8.712% | 9.27% | 6.264% | 1.0954 | 1.1022 | 1.0668
2011-03-27 | 40 | 22.8873 | 10.1745 | 33.0618 | 1.9015 | 0.76558 | 0.24579 | 2.9128 | 8.81% | 9.374% | 6.335% | 1.0966 | 1.1034 | 1.0676
2011-03-27 | 41 | 23.5992 | 10.0997 | 33.6989 | 1.9755 | 0.76558 | 0.25052 | 2.9916 | 8.877% | 9.445% | 6.383% | 1.0974 | 1.1043 | 1.0682
2011-03-27 | 42 | 22.7875 | 9.6226 | 32.4101 | 1.8272 | 0.76558 | 0.24094 | 2.8338 | 8.743% | 9.303% | 6.287% | 1.0958 | 1.1026 | 1.0671
2011-03-27 | 43 | 21.6615 | 9.1069 | 30.7684 | 1.6468 | 0.76558 | 0.22874 | 2.6411 | 8.584% | 9.133% | 6.172% | 1.0939 | 1.1005 | 1.0658
2011-03-27 | 44 | 21.114 | 8.7012 | 29.8152 | 1.5464 | 0.76558 | 0.22165 | 2.5336 | 8.498% | 9.041% | 6.11% | 1.0929 | 1.0994 | 1.0651
2011-03-27 | 45 | 20.1827 | 8.1811 | 28.3638 | 1.3995 | 0.76558 | 0.21086 | 2.3759 | 8.377% | 8.913% | 6.023% | 1.0914 | 1.0978 | 1.0641
2011-03-27 | 46 | 19.0142 | 7.5876 | 26.6017 | 1.231 | 0.76558 | 0.19776 | 2.1943 | 8.249% | 8.777% | 5.931% | 1.0899 | 1.0962 | 1.063
2011-03-27 | 47 | 18.1219 | 7.4393 | 25.5612 | 1.1366 | 0.76558 | 0.19003 | 2.0922 | 8.185% | 8.709% | 5.885% | 1.0891 | 1.0954 | 1.0625
2011-03-27 | 48 | 17.4578 | 7.4499 | 24.9077 | 1.0792 | 0.76558 | 0.18517 | 2.0299 | 8.15% | 8.671% | 5.86% | 1.0887 | 1.0949 | 1.0622
2011-03-28 | 1 | 16.029 | 6.731 | 22.76 | 0.90111 | 0.76558 | 0.1692 | 1.8359 | 8.066% | 8.583% | 5.8% | 1.0877 | 1.0939 | 1.0616
2011-03-28 | 2 | 15.1576 | 6.2387 | 21.3963 | 0.79636 | 0.76558 | 0.15906 | 1.721 | 8.043% | 8.558% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-28 | 3 | 14.254 | 5.9776 | 20.2316 | 0.71202 | 0.76558 | 0.1504 | 1.628 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-28 | 4 | 13.3804 | 5.8858 | 19.2662 | 0.64569 | 0.76558 | 0.14323 | 1.5545 | 8.069% | 8.585% | 5.801% | 1.0878 | 1.0939 | 1.0616
2011-03-28 | 5 | 12.7948 | 5.8716 | 18.6664 | 0.60612 | 0.76558 | 0.13877 | 1.5105 | 8.092% | 8.61% | 5.818% | 1.088 | 1.0942 | 1.0618
2011-03-28 | 6 | 12.6224 | 5.7471 | 18.3695 | 0.58699 | 0.76558 | 0.13656 | 1.4891 | 8.107% | 8.625% | 5.829% | 1.0882 | 1.0944 | 1.0619
2011-03-28 | 7 | 12.5911 | 5.7328 | 18.3239 | 0.58408 | 0.76558 | 0.13622 | 1.4859 | 8.109% | 8.628% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-03-28 | 8 | 12.5278 | 5.5176 | 18.0454 | 0.56646 | 0.76558 | 0.13415 | 1.4662 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-28 | 9 | 12.6789 | 5.4156 | 18.0945 | 0.56954 | 0.76558 | 0.13452 | 1.4696 | 8.122% | 8.642% | 5.84% | 1.0884 | 1.0946 | 1.062
2011-03-28 | 10 | 12.6131 | 5.5115 | 18.1247 | 0.57144 | 0.76558 | 0.13474 | 1.4718 | 8.12% | 8.64% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-03-28 | 11 | 12.6411 | 5.6012 | 18.2423 | 0.57888 | 0.76558 | 0.13562 | 1.4801 | 8.113% | 8.633% | 5.834% | 1.0883 | 1.0945 | 1.0619
2011-03-28 | 12 | 13.0336 | 5.6909 | 18.7245 | 0.60989 | 0.76558 | 0.1392 | 1.5147 | 8.089% | 8.607% | 5.816% | 1.088 | 1.0942 | 1.0618
2011-03-28 | 13 | 14.074 | 5.827 | 19.901 | 0.68894 | 0.76558 | 0.14795 | 1.6025 | 8.052% | 8.568% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-28 | 14 | 14.9953 | 6.0805 | 21.0758 | 0.77269 | 0.76558 | 0.15668 | 1.6949 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-28 | 15 | 16.2791 | 6.6122 | 22.8913 | 0.91154 | 0.76558 | 0.17018 | 1.8473 | 8.07% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-03-28 | 16 | 17.6229 | 7.4205 | 25.0434 | 1.091 | 0.76558 | 0.18618 | 2.0427 | 8.157% | 8.679% | 5.865% | 1.0888 | 1.095 | 1.0623
2011-03-28 | 17 | 19.7426 | 8.4284 | 28.171 | 1.3805 | 0.76558 | 0.20943 | 2.3555 | 8.361% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2011-03-28 | 18 | 21.3424 | 9.3766 | 30.7189 | 1.6415 | 0.76558 | 0.22837 | 2.6355 | 8.579% | 9.128% | 6.169% | 1.0938 | 1.1005 | 1.0657
2011-03-28 | 19 | 23.0631 | 10.0341 | 33.0972 | 1.9055 | 0.76558 | 0.24605 | 2.9172 | 8.814% | 9.378% | 6.337% | 1.0967 | 1.1035 | 1.0677
2011-03-28 | 20 | 23.6177 | 10.2991 | 33.9168 | 2.0011 | 0.76558 | 0.25214 | 3.0188 | 8.901% | 9.47% | 6.4% | 1.0977 | 1.1046 | 1.0684
2011-03-28 | 21 | 24.2121 | 10.1301 | 34.3422 | 2.0516 | 0.76558 | 0.2553 | 3.0725 | 8.947% | 9.519% | 6.433% | 1.0983 | 1.1052 | 1.0687
2011-03-28 | 22 | 23.7319 | 10.0428 | 33.7746 | 1.9843 | 0.76558 | 0.25108 | 3.001 | 8.885% | 9.454% | 6.389% | 1.0975 | 1.1044 | 1.0682
2011-03-28 | 23 | 22.8424 | 9.6551 | 32.4975 | 1.8371 | 0.76558 | 0.24159 | 2.8443 | 8.752% | 9.312% | 6.293% | 1.0959 | 1.1027 | 1.0672
2011-03-28 | 24 | 21.7268 | 9.4573 | 31.1841 | 1.6916 | 0.76558 | 0.23183 | 2.689 | 8.623% | 9.175% | 6.2% | 1.0944 | 1.101 | 1.0661
2011-03-28 | 25 | 21.1 | 9.5294 | 30.6294 | 1.632 | 0.76558 | 0.2277 | 2.6252 | 8.571% | 9.12% | 6.163% | 1.0937 | 1.1003 | 1.0657
2011-03-28 | 26 | 20.621 | 9.11 | 29.731 | 1.5376 | 0.76558 | 0.22102 | 2.5242 | 8.49% | 9.034% | 6.104% | 1.0928 | 1.0993 | 1.065
2011-03-28 | 27 | 20.5693 | 8.9338 | 29.5031 | 1.5142 | 0.76558 | 0.21933 | 2.4991 | 8.471% | 9.013% | 6.09% | 1.0925 | 1.0991 | 1.0649
2011-03-28 | 28 | 19.9682 | 8.8383 | 28.8065 | 1.4435 | 0.76558 | 0.21415 | 2.4232 | 8.412% | 8.95% | 6.048% | 1.0918 | 1.0983 | 1.0644
2011-03-28 | 29 | 19.5654 | 8.5148 | 28.0802 | 1.3716 | 0.76558 | 0.20875 | 2.346 | 8.354% | 8.889% | 6.007% | 1.0912 | 1.0976 | 1.0639
2011-03-28 | 30 | 18.9192 | 8.2755 | 27.1946 | 1.2865 | 0.76558 | 0.20217 | 2.2542 | 8.289% | 8.82% | 5.96% | 1.0904 | 1.0967 | 1.0634
2011-03-28 | 31 | 18.9414 | 8.2238 | 27.1652 | 1.2837 | 0.76558 | 0.20195 | 2.2512 | 8.287% | 8.818% | 5.958% | 1.0904 | 1.0967 | 1.0634
2011-03-28 | 32 | 18.5404 | 8.1589 | 26.6993 | 1.24 | 0.76558 | 0.19849 | 2.2041 | 8.255% | 8.784% | 5.936% | 1.09 | 1.0963 | 1.0631
2011-03-28 | 33 | 19.0198 | 8.5301 | 27.5498 | 1.3203 | 0.76558 | 0.20481 | 2.2907 | 8.315% | 8.847% | 5.978% | 1.0907 | 1.0971 | 1.0636
2011-03-28 | 34 | 19.463 | 8.7122 | 28.1752 | 1.3809 | 0.76558 | 0.20946 | 2.356 | 8.362% | 8.897% | 6.012% | 1.0912 | 1.0977 | 1.064
2011-03-28 | 35 | 19.9488 | 9.0957 | 29.0446 | 1.4675 | 0.76558 | 0.21592 | 2.449 | 8.432% | 8.971% | 6.062% | 1.0921 | 1.0986 | 1.0645
2011-03-28 | 36 | 20.8855 | 9.579 | 30.4644 | 1.6144 | 0.76558 | 0.22648 | 2.6065 | 8.556% | 9.103% | 6.152% | 1.0936 | 1.1002 | 1.0655
2011-03-28 | 37 | 21.7243 | 10.0354 | 31.7597 | 1.7546 | 0.76558 | 0.23611 | 2.7563 | 8.679% | 9.234% | 6.24% | 1.095 | 1.1017 | 1.0666
2011-03-28 | 38 | 22.4522 | 10.0073 | 32.4595 | 1.8328 | 0.76558 | 0.24131 | 2.8397 | 8.748% | 9.308% | 6.29% | 1.0959 | 1.1026 | 1.0671
2011-03-28 | 39 | 23.1886 | 10.2565 | 33.4451 | 1.9458 | 0.76558 | 0.24863 | 2.96 | 8.85% | 9.417% | 6.363% | 1.0971 | 1.104 | 1.068
2011-03-28 | 40 | 24.0793 | 10.6312 | 34.7104 | 2.0958 | 0.76558 | 0.25804 | 3.1194 | 8.987% | 9.562% | 6.462% | 1.0987 | 1.1057 | 1.0691
2011-03-28 | 41 | 25.1677 | 10.9707 | 36.1383 | 2.2718 | 0.76558 | 0.26866 | 3.306 | 9.148% | 9.734% | 6.578% | 1.1007 | 1.1078 | 1.0704
2011-03-28 | 42 | 24.8294 | 10.5717 | 35.4011 | 2.1801 | 0.76558 | 0.26318 | 3.2088 | 9.064% | 9.644% | 6.517% | 1.0997 | 1.1067 | 1.0697
2011-03-28 | 43 | 23.7352 | 9.9551 | 33.6903 | 1.9744 | 0.76558 | 0.25046 | 2.9905 | 8.876% | 9.444% | 6.382% | 1.0974 | 1.1043 | 1.0682
2011-03-28 | 44 | 22.4815 | 9.2089 | 31.6904 | 1.747 | 0.76558 | 0.23559 | 2.7482 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2011-03-28 | 45 | 20.5333 | 8.5151 | 29.0484 | 1.4678 | 0.76558 | 0.21595 | 2.4494 | 8.432% | 8.972% | 6.063% | 1.0921 | 1.0986 | 1.0645
2011-03-28 | 46 | 18.7344 | 7.8474 | 26.5818 | 1.2291 | 0.76558 | 0.19761 | 2.1923 | 8.248% | 8.775% | 5.93% | 1.0899 | 1.0962 | 1.063
2011-03-28 | 47 | 16.9776 | 7.5189 | 24.4965 | 1.0439 | 0.76558 | 0.18211 | 1.9915 | 8.13% | 8.65% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-28 | 48 | 16.2843 | 7.5821 | 23.8664 | 0.99085 | 0.76558 | 0.17743 | 1.9339 | 8.103% | 8.621% | 5.826% | 1.0882 | 1.0943 | 1.0619
2011-03-29 | 1 | 15.3222 | 7.0152 | 22.3374 | 0.86796 | 0.76558 | 0.16606 | 1.7996 | 8.056% | 8.572% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-29 | 2 | 14.2926 | 6.5296 | 20.8222 | 0.7542 | 0.76558 | 0.15479 | 1.6746 | 8.042% | 8.557% | 5.782% | 1.0875 | 1.0936 | 1.0614
2011-03-29 | 3 | 13.7746 | 6.1783 | 19.9529 | 0.69254 | 0.76558 | 0.14833 | 1.6065 | 8.051% | 8.567% | 5.789% | 1.0876 | 1.0937 | 1.0614
2011-03-29 | 4 | 13.2963 | 5.9455 | 19.2418 | 0.64406 | 0.76558 | 0.14305 | 1.5527 | 8.069% | 8.586% | 5.802% | 1.0878 | 1.0939 | 1.0616
2011-03-29 | 5 | 12.7143 | 5.847 | 18.5613 | 0.59931 | 0.76558 | 0.13799 | 1.5029 | 8.097% | 8.615% | 5.822% | 1.0881 | 1.0943 | 1.0618
2011-03-29 | 6 | 12.3592 | 5.783 | 18.1422 | 0.57255 | 0.76558 | 0.13487 | 1.473 | 8.119% | 8.639% | 5.838% | 1.0884 | 1.0946 | 1.062
2011-03-29 | 7 | 12.431 | 5.6876 | 18.1186 | 0.57106 | 0.76558 | 0.1347 | 1.4713 | 8.121% | 8.64% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-29 | 8 | 12.3767 | 5.7248 | 18.1014 | 0.56998 | 0.76558 | 0.13457 | 1.4701 | 8.122% | 8.641% | 5.839% | 1.0884 | 1.0946 | 1.062
2011-03-29 | 9 | 12.7465 | 5.8606 | 18.6071 | 0.60227 | 0.76558 | 0.13833 | 1.5062 | 8.095% | 8.613% | 5.82% | 1.0881 | 1.0942 | 1.0618
2011-03-29 | 10 | 13.0368 | 6.0082 | 19.045 | 0.63095 | 0.76558 | 0.14158 | 1.5381 | 8.076% | 8.593% | 5.807% | 1.0879 | 1.094 | 1.0616
2011-03-29 | 11 | 13.2887 | 6.1339 | 19.4226 | 0.65622 | 0.76558 | 0.14439 | 1.5662 | 8.064% | 8.58% | 5.798% | 1.0877 | 1.0939 | 1.0615
2011-03-29 | 12 | 13.6001 | 6.4024 | 20.0025 | 0.69599 | 0.76558 | 0.1487 | 1.6103 | 8.05% | 8.566% | 5.788% | 1.0876 | 1.0937 | 1.0614
2011-03-29 | 13 | 15.0728 | 7.1067 | 22.1795 | 0.85573 | 0.76558 | 0.16488 | 1.7862 | 8.053% | 8.569% | 5.79% | 1.0876 | 1.0937 | 1.0615
2011-03-29 | 14 | 17.4907 | 8.2604 | 25.7511 | 1.1535 | 0.76558 | 0.19144 | 2.1105 | 8.196% | 8.72% | 5.893% | 1.0893 | 1.0955 | 1.0626
2011-03-29 | 15 | 21.4779 | 10.2128 | 31.6907 | 1.747 | 0.76558 | 0.23559 | 2.7482 | 8.672% | 9.227% | 6.235% | 1.095 | 1.1016 | 1.0665
2011-03-29 | 16 | 24.4362 | 11.7396 | 36.1758 | 2.2765 | 0.76558 | 0.26894 | 3.311 | 9.153% | 9.738% | 6.581% | 1.1007 | 1.1079 | 1.0704
2011-03-29 | 17 | 25.581 | 12.1823 | 37.7633 | 2.4807 | 0.76558 | 0.28074 | 3.527 | 9.34% | 9.938% | 6.715% | 1.103 | 1.1103 | 1.072
2011-03-29 | 18 | 26.6802 | 12.4128 | 39.093 | 2.6585 | 0.76558 | 0.29062 | 3.7147 | 9.502% | 10.11% | 6.832% | 1.105 | 1.1125 | 1.0733
2011-03-29 | 19 | 26.143 | 11.811 | 37.954 | 2.5058 | 0.76558 | 0.28215 | 3.5535 | 9.363% | 9.962% | 6.732% | 1.1033 | 1.1106 | 1.0722
2011-03-29 | 20 | 25.0972 | 11.3285 | 36.4257 | 2.3081 | 0.76558 | 0.27079 | 3.3445 | 9.182% | 9.769% | 6.602% | 1.1011 | 1.1083 | 1.0707
2011-03-29 | 21 | 24.6336 | 11.1819 | 35.8156 | 2.2314 | 0.76558 | 0.26626 | 3.2632 | 9.111% | 9.694% | 6.551% | 1.1002 | 1.1074 | 1.0701
2011-03-29 | 22 | 24.0354 | 10.9282 | 34.9635 | 2.1265 | 0.76558 | 0.25992 | 3.152 | 9.015% | 9.592% | 6.482% | 1.0991 | 1.1061 | 1.0693
2011-03-29 | 23 | 22.8799 | 10.3807 | 33.2606 | 1.9244 | 0.76558 | 0.24726 | 2.9372 | 8.831% | 9.396% | 6.349% | 1.0969 | 1.1037 | 1.0678
2011-03-29 | 24 | 22.0875 | 10.1948 | 32.2824 | 1.8129 | 0.76558 | 0.23999 | 2.8184 | 8.731% | 9.289% | 6.277% | 1.0957 | 1.1024 | 1.067
2011-03-29 | 25 | 21.0962 | 10.1547 | 31.2509 | 1.6989 | 0.76558 | 0.23232 | 2.6968 | 8.629% | 9.182% | 6.205% | 1.0944 | 1.1011 | 1.0661
2011-03-29 | 26 | 20.4972 | 9.6224 | 30.1196 | 1.5781 | 0.76558 | 0.22391 | 2.5676 | 8.525% | 9.07% | 6.129% | 1.0932 | 1.0997 | 1.0653
2011-03-29 | 27 | 20.1588 | 9.5296 | 29.6885 | 1.5332 | 0.76558 | 0.22071 | 2.5195 | 8.487% | 9.03% | 6.102% | 1.0927 | 1.0993 | 1.065
2011-03-29 | 28 | 20.3658 | 9.3812 | 29.747 | 1.5393 | 0.76558 | 0.22114 | 2.526 | 8.492% | 9.035% | 6.106% | 1.0928 | 1.0993 | 1.065
2011-03-29 | 29 | 20.0896 | 9.0686 | 29.1582 | 1.479 | 0.76558 | 0.21677 | 2.4613 | 8.441% | 8.981% | 6.069% | 1.0922 | 1.0987 | 1.0646
2011-03-29 | 30 | 19.9473 | 9.0558 | 29.003 | 1.4633 | 0.76558 | 0.21561 | 2.4445 | 8.428% | 8.968% | 6.06% | 1.092 | 1.0985 | 1.0645
2011-03-29 | 31 | 19.6723 | 9.0947 | 28.767 | 1.4395 | 0.76558 | 0.21386 | 2.419 | 8.409% | 8.947% | 6.046% | 1.0918 | 1.0983 | 1.0644
2011-03-29 | 32 | 19.7029 | 9.2326 | 28.9354 | 1.4564 | 0.76558 | 0.21511 | 2.4371 | 8.423% | 8.962% | 6.056% | 1.092 | 1.0984 | 1.0645
2011-03-29 | 33 | 19.853 | 9.5633 | 29.4163 | 1.5053 | 0.76558 | 0.21868 | 2.4895 | 8.463% | 9.005% | 6.085% | 1.0925 | 1.099 | 1.0648
2011-03-29 | 34 | 20.4237 | 9.8793 | 30.303 | 1.5974 | 0.76558 | 0.22528 | 2.5882 | 8.541% | 9.088% | 6.141% | 1.0934 | 1.1 | 1.0654
2011-03-29 | 35 | 21.3642 | 10.5713 | 31.9355 | 1.7741 | 0.76558 | 0.23741 | 2.7771 | 8.696% | 9.253% | 6.252% | 1.0952 | 1.102 | 1.0667
2011-03-29 | 36 | 22.4888 | 11.1283 | 33.6171 | 1.9659 | 0.76558 | 0.24991 | 2.9814 | 8.869% | 9.436% | 6.377% | 1.0973 | 1.1042 | 1.0681
2011-03-29 | 37 | 23.2486 | 11.3582 | 34.6068 | 2.0833 | 0.76558 | 0.25727 | 3.1062 | 8.976% | 9.55% | 6.453% | 1.0986 | 1.1056 | 1.069
2011-03-29 | 38 | 23.1247 | 11.3052 | 34.4299 | 2.0621 | 0.76558 | 0.25596 | 3.0836 | 8.956% | 9.529% | 6.44% | 1.0984 | 1.1053 | 1.0688
2011-03-29 | 39 | 23.7234 | 10.9009 | 34.6243 | 2.0854 | 0.76558 | 0.2574 | 3.1084 | 8.978% | 9.552% | 6.455% | 1.0986 | 1.1056 | 1.069
2011-03-29 | 40 | 24.5002 | 10.9142 | 35.4144 | 2.1817 | 0.76558 | 0.26328 | 3.2106 | 9.066% | 9.646% | 6.518% | 1.0997 | 1.1068 | 1.0697
2011-03-29 | 41 | 25.4679 | 10.9094 | 36.3773 | 2.302 | 0.76558 | 0.27043 | 3.338 | 9.176% | 9.763% | 6.598% | 1.101 | 1.1082 | 1.0706
2011-03-29 | 42 | 25.0941 | 10.5566 | 35.6507 | 2.2109 | 0.76558 | 0.26503 | 3.2415 | 9.092% | 9.674% | 6.537% | 1.1 | 1.1071 | 1.0699
2011-03-29 | 43 | 23.9541 | 9.8669 | 33.821 | 1.9898 | 0.76558 | 0.25143 | 3.0068 | 8.89% | 9.459% | 6.392% | 1.0976 | 1.1045 | 1.0683
2011-03-29 | 44 | 22.7397 | 9.3736 | 32.1133 | 1.7939 | 0.76558 | 0.23873 | 2.7982 | 8.714% | 9.271% | 6.265% | 1.0955 | 1.1022 | 1.0668
2011-03-29 | 45 | 20.5942 | 8.7509 | 29.3451 | 1.498 | 0.76558 | 0.21815 | 2.4817 | 8.457% | 8.998% | 6.081% | 1.0924 | 1.0989 | 1.0647
2011-03-29 | 46 | 18.2784 | 7.9086 | 26.187 | 1.1929 | 0.76558 | 0.19468 | 2.1532 | 8.222% | 8.748% | 5.912% | 1.0896 | 1.0959 | 1.0628
2011-03-29 | 47 | 16.7797 | 7.6097 | 24.3894 | 1.0348 | 0.76558 | 0.18131 | 1.9816 | 8.125% | 8.645% | 5.842% | 1.0884 | 1.0946 | 1.062
2011-03-29 | 48 | 16.1751 | 7.7212 | 23.8963 | 0.99334 | 0.76558 | 0.17765 | 1.9366 | 8.104% | 8.623% | 5.827% | 1.0882 | 1.0944 | 1.0619
2011-03-30 | 1 | 14.8329 | 6.961 | 21.7939 | 0.82624 | 0.76558 | 0.16202 | 1.7538 | 8.047% | 8.562% | 5.786% | 1.0875 | 1.0936 | 1.0614
2011-03-30 | 2 | 13.8156 | 6.4549 | 20.2705 | 0.71477 | 0.76558 | 0.15069 | 1.631 | 8.046% | 8.561% | 5.785% | 1.0875 | 1.0936 | 1.0614
2011-03-30 | 3 | 12.8822 | 6.2252 | 19.1074 | 0.63509 | 0.76558 | 0.14205 | 1.5427 | 8.074% | 8.591% | 5.805% | 1.0878 | 1.094 | 1.0616
2011-03-30 | 4 | 12.2479 | 6.0853 | 18.3333 | 0.58467 | 0.76558 | 0.13629 | 1.4865 | 8.108% | 8.627% | 5.83% | 1.0882 | 1.0944 | 1.0619
2011-03-30 | 5 | 11.9342 | 5.9685 | 17.9027 | 0.55753 | 0.76558 | 0.13309 | 1.4562 | 8.134% | 8.655% | 5.848% | 1.0885 | 1.0947 | 1.0621
2011-03-30 | 6 | 11.7361 | 5.8779 | 17.614 | 0.5397 | 0.76558 | 0.13094 | 1.4362 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623
2011-03-30 | 7 | 11.8795 | 5.7682 | 17.6477 | 0.54177 | 0.76558 | 0.1312 | 1.4385 | 8.151% | 8.673% | 5.861% | 1.0887 | 1.095 | 1.0623
2011-03-30 | 8 | 11.7115 | 5.5924 | 17.3039 | 0.52086 | 0.76558 | 0.12864 | 1.4151 | 8.178% | 8.701% | 5.88% | 1.0891 | 1.0953 | 1.0625
2011-03-30 | 9 | 11.6741 | 5.6678 | 17.3419 | 0.52315 | 0.76558 | 0.12892 | 1.4177 | 8.175% | 8.698% | 5.878% | 1.089 | 1.0953 | 1.0624
2011-03-30 | 10 | 11.8173 | 5.7692 | 17.5864 | 0.53801 | 0.76558 | 0.13074 | 1.4343 | 8.156% | 8.678% | 5.864% | 1.0888 | 1.095 | 1.0623
2011-03-30 | 11 | 12.0646 | 5.9935 | 18.0581 | 0.56725 | 0.76558 | 0.13425 | 1.4671 | 8.124% | 8.644% | 5.841% | 1.0884 | 1.0946 | 1.062
2011-03-30 | 12 | 12.5259 | 6.4881 | 19.0141 | 0.6289 | 0.76558 | 0.14135 | 1.5358 | 8.077% | 8.594% | 5.808% | 1.0879 | 1.094 | 1.0617
2011-03-30 | 13 | 13.9791 | 7.2123 | 21.1914 | 0.78118 | 0.76558 | 0.15754 | 1.7043 | 8.042% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-30 | 14 | 16.1523 | 8.3234 | 24.4757 | 1.0421 | 0.76558 | 0.18196 | 1.9896 | 8.129% | 8.649% | 5.845% | 1.0885 | 1.0947 | 1.0621
2011-03-30 | 15 | 19.9484 | 10.1392 | 30.0875 | 1.5747 | 0.76558 | 0.22367 | 2.564 | 8.522% | 9.067% | 6.127% | 1.0932 | 1.0997 | 1.0653
2011-03-30 | 16 | 22.4021 | 11.2451 | 33.6473 | 1.9694 | 0.76558 | 0.25014 | 2.9851 | 8.872% | 9.44% | 6.379% | 1.0974 | 1.1042 | 1.0681
2011-03-30 | 17 | 23.7679 | 11.5033 | 35.2712 | 2.1641 | 0.76558 | 0.26221 | 3.1919 | 9.05% | 9.629% | 6.507% | 1.0995 | 1.1065 | 1.0696
2011-03-30 | 18 | 24.0186 | 11.4956 | 35.5143 | 2.194 | 0.76558 | 0.26402 | 3.2236 | 9.077% | 9.658% | 6.526% | 1.0998 | 1.1069 | 1.0698
2011-03-30 | 19 | 24.0784 | 11.1584 | 35.2368 | 2.1599 | 0.76558 | 0.26195 | 3.1874 | 9.046% | 9.625% | 6.504% | 1.0995 | 1.1065 | 1.0696
2011-03-30 | 20 | 23.491 | 10.8107 | 34.3017 | 2.0468 | 0.76558 | 0.255 | 3.0673 | 8.942% | 9.515% | 6.429% | 1.0982 | 1.1051 | 1.0687
2011-03-30 | 21 | 23.6468 | 10.5109 | 34.1576 | 2.0296 | 0.76558 | 0.25393 | 3.0491 | 8.927% | 9.498% | 6.418% | 1.098 | 1.1049 | 1.0686
2011-03-30 | 22 | 22.8508 | 10.5883 | 33.4391 | 1.9451 | 0.76558 | 0.24859 | 2.9593 | 8.85% | 9.416% | 6.363% | 1.0971 | 1.1039 | 1.068
2011-03-30 | 23 | 22.197 | 10.3609 | 32.5578 | 1.8439 | 0.76558 | 0.24204 | 2.8516 | 8.758% | 9.319% | 6.297% | 1.096 | 1.1028 | 1.0672
2011-03-30 | 24 | 21.7853 | 10.3012 | 32.0865 | 1.7909 | 0.76558 | 0.23854 | 2.795 | 8.711% | 9.268% | 6.263% | 1.0954 | 1.1022 | 1.0668
2011-03-30 | 25 | 21.5434 | 10.2378 | 31.7812 | 1.757 | 0.76558 | 0.23627 | 2.7589 | 8.681% | 9.236% | 6.241% | 1.0951 | 1.1018 | 1.0666
2011-03-30 | 26 | 21.0695 | 9.9913 | 31.0608 | 1.6783 | 0.76558 | 0.23091 | 2.6747 | 8.611% | 9.162% | 6.192% | 1.0942 | 1.1009 | 1.066
2011-03-30 | 27 | 20.8451 | 10.0734 | 30.9186 | 1.6629 | 0.76558 | 0.22985 | 2.6584 | 8.598% | 9.148% | 6.182% | 1.0941 | 1.1007 | 1.0659
2011-03-30 | 28 | 20.5512 | 10.4258 | 30.977 | 1.6692 | 0.76558 | 0.23029 | 2.6651 | 8.603% | 9.154% | 6.186% | 1.0941 | 1.1008 | 1.0659
2011-03-30 | 29 | 20.4871 | 10.2537 | 30.7408 | 1.6439 | 0.76558 | 0.22853 | 2.638 | 8.581% | 9.131% | 6.17% | 1.0939 | 1.1005 | 1.0658
2011-03-30 | 30 | 20.3111 | 9.9706 | 30.2817 | 1.5951 | 0.76558 | 0.22512 | 2.5858 | 8.539% | 9.086% | 6.14% | 1.0934 | 1.0999 | 1.0654
2011-03-30 | 31 | 20.7494 | 9.8397 | 30.5891 | 1.6277 | 0.76558 | 0.2274 | 2.6207 | 8.567% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-03-30 | 32 | 20.585 | 10.0066 | 30.5917 | 1.6279 | 0.76558 | 0.22742 | 2.6209 | 8.568% | 9.116% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-03-30 | 33 | 21.0496 | 10.4055 | 31.4551 | 1.7211 | 0.76558 | 0.23384 | 2.7206 | 8.649% | 9.203% | 6.219% | 1.0947 | 1.1014 | 1.0663
2011-03-30 | 34 | 21.1066 | 10.5927 | 31.6993 | 1.748 | 0.76558 | 0.23566 | 2.7492 | 8.673% | 9.228% | 6.236% | 1.095 | 1.1017 | 1.0665
2011-03-30 | 35 | 21.6053 | 11.0517 | 32.6571 | 1.8552 | 0.76558 | 0.24278 | 2.8635 | 8.769% | 9.33% | 6.305% | 1.0961 | 1.1029 | 1.0673
2011-03-30 | 36 | 22.6268 | 11.4791 | 34.1058 | 2.0234 | 0.76558 | 0.25355 | 3.0426 | 8.921% | 9.492% | 6.414% | 1.0979 | 1.1049 | 1.0685
2011-03-30 | 37 | 23.3709 | 11.6875 | 35.0584 | 2.1381 | 0.76558 | 0.26063 | 3.1643 | 9.026% | 9.603% | 6.489% | 1.0992 | 1.1062 | 1.0694
2011-03-30 | 38 | 23.5951 | 11.5983 | 35.1934 | 2.1546 | 0.76558 | 0.26163 | 3.1818 | 9.041% | 9.619% | 6.5% | 1.0994 | 1.1064 | 1.0695
2011-03-30 | 39 | 23.622 | 11.685 | 35.307 | 2.1685 | 0.76558 | 0.26248 | 3.1965 | 9.054% | 9.633% | 6.51% | 1.0995 | 1.1066 | 1.0696
2011-03-30 | 40 | 24.3625 | 11.7841 | 36.1466 | 2.2728 | 0.76558 | 0.26872 | 3.3071 | 9.149% | 9.735% | 6.578% | 1.1007 | 1.1078 | 1.0704
2011-03-30 | 41 | 24.978 | 11.5976 | 36.5756 | 2.3271 | 0.76558 | 0.27191 | 3.3646 | 9.199% | 9.788% | 6.614% | 1.1013 | 1.1085 | 1.0708
2011-03-30 | 42 | 24.6149 | 10.8399 | 35.4547 | 2.1867 | 0.76558 | 0.26357 | 3.2158 | 9.07% | 9.651% | 6.521% | 1.0997 | 1.1068 | 1.0698
2011-03-30 | 43 | 23.6275 | 10.0836 | 33.7111 | 1.9769 | 0.76558 | 0.25061 | 2.9931 | 8.879% | 9.447% | 6.384% | 1.0974 | 1.1043 | 1.0682
2011-03-30 | 44 | 22.4907 | 9.3832 | 31.8739 | 1.7673 | 0.76558 | 0.23695 | 2.7698 | 8.69% | 9.246% | 6.248% | 1.0952 | 1.1019 | 1.0666
2011-03-30 | 45 | 20.7185 | 8.4956 | 29.2142 | 1.4846 | 0.76558 | 0.21718 | 2.4674 | 8.446% | 8.986% | 6.073% | 1.0923 | 1.0987 | 1.0647
2011-03-30 | 46 | 18.6797 | 7.8319 | 26.5116 | 1.2227 | 0.76558 | 0.19709 | 2.1853 | 8.243% | 8.77% | 5.927% | 1.0898 | 1.0961 | 1.063
2011-03-30 | 47 | 16.7416 | 7.5093 | 24.2509 | 1.023 | 0.76558 | 0.18028 | 1.9689 | 8.119% | 8.638% | 5.837% | 1.0884 | 1.0946 | 1.062
2011-03-30 | 48 | 15.8415 | 7.5816 | 23.4231 | 0.95439 | 0.76558 | 0.17413 | 1.8941 | 8.086% | 8.604% | 5.814% | 1.088 | 1.0941 | 1.0617
2011-03-31 | 1 | 14.4596 | 6.7621 | 21.2217 | 0.78342 | 0.76558 | 0.15776 | 1.7068 | 8.043% | 8.557% | 5.783% | 1.0875 | 1.0936 | 1.0614
2011-03-31 | 2 | 13.4002 | 6.2522 | 19.6524 | 0.67184 | 0.76558 | 0.1461 | 1.5835 | 8.058% | 8.573% | 5.793% | 1.0876 | 1.0938 | 1.0615
2011-03-31 | 3 | 12.6106 | 6.0219 | 18.6325 | 0.60391 | 0.76558 | 0.13852 | 1.508 | 8.093% | 8.611% | 5.819% | 1.0881 | 1.0942 | 1.0618
2011-03-31 | 4 | 11.9594 | 5.7651 | 17.7245 | 0.54649 | 0.76558 | 0.13177 | 1.4438 | 8.146% | 8.667% | 5.857% | 1.0887 | 1.0949 | 1.0622
2011-03-31 | 5 | 11.7272 | 5.7047 | 17.4319 | 0.5286 | 0.76558 | 0.12959 | 1.4238 | 8.168% | 8.69% | 5.872% | 1.0889 | 1.0952 | 1.0624
2011-03-31 | 6 | 11.7011 | 5.6966 | 17.3977 | 0.52652 | 0.76558 | 0.12934 | 1.4214 | 8.17% | 8.693% | 5.874% | 1.089 | 1.0952 | 1.0624
2011-03-31 | 7 | 11.7816 | 5.686 | 17.4676 | 0.53077 | 0.76558 | 0.12986 | 1.4262 | 8.165% | 8.687% | 5.871% | 1.0889 | 1.0951 | 1.0624
2011-03-31 | 8 | 11.4155 | 5.5761 | 16.9917 | 0.50224 | 0.76558 | 0.12632 | 1.3941 | 8.205% | 8.73% | 5.899% | 1.0894 | 1.0956 | 1.0627
2011-03-31 | 9 | 11.3321 | 5.7238 | 17.056 | 0.50604 | 0.76558 | 0.1268 | 1.3984 | 8.199% | 8.724% | 5.895% | 1.0893 | 1.0956 | 1.0626
2011-03-31 | 10 | 11.3439 | 5.7741 | 17.1179 | 0.50973 | 0.76558 | 0.12726 | 1.4026 | 8.194% | 8.718% | 5.891% | 1.0892 | 1.0955 | 1.0626
2011-03-31 | 11 | 11.6114 | 5.8901 | 17.5015 | 0.53283 | 0.76558 | 0.13011 | 1.4285 | 8.162% | 8.685% | 5.869% | 1.0889 | 1.0951 | 1.0623
2011-03-31 | 12 | 12.0945 | 6.1862 | 18.2808 | 0.58133 | 0.76558 | 0.1359 | 1.4828 | 8.111% | 8.63% | 5.832% | 1.0883 | 1.0945 | 1.0619
2011-03-31 | 13 | 13.6524 | 6.8655 | 20.5179 | 0.73232 | 0.76558 | 0.15253 | 1.6504 | 8.044% | 8.559% | 5.784% | 1.0875 | 1.0936 | 1.0614
2011-03-31 | 14 | 16.0287 | 8.1321 | 24.1607 | 1.0154 | 0.76558 | 0.17961 | 1.9606 | 8.115% | 8.634% | 5.835% | 1.0883 | 1.0945 | 1.062
2011-03-31 | 15 | 20.1572 | 10.0378 | 30.195 | 1.586 | 0.76558 | 0.22447 | 2.5761 | 8.531% | 9.077% | 6.134% | 1.0933 | 1.0998 | 1.0653
2011-03-31 | 16 | 22.6636 | 11.421 | 34.0846 | 2.0209 | 0.76558 | 0.25339 | 3.0399 | 8.919% | 9.489% | 6.413% | 1.0979 | 1.1048 | 1.0685
2011-03-31 | 17 | 24.1367 | 11.8235 | 35.9602 | 2.2495 | 0.76558 | 0.26733 | 3.2824 | 9.128% | 9.712% | 6.563% | 1.1004 | 1.1076 | 1.0702
2011-03-31 | 18 | 24.0883 | 11.7301 | 35.8184 | 2.2318 | 0.76558 | 0.26628 | 3.2636 | 9.112% | 9.695% | 6.551% | 1.1002 | 1.1074 | 1.0701
2011-03-31 | 19 | 23.7842 | 11.444 | 35.2282 | 2.1588 | 0.76558 | 0.26189 | 3.1863 | 9.045% | 9.624% | 6.503% | 1.0994 | 1.1065 | 1.0696
2011-03-31 | 20 | 23.1841 | 11.086 | 34.2701 | 2.043 | 0.76558 | 0.25477 | 3.0633 | 8.939% | 9.511% | 6.427% | 1.0982 | 1.1051 | 1.0687
2011-03-31 | 21 | 23.0906 | 11.0015 | 34.0921 | 2.0218 | 0.76558 | 0.25344 | 3.0408 | 8.919% | 9.49% | 6.413% | 1.0979 | 1.1049 | 1.0685
2011-03-31 | 22 | 22.3872 | 11.0712 | 33.4585 | 1.9474 | 0.76558 | 0.24873 | 2.9617 | 8.852% | 9.418% | 6.364% | 1.0971 | 1.104 | 1.068
2011-03-31 | 23 | 21.5849 | 10.8877 | 32.4725 | 1.8343 | 0.76558 | 0.2414 | 2.8413 | 8.75% | 9.31% | 6.291% | 1.0959 | 1.1027 | 1.0671
2011-03-31 | 24 | 21.331 | 10.7742 | 32.1052 | 1.793 | 0.76558 | 0.23867 | 2.7973 | 8.713% | 9.27% | 6.265% | 1.0954 | 1.1022 | 1.0668
2011-03-31 | 25 | 21.3647 | 10.831 | 32.1958 | 1.8032 | 0.76558 | 0.23935 | 2.8081 | 8.722% | 9.28% | 6.271% | 1.0956 | 1.1023 | 1.0669
2011-03-31 | 26 | 21.0402 | 10.5817 | 31.6219 | 1.7394 | 0.76558 | 0.23508 | 2.7401 | 8.665% | 9.22% | 6.23% | 1.0949 | 1.1016 | 1.0664
2011-03-31 | 27 | 20.9081 | 10.6632 | 31.5713 | 1.7339 | 0.76558 | 0.23471 | 2.7342 | 8.66% | 9.215% | 6.227% | 1.0948 | 1.1015 | 1.0664
2011-03-31 | 28 | 20.7096 | 10.5724 | 31.282 | 1.7022 | 0.76558 | 0.23255 | 2.7004 | 8.632% | 9.185% | 6.207% | 1.0945 | 1.1011 | 1.0662
2011-03-31 | 29 | 20.3705 | 10.0655 | 30.436 | 1.6114 | 0.76558 | 0.22627 | 2.6033 | 8.553% | 9.101% | 6.15% | 1.0935 | 1.1001 | 1.0655
2011-03-31 | 30 | 20.0217 | 9.9663 | 29.9879 | 1.5643 | 0.76558 | 0.22293 | 2.5528 | 8.513% | 9.058% | 6.121% | 1.0931 | 1.0996 | 1.0652
2011-03-31 | 31 | 20.4798 | 10.1042 | 30.5839 | 1.6271 | 0.76558 | 0.22736 | 2.6201 | 8.567% | 9.115% | 6.16% | 1.0937 | 1.1003 | 1.0656
2011-03-31 | 32 | 20.5295 | 10.1478 | 30.6773 | 1.6371 | 0.76558 | 0.22806 | 2.6307 | 8.575% | 9.124% | 6.166% | 1.0938 | 1.1004 | 1.0657
2011-03-31 | 33 | 20.8614 | 10.5171 | 31.3785 | 1.7128 | 0.76558 | 0.23327 | 2.7116 | 8.642% | 9.195% | 6.213% | 1.0946 | 1.1013 | 1.0662
2011-03-31 | 34 | 20.9125 | 10.6449 | 31.5574 | 1.7324 | 0.76558 | 0.2346 | 2.7325 | 8.659% | 9.213% | 6.226% | 1.0948 | 1.1015 | 1.0664
2011-03-31 | 35 | 20.7701 | 11.0846 | 31.8547 | 1.7651 | 0.76558 | 0.23681 | 2.7675 | 8.688% | 9.244% | 6.247% | 1.0951 | 1.1019 | 1.0666
2011-03-31 | 36 | 21.9314 | 11.6706 | 33.602 | 1.9641 | 0.76558 | 0.2498 | 2.9795 | 8.867% | 9.434% | 6.375% | 1.0973 | 1.1042 | 1.0681
2011-03-31 | 37 | 23.2632 | 11.8097 | 35.0729 | 2.1398 | 0.76558 | 0.26074 | 3.1661 | 9.027% | 9.605% | 6.491% | 1.0992 | 1.1063 | 1.0694
2011-03-31 | 38 | 23.8852 | 11.9836 | 35.8689 | 2.2381 | 0.76558 | 0.26665 | 3.2703 | 9.117% | 9.701% | 6.555% | 1.1003 | 1.1074 | 1.0702
2011-03-31 | 39 | 24.232 | 11.8546 | 36.0866 | 2.2653 | 0.76558 | 0.26827 | 3.2991 | 9.142% | 9.727% | 6.573% | 1.1006 | 1.1078 | 1.0704
2011-03-31 | 40 | 25.1462 | 11.7401 | 36.8863 | 2.3668 | 0.76558 | 0.27422 | 3.4066 | 9.235% | 9.827% | 6.64% | 1.1018 | 1.109 | 1.0711
2011-03-31 | 41 | 25.3396 | 11.6386 | 36.9781 | 2.3786 | 0.76558 | 0.2749 | 3.4191 | 9.246% | 9.838% | 6.648% | 1.1019 | 1.1091 | 1.0712
2011-03-31 | 42 | 25.2442 | 11.3479 | 36.5921 | 2.3292 | 0.76558 | 0.27203 | 3.3668 | 9.201% | 9.79% | 6.615% | 1.1013 | 1.1085 | 1.0708
2011-03-31 | 43 | 24.3182 | 10.8991 | 35.2173 | 2.1575 | 0.76558 | 0.26181 | 3.1849 | 9.043% | 9.622% | 6.502% | 1.0994 | 1.1065 | 1.0695
2011-03-31 | 44 | 23.1883 | 10.2163 | 33.4045 | 1.9411 | 0.76558 | 0.24833 | 2.955 | 8.846% | 9.412% | 6.36% | 1.097 | 1.1039 | 1.0679
2011-03-31 | 45 | 21.5386 | 9.2925 | 30.8311 | 1.6535 | 0.76558 | 0.2292 | 2.6483 | 8.59% | 9.139% | 6.176% | 1.094 | 1.1006 | 1.0658
2011-03-31 | 46 | 19.5548 | 8.429 | 27.9837 | 1.3622 | 0.76558 | 0.20803 | 2.3358 | 8.347% | 8.881% | 6.002% | 1.0911 | 1.0975 | 1.0638
2011-03-31 | 47 | 17.8634 | 8.063 | 25.9264 | 1.1693 | 0.76558 | 0.19274 | 2.1276 | 8.206% | 8.732% | 5.9% | 1.0894 | 1.0957 | 1.0627
2011-03-31 | 48 | 16.7335 | 8.2545 | 24.988 | 1.0862 | 0.76558 | 0.18576 | 2.0375 | 8.154% | 8.676% | 5.863% | 1.0888 | 1.095 | 1.0623

## Loss by Month
|  |  | Relevant Network Area |  | Insert Name of Network Area
Time | Time | Half Hr | Half Hr | Month | Sum Total Load | Sum Total losses | Total overall Loss Factor | Total LV Loss Factor | Total HV Loss Factor | Cumulative Sum Total Load | Cumulative Sum Total losses | Overall Monthly Loss Ratio | Overall Loss Ratio YTD
Time | Time | Half Hr | Half Hr | Apr | 43819.5922 | 3892.3432 | 1.0975 | 1.1025 | 1.067 | 43819.5922 | 3892.3432 | 8.883% | 8.883%
>31/3/10 | <1/5/10
Time | Time | Half Hr | Half Hr | May | 56869.0389 | 5517.5631 | 1.1074 | 1.1126 | 1.0734 | 100688.6311 | 9409.9063 | 9.702% | 9.346%
>30/4/10 | <1/6/10
Time | Time | Half Hr | Half Hr | Jun | 67534.981 | 7312.722 | 1.1214 | 1.1273 | 1.0826 | 168223.6121 | 16722.6282 | 10.83% | 9.941%
>31/5/10 | <1/7/10
Time | Time | Half Hr | Half Hr | July | 74976.9669 | 8466.0094 | 1.1273 | 1.1339 | 1.0867 | 243200.579 | 25188.6376 | 11.29% | 10.36%
>30/6/10 | <1/8/10
Time | Time | Half Hr | Half Hr | Aug | 61543.0621 | 6214.9016 | 1.1123 | 1.1176 | 1.0765 | 304743.6411 | 31403.5392 | 10.1% | 10.3%
>31/7/10 | <1/9/10
Time | Time | Half Hr | Half Hr | Sep | 98856.7768 | 9093.3839 | 1.1013 | 1.1062 | 1.0694 | 403600.4179 | 40496.9232 | 9.199% | 10.03%
>31/8/10 | <1/11/10
Time | Time | Half Hr | Half Hr | Oct | 46897.7844 | 4180.5506 | 1.0979 | 1.1032 | 1.0674 | 450498.2022 | 44677.4738 | 8.914% | 9.917%
>30/9/10 | <1/11/10
Time | Time | Half Hr | Half Hr | Nov | 39970.7256 | 3406.974 | 1.0932 | 1.099 | 1.0648 | 490468.9279 | 48084.4478 | 8.524% | 9.804%
>31/10/10 | <1/12/10
Time | Time | Half Hr | Half Hr | Dec | 41904.9097 | 3590.369 | 1.0937 | 1.0994 | 1.0651 | 532373.8375 | 51674.8168 | 8.568% | 9.706%
>30/11/10 | <1/1/11
Time | Time | Half Hr | Half Hr | Jan | 42456.0409 | 3671.3174 | 1.0947 | 1.1002 | 1.0656 | 574829.8785 | 55346.1342 | 8.647% | 9.628%
>31/12/10 | <1/2/11
Time | Time | Half Hr | Half Hr | Feb | 37324.1452 | 3188.7701 | 1.0934 | 1.0992 | 1.0649 | 612154.0237 | 58534.9043 | 8.543% | 9.562%
>31/1/11 | <1/3/11
Time | Time | Half Hr | Half Hr | Mar | 42013.1483 | 3614.8641 | 1.0941 | 1.0998 | 1.0653 | 654167.172 | 62149.7684 | 8.604% | 9.501%
>28/2/11 | <1/4/11
Totals |  |  |  |  | 654167.172 | 62149.7684 | 1.105 | 1.1087 | 1.0709
[6 empty] | 9.501% | 9.501% | 9.808% | 6.624%

## Loss by Sum Win Day Night
|  | Relevant Network Area |  |  | Insert Name of Network Area
[6 empty] | Sum Total Load MW | Sum Total Losses MW | Total Overall Reconciliation Loss Factor | Total LV Reconciliation Loss Factor | Total HV Reconciliation Loss Factor
Winter Day | Time | Time | Half Hr | Half Hr
| >=1/5/10 | <1/10/10 | >14 | <47 |  | 230548.7868 | 24917.2061
[5 empty] | Winter Day Total | 230548.7868 | 24917.2061 | 1.1212 | 1.1275 | 1.0827
Winter Night | Time | Time | Half Hr | Half Hr |  | 82334.2545 | 7506.8232
| >=1/5/10 | <1/10/10 | <15
| >=1/5/10 | <1/10/10 |  | >46
[5 empty] | Winter Night Total | 82334.2545 | 7506.8232 | 1.1003 | 1.1056 | 1.069
|  |  |  | Winter Total |  | 312883.0413 | 32424.0294 | 1.1156
Summer | Time | Time | Half Hr | Half Hr |  | 294386.3463 | 25545.1884 | 1.095
| >30/9/10 | <1/4/11
| >=1/4/10 | <1/5/10
Winter | Time | Time | Half Hr | Half Hr |  | 312883.0413 | 32424.0294 | 1.1156
| >=1/5/10 | <1/10/10
[5 empty] | S + W | 607269.3876 | 57969.2178 | 1.1055
Summer Day | Time | Time | Half Hr | Half Hr | Summer Day Total | 221949.7045 | 19650.0411 | 1.0971 | 1.1034 | 1.0676
| >30/9/10 | <1/4/11 | >14 | <47
| >31/3/10 | <1/5/10 | >14 | <47
Summer Night | Time | Time | Half Hr | Half Hr |  | 61930.9044 | 5039.1936
| >30/9/10 | <1/4/11 | <15
| >30/9/10 | <1/4/11 |  | >46
| Time | Time | Half Hr | Half Hr |  | 10505.7374 | 855.9538
| >31/3/10 | <1/5/10 | <15
| >31/3/10 | <1/5/10 |  | >46
[5 empty] | Summer Night Total | 72436.6418 | 5895.1473 | 1.0886 | 1.0948 | 1.0621
[5 empty] | Sum D+N | 294386.3463 | 25545.1884 | 1.095
[5 empty] | Summer + Winter | 607269.3876 | 57969.2178 | 1.1055
[7 empty] | 9.546% | 9.546%
[6 empty] | 303634.6938 | 28984.6089
[6 empty] | MWh | MWh