## Assump
Simulated extra for Pole 2 if build 4th cable of extra 200 (MW) | 0 | 0 | <-- Mike P said could increase extent of self-cover if built 4th cable
15 minute overload additional capacity for each pole, sent (MW) | 60 |  |  |  | m (SI MW per NI MW) | c (MW) | c Tiwai | c non Tiwai | Delta range at max (MW)
Losses | 5.714% |  |  | SI Dem relationship w. NI Dem | 0.3 | 630 | 400 | 230 | 50
| 15 minute overload capacity, sent (MW) | Received
Pole 2 | 500 | 471.4286 |  | NI demand (MW) | 4500
Pole 3 | 700 | 660 |  | Max SI demand | 2030
Total | 1200 | 1131.4286 |  | SI Gen | 3339
Assumptions |  |  |  | Available to send | 1279
Max HVDC IR transfer capacity | 220 |  |  | Available to be received | 1205.9143
Single pole normal limit (inluding any overload) (received MW) | 528 |  |  | Net capacity capable of being received | 1131.4286
Modulation risk | 30
Maximum available spare ca[pacity (MW) | 498 |  |  |  | With HVDC | Without HVDC
AC CE (MW) | 400 |  |  | Resultant NI capacity required (MW) | 3982 | 4880
NI IL avail | 20 |  |  |  |  | 898
Note on B14: simon: This is the limit of the pole for temporary operations - i.e. up to 15 min in order to provide reserve cover.
Note on B15: simon: Typically e3p at full output at moment (i.e. 400 MW) If all CCGTs retired, would either be Huntly Rankine unit (250 MW) or if they also went next largest would be Rotokawa (140 MW)
Note on D2: Simon Coates: Complete guess. Should set to zero normally, but just used here to illustrate potential impact of building a 4th cable
Note on D11: Simon Coates: Discussion w. Mike P Mike C said technical capability of FKC is 250 MW which, once the modulation risk is subtracted, gives a practical limite of 220 MW.
Note on D12: simon: Pole 2 is the weakest link. See sec 3.6.3 of SysOp June 2015 FKC Trial technical report. 560 MW sent = 528 MW received.
Note on D13: simon: See sec 3.7 of SysOp June 2015 FKC Trial technical report. Modulation risk reflects risk that DC is operate off its set point to deliver normal frequency response
Note on K4: simon: Based on inspection of NI / SI correlation for 2005 to mid 2008 (i.e. before Tiwai and Christchurch demand interruptions)

## Calc
Graph area. (See below for looking at scenarios of cost allocation)
| Total HVDC transfer (MW) (received) |  |  | MW | MW |  |  |  |  | MW | MW |  | MW | HVDC received | [7 empty] | Headings for scenario area below
HVDC sent |  | Spare for reserve to cover AC CE | Max possible SI IR which can be transferred across DC to meet NI AC CE | Risk from HVDC (NI DC CE) | Min NI IR required to meet NI AC CE (AC risk minus max. possible IR transfer across DC) | Risk from largest NI gen. (NI AC CE) | NI IL avail | NI spinning reserve required (MW) | Delta in NI IR required | NI gen cap required for energy | NI gen cap required for IR | Unusable HVDC range because of SI supply / demand balance | Total NI cap required |  | Risk from largest NI gen. (NI AC CE) | Max possible SI IR which can be transferred across DC to meet NI AC CE | Min NI IR required to meet NI AC CE (AC risk minus max. possible IR transfer across DC) | Risk from HVDC (NI DC CE) | Min IR which must be procured in NI | Total IR procured across both islands | Unit: | Huntly - e3p | TCC | Huntly units 1-4 | Stratford | Glenbrook | Rotokawa | Kawerau | Te Mihi | Manapouri | Clutha -Clyde | Waitaki - Benmore | Waitaki - Pukaki | Waitaki - Ohau
0 | 0 | 220 | 220 | -498 | 180 | 400 | 20 | 160 |  | 4500 | 160 | #N/A | 4660 | 0 | 400 | 220 | 180 | -498 | 180 | 400
5.303 | 5 | 220 | 220 | -493 | 180 | 400 | 20 | 160 | 0 | 4495 | 160 | #N/A | 4655 | 5 | 400 | 220 | 180 | -493 | 180 | 400
10.6061 | 10 | 220 | 220 | -488 | 180 | 400 | 20 | 160 | 0 | 4490 | 160 | #N/A | 4650 | 10 | 400 | 220 | 180 | -488 | 180 | 400
15.9091 | 15 | 220 | 220 | -483 | 180 | 400 | 20 | 160 | 0 | 4485 | 160 | #N/A | 4645 | 15 | 400 | 220 | 180 | -483 | 180 | 400
21.2121 | 20 | 220 | 220 | -478 | 180 | 400 | 20 | 160 | 0 | 4480 | 160 | #N/A | 4640 | 20 | 400 | 220 | 180 | -478 | 180 | 400
26.5152 | 25 | 220 | 220 | -473 | 180 | 400 | 20 | 160 | 0 | 4475 | 160 | #N/A | 4635 | 25 | 400 | 220 | 180 | -473 | 180 | 400
31.8182 | 30 | 220 | 220 | -468 | 180 | 400 | 20 | 160 | 0 | 4470 | 160 | #N/A | 4630 | 30 | 400 | 220 | 180 | -468 | 180 | 400
37.1212 | 35 | 220 | 220 | -463 | 180 | 400 | 20 | 160 | 0 | 4465 | 160 | #N/A | 4625 | 35 | 400 | 220 | 180 | -463 | 180 | 400
42.4242 | 40 | 220 | 220 | -458 | 180 | 400 | 20 | 160 | 0 | 4460 | 160 | #N/A | 4620 | 40 | 400 | 220 | 180 | -458 | 180 | 400
47.7273 | 45 | 220 | 220 | -453 | 180 | 400 | 20 | 160 | 0 | 4455 | 160 | #N/A | 4615 | 45 | 400 | 220 | 180 | -453 | 180 | 400
53.0303 | 50 | 220 | 220 | -448 | 180 | 400 | 20 | 160 | 0 | 4450 | 160 | #N/A | 4610 | 50 | 400 | 220 | 180 | -448 | 180 | 400
58.3333 | 55 | 220 | 220 | -443 | 180 | 400 | 20 | 160 | 0 | 4445 | 160 | #N/A | 4605 | 55 | 400 | 220 | 180 | -443 | 180 | 400
63.6364 | 60 | 220 | 220 | -438 | 180 | 400 | 20 | 160 | 0 | 4440 | 160 | #N/A | 4600 | 60 | 400 | 220 | 180 | -438 | 180 | 400
68.9394 | 65 | 220 | 220 | -433 | 180 | 400 | 20 | 160 | 0 | 4435 | 160 | #N/A | 4595 | 65 | 400 | 220 | 180 | -433 | 180 | 400
74.2424 | 70 | 220 | 220 | -428 | 180 | 400 | 20 | 160 | 0 | 4430 | 160 | #N/A | 4590 | 70 | 400 | 220 | 180 | -428 | 180 | 400
79.5455 | 75 | 220 | 220 | -423 | 180 | 400 | 20 | 160 | 0 | 4425 | 160 | #N/A | 4585 | 75 | 400 | 220 | 180 | -423 | 180 | 400
84.8485 | 80 | 220 | 220 | -418 | 180 | 400 | 20 | 160 | 0 | 4420 | 160 | #N/A | 4580 | 80 | 400 | 220 | 180 | -418 | 180 | 400
90.1515 | 85 | 220 | 220 | -413 | 180 | 400 | 20 | 160 | 0 | 4415 | 160 | #N/A | 4575 | 85 | 400 | 220 | 180 | -413 | 180 | 400
95.4545 | 90 | 220 | 220 | -408 | 180 | 400 | 20 | 160 | 0 | 4410 | 160 | #N/A | 4570 | 90 | 400 | 220 | 180 | -408 | 180 | 400
100.7576 | 95 | 220 | 220 | -403 | 180 | 400 | 20 | 160 | 0 | 4405 | 160 | #N/A | 4565 | 95 | 400 | 220 | 180 | -403 | 180 | 400
106.0606 | 100 | 220 | 220 | -398 | 180 | 400 | 20 | 160 | 0 | 4400 | 160 | #N/A | 4560 | 100 | 400 | 220 | 180 | -398 | 180 | 400
111.3636 | 105 | 220 | 220 | -393 | 180 | 400 | 20 | 160 | 0 | 4395 | 160 | #N/A | 4555 | 105 | 400 | 220 | 180 | -393 | 180 | 400
116.6667 | 110 | 220 | 220 | -388 | 180 | 400 | 20 | 160 | 0 | 4390 | 160 | #N/A | 4550 | 110 | 400 | 220 | 180 | -388 | 180 | 400
121.9697 | 115 | 220 | 220 | -383 | 180 | 400 | 20 | 160 | 0 | 4385 | 160 | #N/A | 4545 | 115 | 400 | 220 | 180 | -383 | 180 | 400
127.2727 | 120 | 220 | 220 | -378 | 180 | 400 | 20 | 160 | 0 | 4380 | 160 | #N/A | 4540 | 120 | 400 | 220 | 180 | -378 | 180 | 400
132.5758 | 125 | 220 | 220 | -373 | 180 | 400 | 20 | 160 | 0 | 4375 | 160 | #N/A | 4535 | 125 | 400 | 220 | 180 | -373 | 180 | 400
137.8788 | 130 | 220 | 220 | -368 | 180 | 400 | 20 | 160 | 0 | 4370 | 160 | #N/A | 4530 | 130 | 400 | 220 | 180 | -368 | 180 | 400
143.1818 | 135 | 220 | 220 | -363 | 180 | 400 | 20 | 160 | 0 | 4365 | 160 | #N/A | 4525 | 135 | 400 | 220 | 180 | -363 | 180 | 400
148.4848 | 140 | 220 | 220 | -358 | 180 | 400 | 20 | 160 | 0 | 4360 | 160 | #N/A | 4520 | 140 | 400 | 220 | 180 | -358 | 180 | 400
153.7879 | 145 | 220 | 220 | -353 | 180 | 400 | 20 | 160 | 0 | 4355 | 160 | #N/A | 4515 | 145 | 400 | 220 | 180 | -353 | 180 | 400
159.0909 | 150 | 220 | 220 | -348 | 180 | 400 | 20 | 160 | 0 | 4350 | 160 | #N/A | 4510 | 150 | 400 | 220 | 180 | -348 | 180 | 400
164.3939 | 155 | 220 | 220 | -343 | 180 | 400 | 20 | 160 | 0 | 4345 | 160 | #N/A | 4505 | 155 | 400 | 220 | 180 | -343 | 180 | 400
169.697 | 160 | 220 | 220 | -338 | 180 | 400 | 20 | 160 | 0 | 4340 | 160 | #N/A | 4500 | 160 | 400 | 220 | 180 | -338 | 180 | 400
175 | 165 | 220 | 220 | -333 | 180 | 400 | 20 | 160 | 0 | 4335 | 160 | #N/A | 4495 | 165 | 400 | 220 | 180 | -333 | 180 | 400
180.303 | 170 | 220 | 220 | -328 | 180 | 400 | 20 | 160 | 0 | 4330 | 160 | #N/A | 4490 | 170 | 400 | 220 | 180 | -328 | 180 | 400
185.6061 | 175 | 220 | 220 | -323 | 180 | 400 | 20 | 160 | 0 | 4325 | 160 | #N/A | 4485 | 175 | 400 | 220 | 180 | -323 | 180 | 400
190.9091 | 180 | 220 | 220 | -318 | 180 | 400 | 20 | 160 | 0 | 4320 | 160 | #N/A | 4480 | 180 | 400 | 220 | 180 | -318 | 180 | 400
196.2121 | 185 | 220 | 220 | -313 | 180 | 400 | 20 | 160 | 0 | 4315 | 160 | #N/A | 4475 | 185 | 400 | 220 | 180 | -313 | 180 | 400
201.5152 | 190 | 220 | 220 | -308 | 180 | 400 | 20 | 160 | 0 | 4310 | 160 | #N/A | 4470 | 190 | 400 | 220 | 180 | -308 | 180 | 400
206.8182 | 195 | 220 | 220 | -303 | 180 | 400 | 20 | 160 | 0 | 4305 | 160 | #N/A | 4465 | 195 | 400 | 220 | 180 | -303 | 180 | 400
212.1212 | 200 | 220 | 220 | -298 | 180 | 400 | 20 | 160 | 0 | 4300 | 160 | #N/A | 4460 | 200 | 400 | 220 | 180 | -298 | 180 | 400
217.4242 | 205 | 220 | 220 | -293 | 180 | 400 | 20 | 160 | 0 | 4295 | 160 | #N/A | 4455 | 205 | 400 | 220 | 180 | -293 | 180 | 400
222.7273 | 210 | 220 | 220 | -288 | 180 | 400 | 20 | 160 | 0 | 4290 | 160 | #N/A | 4450 | 210 | 400 | 220 | 180 | -288 | 180 | 400
228.0303 | 215 | 220 | 220 | -283 | 180 | 400 | 20 | 160 | 0 | 4285 | 160 | #N/A | 4445 | 215 | 400 | 220 | 180 | -283 | 180 | 400
233.3333 | 220 | 220 | 220 | -278 | 180 | 400 | 20 | 160 | 0 | 4280 | 160 | #N/A | 4440 | 220 | 400 | 220 | 180 | -278 | 180 | 400
238.6364 | 225 | 220 | 220 | -273 | 180 | 400 | 20 | 160 | 0 | 4275 | 160 | #N/A | 4435 | 225 | 400 | 220 | 180 | -273 | 180 | 400
243.9394 | 230 | 220 | 220 | -268 | 180 | 400 | 20 | 160 | 0 | 4270 | 160 | #N/A | 4430 | 230 | 400 | 220 | 180 | -268 | 180 | 400
249.2424 | 235 | 220 | 220 | -263 | 180 | 400 | 20 | 160 | 0 | 4265 | 160 | #N/A | 4425 | 235 | 400 | 220 | 180 | -263 | 180 | 400
254.5455 | 240 | 220 | 220 | -258 | 180 | 400 | 20 | 160 | 0 | 4260 | 160 | #N/A | 4420 | 240 | 400 | 220 | 180 | -258 | 180 | 400
259.8485 | 245 | 220 | 220 | -253 | 180 | 400 | 20 | 160 | 0 | 4255 | 160 | #N/A | 4415 | 245 | 400 | 220 | 180 | -253 | 180 | 400
265.1515 | 250 | 220 | 220 | -248 | 180 | 400 | 20 | 160 | 0 | 4250 | 160 | #N/A | 4410 | 250 | 400 | 220 | 180 | -248 | 180 | 400
270.4545 | 255 | 220 | 220 | -243 | 180 | 400 | 20 | 160 | 0 | 4245 | 160 | #N/A | 4405 | 255 | 400 | 220 | 180 | -243 | 180 | 400
275.7576 | 260 | 220 | 220 | -238 | 180 | 400 | 20 | 160 | 0 | 4240 | 160 | #N/A | 4400 | 260 | 400 | 220 | 180 | -238 | 180 | 400
281.0606 | 265 | 220 | 220 | -233 | 180 | 400 | 20 | 160 | 0 | 4235 | 160 | #N/A | 4395 | 265 | 400 | 220 | 180 | -233 | 180 | 400
286.3636 | 270 | 220 | 220 | -228 | 180 | 400 | 20 | 160 | 0 | 4230 | 160 | #N/A | 4390 | 270 | 400 | 220 | 180 | -228 | 180 | 400
291.6667 | 275 | 220 | 220 | -223 | 180 | 400 | 20 | 160 | 0 | 4225 | 160 | #N/A | 4385 | 275 | 400 | 220 | 180 | -223 | 180 | 400
296.9697 | 280 | 220 | 220 | -218 | 180 | 400 | 20 | 160 | 0 | 4220 | 160 | #N/A | 4380 | 280 | 400 | 220 | 180 | -218 | 180 | 400
302.2727 | 285 | 220 | 220 | -213 | 180 | 400 | 20 | 160 | 0 | 4215 | 160 | #N/A | 4375 | 285 | 400 | 220 | 180 | -213 | 180 | 400
307.5758 | 290 | 220 | 220 | -208 | 180 | 400 | 20 | 160 | 0 | 4210 | 160 | #N/A | 4370 | 290 | 400 | 220 | 180 | -208 | 180 | 400
312.8788 | 295 | 220 | 220 | -203 | 180 | 400 | 20 | 160 | 0 | 4205 | 160 | #N/A | 4365 | 295 | 400 | 220 | 180 | -203 | 180 | 400
318.1818 | 300 | 220 | 220 | -198 | 180 | 400 | 20 | 160 | 0 | 4200 | 160 | #N/A | 4360 | 300 | 400 | 220 | 180 | -198 | 180 | 400
323.4848 | 305 | 220 | 220 | -193 | 180 | 400 | 20 | 160 | 0 | 4195 | 160 | #N/A | 4355 | 305 | 400 | 220 | 180 | -193 | 180 | 400
328.7879 | 310 | 220 | 220 | -188 | 180 | 400 | 20 | 160 | 0 | 4190 | 160 | #N/A | 4350 | 310 | 400 | 220 | 180 | -188 | 180 | 400
334.0909 | 315 | 220 | 220 | -183 | 180 | 400 | 20 | 160 | 0 | 4185 | 160 | #N/A | 4345 | 315 | 400 | 220 | 180 | -183 | 180 | 400
339.3939 | 320 | 220 | 220 | -178 | 180 | 400 | 20 | 160 | 0 | 4180 | 160 | #N/A | 4340 | 320 | 400 | 220 | 180 | -178 | 180 | 400
344.697 | 325 | 220 | 220 | -173 | 180 | 400 | 20 | 160 | 0 | 4175 | 160 | #N/A | 4335 | 325 | 400 | 220 | 180 | -173 | 180 | 400
350 | 330 | 220 | 220 | -168 | 180 | 400 | 20 | 160 | 0 | 4170 | 160 | #N/A | 4330 | 330 | 400 | 220 | 180 | -168 | 180 | 400
355.303 | 335 | 220 | 220 | -163 | 180 | 400 | 20 | 160 | 0 | 4165 | 160 | #N/A | 4325 | 335 | 400 | 220 | 180 | -163 | 180 | 400
360.6061 | 340 | 220 | 220 | -158 | 180 | 400 | 20 | 160 | 0 | 4160 | 160 | #N/A | 4320 | 340 | 400 | 220 | 180 | -158 | 180 | 400
365.9091 | 345 | 220 | 220 | -153 | 180 | 400 | 20 | 160 | 0 | 4155 | 160 | #N/A | 4315 | 345 | 400 | 220 | 180 | -153 | 180 | 400
371.2121 | 350 | 220 | 220 | -148 | 180 | 400 | 20 | 160 | 0 | 4150 | 160 | #N/A | 4310 | 350 | 400 | 220 | 180 | -148 | 180 | 400
376.5152 | 355 | 220 | 220 | -143 | 180 | 400 | 20 | 160 | 0 | 4145 | 160 | #N/A | 4305 | 355 | 400 | 220 | 180 | -143 | 180 | 400
381.8182 | 360 | 220 | 220 | -138 | 180 | 400 | 20 | 160 | 0 | 4140 | 160 | #N/A | 4300 | 360 | 400 | 220 | 180 | -138 | 180 | 400
387.1212 | 365 | 220 | 220 | -133 | 180 | 400 | 20 | 160 | 0 | 4135 | 160 | #N/A | 4295 | 365 | 400 | 220 | 180 | -133 | 180 | 400
392.4242 | 370 | 220 | 220 | -128 | 180 | 400 | 20 | 160 | 0 | 4130 | 160 | #N/A | 4290 | 370 | 400 | 220 | 180 | -128 | 180 | 400
397.7273 | 375 | 220 | 220 | -123 | 180 | 400 | 20 | 160 | 0 | 4125 | 160 | #N/A | 4285 | 375 | 400 | 220 | 180 | -123 | 180 | 400
403.0303 | 380 | 220 | 220 | -118 | 180 | 400 | 20 | 160 | 0 | 4120 | 160 | #N/A | 4280 | 380 | 400 | 220 | 180 | -118 | 180 | 400
408.3333 | 385 | 220 | 220 | -113 | 180 | 400 | 20 | 160 | 0 | 4115 | 160 | #N/A | 4275 | 385 | 400 | 220 | 180 | -113 | 180 | 400
413.6364 | 390 | 220 | 220 | -108 | 180 | 400 | 20 | 160 | 0 | 4110 | 160 | #N/A | 4270 | 390 | 400 | 220 | 180 | -108 | 180 | 400
418.9394 | 395 | 220 | 220 | -103 | 180 | 400 | 20 | 160 | 0 | 4105 | 160 | #N/A | 4265 | 395 | 400 | 220 | 180 | -103 | 180 | 400
424.2424 | 400 | 220 | 220 | -98 | 180 | 400 | 20 | 160 | 0 | 4100 | 160 | #N/A | 4260 | 400 | 400 | 220 | 180 | -98 | 180 | 400
429.5455 | 405 | 220 | 220 | -93 | 180 | 400 | 20 | 160 | 0 | 4095 | 160 | #N/A | 4255 | 405 | 400 | 220 | 180 | -93 | 180 | 400
434.8485 | 410 | 220 | 220 | -88 | 180 | 400 | 20 | 160 | 0 | 4090 | 160 | #N/A | 4250 | 410 | 400 | 220 | 180 | -88 | 180 | 400
440.1515 | 415 | 220 | 220 | -83 | 180 | 400 | 20 | 160 | 0 | 4085 | 160 | #N/A | 4245 | 415 | 400 | 220 | 180 | -83 | 180 | 400
445.4545 | 420 | 220 | 220 | -78 | 180 | 400 | 20 | 160 | 0 | 4080 | 160 | #N/A | 4240 | 420 | 400 | 220 | 180 | -78 | 180 | 400
450.7576 | 425 | 220 | 220 | -73 | 180 | 400 | 20 | 160 | 0 | 4075 | 160 | #N/A | 4235 | 425 | 400 | 220 | 180 | -73 | 180 | 400
456.0606 | 430 | 220 | 220 | -68 | 180 | 400 | 20 | 160 | 0 | 4070 | 160 | #N/A | 4230 | 430 | 400 | 220 | 180 | -68 | 180 | 400
461.3636 | 435 | 220 | 220 | -63 | 180 | 400 | 20 | 160 | 0 | 4065 | 160 | #N/A | 4225 | 435 | 400 | 220 | 180 | -63 | 180 | 400
466.6667 | 440 | 220 | 220 | -58 | 180 | 400 | 20 | 160 | 0 | 4060 | 160 | #N/A | 4220 | 440 | 400 | 220 | 180 | -58 | 180 | 400
471.9697 | 445 | 220 | 220 | -53 | 180 | 400 | 20 | 160 | 0 | 4055 | 160 | #N/A | 4215 | 445 | 400 | 220 | 180 | -53 | 180 | 400
477.2727 | 450 | 220 | 220 | -48 | 180 | 400 | 20 | 160 | 0 | 4050 | 160 | #N/A | 4210 | 450 | 400 | 220 | 180 | -48 | 180 | 400
482.5758 | 455 | 220 | 220 | -43 | 180 | 400 | 20 | 160 | 0 | 4045 | 160 | #N/A | 4205 | 455 | 400 | 220 | 180 | -43 | 180 | 400
487.8788 | 460 | 220 | 220 | -38 | 180 | 400 | 20 | 160 | 0 | 4040 | 160 | #N/A | 4200 | 460 | 400 | 220 | 180 | -38 | 180 | 400
493.1818 | 465 | 220 | 220 | -33 | 180 | 400 | 20 | 160 | 0 | 4035 | 160 | #N/A | 4195 | 465 | 400 | 220 | 180 | -33 | 180 | 400
498.4848 | 470 | 220 | 220 | -28 | 180 | 400 | 20 | 160 | 0 | 4030 | 160 | #N/A | 4190 | 470 | 400 | 220 | 180 | -28 | 180 | 400
503.7879 | 475 | 220 | 220 | -23 | 180 | 400 | 20 | 160 | 0 | 4025 | 160 | #N/A | 4185 | 475 | 400 | 220 | 180 | -23 | 180 | 400
509.0909 | 480 | 220 | 220 | -18 | 180 | 400 | 20 | 160 | 0 | 4020 | 160 | #N/A | 4180 | 480 | 400 | 220 | 180 | -18 | 180 | 400
514.3939 | 485 | 220 | 220 | -13 | 180 | 400 | 20 | 160 | 0 | 4015 | 160 | #N/A | 4175 | 485 | 400 | 220 | 180 | -13 | 180 | 400
519.697 | 490 | 220 | 220 | -8 | 180 | 400 | 20 | 160 | 0 | 4010 | 160 | #N/A | 4170 | 490 | 400 | 220 | 180 | -8 | 180 | 400
525 | 495 | 220 | 220 | -3 | 180 | 400 | 20 | 160 | 0 | 4005 | 160 | #N/A | 4165 | 495 | 400 | 220 | 180 | -3 | 180 | 400
530.303 | 500 | 220 | 220 | 2 | 180 | 400 | 20 | 160 | 0 | 4000 | 160 | #N/A | 4160 | 500 | 400 | 220 | 180 | 2 | 180 | 400
535.6061 | 505 | 220 | 220 | 7 | 180 | 400 | 20 | 160 | 0 | 3995 | 160 | #N/A | 4155 | 505 | 400 | 220 | 180 | 7 | 180 | 400
540.9091 | 510 | 220 | 220 | 12 | 180 | 400 | 20 | 160 | 0 | 3990 | 160 | #N/A | 4150 | 510 | 400 | 220 | 180 | 12 | 180 | 400
546.2121 | 515 | 220 | 220 | 17 | 180 | 400 | 20 | 160 | 0 | 3985 | 160 | #N/A | 4145 | 515 | 400 | 220 | 180 | 17 | 180 | 400
551.5152 | 520 | 220 | 220 | 22 | 180 | 400 | 20 | 160 | 0 | 3980 | 160 | #N/A | 4140 | 520 | 400 | 220 | 180 | 22 | 180 | 400
556.8182 | 525 | 220 | 220 | 27 | 180 | 400 | 20 | 160 | 0 | 3975 | 160 | #N/A | 4135 | 525 | 400 | 220 | 180 | 27 | 180 | 400
562.1212 | 530 | 220 | 220 | 32 | 180 | 400 | 20 | 160 | 0 | 3970 | 160 | #N/A | 4130 | 530 | 400 | 220 | 180 | 32 | 180 | 400
567.4242 | 535 | 220 | 220 | 37 | 180 | 400 | 20 | 160 | 0 | 3965 | 160 | #N/A | 4125 | 535 | 400 | 220 | 180 | 37 | 180 | 400
572.7273 | 540 | 220 | 220 | 42 | 180 | 400 | 20 | 160 | 0 | 3960 | 160 | #N/A | 4120 | 540 | 400 | 220 | 180 | 42 | 180 | 400
578.0303 | 545 | 220 | 220 | 47 | 180 | 400 | 20 | 160 | 0 | 3955 | 160 | #N/A | 4115 | 545 | 400 | 220 | 180 | 47 | 180 | 400
583.3333 | 550 | 220 | 220 | 52 | 180 | 400 | 20 | 160 | 0 | 3950 | 160 | #N/A | 4110 | 550 | 400 | 220 | 180 | 52 | 180 | 400
588.6364 | 555 | 220 | 220 | 57 | 180 | 400 | 20 | 160 | 0 | 3945 | 160 | #N/A | 4105 | 555 | 400 | 220 | 180 | 57 | 180 | 400
593.9394 | 560 | 220 | 220 | 62 | 180 | 400 | 20 | 160 | 0 | 3940 | 160 | #N/A | 4100 | 560 | 400 | 220 | 180 | 62 | 180 | 400
599.2424 | 565 | 220 | 220 | 67 | 180 | 400 | 20 | 160 | 0 | 3935 | 160 | #N/A | 4095 | 565 | 400 | 220 | 180 | 67 | 180 | 400
604.5455 | 570 | 220 | 220 | 72 | 180 | 400 | 20 | 160 | 0 | 3930 | 160 | #N/A | 4090 | 570 | 400 | 220 | 180 | 72 | 180 | 400
609.8485 | 575 | 220 | 220 | 77 | 180 | 400 | 20 | 160 | 0 | 3925 | 160 | #N/A | 4085 | 575 | 400 | 220 | 180 | 77 | 180 | 400
615.1515 | 580 | 220 | 220 | 82 | 180 | 400 | 20 | 160 | 0 | 3920 | 160 | #N/A | 4080 | 580 | 400 | 220 | 180 | 82 | 180 | 400
620.4545 | 585 | 220 | 220 | 87 | 180 | 400 | 20 | 160 | 0 | 3915 | 160 | #N/A | 4075 | 585 | 400 | 220 | 180 | 87 | 180 | 400
625.7576 | 590 | 220 | 220 | 92 | 180 | 400 | 20 | 160 | 0 | 3910 | 160 | #N/A | 4070 | 590 | 400 | 220 | 180 | 92 | 180 | 400
631.0606 | 595 | 220 | 220 | 97 | 180 | 400 | 20 | 160 | 0 | 3905 | 160 | #N/A | 4065 | 595 | 400 | 220 | 180 | 97 | 180 | 400
636.3636 | 600 | 220 | 220 | 102 | 180 | 400 | 20 | 160 | 0 | 3900 | 160 | #N/A | 4060 | 600 | 400 | 220 | 180 | 102 | 180 | 400
641.6667 | 605 | 220 | 220 | 107 | 180 | 400 | 20 | 160 | 0 | 3895 | 160 | #N/A | 4055 | 605 | 400 | 220 | 180 | 107 | 180 | 400
646.9697 | 610 | 220 | 220 | 112 | 180 | 400 | 20 | 160 | 0 | 3890 | 160 | #N/A | 4050 | 610 | 400 | 220 | 180 | 112 | 180 | 400
652.2727 | 615 | 220 | 220 | 117 | 180 | 400 | 20 | 160 | 0 | 3885 | 160 | #N/A | 4045 | 615 | 400 | 220 | 180 | 117 | 180 | 400
657.5758 | 620 | 220 | 220 | 122 | 180 | 400 | 20 | 160 | 0 | 3880 | 160 | #N/A | 4040 | 620 | 400 | 220 | 180 | 122 | 180 | 400
662.8788 | 625 | 220 | 220 | 127 | 180 | 400 | 20 | 160 | 0 | 3875 | 160 | #N/A | 4035 | 625 | 400 | 220 | 180 | 127 | 180 | 400
668.1818 | 630 | 220 | 220 | 132 | 180 | 400 | 20 | 160 | 0 | 3870 | 160 | #N/A | 4030 | 630 | 400 | 220 | 180 | 132 | 180 | 400
673.4848 | 635 | 220 | 220 | 137 | 180 | 400 | 20 | 160 | 0 | 3865 | 160 | #N/A | 4025 | 635 | 400 | 220 | 180 | 137 | 180 | 400
678.7879 | 640 | 220 | 220 | 142 | 180 | 400 | 20 | 160 | 0 | 3860 | 160 | #N/A | 4020 | 640 | 400 | 220 | 180 | 142 | 180 | 400
684.0909 | 645 | 220 | 220 | 147 | 180 | 400 | 20 | 160 | 0 | 3855 | 160 | #N/A | 4015 | 645 | 400 | 220 | 180 | 147 | 180 | 400
689.3939 | 650 | 220 | 220 | 152 | 180 | 400 | 20 | 160 | 0 | 3850 | 160 | #N/A | 4010 | 650 | 400 | 220 | 180 | 152 | 180 | 400
694.697 | 655 | 220 | 220 | 157 | 180 | 400 | 20 | 160 | 0 | 3845 | 160 | #N/A | 4005 | 655 | 400 | 220 | 180 | 157 | 180 | 400
700 | 660 | 220 | 220 | 162 | 180 | 400 | 20 | 160 | 0 | 3840 | 160 | #N/A | 4000 | 660 | 400 | 220 | 180 | 162 | 180 | 400
705.303 | 665 | 220 | 220 | 167 | 180 | 400 | 20 | 160 | 0 | 3835 | 160 | #N/A | 3995 | 665 | 400 | 220 | 180 | 167 | 180 | 400
710.6061 | 670 | 220 | 220 | 172 | 180 | 400 | 20 | 160 | 0 | 3830 | 160 | #N/A | 3990 | 670 | 400 | 220 | 180 | 172 | 180 | 400
715.9091 | 675 | 220 | 220 | 177 | 180 | 400 | 20 | 160 | 0 | 3825 | 160 | #N/A | 3985 | 675 | 400 | 220 | 180 | 177 | 180 | 400
721.2121 | 680 | 220 | 220 | 182 | 180 | 400 | 20 | 162 | 2 | 3820 | 162 | #N/A | 3982 | 680 | 400 | 220 | 180 | 182 | 182 | 400
726.5152 | 685 | 220 | 220 | 187 | 180 | 400 | 20 | 167 | 5 | 3815 | 167 | #N/A | 3982 | 685 | 400 | 220 | 180 | 187 | 187 | 400
731.8182 | 690 | 220 | 220 | 192 | 180 | 400 | 20 | 172 | 5 | 3810 | 172 | #N/A | 3982 | 690 | 400 | 220 | 180 | 192 | 192 | 400
737.1212 | 695 | 220 | 220 | 197 | 180 | 400 | 20 | 177 | 5 | 3805 | 177 | #N/A | 3982 | 695 | 400 | 220 | 180 | 197 | 197 | 400
742.4242 | 700 | 220 | 220 | 202 | 180 | 400 | 20 | 182 | 5 | 3800 | 182 | #N/A | 3982 | 700 | 400 | 220 | 180 | 202 | 202 | 400
747.7273 | 705 | 220 | 220 | 207 | 180 | 400 | 20 | 187 | 5 | 3795 | 187 | #N/A | 3982 | 705 | 400 | 220 | 180 | 207 | 207 | 400
753.0303 | 710 | 220 | 220 | 212 | 180 | 400 | 20 | 192 | 5 | 3790 | 192 | #N/A | 3982 | 710 | 400 | 220 | 180 | 212 | 212 | 400
758.3333 | 715 | 220 | 220 | 217 | 180 | 400 | 20 | 197 | 5 | 3785 | 197 | #N/A | 3982 | 715 | 400 | 220 | 180 | 217 | 217 | 400
763.6364 | 720 | 220 | 220 | 222 | 180 | 400 | 20 | 202 | 5 | 3780 | 202 | #N/A | 3982 | 720 | 400 | 220 | 180 | 222 | 222 | 400
768.9394 | 725 | 220 | 220 | 227 | 180 | 400 | 20 | 207 | 5 | 3775 | 207 | #N/A | 3982 | 725 | 400 | 220 | 180 | 227 | 227 | 400
774.2424 | 730 | 220 | 220 | 232 | 180 | 400 | 20 | 212 | 5 | 3770 | 212 | #N/A | 3982 | 730 | 400 | 220 | 180 | 232 | 232 | 400
779.5455 | 735 | 220 | 220 | 237 | 180 | 400 | 20 | 217 | 5 | 3765 | 217 | #N/A | 3982 | 735 | 400 | 220 | 180 | 237 | 237 | 400
784.8485 | 740 | 220 | 220 | 242 | 180 | 400 | 20 | 222 | 5 | 3760 | 222 | #N/A | 3982 | 740 | 400 | 220 | 180 | 242 | 242 | 400
790.1515 | 745 | 220 | 220 | 247 | 180 | 400 | 20 | 227 | 5 | 3755 | 227 | #N/A | 3982 | 745 | 400 | 220 | 180 | 247 | 247 | 400
795.4545 | 750 | 220 | 220 | 252 | 180 | 400 | 20 | 232 | 5 | 3750 | 232 | #N/A | 3982 | 750 | 400 | 220 | 180 | 252 | 252 | 400
800.7576 | 755 | 220 | 220 | 257 | 180 | 400 | 20 | 237 | 5 | 3745 | 237 | #N/A | 3982 | 755 | 400 | 220 | 180 | 257 | 257 | 400
806.0606 | 760 | 220 | 220 | 262 | 180 | 400 | 20 | 242 | 5 | 3740 | 242 | #N/A | 3982 | 760 | 400 | 220 | 180 | 262 | 262 | 400
811.3636 | 765 | 220 | 220 | 267 | 180 | 400 | 20 | 247 | 5 | 3735 | 247 | #N/A | 3982 | 765 | 400 | 220 | 180 | 267 | 267 | 400
816.6667 | 770 | 220 | 220 | 272 | 180 | 400 | 20 | 252 | 5 | 3730 | 252 | #N/A | 3982 | 770 | 400 | 220 | 180 | 272 | 272 | 400
821.9697 | 775 | 220 | 220 | 277 | 180 | 400 | 20 | 257 | 5 | 3725 | 257 | #N/A | 3982 | 775 | 400 | 220 | 180 | 277 | 277 | 400
827.2727 | 780 | 220 | 220 | 282 | 180 | 400 | 20 | 262 | 5 | 3720 | 262 | #N/A | 3982 | 780 | 400 | 220 | 180 | 282 | 282 | 400
832.5758 | 785 | 220 | 220 | 287 | 180 | 400 | 20 | 267 | 5 | 3715 | 267 | #N/A | 3982 | 785 | 400 | 220 | 180 | 287 | 287 | 400
837.8788 | 790 | 220 | 220 | 292 | 180 | 400 | 20 | 272 | 5 | 3710 | 272 | #N/A | 3982 | 790 | 400 | 220 | 180 | 292 | 292 | 400
843.1818 | 795 | 220 | 220 | 297 | 180 | 400 | 20 | 277 | 5 | 3705 | 277 | #N/A | 3982 | 795 | 400 | 220 | 180 | 297 | 297 | 400
848.4848 | 800 | 220 | 220 | 302 | 180 | 400 | 20 | 282 | 5 | 3700 | 282 | #N/A | 3982 | 800 | 400 | 220 | 180 | 302 | 302 | 400
853.7879 | 805 | 220 | 220 | 307 | 180 | 400 | 20 | 287 | 5 | 3695 | 287 | #N/A | 3982 | 805 | 400 | 220 | 180 | 307 | 307 | 400
859.0909 | 810 | 220 | 220 | 312 | 180 | 400 | 20 | 292 | 5 | 3690 | 292 | #N/A | 3982 | 810 | 400 | 220 | 180 | 312 | 312 | 400
864.3939 | 815 | 220 | 220 | 317 | 180 | 400 | 20 | 297 | 5 | 3685 | 297 | #N/A | 3982 | 815 | 400 | 220 | 180 | 317 | 317 | 400
869.697 | 820 | 220 | 220 | 322 | 180 | 400 | 20 | 302 | 5 | 3680 | 302 | #N/A | 3982 | 820 | 400 | 220 | 180 | 322 | 322 | 400
875 | 825 | 220 | 220 | 327 | 180 | 400 | 20 | 307 | 5 | 3675 | 307 | #N/A | 3982 | 825 | 400 | 220 | 180 | 327 | 327 | 400
880.303 | 830 | 220 | 220 | 332 | 180 | 400 | 20 | 312 | 5 | 3670 | 312 | #N/A | 3982 | 830 | 400 | 220 | 180 | 332 | 332 | 400
885.6061 | 835 | 220 | 220 | 337 | 180 | 400 | 20 | 317 | 5 | 3665 | 317 | #N/A | 3982 | 835 | 400 | 220 | 180 | 337 | 337 | 400
890.9091 | 840 | 220 | 220 | 342 | 180 | 400 | 20 | 322 | 5 | 3660 | 322 | #N/A | 3982 | 840 | 400 | 220 | 180 | 342 | 342 | 400
896.2121 | 845 | 220 | 220 | 347 | 180 | 400 | 20 | 327 | 5 | 3655 | 327 | #N/A | 3982 | 845 | 400 | 220 | 180 | 347 | 347 | 400
901.5152 | 850 | 220 | 220 | 352 | 180 | 400 | 20 | 332 | 5 | 3650 | 332 | #N/A | 3982 | 850 | 400 | 220 | 180 | 352 | 352 | 400
906.8182 | 855 | 220 | 220 | 357 | 180 | 400 | 20 | 337 | 5 | 3645 | 337 | #N/A | 3982 | 855 | 400 | 220 | 180 | 357 | 357 | 400
912.1212 | 860 | 220 | 220 | 362 | 180 | 400 | 20 | 342 | 5 | 3640 | 342 | #N/A | 3982 | 860 | 400 | 220 | 180 | 362 | 362 | 400
917.4242 | 865 | 220 | 220 | 367 | 180 | 400 | 20 | 347 | 5 | 3635 | 347 | #N/A | 3982 | 865 | 400 | 220 | 180 | 367 | 367 | 400
922.7273 | 870 | 220 | 220 | 372 | 180 | 400 | 20 | 352 | 5 | 3630 | 352 | #N/A | 3982 | 870 | 400 | 220 | 180 | 372 | 372 | 400
928.0303 | 875 | 220 | 220 | 377 | 180 | 400 | 20 | 357 | 5 | 3625 | 357 | #N/A | 3982 | 875 | 400 | 220 | 180 | 377 | 377 | 400
933.3333 | 880 | 220 | 220 | 382 | 180 | 400 | 20 | 362 | 5 | 3620 | 362 | #N/A | 3982 | 880 | 400 | 220 | 180 | 382 | 382 | 400
938.6364 | 885 | 216.4286 | 216.4286 | 387 | 183.5714 | 400 | 20 | 367 | 5 | 3615 | 367 | #N/A | 3982 | 885 | 400 | 216.4286 | 183.5714 | 387 | 387 | 400
943.9394 | 890 | 211.4286 | 211.4286 | 392 | 188.5714 | 400 | 20 | 372 | 5 | 3610 | 372 | #N/A | 3982 | 890 | 400 | 211.4286 | 188.5714 | 392 | 392 | 400
949.2424 | 895 | 206.4286 | 206.4286 | 397 | 193.5714 | 400 | 20 | 377 | 5 | 3605 | 377 | #N/A | 3982 | 895 | 400 | 206.4286 | 193.5714 | 397 | 397 | 400
954.5455 | 900 | 201.4286 | 201.4286 | 402 | 198.5714 | 400 | 20 | 382 | 5 | 3600 | 382 | #N/A | 3982 | 900 | 400 | 201.4286 | 198.5714 | 402 | 402 | 402
959.8485 | 905 | 196.4286 | 196.4286 | 407 | 203.5714 | 400 | 20 | 387 | 5 | 3595 | 387 | #N/A | 3982 | 905 | 400 | 196.4286 | 203.5714 | 407 | 407 | 407
965.1515 | 910 | 191.4286 | 191.4286 | 412 | 208.5714 | 400 | 20 | 392 | 5 | 3590 | 392 | #N/A | 3982 | 910 | 400 | 191.4286 | 208.5714 | 412 | 412 | 412
970.4545 | 915 | 186.4286 | 186.4286 | 417 | 213.5714 | 400 | 20 | 397 | 5 | 3585 | 397 | #N/A | 3982 | 915 | 400 | 186.4286 | 213.5714 | 417 | 417 | 417
975.7576 | 920 | 181.4286 | 181.4286 | 422 | 218.5714 | 400 | 20 | 402 | 5 | 3580 | 402 | #N/A | 3982 | 920 | 400 | 181.4286 | 218.5714 | 422 | 422 | 422
981.0606 | 925 | 176.4286 | 176.4286 | 427 | 223.5714 | 400 | 20 | 407 | 5 | 3575 | 407 | #N/A | 3982 | 925 | 400 | 176.4286 | 223.5714 | 427 | 427 | 427
986.3636 | 930 | 171.4286 | 171.4286 | 432 | 228.5714 | 400 | 20 | 412 | 5 | 3570 | 412 | #N/A | 3982 | 930 | 400 | 171.4286 | 228.5714 | 432 | 432 | 432
991.6667 | 935 | 166.4286 | 166.4286 | 437 | 233.5714 | 400 | 20 | 417 | 5 | 3565 | 417 | #N/A | 3982 | 935 | 400 | 166.4286 | 233.5714 | 437 | 437 | 437
996.9697 | 940 | 161.4286 | 161.4286 | 442 | 238.5714 | 400 | 20 | 422 | 5 | 3560 | 422 | #N/A | 3982 | 940 | 400 | 161.4286 | 238.5714 | 442 | 442 | 442
1002.2727 | 945 | 156.4286 | 156.4286 | 447 | 243.5714 | 400 | 20 | 427 | 5 | 3555 | 427 | #N/A | 3982 | 945 | 400 | 156.4286 | 243.5714 | 447 | 447 | 447
1007.5758 | 950 | 151.4286 | 151.4286 | 452 | 248.5714 | 400 | 20 | 432 | 5 | 3550 | 432 | #N/A | 3982 | 950 | 400 | 151.4286 | 248.5714 | 452 | 452 | 452
1012.8788 | 955 | 146.4286 | 146.4286 | 457 | 253.5714 | 400 | 20 | 437 | 5 | 3545 | 437 | #N/A | 3982 | 955 | 400 | 146.4286 | 253.5714 | 457 | 457 | 457
1018.1818 | 960 | 141.4286 | 141.4286 | 462 | 258.5714 | 400 | 20 | 442 | 5 | 3540 | 442 | #N/A | 3982 | 960 | 400 | 141.4286 | 258.5714 | 462 | 462 | 462
1023.4848 | 965 | 136.4286 | 136.4286 | 467 | 263.5714 | 400 | 20 | 447 | 5 | 3535 | 447 | #N/A | 3982 | 965 | 400 | 136.4286 | 263.5714 | 467 | 467 | 467
1028.7879 | 970 | 131.4286 | 131.4286 | 472 | 268.5714 | 400 | 20 | 452 | 5 | 3530 | 452 | #N/A | 3982 | 970 | 400 | 131.4286 | 268.5714 | 472 | 472 | 472
1034.0909 | 975 | 126.4286 | 126.4286 | 477 | 273.5714 | 400 | 20 | 457 | 5 | 3525 | 457 | #N/A | 3982 | 975 | 400 | 126.4286 | 273.5714 | 477 | 477 | 477
1039.3939 | 980 | 121.4286 | 121.4286 | 482 | 278.5714 | 400 | 20 | 462 | 5 | 3520 | 462 | #N/A | 3982 | 980 | 400 | 121.4286 | 278.5714 | 482 | 482 | 482
1044.697 | 985 | 116.4286 | 116.4286 | 487 | 283.5714 | 400 | 20 | 467 | 5 | 3515 | 467 | #N/A | 3982 | 985 | 400 | 116.4286 | 283.5714 | 487 | 487 | 487
1050 | 990 | 111.4286 | 111.4286 | 492 | 288.5714 | 400 | 20 | 472 | 5 | 3510 | 472 | #N/A | 3982 | 990 | 400 | 111.4286 | 288.5714 | 492 | 492 | 492
1055.303 | 995 | 106.4286 | 106.4286 | 497 | 293.5714 | 400 | 20 | 477 | 5 | 3505 | 477 | #N/A | 3982 | 995 | 400 | 106.4286 | 293.5714 | 497 | 497 | 497
1060.6061 | 1000 | 101.4286 | 101.4286 | 502 | 298.5714 | 400 | 20 | 482 | 5 | 3500 | 482 | #N/A | 3982 | 1000 | 400 | 101.4286 | 298.5714 | 502 | 502 | 502
1065.9091 | 1005 | 96.4286 | 96.4286 | 507 | 303.5714 | 400 | 20 | 487 | 5 | 3495 | 487 | #N/A | 3982 | 1005 | 400 | 96.4286 | 303.5714 | 507 | 507 | 507
1071.2121 | 1010 | 91.4286 | 91.4286 | 512 | 308.5714 | 400 | 20 | 492 | 5 | 3490 | 492 | #N/A | 3982 | 1010 | 400 | 91.4286 | 308.5714 | 512 | 512 | 512
1076.5152 | 1015 | 86.4286 | 86.4286 | 517 | 313.5714 | 400 | 20 | 497 | 5 | 3485 | 497 | #N/A | 3982 | 1015 | 400 | 86.4286 | 313.5714 | 517 | 517 | 517
1081.8182 | 1020 | 81.4286 | 81.4286 | 522 | 318.5714 | 400 | 20 | 502 | 5 | 3480 | 502 | #N/A | 3982 | 1020 | 400 | 81.4286 | 318.5714 | 522 | 522 | 522
1087.1212 | 1025 | 76.4286 | 76.4286 | 527 | 323.5714 | 400 | 20 | 507 | 5 | 3475 | 507 | #N/A | 3982 | 1025 | 400 | 76.4286 | 323.5714 | 527 | 527 | 527
1092.4242 | 1030 | 71.4286 | 71.4286 | 532 | 328.5714 | 400 | 20 | 512 | 5 | 3470 | 512 | #N/A | 3982 | 1030 | 400 | 71.4286 | 328.5714 | 532 | 532 | 532
1097.7273 | 1035 | 66.4286 | 66.4286 | 537 | 333.5714 | 400 | 20 | 517 | 5 | 3465 | 517 | #N/A | 3982 | 1035 | 400 | 66.4286 | 333.5714 | 537 | 537 | 537
1103.0303 | 1040 | 61.4286 | 61.4286 | 542 | 338.5714 | 400 | 20 | 522 | 5 | 3460 | 522 | #N/A | 3982 | 1040 | 400 | 61.4286 | 338.5714 | 542 | 542 | 542
1108.3333 | 1045 | 56.4286 | 56.4286 | 547 | 343.5714 | 400 | 20 | 527 | 5 | 3455 | 527 | #N/A | 3982 | 1045 | 400 | 56.4286 | 343.5714 | 547 | 547 | 547
1113.6364 | 1050 | 51.4286 | 51.4286 | 552 | 348.5714 | 400 | 20 | 532 | 5 | 3450 | 532 | #N/A | 3982 | 1050 | 400 | 51.4286 | 348.5714 | 552 | 552 | 552
1118.9394 | 1055 | 46.4286 | 46.4286 | 557 | 353.5714 | 400 | 20 | 537 | 5 | 3445 | 537 | #N/A | 3982 | 1055 | 400 | 46.4286 | 353.5714 | 557 | 557 | 557
1124.2424 | 1060 | 41.4286 | 41.4286 | 562 | 358.5714 | 400 | 20 | 542 | 5 | 3440 | 542 | #N/A | 3982 | 1060 | 400 | 41.4286 | 358.5714 | 562 | 562 | 562
1129.5455 | 1065 | 36.4286 | 36.4286 | 567 | 363.5714 | 400 | 20 | 547 | 5 | 3435 | 547 | #N/A | 3982 | 1065 | 400 | 36.4286 | 363.5714 | 567 | 567 | 567
1134.8485 | 1070 | 31.4286 | 31.4286 | 572 | 368.5714 | 400 | 20 | 552 | 5 | 3430 | 552 | #N/A | 3982 | 1070 | 400 | 31.4286 | 368.5714 | 572 | 572 | 572
1140.1515 | 1075 | 26.4286 | 26.4286 | 577 | 373.5714 | 400 | 20 | 557 | 5 | 3425 | 557 | #N/A | 3982 | 1075 | 400 | 26.4286 | 373.5714 | 577 | 577 | 577
1145.4545 | 1080 | 21.4286 | 21.4286 | 582 | 378.5714 | 400 | 20 | 562 | 5 | 3420 | 562 | #N/A | 3982 | 1080 | 400 | 21.4286 | 378.5714 | 582 | 582 | 582
1150.7576 | 1085 | 16.4286 | 16.4286 | 587 | 383.5714 | 400 | 20 | 567 | 5 | 3415 | 567 | #N/A | 3982 | 1085 | 400 | 16.4286 | 383.5714 | 587 | 587 | 587
1156.0606 | 1090 | 11.4286 | 11.4286 | 592 | 388.5714 | 400 | 20 | 572 | 5 | 3410 | 572 | #N/A | 3982 | 1090 | 400 | 11.4286 | 388.5714 | 592 | 592 | 592
1161.3636 | 1095 | 6.4286 | 6.4286 | 597 | 393.5714 | 400 | 20 | 577 | 5 | 3405 | 577 | #N/A | 3982 | 1095 | 400 | 6.4286 | 393.5714 | 597 | 597 | 597
1166.6667 | 1100 | 1.4286 | 1.4286 | 602 | 398.5714 | 400 | 20 | 582 | 5 | 3400 | 582 | #N/A | 3982 | 1100 | 400 | 1.4286 | 398.5714 | 602 | 602 | 602
1171.9697 | 1105 | -3.5714 | 0 | 607 | 400 | 400 | 20 | 587 | 5 | 3395 | 587 | #N/A | 3982 | 1105 | 400 | 0 | 400 | 607 | 607 | 607
1177.2727 | 1110 | -8.5714 | 0 | 612 | 400 | 400 | 20 | 592 | 5 | 3390 | 592 | #N/A | 3982 | 1110 | 400 | 0 | 400 | 612 | 612 | 612
1182.5758 | 1115 | -13.5714 | 0 | 617 | 400 | 400 | 20 | 597 | 5 | 3385 | 597 | #N/A | 3982 | 1115 | 400 | 0 | 400 | 617 | 617 | 617
1187.8788 | 1120 | -18.5714 | 0 | 622 | 400 | 400 | 20 | 602 | 5 | 3380 | 602 | #N/A | 3982 | 1120 | 400 | 0 | 400 | 622 | 622 | 622
1193.1818 | 1125 | -23.5714 | 0 | 627 | 400 | 400 | 20 | 607 | 5 | 3375 | 607 | #N/A | 3982 | 1125 | 400 | 0 | 400 | 627 | 627 | 627
1198.4848 | 1130 | -28.5714 | 0 | 632 | 400 | 400 | 20 | 612 | 5 | 3370 | 612 | #N/A | 3982 | 1130 | 400 | 0 | 400 | 632 | 632 | 632
1203.7879 | 1135 | -33.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1135 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1209.0909 | 1140 | -38.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1140 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1214.3939 | 1145 | -43.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1145 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1219.697 | 1150 | -48.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1150 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1225 | 1155 | -53.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1155 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1230.303 | 1160 | -58.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1160 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1235.6061 | 1165 | -63.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1240.9091 | 1170 | -68.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1170 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1246.2121 | 1175 | -73.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1175 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1251.5152 | 1180 | -78.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1180 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1256.8182 | 1185 | -83.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1185 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1262.1212 | 1190 | -88.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1190 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1267.4242 | 1195 | -93.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1272.7273 | 1200 | -98.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1278.0303 | 1205 | -103.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1205 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1283.3333 | 1210 | -108.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1210 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1288.6364 | 1215 | -113.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1215 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1293.9394 | 1220 | -118.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1220 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1299.2424 | 1225 | -123.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1225 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1304.5455 | 1230 | -128.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1230 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1309.8485 | 1235 | -133.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1235 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1315.1515 | 1240 | -138.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1240 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1320.4545 | 1245 | -143.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1245 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1325.7576 | 1250 | -148.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1250 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1331.0606 | 1255 | -153.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1336.3636 | 1260 | -158.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1260 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1341.6667 | 1265 | -163.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1265 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1346.9697 | 1270 | -168.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1270 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1352.2727 | 1275 | -173.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1275 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1357.5758 | 1280 | -178.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1280 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1362.8788 | 1285 | -183.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1368.1818 | 1290 | -188.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1290 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1373.4848 | 1295 | -193.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1295 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1378.7879 | 1300 | -198.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1300 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1384.0909 | 1305 | -203.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1305 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1389.3939 | 1310 | -208.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1310 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1394.697 | 1315 | -213.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1315 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1400 | 1320 | -218.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1320 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1405.303 | 1325 | -223.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1325 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1410.6061 | 1330 | -228.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1330 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1415.9091 | 1335 | -233.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1335 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1421.2121 | 1340 | -238.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1340 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1426.5152 | 1345 | -243.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1345 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1431.8182 | 1350 | -248.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1350 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1437.1212 | 1355 | -253.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1355 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1442.4242 | 1360 | -258.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1360 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1447.7273 | 1365 | -263.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1365 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1453.0303 | 1370 | -268.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1370 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1458.3333 | 1375 | -273.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1375 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1463.6364 | 1380 | -278.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1380 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1468.9394 | 1385 | -283.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1385 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1474.2424 | 1390 | -288.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1390 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1479.5455 | 1395 | -293.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1395 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
1484.8485 | 1400 | -298.5714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1400 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cost allocation scenarios
[21 empty] | Station | Huntly - e3p | TCC | Huntly units 1-4 | Stratford | Glenbrook | Rotokawa | Kawerau | Te Mihi | Manapouri | Clutha -Clyde | Waitaki - Benmore | Waitaki - Pukaki | Waitaki - Ohau
[21 empty] | Type | Thermal | Thermal | Thermal | Thermal | Thermal | Geo | Geo | Geo | Hydro | Hydro | Hydro | Hydro | Hydro
[21 empty] | Capacity | 400 | 385 | 500 | 200 | 68 | 140 | 100 | 166 | 840 | 432 | 540 | 160 | 264
[21 empty] | # units | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 7 | 4 | 6 | 2 | 4
[21 empty] | Unit size (MW) | 400 | 385 | 250 | 100 | 68 | 140 | 100 | 83 | 120 | 108 | 90 | 80 | 66
[21 empty] | Owner | Genesis | Contact | Genesis | Contact | Alinta | Mighty River Power | Mighty River Power | Contact | Meridian | Contact | Meridian | Meridian | Meridian
[21 empty] | Island | N | N | N | N | N | N | N | N | S | S | S | S | S | ~~~
Reserve procured from own or other island to meet own risk
[36 empty] | DC CE |  |  | AC CE |  | CE |  | DC received |  | Able to be provided |  | Total IR provided (MW) |  | Price of IR ($/MW/hr) |  | Cost in TP ($) |  |  | N |  | S |  | Risk
[22 empty] | Average unit output | [13 empty] | N | S |  | N | S | N | S | N | S | IR S-->N | IR N--> S | N | S | N | S | N | S | Tot | Own | Other | Own | Other | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | Reserve procured from other island | Reserve procured from own island
1007.5758 | 950 | 151.4286 | 151.4286 | 452 | 248.5715 | 400 | 20 | 432 | 432 | 3550 | 432 | #N/A | 3982 | [7 empty] | ~~~ | 400 | 385 | 250 | 100 | 68 | 140 | 100 | 83 | 120 | 108 | 90 | 80 | 66 | ~~~ | 452 | 0 | ~~~ | 400 | 120 | 452 | 120 | 950 | 0 | 151.4286 | 220 | 300.5715 | 151.4286 | 30 | 3 | 4508.5721 | 227.1429 | 227.1429 | 300.5715 | 151.4286 | 120 | 0 | 452 | 400 | 385 | 250 | 140 | 120 | 108 | 100 | 100 | 90 | 83 | 80 | 68 | 66
Note on E3: Simon Coates: See section 3.6-7 of June 2015 FKC trial technical report.
Note on AA289: Simon Coates: From Generation units over 60MW_v02
Note on BE299: Simon Coates: Divide by 2 because only a half-hour.

## Bk (hidden)
BookName | HVDC Self IR Cover_v12_2publish.xlsm

## Misc
Benefit of NIRM
|  | Average SI reserve used to displace NI | 100
|  | Cost of displaced NI ($/MW/h) | 1
|  | Annual cost saving ($m) | 0.876
Query to consider extent to which thermal plant are likely to be available to offer reserve
company | gxp | station | unit | speed | AvgPwr | MaxPwr
CTCT | SFD2201 | SFD | 21 | FIR | 37.4266 | 37.6
CTCT | SFD2201 | SFD | 21 | SIR | 56.8146 | 57
CTCT | SFD2201 | SFD | 22 | FIR | 42.4473 | 42.8
CTCT | SFD2201 | SFD | 22 | SIR | 56.6231 | 56.9
CTCT | SFD2201 | SPL | 0 | FIR | 7.7 | 7.7
CTCT | SFD2201 | SPL | 0 | SIR | 61.2 | 61.2
GENE | HLY2201 | HLY | 1 | FIR | 2.7495 | 27
GENE | HLY2201 | HLY | 1 | SIR | 3.5081 | 35
GENE | HLY2201 | HLY | 2 | FIR | 3.1741 | 27
GENE | HLY2201 | HLY | 2 | SIR | 4.0964 | 35
GENE | HLY2201 | HLY | 4 | FIR | 5.5338 | 27
GENE | HLY2201 | HLY | 4 | SIR | 7.0968 | 35
SKOG | KAW0111 | n/a | 0 | FIR | 6 | 6
SKOG | KAW0111 | n/a | 0 | SIR | 6 | 6
|  |  |  | FIR | 105.0312 | 175.1
|  |  |  | SIR | 195.339 | 286.1
Existing SI Capacity available to meet NI peak
Table 6 & 7 from Feb 2016 Sys Op Annual SoS assessment
|  | What | Nameplate (MW) | Capacity contribution (MW)
Table 7 | Waitaki | Hydro |  | 1685
Table 7 | Clutha | Hydro |  | 666
Table 6 | Branch | Hydro |  | 6
Table 6 | Cobb | Hydro |  | 31
Table 6 | Coleridge | Hydro |  | 39
Table 6 | Deep Stream | Hydro |  | 5
Table 6 | Highbank | Hydro |  | 23
Table 6 | Kumara | Hydro |  | 8
Table 6 | Mahinerangi | Wind |  | 8
Table 6 | Manapouri | Hydro |  | 784
Table 6 | Paerau | Hydro |  | 7 |  |  | c.f. original analysis
Table 6 | Waipori | Hydro |  | 64 |  | SI Max gen | 2850
Table 6 | Whitehill | Wind |  | 13 |  | Plus extra released by TPM | 300
| Total |  |  | 3339 |  | Total | 3150
Note on A10: Simon Coates: SELECT company, gxp, station, unit, speed, AVG(Pwr) AS AvgPwr, MAX(Pwr) AS MaxPwr FROM (SELECT company, record_Date, halfhour_number, gxp, station, unit, speed, SUM(POWER) AS Pwr FROM `wits_allreserves` WHERE gxp IN ('HLY2201', 'SWN2201', 'SFD2201', 'GLN0332', 'KAW0111', 'KIN0112', 'TMU1101', 'TWH0331', 'HWA1102', 'MKE1101', 'WHI2201') AND record_Date >= '2015-01-01' GROUP BY company, record_Date, halfhour_number,gxp, station, unit, speed) a GROUP BY company,gxp, station, unit, speed;
Note on H43: simon: 2,850 based on inspection of maximum ever coincident SI generation output.

## Sheet1
Section 8.2 from Feb 2016 annual security assessment
Assumed contribution to capacity margins
| 3336 | 988 | 1166 | 2351 | Total
| NI individual generators | SI Individual generators | NI schemes | SI schemes | NI | SI | NZ
| 14 | 6 | 1031 | 1685 | 4502 | 3339 | 7841
| 42 | 31 | 135 | 666
| 471 | 39
| 373 | 5
| 47 | 23
| 31 | 8
| 14 | 8
| 94 | 784
| 54 | 7
| 21 | 64
| 23 | 13
66
97
15
101
120
74
45
26
49
71
31
194
17
23
366
22
25
149
25
12
16
216
119
35
68
20
150

## Chart5
SI IR price = $1/MW/h,
NI IR price = $10/MW/h

## Chart2
HVDC Self IR Cover_v12_2publish.xlsm

## Chart4
HVDC Self IR Cover_v12_2publish.xlsm
General allocation approach = Runway.
No large thermals are retired.
SI IR price = $1/MW/h,
NI IR price = $10/MW/h
.
Energy transfer across HVDC
[NI DC CE risk]

## CostAllocationExample
| Max transfer of HVDC for illustration | 220
| With large thermals (1) or without large thermals (0) | 1 | [60 empty] | Pro-rata (P) or Runway ® | R
| Max DC received | 1130
[52 empty] | Risk type: AC or DC or Both | B | AC | AC | AC | AC | B | DC | [30 empty] | AC | AC | DC |  | Net
[44 empty] | N | B | S | N | B | S |  |  | Island (North/South/Both) | N | B | S | N | B | S | N |  |  |  | 0 | 1 | 2 | 0 | 1 | 2 | [9 empty] | IR Cost allocation | [8 empty] | N | S | N | N | S | N |  | Island | [5 empty] | National | [5 empty] | Factored by sharing limit | [5 empty] | Cost to island causer
[6 empty] | Price ($/MW/hr) |  | Gen risk (MW) |  |  | Island Risk (MW) |  | Total capacity above de minimis (MW) |  |  |  | Quantity (MW) |  |  | Cost ($) |  |  | Physical transfer limit across DC | HVDC risk |  | Quantity (MW) | [17 empty] | Cost ($) | [8 empty] | Cost ($) | [9 empty] | 0: Share of national (pro-rata); 0: Share of island | Factored by sharing limit |  | Sharing of IR procured for shared, across AC risks only | [6 empty] | Island |  |  | National |  |  | Factored by sharing limit |  |  | Cost to island causer |  |  | Cost to DC then island |  |  |  | North |  |  | South |  |  | N |  |  | S |  |  | N |  |  | S |  |  | N |  |  | S
HVDC energy transfer (MW) | Physical transfer limit of IR across HVDC (MW) | Actual transfer limit of IR North across HVDC (MW) i.e. factored by ability to deliver IR given extent of HVDC going North | NI DC CE risk (MW) | Quantity of SI IR which is cheaper than NI IR (MW) | IR Transferred North on HVDC | N | S | N | S | DC | N | S | N | S | DC | Feasibility of scenario | N | S | Tot | N | S | Tot |  |  |  | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk | Tot |  |  | NI_IR_4_NI_CE | NI_IR 4 shared_AC_risk | NI_IR 4 SI_AC_Risk | SI_IR 4 NI_AC_Risk | SI_IR 4 shared_AC_risk | SI_IR 4 SI_Risk | NI_IR_4_NI_DC_CE |  |  | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk | Tot |  |  | NI_IR_4_NI_CE | NI_IR 4 shared_AC_risk | NI_IR 4 SI_AC_Risk | SI_IR 4 NI_AC_Risk | SI_IR 4 shared_AC_risk | SI_IR 4 SI_Risk | NI_IR_4_NI_DC_CE | Tot |  | Runway allocation offset number | North gen. > de minimis | South gen. > de minimis | HVDC | North gen. > de minimis | South gen. > de minimis | HVDC | Share of total cost allocated nationally | Residual share to SI | North gen. > de minimis | South gen. > de minimis | HVDC |  |  |  |  | North gen. > de minimis | South gen. > de minimis | HVDC | North gen. > de minimis | South gen. > de minimis | HVDC | North gen. > de minimis | South gen. > de minimis | HVDC | North gen. > de minimis | South gen. > de minimis | HVDC | North gen. > de minimis | South gen. > de minimis | HVDC |  | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net | Earned | Allocated | Net
600 | 0 | 0 | 102 | 0 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 | 0 MW | 102 MW | 0 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 0% | 100% | 80.44% | 19.56% | 0% |  |  |  | 0 | 3874.5332 | 122 | 125.4668 | 3287.767 | 799.6968 | 34.5361 | 3874.5332 | 122 | 125.4668 | 3958.4191 | 122 | 41.5809 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3287.767 | 712.233 | 122 | -834.233 | -712.233 | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3958.4191 | 41.5809 | 122 | -163.5809 | -41.5809
600 | 0 | 0 | 102 | 10 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 10 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 0% | 100% | 80.44% | 19.56% | 0% |  |  |  | 10 | 3874.5332 | 122 | 125.4668 | 3287.767 | 799.6968 | 34.5361 | 3874.5332 | 122 | 125.4668 | 3958.4191 | 122 | 41.5809 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3287.767 | 712.233 | 122 | -834.233 | -712.233 | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3958.4191 | 41.5809 | 122 | -163.5809 | -41.5809
600 | 0 | 0 | 102 | 100 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 100 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 0% | 100% | 80.44% | 19.56% | 0% |  |  |  | 100 | 3874.5332 | 122 | 125.4668 | 3287.767 | 799.6968 | 34.5361 | 3874.5332 | 122 | 125.4668 | 3958.4191 | 122 | 41.5809 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3287.767 | 712.233 | 122 | -834.233 | -712.233 | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3958.4191 | 41.5809 | 122 | -163.5809 | -41.5809
600 | 0 | 0 | 102 | 220 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 220 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 0% | 100% | 80.44% | 19.56% | 0% |  |  |  | 220 | 3874.5332 | 122 | 125.4668 | 3287.767 | 799.6968 | 34.5361 | 3874.5332 | 122 | 125.4668 | 3958.4191 | 122 | 41.5809 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3287.767 | 712.233 | 122 | -834.233 | -712.233 | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3958.4191 | 41.5809 | 122 | -163.5809 | -41.5809
800 | 0 | 0 | 302 | 0 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  | 302 MW | 0 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 0% | 100% | 78.25% | 21.75% | 0% |  |  |  | 0 | 3371.0201 | 122 | 628.9799 | 2845.0744 | 790.7227 | 486.2029 | 3371.0201 | 122 | 628.9799 | 3416.1965 | 122 | 583.8035 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -2845.0744 | 1154.9256 | 122 | -1276.9256 | -1154.9256 | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -3416.1965 | 583.8035 | 122 | -705.8035 | -583.8035
800 | 0 | 0 | 302 | 10 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 10 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 0% | 100% | 78.25% | 21.75% | 0% |  |  |  | 10 | 3371.0201 | 122 | 628.9799 | 2845.0744 | 790.7227 | 486.2029 | 3371.0201 | 122 | 628.9799 | 3416.1965 | 122 | 583.8035 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -2845.0744 | 1154.9256 | 122 | -1276.9256 | -1154.9256 | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -3416.1965 | 583.8035 | 122 | -705.8035 | -583.8035
800 | 0 | 0 | 302 | 100 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 100 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 0% | 100% | 78.25% | 21.75% | 0% |  |  |  | 100 | 3371.0201 | 122 | 628.9799 | 2845.0744 | 790.7227 | 486.2029 | 3371.0201 | 122 | 628.9799 | 3416.1965 | 122 | 583.8035 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -2845.0744 | 1154.9256 | 122 | -1276.9256 | -1154.9256 | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -3416.1965 | 583.8035 | 122 | -705.8035 | -583.8035
800 | 0 | 0 | 302 | 220 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 220 | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 | [10 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 0% | 100% | 78.25% | 21.75% | 0% |  |  |  | 220 | 3371.0201 | 122 | 628.9799 | 2845.0744 | 790.7227 | 486.2029 | 3371.0201 | 122 | 628.9799 | 3416.1965 | 122 | 583.8035 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -2845.0744 | 1154.9256 | 122 | -1276.9256 | -1154.9256 | 4000 | -3371.0201 | 628.9799 | 122 | -750.9799 | -628.9799 | 4000 | -3416.1965 | 583.8035 | 122 | -705.8035 | -583.8035
1000 | 0 | 0 | 502 | 0 | 0 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 122 | 624 | 5020 | 122 | 5142 |  | 502 MW | 0 | 502 | 0 | 0 | 0 | 0 | 122 | 624 | 1 | [10 empty] | 5020 | 0 | 0 | 0 | 0 | 122 | 5142 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 0% | 100% | 75.84% | 24.16% | 0% |  |  |  | 0 | 3744.0713 | 122 | 1275.9287 | 2467.7516 | 785.9675 | 1888.2809 | 3744.0713 | 122 | 1275.9287 | 2843.8982 | 122 | 2176.1018 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2467.7516 | 2552.2484 | 122 | -2674.2484 | -2552.2484 | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2843.8982 | 2176.1018 | 122 | -2298.1018 | -2176.1018
1000 | 0 | 0 | 502 | 10 | 0 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 122 | 624 | 5020 | 122 | 5142 |  |  | 10 | 502 | 0 | 0 | 0 | 0 | 122 | 624 | 1 | [10 empty] | 5020 | 0 | 0 | 0 | 0 | 122 | 5142 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 0% | 100% | 75.84% | 24.16% | 0% |  |  |  | 10 | 3744.0713 | 122 | 1275.9287 | 2467.7516 | 785.9675 | 1888.2809 | 3744.0713 | 122 | 1275.9287 | 2843.8982 | 122 | 2176.1018 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2467.7516 | 2552.2484 | 122 | -2674.2484 | -2552.2484 | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2843.8982 | 2176.1018 | 122 | -2298.1018 | -2176.1018
1000 | 0 | 0 | 502 | 100 | 0 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 122 | 624 | 5020 | 122 | 5142 |  |  | 100 | 502 | 0 | 0 | 0 | 0 | 122 | 624 | 1 | [10 empty] | 5020 | 0 | 0 | 0 | 0 | 122 | 5142 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 0% | 100% | 75.84% | 24.16% | 0% |  |  |  | 100 | 3744.0713 | 122 | 1275.9287 | 2467.7516 | 785.9675 | 1888.2809 | 3744.0713 | 122 | 1275.9287 | 2843.8982 | 122 | 2176.1018 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2467.7516 | 2552.2484 | 122 | -2674.2484 | -2552.2484 | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2843.8982 | 2176.1018 | 122 | -2298.1018 | -2176.1018
1000 | 0 | 0 | 502 | 220 | 0 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 122 | 624 | 5020 | 122 | 5142 |  |  | 220 | 502 | 0 | 0 | 0 | 0 | 122 | 624 | 1 | [10 empty] | 5020 | 0 | 0 | 0 | 0 | 122 | 5142 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 0% | 100% | 75.84% | 24.16% | 0% |  |  |  | 220 | 3744.0713 | 122 | 1275.9287 | 2467.7516 | 785.9675 | 1888.2809 | 3744.0713 | 122 | 1275.9287 | 2843.8982 | 122 | 2176.1018 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2467.7516 | 2552.2484 | 122 | -2674.2484 | -2552.2484 | 5020 | -3744.0713 | 1275.9287 | 122 | -1397.9287 | -1275.9287 | 5020 | -2843.8982 | 2176.1018 | 122 | -2298.1018 | -2176.1018
600 | 10 | 10 | 102 | 0 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 112 | 512 | 4000 | 112 | 4112 | 10 MW | 102 MW | 0 | 390 | 10 | 0 | 0 | 0 | 112 | 512 | 1 | [10 empty] | 3900 | 100 | 0 | 0 | 0 | 112 | 4112 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 1.953% | 100% | 80.44% | 19.56% | 0% |  |  |  | 0 | 3874.5332 | 112 | 125.4668 | 3279.7909 | 797.7568 | 34.4523 | 3862.9172 | 125.3937 | 123.6891 | 3939.22 | 131.4007 | 41.3793 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 112 | -237.4668 | -125.4668 | 4000 | -3279.7909 | 720.2091 | 112 | -832.2091 | -720.2091 | 4000 | -3862.9172 | 137.0828 | 112 | -249.0828 | -137.0828 | 4000 | -3939.22 | 60.78 | 112 | -172.78 | -60.78
600 | 10 | 10 | 102 | 10 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 10 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 1.992% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 10 | 3777.6699 | 112 | 122.3301 | 3200.0294 | 778.3561 | 33.6145 | 3766.1631 | 125.274 | 120.5629 | 3848.2357 | 123.3408 | 40.4235 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 112 | -234.3301 | -122.3301 | 3900 | -3200.0294 | 699.9706 | 112 | -811.9706 | -699.9706 | 3900 | -3766.1631 | 133.8369 | 112 | -245.8369 | -133.8369 | 3900 | -3848.2357 | 51.7643 | 112 | -163.7643 | -51.7643
600 | 10 | 10 | 102 | 100 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 100 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 1.992% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 100 | 3777.6699 | 112 | 122.3301 | 3200.0294 | 778.3561 | 33.6145 | 3766.1631 | 125.274 | 120.5629 | 3848.2357 | 123.3408 | 40.4235 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 112 | -234.3301 | -122.3301 | 3900 | -3200.0294 | 699.9706 | 112 | -811.9706 | -699.9706 | 3900 | -3766.1631 | 133.8369 | 112 | -245.8369 | -133.8369 | 3900 | -3848.2357 | 51.7643 | 112 | -163.7643 | -51.7643
600 | 10 | 10 | 102 | 220 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 220 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 1.992% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 220 | 3777.6699 | 112 | 122.3301 | 3200.0294 | 778.3561 | 33.6145 | 3766.1631 | 125.274 | 120.5629 | 3848.2357 | 123.3408 | 40.4235 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 112 | -234.3301 | -122.3301 | 3900 | -3200.0294 | 699.9706 | 112 | -811.9706 | -699.9706 | 3900 | -3766.1631 | 133.8369 | 112 | -245.8369 | -133.8369 | 3900 | -3848.2357 | 51.7643 | 112 | -163.7643 | -51.7643
800 | 10 | 10 | 302 | 0 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 112 | 512 | 4000 | 112 | 4112 |  | 302 MW | 0 | 390 | 10 | 0 | 0 | 0 | 112 | 512 | 1 | [10 empty] | 3900 | 100 | 0 | 0 | 0 | 112 | 4112 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 1.953% | 100% | 78.25% | 21.75% | 0% |  |  |  | 0 | 3371.0201 | 112 | 628.9799 | 2838.1722 | 788.8044 | 485.0233 | 3360.613 | 125.2188 | 626.1682 | 3399.8132 | 131.183 | 581.0038 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 112 | -740.9799 | -628.9799 | 4000 | -2838.1722 | 1161.8278 | 112 | -1273.8278 | -1161.8278 | 4000 | -3360.613 | 639.387 | 112 | -751.387 | -639.387 | 4000 | -3399.8132 | 600.1868 | 112 | -712.1868 | -600.1868
800 | 10 | 10 | 302 | 10 | 10 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 10 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 1.992% | 91.8% | 78.25% | 21.75% | 0% |  |  |  | 10 | 3286.7446 | 112 | 613.2554 | 2769.1505 | 769.6214 | 473.228 | 3276.434 | 125.1 | 610.466 | 3321.3105 | 123.1013 | 567.5882 | 0 | 0 | 0 |  | 3900 | -3286.7446 | 613.2554 | 112 | -725.2554 | -613.2554 | 3900 | -2769.1505 | 1130.8495 | 112 | -1242.8495 | -1130.8495 | 3900 | -3276.434 | 623.566 | 112 | -735.566 | -623.566 | 3900 | -3321.3105 | 578.6895 | 112 | -690.6895 | -578.6895
800 | 10 | 10 | 302 | 100 | 10 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 100 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 1.992% | 91.8% | 78.25% | 21.75% | 0% |  |  |  | 100 | 3286.7446 | 112 | 613.2554 | 2769.1505 | 769.6214 | 473.228 | 3276.434 | 125.1 | 610.466 | 3321.3105 | 123.1013 | 567.5882 | 0 | 0 | 0 |  | 3900 | -3286.7446 | 613.2554 | 112 | -725.2554 | -613.2554 | 3900 | -2769.1505 | 1130.8495 | 112 | -1242.8495 | -1130.8495 | 3900 | -3276.434 | 623.566 | 112 | -735.566 | -623.566 | 3900 | -3321.3105 | 578.6895 | 112 | -690.6895 | -578.6895
800 | 10 | 10 | 302 | 220 | 10 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 220 | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 1.992% | 91.8% | 78.25% | 21.75% | 0% |  |  |  | 220 | 3286.7446 | 112 | 613.2554 | 2769.1505 | 769.6214 | 473.228 | 3276.434 | 125.1 | 610.466 | 3321.3105 | 123.1013 | 567.5882 | 0 | 0 | 0 |  | 3900 | -3286.7446 | 613.2554 | 112 | -725.2554 | -613.2554 | 3900 | -2769.1505 | 1130.8495 | 112 | -1242.8495 | -1130.8495 | 3900 | -3276.434 | 623.566 | 112 | -735.566 | -623.566 | 3900 | -3321.3105 | 578.6895 | 112 | -690.6895 | -578.6895
1000 | 10 | 10 | 502 | 0 | -10 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 112 | 614 | 5020 | 112 | 5132 |  | 502 MW | 0 | 492 | 10 | 0 | 0 | 0 | 112 | 614 | 1 | [10 empty] | 4920 | 100 | 0 | 0 | 0 | 112 | 5132 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 1.629% | 100% | 75.84% | 24.16% | 0% |  |  |  | 0 | 3744.0713 | 112 | 1275.9287 | 2462.9524 | 784.439 | 1884.6087 | 3723.2062 | 122.9518 | 1285.842 | 2835.2389 | 127.2852 | 2169.4759 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 112 | -1387.9287 | -1275.9287 | 5020 | -2462.9524 | 2557.0476 | 112 | -2669.0476 | -2557.0476 | 5020 | -3723.2062 | 1296.7938 | 112 | -1408.7938 | -1296.7938 | 5020 | -2835.2389 | 2184.7611 | 112 | -2296.7611 | -2184.7611
1000 | 10 | 10 | 502 | 10 | -10 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 112 | 614 | 5020 | 112 | 5132 |  |  | 10 | 492 | 10 | 0 | 0 | 0 | 112 | 614 | 1 | [10 empty] | 4920 | 100 | 0 | 0 | 0 | 112 | 5132 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 1.629% | 100% | 75.84% | 24.16% | 0% |  |  |  | 10 | 3744.0713 | 112 | 1275.9287 | 2462.9524 | 784.439 | 1884.6087 | 3723.2062 | 122.9518 | 1285.842 | 2835.2389 | 127.2852 | 2169.4759 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 112 | -1387.9287 | -1275.9287 | 5020 | -2462.9524 | 2557.0476 | 112 | -2669.0476 | -2557.0476 | 5020 | -3723.2062 | 1296.7938 | 112 | -1408.7938 | -1296.7938 | 5020 | -2835.2389 | 2184.7611 | 112 | -2296.7611 | -2184.7611
1000 | 10 | 10 | 502 | 100 | -10 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 112 | 614 | 5020 | 112 | 5132 |  |  | 100 | 492 | 10 | 0 | 0 | 0 | 112 | 614 | 1 | [10 empty] | 4920 | 100 | 0 | 0 | 0 | 112 | 5132 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 1.629% | 100% | 75.84% | 24.16% | 0% |  |  |  | 100 | 3744.0713 | 112 | 1275.9287 | 2462.9524 | 784.439 | 1884.6087 | 3723.2062 | 122.9518 | 1285.842 | 2835.2389 | 127.2852 | 2169.4759 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 112 | -1387.9287 | -1275.9287 | 5020 | -2462.9524 | 2557.0476 | 112 | -2669.0476 | -2557.0476 | 5020 | -3723.2062 | 1296.7938 | 112 | -1408.7938 | -1296.7938 | 5020 | -2835.2389 | 2184.7611 | 112 | -2296.7611 | -2184.7611
1000 | 10 | 10 | 502 | 220 | -10 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 112 | 614 | 5020 | 112 | 5132 |  |  | 220 | 492 | 10 | 0 | 0 | 0 | 112 | 614 | 1 | [10 empty] | 4920 | 100 | 0 | 0 | 0 | 112 | 5132 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 1.629% | 100% | 75.84% | 24.16% | 0% |  |  |  | 220 | 3744.0713 | 112 | 1275.9287 | 2462.9524 | 784.439 | 1884.6087 | 3723.2062 | 122.9518 | 1285.842 | 2835.2389 | 127.2852 | 2169.4759 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 112 | -1387.9287 | -1275.9287 | 5020 | -2462.9524 | 2557.0476 | 112 | -2669.0476 | -2557.0476 | 5020 | -3723.2062 | 1296.7938 | 112 | -1408.7938 | -1296.7938 | 5020 | -2835.2389 | 2184.7611 | 112 | -2296.7611 | -2184.7611
600 | 100 | 100 | 102 | 0 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 22 | 422 | 4000 | 22 | 4022 | 100 MW | 102 MW | 0 | 300 | 100 | 0 | 0 | 0 | 22 | 422 | 1 | [10 empty] | 3000 | 1000 | 0 | 0 | 0 | 22 | 4022 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 23.7% | 100% | 80.44% | 19.56% | 0% |  |  |  | 0 | 3874.5332 | 22 | 125.4668 | 3208.0056 | 780.2961 | 33.6983 | 3716.5883 | 201.691 | 103.7207 | 3766.4288 | 216.007 | 39.5642 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 22 | -147.4668 | -125.4668 | 4000 | -3208.0056 | 791.9944 | 22 | -813.9944 | -791.9944 | 4000 | -3716.5883 | 283.4117 | 22 | -305.4117 | -283.4117 | 4000 | -3766.4288 | 233.5712 | 22 | -255.5712 | -233.5712
600 | 100 | 100 | 102 | 10 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 22 | 412 | 3900 | 22 | 3922 |  |  | 10 | 290 | 100 | 0 | 0 | 10 | 12 | 412 | 1 | [10 empty] | 2900 | 1000 | 0 | 0 | 10 | 12 | 3922 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 24.27% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 10 | 3777.6699 | 22 | 122.3301 | 3128.2441 | 760.8954 | 32.8604 | 3620.0423 | 201.3436 | 100.6142 | 3675.4445 | 207.9471 | 38.6084 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 22 | -144.3301 | -122.3301 | 3900 | -3128.2441 | 771.7559 | 22 | -793.7559 | -771.7559 | 3900 | -3620.0423 | 279.9577 | 22 | -301.9577 | -279.9577 | 3900 | -3675.4445 | 224.5555 | 22 | -246.5555 | -224.5555
600 | 100 | 100 | 102 | 100 | 100 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 300 | 100 | 400 | 3000 | 100 | 3100 |  |  | 100 | 278 | 22 | 0 | 0 | 100 | 0 | 400 | 1 | [10 empty] | 2780 | 220 | 0 | 0 | 100 | 0 | 3100 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 25% | 18.03% | 80.44% | 19.56% | 0% |  |  |  | 100 | 2905.8999 | 100 | 94.1001 | 2472.605 | 601.4217 | 25.9733 | 2797.5762 | 225.3554 | 77.0684 | 3006.3379 | 62.0822 | 31.5799 | 0 | 0 | 0 |  | 3000 | -2905.8999 | 94.1001 | 100 | -194.1001 | -94.1001 | 3000 | -2472.605 | 527.395 | 100 | -627.395 | -527.395 | 3000 | -2797.5762 | 202.4238 | 100 | -302.4238 | -202.4238 | 3000 | -3006.3379 | -6.3379 | 100 | -93.6621 | 6.3379
600 | 100 | 100 | 102 | 220 | 100 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 300 | 100 | 400 | 3000 | 100 | 3100 |  |  | 220 | 278 | 22 | 0 | 0 | 100 | 0 | 400 | 1 | [10 empty] | 2780 | 220 | 0 | 0 | 100 | 0 | 3100 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 25% | 18.03% | 80.44% | 19.56% | 0% |  |  |  | 220 | 2905.8999 | 100 | 94.1001 | 2472.605 | 601.4217 | 25.9733 | 2797.5762 | 225.3554 | 77.0684 | 3006.3379 | 62.0822 | 31.5799 | 0 | 0 | 0 |  | 3000 | -2905.8999 | 94.1001 | 100 | -194.1001 | -94.1001 | 3000 | -2472.605 | 527.395 | 100 | -627.395 | -527.395 | 3000 | -2797.5762 | 202.4238 | 100 | -302.4238 | -202.4238 | 3000 | -3006.3379 | -6.3379 | 100 | -93.6621 | 6.3379
800 | 100 | 100 | 302 | 0 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 22 | 422 | 4000 | 22 | 4022 |  | 302 MW | 0 | 300 | 100 | 0 | 0 | 0 | 22 | 422 | 1 | [10 empty] | 3000 | 1000 | 0 | 0 | 0 | 22 | 4022 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 23.7% | 100% | 78.25% | 21.75% | 0% |  |  |  | 0 | 3371.0201 | 22 | 628.9799 | 2776.0527 | 771.5397 | 474.4076 | 3230.0326 | 199.616 | 592.3513 | 3252.3643 | 213.8299 | 555.8058 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 22 | -650.9799 | -628.9799 | 4000 | -2776.0527 | 1223.9473 | 22 | -1245.9473 | -1223.9473 | 4000 | -3230.0326 | 769.9674 | 22 | -791.9674 | -769.9674 | 4000 | -3252.3643 | 747.6357 | 22 | -769.6357 | -747.6357
800 | 100 | 100 | 302 | 10 | 10 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 390 | 22 | 412 | 3900 | 22 | 3922 |  |  | 10 | 290 | 100 | 0 | 0 | 10 | 12 | 412 | 1 | [10 empty] | 2900 | 1000 | 0 | 0 | 10 | 12 | 3922 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 24.27% | 91.8% | 78.25% | 21.75% | 0% |  |  |  | 10 | 3286.7446 | 22 | 613.2554 | 2707.031 | 752.3567 | 462.6122 | 3146.0375 | 199.2711 | 576.6915 | 3173.8616 | 205.7482 | 542.3902 | 0 | 0 | 0 |  | 3900 | -3286.7446 | 613.2554 | 22 | -635.2554 | -613.2554 | 3900 | -2707.031 | 1192.969 | 22 | -1214.969 | -1192.969 | 3900 | -3146.0375 | 753.9625 | 22 | -775.9625 | -753.9625 | 3900 | -3173.8616 | 726.1384 | 22 | -748.1384 | -726.1384
800 | 100 | 100 | 302 | 100 | 98 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 302 | 98 | 400 | 3020 | 98 | 3118 |  |  | 100 | 278 | 24 | 0 | 0 | 98 | 0 | 400 | 1 | [10 empty] | 2780 | 240 | 0 | 0 | 98 | 0 | 3118 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 25% | 19.67% | 78.25% | 21.75% | 0% |  |  |  | 100 | 2545.1202 | 98 | 474.8798 | 2152.0966 | 598.1255 | 367.7779 | 2446.8643 | 223.0314 | 448.1043 | 2607.5499 | 64.8385 | 445.6116 | 0 | 0 | 0 |  | 3020 | -2545.1202 | 474.8798 | 98 | -572.8798 | -474.8798 | 3020 | -2152.0966 | 867.9034 | 98 | -965.9034 | -867.9034 | 3020 | -2446.8643 | 573.1357 | 98 | -671.1357 | -573.1357 | 3020 | -2607.5499 | 412.4501 | 98 | -510.4501 | -412.4501
800 | 100 | 100 | 302 | 220 | 98 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 302 | 98 | 400 | 3020 | 98 | 3118 |  |  | 220 | 278 | 24 | 0 | 0 | 98 | 0 | 400 | 1 | [10 empty] | 2780 | 240 | 0 | 0 | 98 | 0 | 3118 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 25% | 19.67% | 78.25% | 21.75% | 0% |  |  |  | 220 | 2545.1202 | 98 | 474.8798 | 2152.0966 | 598.1255 | 367.7779 | 2446.8643 | 223.0314 | 448.1043 | 2607.5499 | 64.8385 | 445.6116 | 0 | 0 | 0 |  | 3020 | -2545.1202 | 474.8798 | 98 | -572.8798 | -474.8798 | 3020 | -2152.0966 | 867.9034 | 98 | -965.9034 | -867.9034 | 3020 | -2446.8643 | 573.1357 | 98 | -671.1357 | -573.1357 | 3020 | -2607.5499 | 412.4501 | 98 | -510.4501 | -412.4501
1000 | 100 | 100 | 502 | 0 | -100 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 22 | 524 | 5020 | 22 | 5042 |  | 502 MW | 0 | 402 | 100 | 0 | 0 | 0 | 22 | 524 | 1 | [10 empty] | 4020 | 1000 | 0 | 0 | 0 | 22 | 5042 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.08% | 100% | 75.84% | 24.16% | 0% |  |  |  | 0 | 3744.0713 | 22 | 1275.9287 | 2419.7595 | 770.6822 | 1851.5582 | 3491.3401 | 164.8783 | 1385.7817 | 2757.3052 | 174.8525 | 2109.8423 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 22 | -1297.9287 | -1275.9287 | 5020 | -2419.7595 | 2600.2405 | 22 | -2622.2405 | -2600.2405 | 5020 | -3491.3401 | 1528.6599 | 22 | -1550.6599 | -1528.6599 | 5020 | -2757.3052 | 2262.6948 | 22 | -2284.6948 | -2262.6948
1000 | 100 | 100 | 502 | 10 | -100 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 22 | 524 | 5020 | 22 | 5042 |  |  | 10 | 402 | 100 | 0 | 0 | 0 | 22 | 524 | 1 | [10 empty] | 4020 | 1000 | 0 | 0 | 0 | 22 | 5042 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.08% | 100% | 75.84% | 24.16% | 0% |  |  |  | 10 | 3744.0713 | 22 | 1275.9287 | 2419.7595 | 770.6822 | 1851.5582 | 3491.3401 | 164.8783 | 1385.7817 | 2757.3052 | 174.8525 | 2109.8423 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 22 | -1297.9287 | -1275.9287 | 5020 | -2419.7595 | 2600.2405 | 22 | -2622.2405 | -2600.2405 | 5020 | -3491.3401 | 1528.6599 | 22 | -1550.6599 | -1528.6599 | 5020 | -2757.3052 | 2262.6948 | 22 | -2284.6948 | -2262.6948
1000 | 100 | 100 | 502 | 100 | -100 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 22 | 524 | 5020 | 22 | 5042 |  |  | 100 | 402 | 100 | 0 | 0 | 0 | 22 | 524 | 1 | [10 empty] | 4020 | 1000 | 0 | 0 | 0 | 22 | 5042 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.08% | 100% | 75.84% | 24.16% | 0% |  |  |  | 100 | 3744.0713 | 22 | 1275.9287 | 2419.7595 | 770.6822 | 1851.5582 | 3491.3401 | 164.8783 | 1385.7817 | 2757.3052 | 174.8525 | 2109.8423 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 22 | -1297.9287 | -1275.9287 | 5020 | -2419.7595 | 2600.2405 | 22 | -2622.2405 | -2600.2405 | 5020 | -3491.3401 | 1528.6599 | 22 | -1550.6599 | -1528.6599 | 5020 | -2757.3052 | 2262.6948 | 22 | -2284.6948 | -2262.6948
1000 | 100 | 100 | 502 | 220 | -100 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 22 | 524 | 5020 | 22 | 5042 |  |  | 220 | 402 | 100 | 0 | 0 | 0 | 22 | 524 | 1 | [10 empty] | 4020 | 1000 | 0 | 0 | 0 | 22 | 5042 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.08% | 100% | 75.84% | 24.16% | 0% |  |  |  | 220 | 3744.0713 | 22 | 1275.9287 | 2419.7595 | 770.6822 | 1851.5582 | 3491.3401 | 164.8783 | 1385.7817 | 2757.3052 | 174.8525 | 2109.8423 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 22 | -1297.9287 | -1275.9287 | 5020 | -2419.7595 | 2600.2405 | 22 | -2622.2405 | -2600.2405 | 5020 | -3491.3401 | 1528.6599 | 22 | -1550.6599 | -1528.6599 | 5020 | -2757.3052 | 2262.6948 | 22 | -2284.6948 | -2262.6948
600 | 220 | 220 | 102 | 0 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 0 | 400 | 4000 | 0 | 4000 | 220 MW | 102 MW | 0 | 278 | 122 | 0 | 0 | 0 | 0 | 400 | 1 | [10 empty] | 2780 | 1220 | 0 | 0 | 0 | 0 | 4000 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 55% | 100% | 80.44% | 19.56% | 0% |  |  |  | 0 | 3874.5332 | 0 | 125.4668 | 3190.4581 | 776.028 | 33.5139 | 3498.2919 | 426.8154 | 74.8927 | 3724.191 | 236.6885 | 39.1205 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 0 | -125.4668 | -125.4668 | 4000 | -3190.4581 | 809.5419 | 0 | -809.5419 | -809.5419 | 4000 | -3498.2919 | 501.7081 | 0 | -501.7081 | -501.7081 | 4000 | -3724.191 | 275.809 | 0 | -275.809 | -275.809
600 | 220 | 220 | 102 | 10 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 10 | 400 | 3900 | 10 | 3910 |  |  | 10 | 278 | 112 | 0 | 0 | 10 | 0 | 400 | 1 | [10 empty] | 2780 | 1120 | 0 | 0 | 10 | 0 | 3910 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 55% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 10 | 3777.6699 | 10 | 122.3301 | 3118.6728 | 758.5674 | 32.7599 | 3415.2215 | 421.7121 | 73.0665 | 3652.4057 | 219.2279 | 38.3664 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 10 | -132.3301 | -122.3301 | 3900 | -3118.6728 | 781.3272 | 10 | -791.3272 | -781.3272 | 3900 | -3415.2215 | 484.7785 | 10 | -494.7785 | -484.7785 | 3900 | -3652.4057 | 247.5943 | 10 | -257.5943 | -247.5943
600 | 220 | 220 | 102 | 100 | 100 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 300 | 100 | 400 | 3000 | 100 | 3100 |  |  | 100 | 278 | 22 | 0 | 0 | 100 | 0 | 400 | 1 | [10 empty] | 2780 | 220 | 0 | 0 | 100 | 0 | 3100 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 55% | 18.03% | 80.44% | 19.56% | 0% |  |  |  | 100 | 2905.8999 | 100 | 94.1001 | 2472.605 | 601.4217 | 25.9733 | 2667.5877 | 375.7819 | 56.6304 | 3006.3379 | 62.0822 | 31.5799 | 0 | 0 | 0 |  | 3000 | -2905.8999 | 94.1001 | 100 | -194.1001 | -94.1001 | 3000 | -2472.605 | 527.395 | 100 | -627.395 | -527.395 | 3000 | -2667.5877 | 332.4123 | 100 | -432.4123 | -332.4123 | 3000 | -3006.3379 | -6.3379 | 100 | -93.6621 | 6.3379
600 | 220 | 220 | 102 | 220 | 220 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 180 | 220 | 400 | 1800 | 220 | 2020 |  |  | 220 | 180 | 0 | 0 | 98 | 122 | 0 | 400 | 1 | [10 empty] | 1800 | 0 | 0 | 98 | 122 | 0 | 2020 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 55% | 0% | 80.44% | 19.56% | 0% |  |  |  | 220 | 1743.54 | 220 | 56.46 | 1611.1813 | 391.8941 | 16.9245 | 1670.7427 | 314.5418 | 34.7155 | 1975.5788 | 23.6689 | 20.7523 | 0 | 0 | 0 |  | 1800 | -1743.54 | 56.46 | 220 | -276.46 | -56.46 | 1800 | -1611.1813 | 188.8187 | 220 | -408.8187 | -188.8187 | 1800 | -1670.7427 | 129.2573 | 220 | -349.2573 | -129.2573 | 1800 | -1975.5788 | -175.5788 | 220 | -44.4212 | 175.5788
800 | 220 | 220 | 302 | 0 | 0 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 400 | 0 | 400 | 4000 | 0 | 4000 |  | 302 MW | 0 | 278 | 122 | 0 | 0 | 0 | 0 | 400 | 1 | [10 empty] | 2780 | 1220 | 0 | 0 | 0 | 0 | 4000 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 55% | 100% | 78.25% | 21.75% | 0% |  |  |  | 0 | 3371.0201 | 0 | 628.9799 | 2760.8679 | 767.3195 | 471.8126 | 3035.4364 | 422.0257 | 542.5379 | 3216.3213 | 234.0324 | 549.6463 | 0 | 0 | 0 |  | 4000 | -3371.0201 | 628.9799 | 0 | -628.9799 | -628.9799 | 4000 | -2760.8679 | 1239.1321 | 0 | -1239.1321 | -1239.1321 | 4000 | -3035.4364 | 964.5636 | 0 | -964.5636 | -964.5636 | 4000 | -3216.3213 | 783.6787 | 0 | -783.6787 | -783.6787
800 | 220 | 220 | 302 | 10 | 10 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 390 | 10 | 400 | 3900 | 10 | 3910 |  |  | 10 | 278 | 112 | 0 | 0 | 10 | 0 | 400 | 1 | [10 empty] | 2780 | 1120 | 0 | 0 | 10 | 0 | 3910 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 55% | 91.8% | 78.25% | 21.75% | 0% |  |  |  | 10 | 3286.7446 | 10 | 613.2554 | 2698.7484 | 750.0548 | 461.1968 | 2963.3467 | 417.0301 | 529.6232 | 3154.2017 | 216.7678 | 539.0305 | 0 | 0 | 0 |  | 3900 | -3286.7446 | 613.2554 | 10 | -623.2554 | -613.2554 | 3900 | -2698.7484 | 1201.2516 | 10 | -1211.2516 | -1201.2516 | 3900 | -2963.3467 | 936.6533 | 10 | -946.6533 | -936.6533 | 3900 | -3154.2017 | 745.7983 | 10 | -755.7983 | -745.7983
800 | 220 | 220 | 302 | 100 | 98 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 302 | 98 | 400 | 3020 | 98 | 3118 |  |  | 100 | 278 | 24 | 0 | 0 | 98 | 0 | 400 | 1 | [10 empty] | 2780 | 240 | 0 | 0 | 98 | 0 | 3118 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 55% | 19.67% | 78.25% | 21.75% | 0% |  |  |  | 100 | 2545.1202 | 98 | 474.8798 | 2152.0966 | 598.1255 | 367.7779 | 2328.9572 | 373.069 | 415.9738 | 2607.5499 | 64.8385 | 445.6116 | 0 | 0 | 0 |  | 3020 | -2545.1202 | 474.8798 | 98 | -572.8798 | -474.8798 | 3020 | -2152.0966 | 867.9034 | 98 | -965.9034 | -867.9034 | 3020 | -2328.9572 | 691.0428 | 98 | -789.0428 | -691.0428 | 3020 | -2607.5499 | 412.4501 | 98 | -510.4501 | -412.4501
800 | 220 | 220 | 302 | 220 | 98 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 302 | 98 | 400 | 3020 | 98 | 3118 |  |  | 220 | 278 | 24 | 0 | 0 | 98 | 0 | 400 | 1 | [10 empty] | 2780 | 240 | 0 | 0 | 98 | 0 | 3118 | 1 | [10 empty] | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 55% | 19.67% | 78.25% | 21.75% | 0% |  |  |  | 220 | 2545.1202 | 98 | 474.8798 | 2152.0966 | 598.1255 | 367.7779 | 2328.9572 | 373.069 | 415.9738 | 2607.5499 | 64.8385 | 445.6116 | 0 | 0 | 0 |  | 3020 | -2545.1202 | 474.8798 | 98 | -572.8798 | -474.8798 | 3020 | -2152.0966 | 867.9034 | 98 | -965.9034 | -867.9034 | 3020 | -2328.9572 | 691.0428 | 98 | -789.0428 | -691.0428 | 3020 | -2607.5499 | 412.4501 | 98 | -510.4501 | -412.4501
1000 | 220 | 100 | 502 | 0 | -102 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 0 | 502 | 5020 | 0 | 5020 |  | 502 MW | 0 | 380 | 122 | 0 | 0 | 0 | 0 | 502 | 1 | [10 empty] | 3800 | 1220 | 0 | 0 | 0 | 0 | 5020 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.92% | 100% | 75.84% | 24.16% | 0% |  |  |  | 0 | 3744.0713 | 0 | 1275.9287 | 2409.2013 | 767.3195 | 1843.4792 | 3478.1609 | 152.8525 | 1388.9866 | 2738.2547 | 186.48 | 2095.2653 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 0 | -1275.9287 | -1275.9287 | 5020 | -2409.2013 | 2610.7987 | 0 | -2610.7987 | -2610.7987 | 5020 | -3478.1609 | 1541.8391 | 0 | -1541.8391 | -1541.8391 | 5020 | -2738.2547 | 2281.7453 | 0 | -2281.7453 | -2281.7453
1000 | 220 | 100 | 502 | 10 | -102 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 0 | 502 | 5020 | 0 | 5020 |  |  | 10 | 380 | 122 | 0 | 0 | 0 | 0 | 502 | 1 | [10 empty] | 3800 | 1220 | 0 | 0 | 0 | 0 | 5020 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.92% | 100% | 75.84% | 24.16% | 0% |  |  |  | 10 | 3744.0713 | 0 | 1275.9287 | 2409.2013 | 767.3195 | 1843.4792 | 3478.1609 | 152.8525 | 1388.9866 | 2738.2547 | 186.48 | 2095.2653 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 0 | -1275.9287 | -1275.9287 | 5020 | -2409.2013 | 2610.7987 | 0 | -2610.7987 | -2610.7987 | 5020 | -3478.1609 | 1541.8391 | 0 | -1541.8391 | -1541.8391 | 5020 | -2738.2547 | 2281.7453 | 0 | -2281.7453 | -2281.7453
1000 | 220 | 100 | 502 | 100 | -102 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 0 | 502 | 5020 | 0 | 5020 |  |  | 100 | 380 | 122 | 0 | 0 | 0 | 0 | 502 | 1 | [10 empty] | 3800 | 1220 | 0 | 0 | 0 | 0 | 5020 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.92% | 100% | 75.84% | 24.16% | 0% |  |  |  | 100 | 3744.0713 | 0 | 1275.9287 | 2409.2013 | 767.3195 | 1843.4792 | 3478.1609 | 152.8525 | 1388.9866 | 2738.2547 | 186.48 | 2095.2653 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 0 | -1275.9287 | -1275.9287 | 5020 | -2409.2013 | 2610.7987 | 0 | -2610.7987 | -2610.7987 | 5020 | -3478.1609 | 1541.8391 | 0 | -1541.8391 | -1541.8391 | 5020 | -2738.2547 | 2281.7453 | 0 | -2281.7453 | -2281.7453
1000 | 220 | 100 | 502 | 220 | -102 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 0 | 502 | 5020 | 0 | 5020 |  |  | 220 | 380 | 122 | 0 | 0 | 0 | 0 | 502 | 1 | [10 empty] | 3800 | 1220 | 0 | 0 | 0 | 0 | 5020 | 1 | [10 empty] | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.92% | 100% | 75.84% | 24.16% | 0% |  |  |  | 220 | 3744.0713 | 0 | 1275.9287 | 2409.2013 | 767.3195 | 1843.4792 | 3478.1609 | 152.8525 | 1388.9866 | 2738.2547 | 186.48 | 2095.2653 | 0 | 0 | 0 |  | 5020 | -3744.0713 | 1275.9287 | 0 | -1275.9287 | -1275.9287 | 5020 | -2409.2013 | 2610.7987 | 0 | -2610.7987 | -2610.7987 | 5020 | -3478.1609 | 1541.8391 | 0 | -1541.8391 | -1541.8391 | 5020 | -2738.2547 | 2281.7453 | 0 | -2281.7453 | -2281.7453
Illustrate IR transfer capability of HVDC
[26 empty] | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk | [12 empty] | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk | Tot | [26 empty] | IR transfer capability of HVDC
600 | 0 | 0 | 102 | 220 | 0 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 400 | 122 | 522 | 4000 | 122 | 4122 |  |  | 0 MW | 400 | 0 | 0 | 0 | 0 | 122 | 522 | 1 |  | NEED TO GET THIS FORMULA REFERRING TO THE TRANSFER = 0 OPTION FOR ALL CASES! | [8 empty] | 4000 | 0 | 0 | 0 | 0 | 122 | 4122 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 0% | 100% | 80.44% | 19.56% | 0% | SI IR price = $1/MW/h, NI IR price = $10/MW/h |  |  | 0 MW | 3874.5332 | 122 | 125.4668 | 3287.767 | 799.6968 | 34.5361 | 3874.5332 | 122 | 125.4668 | 3958.4191 | 122 | 41.5809 | 0 | 0 | 0 |  | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3287.767 | 712.233 | 122 | -834.233 | -712.233 | 4000 | -3874.5332 | 125.4668 | 122 | -247.4668 | -125.4668 | 4000 | -3958.4191 | 41.5809 | 122 | -163.5809 | -41.5809
600 | 10 | 10 | 102 | 220 | 10 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 390 | 112 | 502 | 3900 | 112 | 4012 |  |  | 10 MW | 380 | 10 | 0 | 0 | 10 | 102 | 502 | 1 | [10 empty] | 3800 | 100 | 0 | 0 | 10 | 102 | 4012 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 1.992% | 91.8% | 80.44% | 19.56% | 0% |  |  |  | 10 MW | 3777.6699 | 112 | 122.3301 | 3200.0294 | 778.3561 | 33.6145 | 3766.1631 | 125.274 | 120.5629 | 3848.2357 | 123.3408 | 40.4235 | 0 | 0 | 0 |  | 3900 | -3777.6699 | 122.3301 | 112 | -234.3301 | -122.3301 | 3900 | -3200.0294 | 699.9706 | 112 | -811.9706 | -699.9706 | 3900 | -3766.1631 | 133.8369 | 112 | -245.8369 | -133.8369 | 3900 | -3848.2357 | 51.7643 | 112 | -163.7643 | -51.7643
600 | 50 | 50 | 102 | 220 | 50 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 350 | 72 | 422 | 3500 | 72 | 3572 |  |  | 50 MW | 300 | 50 | 0 | 0 | 50 | 22 | 422 | 1 | [10 empty] | 3000 | 500 | 0 | 0 | 50 | 22 | 3572 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 11.85% | 59.02% | 80.44% | 19.56% | 0% |  |  |  | 50 MW | 3390.2166 | 72 | 109.7834 | 2849.0791 | 692.993 | 29.9279 | 3326.1008 | 145.5774 | 100.3219 | 3407.5023 | 128.7038 | 35.7939 | 0 | 0 | 0 |  | 3500 | -3390.2166 | 109.7834 | 72 | -181.7834 | -109.7834 | 3500 | -2849.0791 | 650.9209 | 72 | -722.9209 | -650.9209 | 3500 | -3326.1008 | 173.8992 | 72 | -245.8992 | -173.8992 | 3500 | -3407.5023 | 92.4977 | 72 | -164.4977 | -92.4977
600 | 100 | 100 | 102 | 220 | 100 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 300 | 100 | 400 | 3000 | 100 | 3100 |  |  | 100 MW | 278 | 22 | 0 | 0 | 100 | 0 | 400 | 1 | [10 empty] | 2780 | 220 | 0 | 0 | 100 | 0 | 3100 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 25% | 18.03% | 80.44% | 19.56% | 0% |  |  |  | 100 MW | 2905.8999 | 100 | 94.1001 | 2472.605 | 601.4217 | 25.9733 | 2797.5762 | 225.3554 | 77.0684 | 3006.3379 | 62.0822 | 31.5799 | 0 | 0 | 0 |  | 3000 | -2905.8999 | 94.1001 | 100 | -194.1001 | -94.1001 | 3000 | -2472.605 | 527.395 | 100 | -627.395 | -527.395 | 3000 | -2797.5762 | 202.4238 | 100 | -302.4238 | -202.4238 | 3000 | -3006.3379 | -6.3379 | 100 | -93.6621 | 6.3379
600 | 220 | 220 | 102 | 220 | 220 | 10 | 1 | 400 | 122 | 102 | 400 | 122 | 1297 | 864 | 42 | 1 | 180 | 220 | 400 | 1800 | 220 | 2020 |  |  | 220 MW | 180 | 0 | 0 | 98 | 122 | 0 | 400 | 1 | [10 empty] | 1800 | 0 | 0 | 98 | 122 | 0 | 2020 | 1 | [10 empty] | 2 | 79.76% | 19.4% | 0.8378% | 98.96% | 100% | 1.04% | 55% | 0% | 80.44% | 19.56% | 0% |  |  |  | 220 MW | 1743.54 | 220 | 56.46 | 1611.1813 | 391.8941 | 16.9245 | 1670.7427 | 314.5418 | 34.7155 | 1975.5788 | 23.6689 | 20.7523 | 0 | 0 | 0 |  | 1800 | -1743.54 | 56.46 | 220 | -276.46 | -56.46 | 1800 | -1611.1813 | 188.8187 | 220 | -408.8187 | -188.8187 | 1800 | -1670.7427 | 129.2573 | 220 | -349.2573 | -129.2573 | 1800 | -1975.5788 | -175.5788 | 220 | -44.4212 | 175.5788
Illustrate impact of high HVDC transfers | [24 empty] | HVDC transfer
[26 empty] | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk |  |  |  | NI_IR_4_NI_CE | NI_IR 4 shared_AC_risk | NI_IR 4 SI_AC_Risk | SI_IR 4 NI_AC_Risk | SI_IR 4 shared_AC_risk | SI_IR 4 SI_Risk | NI_IR_4_NI_DC_CE |  |  | NI_IR 4 NI_Risk | NI_IR 4 shared_risk | NI_IR 4 SI_Risk | SI_IR 4 NI_Risk | SI_IR 4 shared_risk | SI_IR 4 SI_Risk | Tot |  |  | NI_IR_4_NI_CE | NI_IR 4 shared_AC_risk | NI_IR 4 SI_AC_Risk | SI_IR 4 NI_AC_Risk | SI_IR 4 shared_AC_risk | SI_IR 4 SI_Risk | NI_IR_4_NI_DC_CE | Tot | [16 empty] | Energy transfer across HVDC [NI DC CE risk]
0 | 220 | 220 | 0 | 220 | 220 | 10 | 1 | 400 | 122 | 0 | 400 | 122 | 1297 | 864 | 0 | 1 | 180 | 220 | 400 | 1800 | 220 | 2020 |  |  | 0 MW [0 MW] | 180 | 0 | 0 | 98 | 122 | 0 | 400 | 1 | 0 MW [0 MW] | 180 | 0 | 0 | 98 | 122 | 0 | 0 | 400 | 1 | 1800 | 0 | 0 | 98 | 122 | 0 | 2020 | 1 |  | 1800 | 0 | 0 | 98 | 122 | 0 | 0 | 2020 | 1 | 1 | 80.05% | 19.95% | 0% | 100% | 100% | 0% | 55% | 0% | 80.05% | 19.95% | 0% | SI IR price = $1/MW/h, NI IR price = $10/MW/h |  |  | 0 MW [0 MW] | 1800 | 220 | 0 | 1616.9888 | 403.0112 | 0 | 1699.3438 | 320.6562 | 0 | 1995.6597 | 24.3403 | 0 | 1995.6597 | 24.3403 | 0 |  | 1800 | -1800 | 0 | 220 | -220 | 0 | 1800 | -1616.9888 | 183.0112 | 220 | -403.0112 | -183.0112 | 1800 | -1699.3438 | 100.6562 | 220 | -320.6562 | -100.6562 | 1800 | -1995.6597 | -195.6597 | 220 | -24.3403 | 195.6597
700 | 220 | 220 | 202 | 220 | 198 | 10 | 1 | 400 | 122 | 202 | 400 | 122 | 1297 | 864 | 142 | 1 | 202 | 198 | 400 | 2020 | 198 | 2218 |  |  | 700 MW [202 MW] | 202 | 0 | 0 | 76 | 122 | 0 | 400 | 1 | 700 MW [202 MW] | 180 | 0 | 0 | 76 | 122 | 0 | 22 | 400 | 1 | 2020 | 0 | 0 | 76 | 122 | 0 | 2218 | 1 |  | 1800 | 0 | 0 | 76 | 122 | 0 | 220 | 2218 | 1 | 3 | 75.76% | 19.18% | 5.062% | 93.74% | 100% | 6.264% | 55% | 0% | 79.79% | 20.21% | 0% |  |  |  | 700 MW [202 MW] | 1820.6671 | 198 | 199.3329 | 1680.2466 | 425.4786 | 112.2747 | 1743.4358 | 323.1133 | 151.4509 | 2057.138 | 23.4032 | 137.4588 | 1860.6058 | 24.6511 | 332.7432 |  | 2020 | -1820.6671 | 199.3329 | 198 | -397.3329 | -199.3329 | 2020 | -1680.2466 | 339.7534 | 198 | -537.7534 | -339.7534 | 2020 | -1743.4358 | 276.5642 | 198 | -474.5642 | -276.5642 | 2020 | -2057.138 | -37.138 | 198 | -160.862 | 37.138
800 | 220 | 220 | 302 | 220 | 98 | 10 | 1 | 400 | 122 | 302 | 400 | 122 | 1297 | 864 | 242 | 1 | 302 | 98 | 400 | 3020 | 98 | 3118 |  |  | 800 MW [302 MW] | 278 | 24 | 0 | 0 | 98 | 0 | 400 | 1 | 800 MW [302 MW] | 180 | 0 | 0 | 0 | 98 | 0 | 122 | 400 | 1 | 2780 | 240 | 0 | 0 | 98 | 0 | 3118 | 1 |  | 1800 | 0 | 0 | 0 | 98 | 0 | 1220 | 3118 | 1 | 4 | 69.02% | 19.18% | 11.8% | 85.4% | 100% | 14.6% | 55% | 19.67% | 78.25% | 21.75% | 0% |  |  |  | 800 MW [302 MW] | 2545.1202 | 98 | 474.8798 | 2152.0966 | 598.1255 | 367.7779 | 2328.9572 | 373.069 | 415.9738 | 2607.5499 | 64.8385 | 445.6116 | 1613.9751 | 21.3133 | 1482.7116 |  | 3020 | -2545.1202 | 474.8798 | 98 | -572.8798 | -474.8798 | 3020 | -2152.0966 | 867.9034 | 98 | -965.9034 | -867.9034 | 3020 | -2328.9572 | 691.0428 | 98 | -789.0428 | -691.0428 | 3020 | -2607.5499 | 412.4501 | 98 | -510.4501 | -412.4501
900 | 220 | 200 | 402 | 220 | -2 | 10 | 1 | 400 | 122 | 402 | 402 | 122 | 1297 | 864 | 342 | 1 | 402 | 0 | 402 | 4020 | 0 | 4020 |  |  | 900 MW [402 MW] | 280 | 122 | 0 | 0 | 0 | 0 | 402 | 1 | 900 MW [402 MW] | 180 | 0 | 0 | 0 | 0 | 0 | 222 | 402 | 1 | 2800 | 1220 | 0 | 0 | 0 | 0 | 4020 | 1 |  | 1800 | 0 | 0 | 0 | 0 | 0 | 2220 | 4020 | 1 | 5 | 59.93% | 19.09% | 20.98% | 74.07% | 100% | 25.93% | 49.75% | 100% | 75.84% | 24.16% | 0% |  |  |  | 900 MW [402 MW] | 3181.1714 | 0 | 838.8286 | 2409.2013 | 767.3195 | 843.4792 | 2797.1067 | 381.751 | 841.1423 | 2805.0597 | 232.8681 | 982.0722 | 1333.2272 | 0 | 2686.7728 |  | 4020 | -3181.1714 | 838.8286 | 0 | -838.8286 | -838.8286 | 4020 | -2409.2013 | 1610.7987 | 0 | -1610.7987 | -1610.7987 | 4020 | -2797.1067 | 1222.8933 | 0 | -1222.8933 | -1222.8933 | 4020 | -2805.0597 | 1214.9403 | 0 | -1214.9403 | -1214.9403
1000 | 220 | 100 | 502 | 220 | -102 | 10 | 1 | 400 | 122 | 502 | 502 | 122 | 1297 | 864 | 442 | 1 | 502 | 0 | 502 | 5020 | 0 | 5020 |  |  | 1000 MW [502 MW] | 380 | 122 | 0 | 0 | 0 | 0 | 502 | 1 | 1000 MW [502 MW] | 180 | 0 | 0 | 0 | 0 | 0 | 322 | 502 | 1 | 3800 | 1220 | 0 | 0 | 0 | 0 | 5020 | 1 |  | 1800 | 0 | 0 | 0 | 0 | 0 | 3220 | 5020 | 1 | 6 | 47.99% | 15.29% | 36.72% | 56.65% | 100% | 43.35% | 19.92% | 100% | 75.84% | 24.16% | 0% |  |  |  | 1000 MW [502 MW] | 3744.0713 | 0 | 1275.9287 | 2409.2013 | 767.3195 | 1843.4792 | 3478.1609 | 152.8525 | 1388.9866 | 2738.2547 | 186.48 | 2095.2653 | 1019.7244 | 0 | 4000.2756 |  | 5020 | -3744.0713 | 1275.9287 | 0 | -1275.9287 | -1275.9287 | 5020 | -2409.2013 | 2610.7987 | 0 | -2610.7987 | -2610.7987 | 5020 | -3478.1609 | 1541.8391 | 0 | -1541.8391 | -1541.8391 | 5020 | -2738.2547 | 2281.7453 | 0 | -2281.7453 | -2281.7453
[75 empty] | Which example to look at: IR transfer capability (0) or Imapct of high HVDC transfers (1) | 1
8
.
[15 empty] | Impact of different transfer levels | [60 empty] | General allocation approach = Runway. No large thermals are retired. SI IR price = $1/MW/h, NI IR price = $10/MW/h
[76 empty] | Energy transfer across HVDC [NI DC CE risk] |  | North gen. > de minimis | South gen. > de minimis | HVDC | Total
[63 empty] | 0: North 2 gen.; 1: South via HVDC; 2: South 2 gen. | [5 empty] | 1 | 1 | 0 MW [0 MW] | Island | 1800 | 220 | 0 | 2020
[63 empty] | 0: 79.76%; 1: 0.8378%; 2: 19.4% | [5 empty] | 1 | 2 |  | National | 1616.9888 | 403.0112 | 0 | 2020
[74 empty] | 1 | 3 |  | Factored by sharing limit | 1699.3438 | 320.6562 | 0 | 2020 | [12 empty] | Earned | Allocated | Net
[74 empty] | 1 | 4 |  | Cost to island causer | 1995.6597 | 24.3403 | 0 | 2020 |  |  |  | 1 | 0 | 1 | 0 MW [0 MW] IR transferred | North |  |  |  | Island | 1800 | -1800 | 0
[74 empty] | 1 | 5 |  | Cost to DC then island | 1995.6597 | 24.3403 | 0 | 2020 |  |  |  | 1 | 0 | 2 | [5 empty] | National | 1800 | -1616.9888 | 183.0112
[74 empty] | 2 | 1 | 700 MW [202 MW] | Island | 1820.6671 | 198 | 199.3329 | 2218 |  |  |  | 1 | 0 | 3 | [5 empty] | Factored by sharing limit | 1800 | -1699.3438 | 100.6562
[74 empty] | 2 | 2 |  | National | 1680.2466 | 425.4786 | 112.2747 | 2218 |  |  |  | 1 | 0 | 4 | [5 empty] | Cost to island causer | 1800 | -1995.6597 | -195.6597
[74 empty] | 2 | 3 |  | Factored by sharing limit | 1743.4358 | 323.1133 | 151.4509 | 2218 |  |  |  | 1 | 3 | 1 |  | South |  |  |  | Island | 220 | -220 | 0
[74 empty] | 2 | 4 |  | Cost to island causer | 2057.138 | 23.4032 | 137.4588 | 2218 |  |  |  | 1 | 3 | 2 | [5 empty] | National | 220 | -403.0112 | -183.0112
[74 empty] | 2 | 5 |  | Cost to DC then island | 1860.6058 | 24.6511 | 332.7432 | 2218 |  |  |  | 1 | 3 | 3 | [5 empty] | Factored by sharing limit | 220 | -320.6562 | -100.6562
[74 empty] | 4 | 1 | 900 MW [402 MW] | Island | 3181.1714 | 0 | 838.8286 | 4020 |  |  |  | 1 | 3 | 4 | [5 empty] | Cost to island causer | 220 | -24.3403 | 195.6597
[74 empty] | 4 | 2 |  | National | 2409.2013 | 767.3195 | 843.4792 | 4020 |  |  |  | 1 | 0 | 1 | 0 MW [0 MW] IR transferred | North |  |  |  | Island | 1800 | -1800 | 0
[74 empty] | 4 | 3 |  | Factored by sharing limit | 2797.1067 | 381.751 | 841.1423 | 4020 |  |  |  | 1 | 0 | 2 | [5 empty] | National | 1800 | -1616.9888 | 183.0112
[74 empty] | 4 | 4 |  | Cost to island causer | 2805.0597 | 232.8681 | 982.0722 | 4020 |  |  |  | 1 | 0 | 3 | [5 empty] | Factored by sharing limit | 1800 | -1699.3438 | 100.6562
[74 empty] | 4 | 5 |  | Cost to DC then island | 1333.2272 | 0 | 2686.7728 | 4020 |  |  |  | 1 | 0 | 4 | [5 empty] | Cost to island causer | 1800 | -1995.6597 | -195.6597
[74 empty] | 5 | 1 | 1000 MW [502 MW] | Island | 3744.0713 | 0 | 1275.9287 | 5020 |  |  |  | 1 | 3 | 1 |  | South |  |  |  | Island | 220 | -220 | 0
[74 empty] | 5 | 2 |  | National | 2409.2013 | 767.3195 | 1843.4792 | 5020 |  |  |  | 1 | 3 | 2 | [5 empty] | National | 220 | -403.0112 | -183.0112
[74 empty] | 5 | 3 |  | Factored by sharing limit | 3478.1609 | 152.8525 | 1388.9866 | 5020 |  |  |  | 1 | 3 | 3 | [5 empty] | Factored by sharing limit | 220 | -320.6562 | -100.6562
[74 empty] | 5 | 4 |  | Cost to island causer | 2738.2547 | 186.48 | 2095.2653 | 5020 |  |  |  | 1 | 3 | 4 | [5 empty] | Cost to island causer | 220 | -24.3403 | 195.6597
[74 empty] | 5 | 5 |  | Cost to DC then island | 1019.7244 | 0 | 4000.2756 | 5020 |  |  |  | 2 | 0 | 1 | 700 MW [202 MW] IR transferred | North |  |  |  | Island | 2020 | -1820.6671 | 199.3329
[85 empty] | 2 | 0 | 2 | [5 empty] | National | 2020 | -1680.2466 | 339.7534
[85 empty] | 2 | 0 | 3 | [5 empty] | Factored by sharing limit | 2020 | -1743.4358 | 276.5642
[85 empty] | 2 | 0 | 4 | [5 empty] | Cost to island causer | 2020 | -2057.138 | -37.138
[85 empty] | 2 | 3 | 1 |  | South |  |  |  | Island | 198 | -397.3329 | -199.3329
[85 empty] | 2 | 3 | 2 | [5 empty] | National | 198 | -537.7534 | -339.7534
[85 empty] | 2 | 3 | 3 | [5 empty] | Factored by sharing limit | 198 | -474.5642 | -276.5642
[85 empty] | 2 | 3 | 4 | [5 empty] | Cost to island causer | 198 | -160.862 | 37.138
Note on A7: Simon Coates: Ideally Make this in increments of 100 above 600 MW. For lookup purposes for therunway illustration
Note on C1: Simon Coates: Could do 220 less 5% losses to reflect SIR capability received.
Note on Q7: Simon Coates: It is infeasible to not have price separation in a situation where high HVDC energy transfers means that all IR needs to be procured in the receiving island.
Note on BW7: Simon Coates: The divide by 8 term for the second half of the runway approach is to crudely estimate the proportion which wasn't solely attributable to the HVDC which would be picked up by the HVDC as its share.
Note on BX6: Simon Coates: Option C in March 2016 consultation
Note on CN6: Simon Coates: Option C in March 2016 consultation

## GenUnits
[18 empty] | HVDC transfer level, received (MW) | 600
Station | Huntly - e3p | TCC | Huntly Rankines | Stratford pkrs | Glenbrook | Nga Awa Purua | Kawerau | Te Mihi | Manapouri | Clutha -Clyde | Waitaki - Benmore | Waitaki - Tekapo | Waitaki - Ohau | HVDC CE risk | . | . |  | de minimis | 60 | 60 MW de minimis; 600 MW HVDC transfer = 102 MW NI DC CE risk
Type | Thermal | Thermal | Thermal | Thermal | Thermal | Geothermal | Geothermal | Geothermal | Hydro | Hydro | Hydro | Hydro | Hydro | HVDC | All | All
Capacity | 400 | 385 | 500 | 200 | 68 | 138 | 100 | 166 | 854 | 432 | 540 | 154 | 264 | 102 | 2545 | 1095
# units | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 7 | 4 | 6 | 2 | 4 | 1 | 1 | 1
Unit size (MW) | 400 | 385 | 250 | 100 | 68 | 138 | 100 | 83 | 122 | 108 | 90 | 77 | 66 | 102 | 2545 | 1095
Factor | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0%
Unit size (MW) | 400 | 385 | 250 | 100 | 68 | 138 | 100 | 83 | 122 | 108 | 90 | 77 | 66 | 102 | 0 | 0
Above de minimis | 340 | 325 | 190 | 40 | 8 | 78 | 40 | 23 | 62 | 48 | 30 | 17 | 6 | 42 | 0 | 0 |  |  |  |  | N | S | HVDC
Owner | Genesis | Contact | Genesis | Contact | Alinta | Mercury | Mercury | Contact | Meridian | Contact | Meridian | Genesis | Meridian | Transpower | [5 empty] | Total gen. above de minimis (excl. HVDC) | 1297 | 864
Island | N | N | N | N | N | N | N | N | S | S | S | S | S | N | N | S |  |  |  | Max gen. | 400 | 122 | 102
Offset | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
| 1 | 2 | 4 | 6 | 7 | 8 | 9 | 11 | 18 | 22 | 28 | 30 | 34 | 35 | 36 | 37
| Huntly - e3p ¦ 1 ¦ Therm | TCC ¦ 1 ¦ Therm | Huntly Rankines ¦ 2 ¦ Therm | Stratford pkrs ¦ 2 ¦ Therm | Glenbrook ¦ 1 ¦ Therm | Nga Awa Purua ¦ 1 ¦ Geoth | Kawerau ¦ 1 ¦ Geoth | Te Mihi ¦ 2 ¦ Geoth | Manapouri ¦ 7 ¦ Hydro | Clutha -Clyde ¦ 4 ¦ Hydro | Waitaki - Benmore ¦ 6 ¦ Hydro | Waitaki - Tekapo ¦ 2 ¦ Hydro | Waitaki - Ohau ¦ 4 ¦ Hydro | HVDC CE risk ¦ 1 ¦ HVDC
Genesis | 400 |  | 250 | [8 empty] | 77
Contact |  | 385 |  | 100 |  |  |  | 83 |  | 108
Meridian | [8 empty] | 122 |  | 90 |  | 66
Mercury | [5 empty] | 138 | 100
Alinta |  |  |  |  | 68
Transpower | [13 empty] | 102
| Choose capacity (0) or above de minimis (1) | 1
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37
Offset | 1 | 2 | 3 | 3 | 4 | 4 | 5 | 6 | 7 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 13 | 13 | 13 | 13 | 14 | 15 | 16
Name | Huntly - e3p | TCC | Huntly Rankines | Huntly Rankines | Stratford pkrs | Stratford pkrs | Glenbrook | Nga Awa Purua | Kawerau | Te Mihi | Te Mihi | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Clutha -Clyde | Clutha -Clyde | Clutha -Clyde | Clutha -Clyde | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Tekapo | Waitaki - Tekapo | Waitaki - Ohau | Waitaki - Ohau | Waitaki - Ohau | Waitaki - Ohau | HVDC CE risk | . | .
| Huntly - e3p | TCC | Huntly Rankines | '' | Stratford pkrs | '' | Glenbrook | Nga Awa Purua | Kawerau | Te Mihi | '' | Manapouri | '' | '' | '' | '' | '' | '' | Clutha -Clyde | '' | '' | '' | Waitaki - Benmore | '' | '' | '' | '' | '' | Waitaki - Tekapo | '' | Waitaki - Ohau | '' | '' | '' | HVDC CE risk
Owner | Genesis | Contact | Genesis | Genesis | Contact | Contact | Alinta | Mercury | Mercury | Contact | Contact | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Contact | Contact | Contact | Contact | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Genesis | Genesis | Meridian | Meridian | Meridian | Meridian | Transpower | 0 | 0
Island | N | N | N | N | N | N | N | N | N | N | N | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | S | N | N | S
Pro-rata Unit output (MW) | 340 | 325 | 190 | 190 | 40 | 40 | 8 | 78 | 40 | 23 | 23 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 48 | 48 | 48 | 48 | 30 | 30 | 30 | 30 | 30 | 30 | 17 | 17 | 6 | 6 | 6 | 6 | 42 | 3.7e-07 | 3.8e-07 | ~~~ | 2161 | FALSE
Runway Unit output | 400 | 385 | 250 | 250 | 100 | 100 | 68 | 138 | 100 | 83 | 83 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 108 | 108 | 108 | 108 | 90 | 90 | 90 | 90 | 90 | 90 | 77 | 77 | 66 | 66 | 66 | 66 | 102 | 3.7e-07 | 3.8e-07 | ~~~ | [8 empty] | Hard-wired runway allocatino - for use in illustration of cost allcoatino outcomes | [5 empty] | National Runway allocation | [5 empty] | Within-island
National rank | 1 | 2 | 4 | 3 | 20 | 19 | 31 | 5 | 18 | 28 | 27 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 16 | 15 | 14 | 13 | 26 | 25 | 24 | 23 | 22 | 21 | 30 | 29 | 35 | 34 | 33 | 32 | 17 | 37 | 36 | ~~~ |  |  | Total runway allocation | [5 empty] | 0 = No large thermals |  |  | 1 = With large thermals |  |  | 0 = No large thermals |  |  | 1 = With large thermals |  |  | 0 = No large thermals |  |  | 1 = With large thermals
National runway allocation share | 118.5931 | 103.5931 | 36.0931 | 36.0931 | 3.2337 | 3.2337 | 1.9502 | 8.0931 | 3.2337 | 2.4645 | 2.4645 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 3.7264 | 3.7264 | 3.7264 | 3.7264 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.2502 | 2.2502 | 1.8857 | 1.8857 | 1.8857 | 1.8857 | 3.3514 | #N/A | #N/A |  |  |  | N | S | HVDC | Total |  |  | N | S | HVDC | N | S | HVDC | N | S | HVDC | N | S | HVDC | N | S | HVDC | N | S | HVDC | 0
[41 empty] | 319.0458 | 77.6028 | 3.3514 | 400 | HVDC Energy transfer | 0 | 42.0803 | 95.9197 | 0 | 320.1958 | 79.8042 | 0 | 30.49% | 69.51% | 0% | 80.05% | 19.95% | 0% | 100% | 100% | 0% | 100% | 100% | 0%
[40 empty] | Share of Total | 79.76% | 19.4% | 0.8378% |  |  | 600 | 41.1752 | 92.9285 | 3.8963 | 319.0458 | 77.6028 | 3.3514 | 29.84% | 67.34% | 2.823% | 79.76% | 19.4% | 0.8378% | 91.36% | 100% | 8.645% | 98.96% | 100% | 1.04%
Col offset | 1 | 2 | 4 | 3 | 8 | 18 | 17 | 16 | 15 | 14 | 13 | 12 | 22 | 21 | 20 | 19 | 35 | 9 | 6 | 5 | 28 | 27 | 26 | 25 | 24 | 23 | 11 | 10 | 30 | 29 | 7 | 34 | 33 | 32 | 31 |  |  |  |  | Share of Non-HVDC total | 80.44% | 19.56% |  |  |  | 700 | 32.9423 | 91.1443 | 77.9134 | 303.0201 | 76.7319 | 20.2479 | 16.31% | 45.12% | 38.57% | 75.76% | 19.18% | 5.062% | 29.72% | 100% | 70.28% | 93.74% | 100% | 6.264%
What | Huntly - e3p | TCC | Huntly Rankines | Huntly Rankines | Nga Awa Purua | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Manapouri | Clutha -Clyde | Clutha -Clyde | Clutha -Clyde | Clutha -Clyde | HVDC CE risk | Kawerau | Stratford pkrs | Stratford pkrs | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Waitaki - Benmore | Te Mihi | Te Mihi | Waitaki - Tekapo | Waitaki - Tekapo | Glenbrook | Waitaki - Ohau | Waitaki - Ohau | Waitaki - Ohau | Waitaki - Ohau | [10 empty] | 800 | 32.9423 | 91.1443 | 177.9134 | 276.0868 | 76.7319 | 47.1813 | 10.91% | 30.18% | 58.91% | 69.02% | 19.18% | 11.8% | 15.62% | 100% | 84.38% | 85.4% | 100% | 14.6%
| Huntly - e3p | TCC | Huntly Rankines |  | Nga Awa Purua | Manapouri | [6 empty] | Clutha -Clyde |  |  |  | HVDC CE risk | Kawerau | Stratford pkrs |  | Waitaki - Benmore | [5 empty] | Te Mihi |  | Waitaki - Tekapo |  | Glenbrook | Waitaki - Ohau | [13 empty] | 900 | 32.9423 | 91.1443 | 277.9134 | 240.9201 | 76.7319 | 84.3479 | 8.195% | 22.67% | 69.13% | 59.93% | 19.09% | 20.98% | 10.6% | 100% | 89.4% | 74.07% | 100% | 25.93%
[46 empty] | 1000 | 32.9423 | 91.1443 | 377.9134 | 240.9201 | 76.7319 | 184.3479 | 6.562% | 18.16% | 75.28% | 47.99% | 15.29% | 36.72% | 8.018% | 100% | 91.98% | 56.65% | 100% | 43.35%
Size | 400 | 385 | 250 | 250 | 138 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 108 | 108 | 108 | 108 | 102 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 83 | 83 | 77 | 77 | 68 | 66 | 66 | 66 | 66 | 0 | [9 empty] | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~ | ~~~
Incremental risk | 15 | 135 | 0 | 112 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 6 | 0 | 9 | 2 | 0 | 0 | 0 | 66
Cost allocation proportions | 118.5931 | 103.5931 | 36.0931 | 36.0931 | 8.0931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 3.7264 | 3.7264 | 3.7264 | 3.7264 | 3.3514 | 3.2337 | 3.2337 | 3.2337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.4645 | 2.4645 | 2.2502 | 2.2502 | 1.9502 | 1.8857 | 1.8857 | 1.8857 | 1.8857
Owner | Genesis | Contact | Genesis | Genesis | Mercury | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Contact | Contact | Contact | Contact | Transpower | Mercury | Contact | Contact | Meridian | Meridian | Meridian | Meridian | Meridian | Meridian | Contact | Contact | Genesis | Genesis | Alinta | Meridian | Meridian | Meridian | Meridian
| Huntly - e3p | TCC | Huntly Rankines |  | Nga Awa Purua | Manapouri | [6 empty] | Clutha -Clyde |  |  |  | HVDC CE risk | Kawerau | Stratford pkrs |  | Waitaki - Benmore | [5 empty] | Te Mihi |  | Waitaki - Tekapo |  | Glenbrook | Waitaki - Ohau
Genesis | 118.5931 |  | 36.0931 | 36.0931 | [24 empty] | 2.2502 | 2.2502
Contact |  | 103.5931 | [10 empty] | 3.7264 | 3.7264 | 3.7264 | 3.7264 |  |  | 3.2337 | 3.2337 | [6 empty] | 2.4645 | 2.4645
Meridian | [5 empty] | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | 4.8931 | [8 empty] | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | 2.7337 | [5 empty] | 1.8857 | 1.8857 | 1.8857 | 1.8857
Mercury |  |  |  |  | 8.0931 | [12 empty] | 3.2337
Alinta | [30 empty] | 1.9502
Transpower | [16 empty] | 3.3514
Note on A3: Simon Coates: From Generation units over 60MW_v02
Note on A40: Simon Coates: Takes no account of de minimis
Note on G3: Simon Coates: On the Rotokawa geothermal field. Note: There is a smaller (38 MW) Rotokawa power station as well.