## Instructions
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Introduction
Clause 8(2)(a) of Technical Code A of Schedule 8.3 of the Code requires each asset owner to carry out periodic testing of its assets in accordance with Appendix B of Technical Code A of Schedule 8.3.
The Electricity Authority is undertaking a stocktake of asset owners' compliance with the testing requirements set out in Appendix B of Technical Code A.
The Authority will be sharing the information it gathers with the system operator.
Your organisation warrants that the information it provides to the Electricity Authority is correct.
Instructions for completing the tables in this workbook
This Excel workbook contains 6 worksheets - shown by the 6 tabs across the bottom of the workbook.
The first tab contains this 'Instructions' worksheet
Each of the remaining 5 tabs contains a worksheet with several tables to be completed. Each worksheet relates to a different clause in Appendix B of Technical Code A.
The worksheet relating to clause 2 contains 4 tables to be completed.
The worksheet relating to clause 3 contains 3 tables to be completed.
The worksheet relating to clause 4 contains 3 tables to be completed.
The worksheet relating to clause 5 contains 3 tables to be completed.
The worksheet relating to clause 13 contains 8 tables to be completed.
Scroll across the worksheet in each tab to move between the tables.
Complete each table by populating data down the worksheet. Please continue to populate data down the worksheet if you reach the end of the highlighted table.
PLEASE NOTE:
1. You are required to complete the tables in worksheets 2-5 only if you own generation >10 MW at your site(s) for which wind is NOT the primary power source. In other words, please complete only the 6 tables in the final worksheet (which relates to clause 13 of Appendix B), if you have no generation at your site(s) or all of the generation you own at your site(s) that is >10 MW uses wind as its primary power source.
2. You are not required to complete the tables in worksheets 2-3 for any excluded generation station asset at your site. Please refer to clause 8.21(1) of the Code for the definition of excluded generating station.
For further information
If you have any queries, please contact Peter Wakefield of the Authority's compliance team.
Peter's contact details are: (04) 460 8864 or peter.wakefield@ea.govt.nz

## Appendix B Clause 2
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Generating unit frequency response
(Schedule 8.3, Technical Code A, Appendix B, clause 2)
Clause 2(a) Test the trip frequencies and trip time delays of each generating unit’s analogue over-frequency relays and analogue under-frequency relays at least once every 4 years | [7 empty] | Clause 2(b) Test the trip frequencies and trip time delays of each generating unit’s non-self monitoring digital over-frequency relays and non-self monitoring digital under-frequency relays at least once every 4 years | [7 empty] | Clause 2(c) Test the trip frequencies and trip time delays of each generating unit’s self monitoring digital over-frequency relays and self monitoring digital under-frequency relays at least once every 10 years | [7 empty] | Clauses 2(d) and 2(e) Based on the tests under paragraphs 2(a)-2(c), provide a verified set of under- and over-frequency trip settings and time delays to the system operator in an updated asset capability statement
Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Was a verified set of under-frequency trip settings and time delays provided to the system operator? | Was a verified set of over-frequency trip settings and time delays provided to the system operator? | Was the verified set of trip settings and time delays provided in an updated asset capability statement?

## Appendix B Clause 3
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Generating unit governor and speed control
(Schedule 8.3, Technical Code A, Appendix B, clause 3)
Clause 3(a) Test the governor system response of each generating unit’s mechanical or analogue speed governors at least once every 5 years | [10 empty] | Clause 3(b) Test the governor system response of each generating unit’s digital or electro-hydraulic speed governors at least once every 10 years | [10 empty] | Clause 3(c) Based on the tests under paragraphs 3(a)-3(b), or based on representative sampling, provide a verified set of modelling parameters and governor system response data to the system operator in an updated asset capability statement
[6 empty] | If representative sampling used - | [10 empty] | If representative sampling used -
Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Representative sampling used? (Refer to clause 14 of Appendix B of Technical Code A) (Y/N) | Which asset is the ‘parent’ for the purposes of representative testing? | Date when the ‘parent' asset was last tested | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Representative sampling used? (Refer to clause 14 of Appendix B of Technical Code A) (Y/N) | Which asset is the ‘parent’ for the purposes of representative testing? | Date when the ‘parent' asset was last tested | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Was a verified set of modelling parameters and voltage response data provided to the system operator? | Was the verified set of modelling parameters and voltage response data provided in an updated asset capability statement?

## Appendix B Clause 4
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Generating unit transformer voltage control
(Schedule 8.3, Technical Code A, Appendix B, clause 4)
Clause 4(a) Test the operation of each generating unit transformer’s on‑load tap changer analogue control systems at least once every 4 years | [7 empty] | Clause 4(b) Test the operation of each generating unit transformer’s on‑load tap changer digital control systems at least once every 10 years | [7 empty] | Clause 4(c) Based on the tests under paragraphs 4(a)-4(b), provide a verified set of control parameters including voltage set points, operating dead bands and response times to the system operator in an updated asset capability statement
Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Was a verified set of control parameters provided to the system operator? | Was the verified set of control parameters provided in an updated asset capability statement?

## Appendix B Clause 5
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Generating unit voltage response and control
(Schedule 8.3, Technical Code A, Appendix B, clause 5)
Clause 5(a) Test the modelling parameters and voltage response of each generating unit’s analogue excitation systems at least once every 5 years | [10 empty] | Clause 5(b) Test the modelling parameters and voltage response of each generating units’ digital excitation systems at least once every 10 years | [10 empty] | Clause 5(c) Based on the tests under paragraphs 5(a)-5(b), or based on representative sampling, provide a verified set of modelling parameters and voltage response data to the system operator in an updated asset capability statement
[6 empty] | If representative sampling used - | [10 empty] | If representative sampling used -
Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Representative sampling used? (Refer to clause 14 of Appendix B of Technical Code A) (Y/N) | Which asset is the ‘parent’ for the purposes of representative testing? | Date when the ‘parent' asset was last tested | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Representative sampling used? (Refer to clause 14 of Appendix B of Technical Code A) (Y/N) | Which asset is the ‘parent’ for the purposes of representative testing? | Date when the ‘parent' asset was last tested | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Was a verified set of modelling parameters and voltage response data provided to the system operator? | Was the verified set of modelling parameters and voltage response data provided in an updated asset capability statement?

## Appendix B Clause 13
Monitoring of compliance with Code requirements for periodic testing of assets
As at 30 June 2017
Asset owner a.c. protection systems
(Schedule 8.3, Technical Code A, Appendix B, clause 13)
Clause 13(a) Test the operation of the analogue protection systems on the a.c. assets at least once every 4 years | [7 empty] | Clause 13(b) Test the operation of the non-self monitoring digital protection systems on the a.c assets at least once every 4 years | [7 empty] | Clause 13(c) Test the operation of the self monitoring digital protection systems on the a.c. assets at least once every 10 years | [7 empty] | Clause 13(d) Test the operation of the protection system measuring circuits on the a.c. assets by secondary injection at least once every 4 years | [7 empty] | Clause 13(e) Test the operation of the protection system trip circuits, including circuit breaker trips, on the a.c. assets at least once every 4 years | [7 empty] | Clause 13(f) Confirm, at least once every 4 years, that the protection settings are identified, co-ordinated, applied correctly and meet the requirements of the AOPOs and the technical codes | [7 empty] | Clause 13(g) Based on the tests under paragraphs 13(a)-13(e), provide a verification to the system operator in an updated asset capability statement that the protection systems meet the requirements of the AOPOs and technical codes |  | Clause 13(h) Based on the confirmation under paragraph 13(f), provide an updated asset capability statement
Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Participant name | Site name (eg, HLY, SFD) | Asset ID (e.g. G1 or HLY CB 362) | Nameplate capacity | Test date (dd/mm/yyyy) | Were the test results provided to the system operator? | What action is being taken to address any non-compliance? | Intended date for resolution of non-compliance (if applicable) (mm/yyyy) | Was the system operator provided with a verification that the protection systems meet the requirements of the AOPOs and technical codes? | Was the verification provided in an updated asset capability statement? | Was an updated asset capability statement provided to the system operator following a confirmation under paragraph 13(f)?