## Sheet1
Code/ Provision | Details of Provisions | Explanation
Clauses 10.6, 10.20(b), 10.43(2)(b) and clause 4(1)(a) of Schedule 10.6, clause 19(1)(b) and (2)(f) of Schedule 10.7 and clause 7 of Schedule 11.4 | Participant to provide accurate information Obligations of metering equipment provider Metering installations that are inaccurate, defective, or not fit for purpose to be investigated Metering equipment provider record keeping and documentation Modification of metering installations Metering equipment provider to provide registry metering records to registry | A claim was made that incorrect ICP information in the registry had resulted in double-billing a customer. The double-biling however resulted from the ICP's incorrect status setting ("active") rather than the information provided to the registry. The incorrect information related to a decomissioned ICP which meant there was no Code obligation on the MEP and therefore no responsibility for any loss.. The Committee decided to take no further action on the alleged breach under regulation 11(1)(b).
clause 13.82(2) | Dispatch instructions to be complied with as issued by the system operator | As a result of a distraction when managing a bona-fide event at a different generation plant, the generation controller failed to implement a dispatch instruction. The breach caused minimal impact. Steps have been taken to prevent recurrence. It was noted this is the third dispatch breach in a very short timeframe related to ramping up/down a dispatch block. The Committee: (a) decided to take no further action on the alleged breach under regulation 11(1)(c) (b) issued a strong warning letter requesting the particiant advise what steps are to be taken to avoid repeat breach occurrences of this nature.
clause 11.15AB(4) | Switch saving protection - A losing trader referred to in subclause (2) …. must not, by any means, initiate contact with the customer to attempt to persuade the customer to terminate the arrangement referred to in subclause (2) or subclause (3) (as the case may be) during the period specified in subclause (5), including by— (a) making a counter-offer to the customer; or (b) offering an enticement to the customer. | The participant breached clause 11.15AB(4) by attempting to persuade a former customer to terminate its new arrangement with a save-protected retailer. The participan contacted its former customer before the event date of switching (the save protection period). The win back call was initiated to win the customer back because the customer had switched its gas contract to another retailer as well and there is no protection period for gas switching. The impact of the breach resulted in a successful save attempt by the participant with the save-protected retailer loosing out. The Committee: (a) decided to take no further action on the alleged breach under regulation 11(1)(c) (b) issued a strong warning letter.
Clause 5(1)(c)(ii) of Technical Code A of Schedule 8.3 and rule 5.1.3.2 of Technical Code A of Schedule C3 of Part C | Specific requirements for generators | There was no breach of clause 5(1)(c)(ii) of Technical Code A of Schedule 8.3 (or rule 5.1.3.2 of Technical Code A of Schedule C3 of Part C). The Code only requires that speed governors have an adjustable droop over the range of 0 %–7 %, and this requirement was met. The actual setting requirements are set out in clause 5(1)(d) of Technical Code A of Schedule 8.3. There is no evidence that the participant did not comply with this provision. The Committee decided to take no further action on the alleged breach under regulation 11(1)(b).
Clauses 8.19(3)(a) and 8.17 and clause 5(1)(a)(i) of Schedule 8.3, Technical Code A | Contributions to frequency support in under-frequency events Contribution by injections to overall frequency management Specific requirements for generators | During a serious under-frequency event which required automatic under-frequency load shedding (AUFLS), the generation station reduced its generation output due to incorrect governor settings. This breach caused a second fall in frequency, which reached a low of 48.52 Hz about five minutes after the first under frequency event. There was a significant security impact on the system. Steps have been taken to prevent recurrence. The system operator is also preparing a report including recommendations which will prevent recurrence. The Committee: (a) decided to take no further action on the alleged breach under regulation 11(1)(c) (b) issued a strong warning letter.
clause 13.69A | The system operator must prepare a dispatch schedule | The system operator breached clause 13.69A when it failed to prepare the dispatch schedule according to the methodology described in Schedule 13.3. The breach caused a systerm impact creating a potential security risk. Steps have been taken to prevent recurrence. The Committee: (a) decided to take no further action on the alleged breach under regulation 11(1)(c) (b) issued a strong warning letter.
clause 13.71(1)(b) | System operator to use certain things - (1) In determining dispatch instructions when implementing a dispatch schedule under clause 13.72(1)(a), the system operator must use— (b) any revised offer from a generator notified in accordance with clause 13.19 (except for revised offers submitted by an intermittent generator under clause 13.19(1)(a)(iii)); and… | The system operator failed to use a revised offer in determining dispatch instructions. A bona fide offer revision for a geothermal generating station was submitted. However, the resultant discretionary constraint was mistakenly applied to a different generator. This caused a subsequent constraint for approximately 30 minutes. There was negligible market impact. Steps have been taken to prevent recurrence. The Committee: (a) decided to take no further action on the alleged breach under regulation 11(1)(c) (b) issued a warning letter.
clause 13.69A | The system operator must prepare a dispatch schedule | Due to a manual input error, incorrect constraint limits were applied breaching clause 13.69A of the Code. Impact was negligible. The Committee decided to take no further action on the alleged breach under regulation 11(1)(c).