## Sheet1
Code/ Provision | Details of Provisions | Explanation
Numerous clauses Part 10 • clause 10.38(a) • clauses 10.44(1)(a) and 10.44(3)(a) • clause 4(1)(a) and (b) of Schedule 10.6 • clauses 1 and 15 of Schedule 10.7 • Table 1 of Schedule 11.4. | 10.38 Certification of metering installations A metering equipment provider must— (a) obtain and maintain certification in accordance with this Part— (i) for each metering installation for which it is responsible; and (ii) for each metering component in a metering installation for which it is responsible; and 10.44 Metering installations that are inaccurate, defective, or not fit for purpose to be tested 4 Metering equipment provider record keeping and documentation 1 Maintenance and repair of metering installations 15 Recertification programme Table 1 of Schedule 11.4 sets out the required and optional registry metering records. | The participant breached clauses 4(1)(a) and (b) of Schedule 10.6 by failing to keep accurate and correct records and breached clause 1 of Schedule 10.7 by not maintaining the records of the metering installation. The participant also breached clause 15 of Schedule 10.7 by not having a recertification programme in place to ensure recertification of this metering installation was completed prior to certification expiry. However, the participant did not breach clauses 10.44(1) and 10.44(3) because it did arrange for testing of the metering installation. Table 1 of Schedule 11.4, cannot be breached because this table defines the registry metering records. The obligation for an MEP to keep accurate and correct records as specified in Table 1, is contained in clause 4(1)(a) and (b) of Schedule 10.6. The participant did breach clause 10.38(a) by failing to maintain metering certification at the ICP. However on 26 May 2016, the Committee decided to take no further action on breaches of clause 10.38(a) concerning all of the particiants uncertified metering installations which included the metering installation in this case. The Committee: (a) decided to take no further action on the alleged breaches of clause 4(1)(a) and (b) of Schedule 10.6, and clause 15 of Schedule 10.7 under regulation 11(1)(c) (b) decided to take no further action on the alleged breaches of clauses 10.44(1)(a), 10.44(3)(a), clause 1 of Schedule 10.7, and Table 1 of Schedule 11.4 under regulation 11(1)(b) (c) noted it could not take further action on the alleged breach of clause 10.38(a) as it had previously declined to take action under regulation 11. The reasons for the Committee’s decision under regulation 11(1)(c) were: (i) there was no market impact (ii) the metering installation has been replaced and certified (iii) metering data from the new meter indicated the old meter was accurate.
clause 4(4)(a)(i) of Technical Code A, Schedule 8.3 | 4 Requirements for grid and grid interface … (4) Each asset owner must ensure that it provides protection systems for its assets that are connected to, or form part of, the grid. Each asset owner must also ensure that as a minimum requirement― 13 Asset owner a.c. protection systems Each asset owner must― (f) confirm at least once every 4 years that its protection settings are identified, co-ordinated, applied correctly and meet the requirements of the AOPOs and the technical codes; and | In this case the participant breached, and continues to breach, clause 4(4)(a)(i) of Technical Code A of Schedule 8.3 of the Code due to its failure to ensure that its asset protection systems’ settings were applied, and continue to be applied, so as to electrically disconnect faulted assets in minimum practical time and with minimum disruption to the grid and other assets. The participants protection systems were compliant when commissioned, however changes in conditions/protection settings resulted in co-ordination issues. The participant identified 14 non-compliant protection system settings across four sites during a review of the protection settings of its generation assets. It has put in place a plan which is aligned with planned maintenance outages to achieve compliance by December 2020 and implemented a business process to properly monitor protection settings in the future. This is an ongoing breach of the asset owner performance obligation requirements under Part 8 of the Code The Committee decided: (a) to take no further action on the breaches under regulation 11(1)(c) (b) to issue a strong warning letter. The reasons for the Committee's decisions were: (i) improvements have been made to processes to record, monitor, and apply correct protection settings and co-ordinate these activities with the system operator and the grid owner (ii) Compliance will monitor progress to achieving compliance with the requirements of clause 4(4)(a)(i) (ii) it expects participants to have best practice processes in place to monitor compliance with Part 8 obligations.
13.58A(1)(e)(i), 13.58A(2)(d)(i), clause 7(g)(i) of Schedue 13.3 | 13.58A Inputs for price-responsive schedule and non-response schedule … (2) The system operator must prepare a non-response schedule using the following inputs: … (d) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 referring to— (i) the AC transmission system configuration, capacity, and losses; and ... | The system operator breached clause 13.58A(1)(e)(i) and clause 13.58A(2)(d)(i) and 13.69A and clause 7(g)(i) of Schedule 7(g)(i) when it did not accurately model a change to the offered status and associated MW limits of the Omaru-Waitaki special protection scheme (SPS). At 6.00 am on 3 May 2019 the system operator noticed the discrepancy and corrected it at 6:10 am for the new outage period using overrides. This meant that between 7:30 pm on 2 May 2019 to 6:10 am on 3 May 2019 the market system did not have the MW limits for the SPS modelled correctly in real-time operation. The system operator identified on 3 May 2019 that the market modelling of the SPS used the enabled limits when the scheme’s disabled limits should have been used. This prompted the system operator to enter manual overrides in the system until the modelling of the SPS could be accurately determined. The application of these manual overrides for normal operation ended the issue that also appeared in the schedules. The system operator applied the correct overrides at 10:00 am on 3 May 2019. The misunderstanding of the nature of the change to default of ‘disabled’ from default ‘enabled’ confused the system operator’s technical specialist because the system operator failed to ensure that technical staff clearly understood all aspects of the introduced changes. The Committee decided to take no further action on the breaches under regulation 11(1)(c). The reasons for the Committee's decision were: (i) the error was the result of a human error (ii) the breaches caused no impact because none of the MW limits bound (iii) steps have been taken to prevent recurrence.
13.58A(1)(e)(i) and 13.58A(2)(d)(i) | 13.58A Inputs for price-responsive schedule and non-response schedule … (2) The system operator must prepare a non-response schedule using the following inputs: … (d) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 referring to— (i) the AC transmission system configuration, capacity, and losses; and ... | The system operator breached clause 13.58A(1)(e)(i) and clause 13.58A(2)(d)(i) when some forecast schedules showed a circuit breaker (MPE_CB_252) as modelled in service when it should have been modelled out of service. On 7 May 2019 the system operator identified the incorrect modelling and created an override and attached it to the original outage block to resolve the issue in the forward-looking schedules. The system operator subsequently analysed the outage logic in the database and confirmed a logic issue which could cause outage start times to overlap when the start time is moved earlier. In this instance, the outage start time was moved from 7 May to 6 May 2019. In June 2019, the system operator deployed a software fix. The Committee decided to take no further action on the breaches under regulation 11(1)(c) of the Regulations. The reason for the Commitee's decision was: (i) There was no market impact because the system operator applied manual overrides to manage the issue (ii) The system operator has issued a software update.
clauses 10.12, 10.31B, 10.33A and clause 3 of Schedule 11.1 | 10.12 Interference with metering installation A participant must not directly or indirectly interfere with a metering installation for which it is not the metering equipment provider, unless— (a) it is instructed or permitted to do so by the metering equipment provider responsible for the metering installation; or (b) the participant has an arrangement with the trader responsible for the metering installation as the gaining metering equipment provider who will be responsible for the metering installation. | The distributor was alleged to have breached a number of clauses when it reconfigured an 11 kV network. The basis of the alleged breaches was that the participant created and electrically connected ICPs on its own initiative when it was not permitted to do so. However, the distributor created the ICPs at the request of a trader and therefore did not interfere with a metering installation. That same trader also electrically connected the ICPs, not the participant as alleged. The distributor did not breach: a) clause 10.31B because it did not electrically connect the ICPs. The trader engaged electrical inspectors to electrically connect the ICPs. Clause 10.31B therefore does not apply in this case. b) clause 10.33A because it did not electrically connect the ICPs. The trader responsible for the ICP, engaged electrical inspectors to electrically connect the ICPs. c) clause 3 of Schedule 11.1 - this is because the ICP was created before 7 October 2002 and therefore clause 3 of Schedule 11.1 does not apply. This has been identified as an apparent gap in the Code for which the market adminisrator has initiated a Code amendment proposal. The Committee decided to take further action on the alleged breaches under regulation 11(1)(b) of the Regulations. The reason for the Committee’s decision was the failure to establish a primae facie case for the breaches.