## Sheet1
Code/ Provision | Details of Provisions | Explanation
clause 13.82(2) | 13.82 Dispatch instructions to be complied with (1) This clause applies to— (a) a generator; and … (2) Each participant to which this clause applies must comply with a dispatch instruction properly issued by the system operator under clause 13.72 unless, - | In this case the participant failed to comply with dispatch instructions. It began generating a unit at 12 MW for part of trading period 14 when it did not have a dispatch instruction. In trading period 15 the unit was generating below its dispatched level on average by 57 MW. In trading 16 the unit was generating above its dispatched level on average by 66 MW. The participant operator misread the offer viewer and commenced generating too early. When the unit began generating, its control system determined and locked in a warm start profile compared to its offer and dispatch based on a hot start profile. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) the participant promptly informed the system operator and was able to use station dispatch to partly compensate for the dispatch discrepancy preventing any market impact ii) the participant has identified and completed a number of actions to prevent recurrence.
clause 13.9A | 13.9A Offer not to exceed capability (1) The total MW specified in each offer submitted by a generator must, in relation to the generating plant that is the subject of the offer, not exceed the total MW that the generator expects to be capable of generating at the relevant point of connection to the grid for the relevant trading period. | Due to a human error in not following internal processes following a shift change, the participant had incorrect offers in the market. The participant realised the error only in real time when the station concerned was dispatched in accordance with the incorrect offer. The MW discrepancy in the offer was too small to have any impact. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) there was no impact ii) steps have been taken to prevent recurrence.
clause 11.15AB | 11.15AB Switch saving protection (1) This clause applies if a trader (the "protected trader") has switch saving protection. (2) If the protected trader enters into an arrangement with a customer of another trader (the "losing trader") to commence trading electricity with the customer, the losing trader must comply with subclause (4). (3) If a trader enters into an arrangement with a customer of a protected trader to commence trading electricity with the customer, the protected trader must comply with subclause (4). (4) A losing trader referred to in subclause (2) …. must not, by any means, initiate contact with the customer to attempt to persuade the customer to terminate the arrangement referred to in subclause (2) or subclause (3) (as the case may be) during the period specified in subclause (5), including by— (a) making a counter-offer to the customer; or (b) offering an enticement to the customer. (5) The period starts on the day on which the trader receives notice of the switch request under clause 22(a) of Schedule 11.3, and ends on the event date for the switch. | This participant breached clause 11.15AB when it contacted a customer who is a save-protected retailer. The breach caused no impact as the participants attempt was unsuccesful in pursuading the customer to remain with it. The participant has not previously breached this provision. The Committee decided: (a) to take no further action on the breach under regulation 11(1)(c) (b) to issue a warning letter. The reasons for the Committee's decisions were: i) the participant acknowledged and apologised for the breach ii) has taken steps to prevent recurrence iii) a warning letter was appropriate as save protection is important for enabling competition.
clause 8.21(2) | 8.21 Excluded generating stations (1) For the purposes ... (2) Whether likely to be an excluded generation station or not, a generator who is planning to connect to the grid or a local network a generating unit with rated net maximum capacity equal to or greater than 1 MW must provide the system operator with written advice of its intention to connect together with other information relating to that generating unit in accordance with clause 8.25(4). | In this case, the participant failed to advise the system operator of its intention to connect a new generating unit to a distribution network. The participant has updated its processes to include early engagement with the system operator to provide the required information. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) there was no impact ii) steps have been taken to prevent recurrence.
clause 13.58A(1)(e)(i) and (2)(d)(i) and clause 25 of the Policy Statement | 13.58A Inputs for price-responsive schedule and non-response schedule (1) The system operator must prepare a price-responsive schedule using the following inputs: … (e) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 about— (i) the AC transmission system configuration, capacity, and losses; and … (2) The system operator must prepare a non-response schedule using the following inputs: ... (d) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 referring to— (i) the AC transmission system configuration, capacity, and losses; and clause 25 of the Policy Statement. | The system operator breached clauses13.58A(1)(e)(i) and (2)(d)(i) of the Code 2010 by not using the grid owner’s offer for the status of special protection schemes (SPS) in forward schedules and clause 25 of the Policy Statement incorporated by reference into the Code by clause 8.10 by not building constraints to manage the unavailability of the SPSs. These breaches are a further consequence of the implementation of the system operator’s SPS automation project that caused other breaches that are currently the subject of formal investigation. The investigation is considering the wider aspects of such system changes. Therefore, there was no need to investigate this case or issue a warning letter. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) the breaches caused no apparent impact ii) a software fix to prevent recurrence of this specific error has been implemented by the systerm operator.
clause 13.58A(1)(e)(i) and (2)(d)(i) | 13.58A Inputs for price-responsive schedule and non-response schedule (1) The system operator must prepare a price-responsive schedule using the following inputs: … (e) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 about— (i) the AC transmission system configuration, capacity, and losses; and … (2) The system operator must prepare a non-response schedule using the following inputs: ... (d) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 referring to— (i) the AC transmission system configuration, capacity, and losses; ... | The system operator breached clause 13.58A(1)(e)(i) and (2)(d)(i) of the Code by not using the grid owner’s offer for the status of two transformers. One was modelled in service when it was out of service, and the other was not modelled at a new lower rating when preparing price-responsive shedule and non-response schedule. The breaches were caused by human error in a re-rating change, involving multiple tasks, that would normally be undertaken well ahead of real-time. The system operator was required to re-rate assets, on advice from the grid owner, in real-time which is a very infrequent requirement. The breaches were of short duration. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) it was unusual for re-ratings to be made in real time ii) the breaches were of short duration, caused no operational or market impact, and the system operator has taken steps to prevent recurrence.
clause 13.88(3) and clause 13.3(6) of Schedule 13.3 | 13.88 Preparation of schedule of real time prices (1) The purpose of ... (3) In preparing each schedule of real time prices, the system operator must use the methodology in Schedule 13.3. 6 Schedule of real time prices For a schedule of real time prices, the schedule must use— (a) the final information for each real time pricing period provided to the system operator under subpart 1 of Part 13, including— (i) offers revised under clause 13.19; and (ii) nominated dispatch bids revised under clause 13.19A; and (iii) reserve offers revised under clause 13.47; and (iv) information updated under clause 13.34(1); and (b) existing generation configuration specifying the instantaneous MW injection at each grid injection point at the beginning of the relevant real time pricing period for generating plant or generating units that were the subject of offers for the relevant trading period, or, if no such information is available, a reasonable estimate of such data; and | The system operator breached clause 13.88(3) and clause 13.3(6) of Scedule 13.3 when it did not use a reasonable estimate of instantaneous injection for Tararua Wind Farms in preparing the real time pricing (RTP) schedules. The breaches occurred after the system operator returned the market system from an outage to implement changes for the wind offer arrangements project. The system operator’s obligation to produce RTP schedules is on a reasonable endeavours basis. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) the system operator promptly corrected the error upon discovery ii) there was no impact on final prices iii) steps have been taken to update procedures to prevent recurrence.
clause13.69 and clause 12(2) of Schedule 13.3 | 13.69A System operator to prepare dispatch schedule The system operator must prepare a dispatch schedule in accordance with the methodology set out in Schedule 13.3. 12 Constraints relating to instantaneous reserve (1) The modelling system ... (2) In making the calculation in subclause (1), the modelling system must identify the risk (in MW) associated with the largest “Contingent Event” as the largest of— (a) the transfer on a single pole of the HVDC link; or (b) the generation from a single generating unit (whether or not this is a generator’s generating unit); or (c) any other risk specified in the dispatch objective. … | The system operator, breached clause 13.69A of the Code for not following the methodology under clause 12(2) of Schedule 13.3. Following successful commissioning testing, the system operator failed to remove Whareroa generation as the contingent event risk. The breaches were the result of the system operator’s staff not following standard process. The error caused an over-procurement of reserves for 40 trading periods. The Committee decided: (a) to take no further action on the breach under regulation 11(1)(c) (b) to request Compliance issue a warning letter. The reasons for the Committee's decisions were: i) the market impact was minor and there was no security impact iii) the system operator has taken steps to prevent recurrence.
clause 13.58A(1)(e)(i) and (2)(d)(i) | 13.58A Inputs for price-responsive schedule and non-response schedule (1) The system operator must prepare a price-responsive schedule using the following inputs: … (e) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 about— (i) the AC transmission system configuration, capacity, and losses; and ... (2) The system operator must prepare a non-response schedule using the following inputs: ... (d) information provided to the system operator by a grid owner under clauses 13.29 to 13.34 referring to— (i) the AC transmission system configuration, capacity, and losses; ... | The system operator breached clause 13.58A(1)(e)(i) and clause 13.58A(2)(d)(i) when it failed to use the grid owner’s information about an outage in the forward schedules. The system operator’s check tools immediately identified the error, but the error affected two forecast schedules. The breaches were a result of human error. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) there was no impact ii) steps have been taken to prevent recurrence.
clause 13.5 | 13.5 Bids and offers must be lawful A purchaser, generator or ancillary service agent must not make or maintain a bid, offer or reserve offer if the purchaser or generator or ancillary service agent knows or ought reasonably to know that acting in accordance with the bid, offer or reserve offer would contravene any law. | On 12 September 2019, the participant breached clause 13.5 because its offer structure was not in accordance with its resource consent conditions made under the Resource Management Act 1991, and therefore not lawful. Its resource consent does not allow it to have a difference between offer quantities of more than 6.5 MW between trading periods. The Committee decided to take no further action on the breach under regulation 11(1)(c). The reasons for the Committee’s decision were: i) there was no impact ii) the participant has taken steps to prevent recurrence.